## Expansion facilities
aquatherm Pipe Systems Pty Limited
Only the green cells can be edited
Calculation of expansion (ΔL), bending side (Lbs)
and minimum width of expansion loop (Amin)
α [mm/ mK]
linear expansion Copper pipe | [5 empty] | 0.0177 | mm / mK
linear expansion aquatherm green pipe MF and aquatherm blue pipe MF | [5 empty] | 0.035 | mm / mK
Δ L = α x pipe length x Δ T
pipe length | 30 | meter | Δ T = | 50 | °C / K
Δ L = | 26.55 | mm with Copper pipe
Δ L = | 52.5 | mm with aquatherm green pipe MF and aquatherm blue pipe MF
Refer to page 70 aquatherm green pipe brochure NZ10101
Edition: 03/2015
Refer to page 54 Plumbers Handbook (ICAA)
Edition No.9 March 2016
Calculational determination of the bending side length (Lbs/LOffset) | [5 empty] | Lbs = K x √ (d x ΔL)
For straight pipe lengths not longer than 40 metres (< 40 mtr.). | [5 empty] | LOffset = C x √ (d x ΔL)
C= Material specific constant copper pipe = |  |  | 61.2 |  | OD copper pipe = |  | DN40 | 38.1 | mm
K= Material specific constant aquatherm pipe = |  |  | 15 |  | Ø (OD) aquatherm pipe = |  | 50 | mm
LOffset = | 1.9465 | metre for Copper pipe
Lbs = | 0.76852 | metre for aquatherm green pipe MF and aquatherm blue pipe MF
Refer to page 73 - 76 aquatherm pipesystems
brochure NZ10101
Edition: 03/2015
Lbs = K x √ (d x ΔL)
Refer to page 64-67 Plumbing Connection Magazine
Winter 2017 Edition
LOffset = C x √ (d x ΔL)
Calculational determination of the bending side length (Lbs/LOffset) | [5 empty] | Lbs = K x √ (d x ΔL/2)
For straight pipe lengths longer than 40 metres (> 40 mtr.). | [5 empty] | LOffset = C x √ (d x ΔL/2)
C= Material specific constant copper pipe = |  |  | 61.2 |  | OD copper pipe = |  | DN40 | 38.1 | mm
K= Material specific constant aquatherm pipe = |  |  | 15 |  | Ø (OD) aquatherm pipe = |  | 50 | mm
LOffset = | 1.3764 | metre for Copper pipe
Lbs = | 0.54343 | metre for aquatherm green pipe MF and aquatherm blue pipe MF
Calculational determination of min. width of the expansion loop (Amin) | [5 empty] | Amin = 2 x Δ L + SD |  | SD [mm] = 150mm
Amin = 1/2 x Loffset
Amin = | 0.68818 | metre for Copper pipe
Amin = | 0.2025 | metre for aquatherm green pipe MF and aquatherm blue pipe MF
Amin should be at least 210mm (0.21 metre) for aquatherm PP-R pipes
Refer to page 73 - 76 aquatherm pipesystems
brochure NZ10101
Edition: 03/2015
Amin = 2 x Δ L + SD
Refer to page 64-67 Plumbing Connection Magazine
Winter 2017 Edition
Amin = 1/2 x Loffset
To calculate the linear expansion forces, please ask for the Aquatherm linear expansion forces calculation (Excel).
The user of this program ultimately remains responsible for the interpretation of the data.
Aquatherm Pipe Systems Pty Ltd can in no way be held liable for the incorrect interpretation of these data.
aquatherm Pipe Systems
The Professional Plumbers Alternative
www.aquatherm.com.au
aquatherm@aquatherm.com.au

## Blad2
| aquatherm green pipe SDR7,4 MF |  |  |  | Copper tube AS 1432 : 2004 type B
Flange | OD | Wall thickness | Dimensions | Bore | OD | Wall thickness | Dimensions | Bore
[DN] | mm | mm | mm | mm | mm | mm | mm | mm
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9
DN15 | 20 | 2.8 | 20x2,8 | 14.4 | 12.7 | 0.91 | 12.7x0.9 | 10.88
DN20 | 25 | 3.5 | 25x3,5 | 18 | 19.05 | 1.02 | 19.1x1.0 | 17.01
DN25 | 32 | 4.4 | 32x4,4 | 23.2 | 25.4 | 1.22 | 25.4x1.2 | 22.96
DN32 | 40 | 5.5 | 40x5,5 | 29 | 31.75 | 1.22 | 31.8x1.2 | 29.31
DN40 | 50 | 6.9 | 50x6,9 | 36.2 | 38.1 | 1.22 | 38.1x1.2 | 35.66
DN50 | 63 | 8.6 | 63x8,6 | 45.8 | 50.8 | 1.22 | 50.8x1.2 | 48.36
DN65 | 75 | 10.3 | 75x10,3 | 54.4 | 63.5 | 1.22 | 63.5x1.2 | 61.06
DN80 | 90 | 12.3 | 90x12,3 | 65.4 | 76.2 | 1.63 | 76.2x1.6 | 72.94
DN90 |  |  |  |  | 88.9 | 1.63 | 88.9x1.6 | 85.64
DN100 | 110 | 15.1 | 110x15,1 | 79.8 | 101.6 | 1.63 | 101.6x1.6 | 98.34
DN125 | 125 | 17.1 | 125x17,1 | 90.8 | 127 | 1.63 | 127.0x1.6 | 123.74
DN150 | 160 | 21.9 | 160x21,9 | 116.2 | 152.4 | 2.03 | 152.4x2.0 | 148.34
DN200 | 200 | 27.4 | 200x27,4 | 145.2 | 203.2 | 2.03 | 203.2x2.0 | 199.14
DN250 | 250 | 34.2 | 250x34,2 | 181.6
Note on F2: Source: Plumbers Handbook No.9 page 14. ICAA