## SDR7.4 & SDR11
aquatherm Pipe Systems Pty Limited
Ecological pipe systems: just say yes to a better world!
m³/h | l/h | l/min | l/s
2 | 2000 | 33.3333 | 0.55556 | aquatherm blue pipe SDR7.4 / SDR11 MF vs Seamless Carbon Steel pipe
10 | 10000 | 166.6667 | 2.7778 | (velocity [m/s] => flow rate [l/s or l/h])
99.96 | 99960 | 1666 | 27.7667 |  |  |  |  | Only the green cells can be edited
999.612 | 999612 | 16660.2 | 277.67
| Steel pipe |  |  | aquatherm blue pipe MF |  |  |  | Steel pipe | aquatherm blue pipe MF | Steel pipe | aquatherm blue pipe MF
Flange | DIN 2448 |  |  | SDR 7.4/SDR11 |  |  | velocity | DIN 2448 | SDR 7.4/SDR11 | DIN 2448 | SDR 7.4/SDR11
DN | OD | wall | bore | ø | wall | bore | m/s | l/s | l/s | l/h | l/h
15 | 21.3 | 2 | 17.3 | 20 | 2.8 | 14.4 | 1 | 0.23505 | 0.16286 | 846.1976 | 586.2793
20 | 26.9 | 2.3 | 22.3 | 25 | 3.5 | 18 | 3 | 1.1717 | 0.76338 | 4218.0386 | 2748.1842
25 | 33.7 | 2.6 | 28.5 | 32 | 2.9 | 26.2 | 1.5 | 0.95688 | 0.80867 | 3444.7726 | 2911.2092
32 | 42.4 | 2.6 | 37.2 | 40 | 3.7 | 32.6 | 1 | 1.0868 | 0.83467 | 3912.6 | 3004.7945
40 | 48.3 | 2.6 | 43.1 | 50 | 4.6 | 40.8 | 1 | 1.4589 | 1.3074 | 5252.1136 | 4706.5199
50 | 60.3 | 2.9 | 54.5 | 63 | 5.8 | 51.4 | 3 | 6.9983 | 6.2248 | 25193.809 | 22409.2368
65 | 76.1 | 2.9 | 70.3 | 75 | 6.9 | 61.2 | 1 | 3.8814 | 2.9416 | 13973.0182 | 10589.6698
80 | 88.9 | 3.2 | 82.5 | 90 | 8.2 | 73.6 | 1 | 5.3455 | 4.2543 | 19243.6509 | 15315.6419
100 | 114.3 | 3.6 | 107.1 | 110 | 10 | 90 | 1 | 9.0086 | 6.3615 | 32430.8637 | 22901.535
125 | 127 | 4 | 119 | 125 | 11.4 | 102.2 | 1 | 11.1217 | 8.2031 | 40038.1034 | 29531.2184
150 | 168.3 | 4.5 | 159.3 | 160 | 14.6 | 130.8 | 2.5 | 49.8252 | 33.5917 | 179370.5475 | 120930.2833
200 | 219.1 | 5.9 | 207.3 | 200 | 18.2 | 163.6 | 1 | 33.7501 | 21.0205 | 121500.5315 | 75673.9097
250 | 273 | 6.3 | 260.4 | 250 | 22.7 | 204.6 | 1 | 53.2548 | 32.8767 | 191717.4012 | 118356.1507
300 | 323.9 | 7.1 | 309.7 | 315 | 28.6 | 257.8 | 1 | 75.3285 | 52.1967 | 271182.7024 | 187908.056
350 | 355.6 | 8 | 339.6 | 355 | 32.2 | 290.6 | 1 | 90.5759 | 66.3236 | 326073.0732 | 238765.0706
400 | 406.4 | 8.8 | 388.8 | 400 | 36.3 | 327.4 | 1 | 118.7216 | 84.1849 | 427397.6068 | 303065.7953
450 | 457 | 10 | 437 | 450 | 40.9 | 368.2 | 1 | 149.9823 | 106.4743 | 539936.2022 | 383307.3454
m³/h | l/h | l/min | l/s
0.72 | 720 | 12 | 0.2 | aquatherm blue pipe SDR7.4 / SDR11 MF vs Seamless Carbon Steel pipe
0.72 | 720 | 12 | 0.2 | (flow rate [l/s] => velocity [m/s])
0.72 | 720 | 12 | 0.2 |  |  |  | Only the green cells can be edited
0.72 | 720 | 12 | 0.2
| Steel pipe |  |  | aquatherm blue pipe MF |  |  | Steel pipe | aquatherm blue pipe MF | Steel pipe | aquatherm blue pipe MF
Flange | DIN 2448 |  |  | SDR 7.4/SDR11 |  |  | DIN 2448 | SDR 7.4/SDR11 | DIN 2448 | SDR 7.4/SDR11
DN | OD | wall | bore | ø | wall | bore | l/s | l/s | m/s | m/s
15 | 21.3 | 2 | 17.3 | 20 | 2.8 | 14.4 | 0 | 0 | 0 | 0
20 | 26.9 | 2.3 | 22.3 | 25 | 3.5 | 18 | 0 | 0 | 0 | 0
25 | 33.7 | 2.6 | 28.5 | 32 | 2.9 | 26.2 | 0 | 0 | 0 | 0
32 | 42.4 | 2.6 | 37.2 | 40 | 3.7 | 32.6 | 0 | 0 | 0 | 0
40 | 48.3 | 2.6 | 43.1 | 50 | 4.6 | 40.8 | 0 | 0 | 0 | 0
50 | 60.3 | 2.9 | 54.5 | 63 | 5.8 | 51.4 | 0 | 0 | 0 | 0
65 | 76.1 | 2.9 | 70.3 | 75 | 6.9 | 61.2 | 0 | 0 | 0 | 0
80 | 88.9 | 3.2 | 82.5 | 90 | 8.2 | 73.6 | 0 | 0 | 0 | 0
100 | 114.3 | 3.6 | 107.1 | 110 | 10 | 90 | 0 | 0 | 0 | 0
125 | 127 | 4 | 119 | 125 | 11.4 | 102.2 | 0 | 0 | 0 | 0
150 | 168.3 | 4.5 | 159.3 | 160 | 14.6 | 130.8 | 0 | 0 | 0 | 0
200 | 219.1 | 5.9 | 207.3 | 200 | 18.2 | 163.6 | 0 | 0 | 0 | 0
250 | 273 | 6.3 | 260.4 | 250 | 22.7 | 204.6 | 0 | 0 | 0 | 0
300 | 323.9 | 7.1 | 309.7 | 315 | 28.6 | 257.8 | 0 | 0 | 0 | 0
350 | 355.6 | 8 | 339.6 | 355 | 32.2 | 290.6 | 0 | 0 | 0 | 0
400 | 406.4 | 8.8 | 388.8 | 400 | 36.3 | 327.4 | 0 | 0 | 0 | 0
450 | 457 | 10 | 437 | 450 | 40.9 | 368.2 | 0 | 0 | 0 | 0
The user of this program ultimately remains responsible for the interpretation of the data.
Aquatherm Pipe Systems Pty Ltd can in no way be held liable for the incorrect interpretation of these data.
aquatherm Pipe Systems
The Professional Plumbers Alternative
www.aquatherm.com.au
aquatherm@aquatherm.com.au
Note on I14: Recommended velocities: < 3.0 m/s (transport pipes) < 2.0 m/s (riser pipes) < 1.5 m/s (floor pipes) < 1.0 m/s (unit connections)
Note on K43: Recommended velocities: < 3.0 m/s (transport pipes) < 2.0 m/s (riser pipes) < 1.5 m/s (floor pipes) < 1.0 m/s (unit connections)
Note on L43: Recommended velocities: < 3.0 m/s (transport pipes) < 2.0 m/s (riser pipes) < 1.5 m/s (floor pipes) < 1.0 m/s (unit connections)

## SDR17.6
aquatherm Pipe Systems Pty Limited
Ecological pipe systems: just say yes to a better world!
m³/h | l/h | l/min | l/s
0.72 | 720 | 12 | 0.2 | aquatherm blue pipe SDR17.6 MF vs Seamless Carbon Steel pipe
0.72 | 720 | 12 | 0.2 | (velocity [m/s] => flow rate [l/s or l/h])
0.72 | 720 | 12 | 0.2 |  |  |  |  | Only the green cells can be edited
0.72 | 720 | 12 | 0.2
| Steel pipe |  |  | aquatherm blue pipe MF |  |  |  | Steel pipe | aquatherm blue pipe MF | Steel pipe | aquatherm blue pipe MF
Flange | DIN 2448 |  |  | SDR 17.6 |  |  | velocity | DIN 2448 | SDR 17.6 | DIN 2448 | SDR 17.6
DN | OD | wall | bore | ø | wall | bore | m/s | l/s | l/s | l/h | l/h
125 | 127 | 4 | 119 | 125 | 7.1 | 110.8 | 1 | 11.1217 | 9.6418 | 40038.1034 | 34710.3581
150 | 168.3 | 4.5 | 159.3 | 160 | 9.1 | 141.8 | 1 | 19.9301 | 15.7917 | 71748.219 | 56850.205
200 | 219.1 | 5.9 | 207.3 | 200 | 11.4 | 177.2 | 1.5 | 50.6252 | 36.991 | 182250.7972 | 133167.5064
250 | 273 | 6.3 | 260.4 | 250 | 14.2 | 221.6 | 3 | 159.7645 | 115.7012 | 575152.2035 | 416524.2972
300 | 323.9 | 7.1 | 309.7 | 315 | 17.9 | 279.2 | 1 | 75.3285 | 61.2221 | 271182.7024 | 220399.3967
350 | 355.6 | 8 | 339.6 | 355 | 20.1 | 314.8 | 1 | 90.5759 | 77.8299 | 326073.0732 | 280187.6707
400 | 406.4 | 8.8 | 388.8 | 400 | 22.7 | 354.6 | 1 | 118.7216 | 98.754 | 427397.6068 | 355514.2687
450 | 457 | 10 | 437 | 450 | 25.5 | 399 | 1 | 149.9823 | 125.0325 | 539936.2022 | 450116.9474
500 | 508 | 11 | 486 | 500 | 28.4 | 443.2 | 1 | 185.5024 | 154.2683 | 667808.7606 | 555365.7297
550 | 559 | 12.5 | 534 | 560 | 31.7 | 496.6 | 1 | 223.9544 | 193.6826 | 806235.8166 | 697257.1942
600 | 610 | 12.5 | 585 | 630 | 35.7 | 558.6 | 1 | 268.775 | 245.0637 | 967589.8538 | 882229.2168
m³/h | l/h | l/min | l/s
0.72 | 720 | 12 | 0.2 | aquatherm blue pipe SDR17.6 MF vs Seamless Carbon Steel pipe
0.72 | 720 | 12 | 0.2 | (flow rate [l/s] => velocity [m/s])
0.72 | 720 | 12 | 0.2 |  |  |  | Only the green cells can be edited
0.72 | 720 | 12 | 0.2
| Steel pipe |  |  | aquatherm blue pipe MF |  |  | Steel pipe | aquatherm blue pipe MF | Steel pipe | aquatherm blue pipe MF
Flange | DIN 2448 |  |  | SDR 17.6 |  |  | DIN 2448 | SDR 17.6 | DIN 2448 | SDR 17.6
DN | OD | wall | bore | ø | wall | bore | l/s | l/s | m/s | m/s
125 | 127 | 4 | 119 | 125 | 7.1 | 110.8 | 0 | 0 | 0 | 0
150 | 168.3 | 4.5 | 159.3 | 160 | 9.1 | 141.8 | 0 | 0 | 0 | 0
200 | 219.1 | 5.9 | 207.3 | 200 | 11.4 | 177.2 | 0 | 0 | 0 | 0
250 | 273 | 6.3 | 260.4 | 250 | 14.2 | 221.6 | 0 | 0 | 0 | 0
300 | 323.9 | 7.1 | 309.7 | 315 | 17.9 | 279.2 | 0 | 0 | 0 | 0
350 | 355.6 | 8 | 339.6 | 355 | 20.1 | 314.8 | 0 | 0 | 0 | 0
400 | 406.4 | 8.8 | 388.8 | 400 | 22.7 | 354.6 | 0 | 0 | 0 | 0
450 | 457 | 10 | 437 | 450 | 25.5 | 399 | 0 | 0 | 0 | 0
500 | 508 | 11 | 486 | 500 | 28.4 | 443.2 | 0 | 0 | 0 | 0
550 | 559 | 12.5 | 534 | 560 | 31.7 | 496.6 | 0 | 0 | 0 | 0
600 | 610 | 12.5 | 585 | 630 | 35.7 | 558.6 | 0 | 0 | 0 | 0
The user of this program ultimately remains responsible for the interpretation of the data.
Aquatherm Pipe Systems Pty Ltd can in no way be held liable for the incorrect interpretation of these data.
aquatherm Pipe Systems
The Professional Plumbers Alternative
www.aquatherm.com.au
aquatherm@aquatherm.com.au
Note on I14: Recommended velocities: < 3.0 m/s (transport pipes) < 2.0 m/s (riser pipes) < 1.5 m/s (floor pipes) < 1.0 m/s (unit connections)
Note on K37: Recommended velocities: < 3.0 m/s (transport pipes) < 2.0 m/s (riser pipes) < 1.5 m/s (floor pipes) < 1.0 m/s (unit connections)
Note on L37: Recommended velocities: < 3.0 m/s (transport pipes) < 2.0 m/s (riser pipes) < 1.5 m/s (floor pipes) < 1.0 m/s (unit connections)

## Dimensions
| aquatherm blue pipe SDR7.4/SDR11 MF |  |  |  | Seamless Carbon Steel pipes DIN 2448
Flange | OD | Wall thickness | Dimensions | Bore | OD | Wall thickness | Dimensions | Bore
[DN] | mm | mm | mm | mm | mm | mm | mm | mm
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9
15 | 20 | 2.8 | 20x2,8 | 14.4 | 21.3 | 2 | 21,3 x 2,0 | 17.3
20 | 25 | 3.5 | 25x3,5 | 18 | 26.9 | 2.3 | 26,9 x 2,3 | 22.3
25 | 32 | 2.9 | 32x2,9 | 26.2 | 33.7 | 2.6 | 33,7 x 2,6 | 28.5
32 | 40 | 3.7 | 40x3,7 | 32.6 | 42.4 | 2.6 | 42,4 x 2,6 | 37.2
40 | 50 | 4.6 | 50x4,6 | 40.8 | 48.3 | 2.6 | 48,3 x 2,6 | 43.1
50 | 63 | 5.8 | 63x5,8 | 51.4 | 60.3 | 2.9 | 60,3 x 2,9 | 54.5
65 | 75 | 6.9 | 75x6,9 | 61.2 | 76.1 | 2.9 | 76,1 x 2,9 | 70.3
80 | 90 | 8.2 | 90x8,2 | 73.6 | 88.9 | 3.2 | 88,9 x 3,2 | 82.5
100 | 110 | 10 | 110x10 | 90 | 114.3 | 3.6 | 114,3 x 3,6 | 107.1
125 | 125 | 11.4 | 125x11,4 | 102.2 | 127 | 4 | 127,0 x 4,0 | 119
150 | 160 | 14.6 | 160x14,6 | 130.8 | 168.3 | 4.5 | 168,3 x 4,5 | 159.3
200 | 200 | 18.2 | 200x18,2 | 163.6 | 219.1 | 5.9 | 219,1 x 5,9 | 207.3
250 | 250 | 22.7 | 250x22,7 | 204.6 | 273 | 6.3 | 273,0 x 6,3 | 260.4
300 | 315 | 28.6 | 315x28,6 | 257.8 | 323.9 | 7.1 | 323,9 x 7,1 | 309.7
350 | 355 | 32.2 | 355x32,2 | 290.6 | 355.6 | 8 | 355,6 x 8,0 | 339.6
400 | 400 | 36.3 | 400x36,3 | 327.4 | 406.4 | 8.8 | 406,4 x 8,8 | 388.8
450 | 450 | 40.9 | 450x40,9 | 368.2 | 457 | 10 | 457,0 x 10,0 | 437
| aquatherm blue pipe SDR17.6 MF |  |  |  | Seamless Carbon Steel pipes DIN 2448
Flange | OD | Wall thickness | Dimensions | Bore | OD | Wall thickness | Dimensions | Bore
[DN] | mm | mm | mm | mm | mm | mm | mm | mm
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9
125 | 125 | 7.1 | 125x7,1 | 110.8 | 127 | 4 | 127,0 x 4,0 | 119
150 | 160 | 9.1 | 160x9,1 | 141.8 | 168.3 | 4.5 | 168,3 x 4,5 | 159.3
200 | 200 | 11.4 | 200x11,4 | 177.2 | 219.1 | 5.9 | 219,1 x 5,9 | 207.3
250 | 250 | 14.2 | 250x14,2 | 221.6 | 273 | 6.3 | 273,0 x 6,3 | 260.4
300 | 315 | 17.9 | 315x17,9 | 279.2 | 323.9 | 7.1 | 323,9 x 7,1 | 309.7
350 | 355 | 20.1 | 355x20,1 | 314.8 | 355.6 | 8 | 355,6 x 8,0 | 339.6
400 | 400 | 22.7 | 400x22,7 | 354.6 | 406.4 | 8.8 | 406,4 x 8,8 | 388.8
450 | 450 | 25.5 | 450x25,5 | 399 | 457 | 10 | 457,0 x 10,0 | 437
500 | 500 | 28.4 | 500x28,4 | 443.2 | 508 | 11 | 508,0 x 11,0 | 486
550 | 560 | 31.7 | 560x31,7 | 496.6 | 559 | 12.5 | 559,0 x 12,5 | 534
600 | 630 | 35.7 | 630x35,7 | 558.6 | 610 | 12.5 | 610,0 x 12,5 | 585