## Heat Exchange
aquatherm Pipe Systems Pty Limited
Ecological pipe systems: just say yes to a better world!
Heat exchange and water temperature
in combination with
aquatherm green pipe SDR7.4 MF, aquatherm blue pipe SDR7.4 MF / SDR11 MF and SDR17.6 MF,
Seamless Carbon Steel DIN 2448 and Copper AS 1432 : 2000 type B pipes
Only the green cells and column B "pipe length" can be edited
Calculations conditions:
1) Conveying water with a density of 1x 10³ kg/m³.
2) Water velocity of 1 m/s.
3) Specific heat capacity of water of 4187 J/kgK.
[6 empty] | 4) Thermal conductivity (λ) of fusiolen® PP-R = 0.15 W/mK. | [6 empty] | λ fusiolen® PP-R | 0.15 W/mK
[6 empty] | 5) Thermal conductivity (λ) of Carbon Steel = 50 W/mK. | [6 empty] | λ Steel | 50 W/mK
[6 empty] | 6) Thermal conductivity (λ) of Copper = 384 W/mK. | [6 empty] | λ Copper | 384 W/mK
7) To calculate the water end temperature, the total pipe length is differentiated in 1 meter lengths.
reason: the ΔT (T water - T ambient) doesn't run linear.
! Maximum pipe length to be filled in column "B" is 236 meter.
! Don't use any decimals with pipe length (for example: not 1.5).
For the exact air flow into the area, we can not record real terms, since we do not know the site conditions.
For the below calculations we use an avarage α Air value of 15 W/m²K (slight air flow around pipe).
If you want to use another value, you can change this in cell D36.
Ambient temperature |  | 23 | ⁰C |  | α Air | W/m²K
α Air |  | 15 | W/m²K |  | still air | 8 | [5 empty] | ⁰C | ⁰F | K | ⁰R
[5 empty] | fast moving air | 30 | [5 empty] | 20 | 68 | 293.16 | 527.67
Insulation Copper |  | 0 | mm |  | default | 15 | [5 empty] | 0 | 32 | 273.16 | 491.67
Insulation Steel |  | 0 | mm | [8 empty] | 16.84 | 62.312 | 290 | 521.982
Insulation PP-R |  | 0 | mm |  | Armaflex | 0.037 W/mK | [5 empty] | 60.1833 | 140.33 | 333.3433 | 600
λ Insulation |  | 0.025 | W/mK |  | Rockwool | 0.025 W/mK
[12 empty] | aquatherm green pipe |  | aquatherm blue pipe |  | aquatherm blue pipe |  | Seamless Steel |  | Copper
Pipe | Starting | aquatherm green pipe |  | aquatherm blue pipe |  | aquatherm blue pipe |  | Seamless Steel |  | Copper |  | SDR7.4 MF |  | SDR7.4 MF / SDR11 MF |  | SDR17.6 MF |  | DIN 2448 |  | AS 1432:2000 type B
length | Temperature | SDR7.4 MF |  | SDR7.4 MF / SDR11 MF |  | SDR17.6 MF |  | DIN 2448 |  | AS 1432:2000 type B |  | Heat exchange | End temperature | Heat exchange | End temperature | Heat exchange | End temperature | Heat exchange | End temperature | Heat exchange | End temperature
[m] | ⁰C | Dimension | dh | Dimension | dh | Dimension | dh | Dimension | dh | Dimension | dh | W | ⁰C | W | ⁰C | W | ⁰C | W | ⁰C | W | ⁰C
100 | 6 | 20x2.8 | 14.4 | 20x2.8 | 14.4 |  |  | 21.3x2.0 | 17.3 | 19.1x1.0 | 17.1 | 1129.1656 | 7.6559 | 1129.1656 | 7.6559 |  |  | 1594.0299 | 7.6196 | 1438.2811 | 7.4957
100 | 6 | 25x3.5 | 18 | 25x3.5 | 18 |  |  | 26.9x2.3 | 22.3 | 25.4x1.2 | 23 | 1346.9316 | 7.2642 | 1346.9316 | 7.2642 |  |  | 2037.3902 | 7.2459 | 1935.955 | 7.1129
100 | 6 | 32x4.4 | 23.2 | 32x2.9 | 26.2 |  |  | 33.7x2.6 | 28.5 | 31.8x1.2 | 29.4 | 1624.7649 | 6.918 | 1868.9738 | 6.828 |  |  | 2575.3281 | 6.9642 | 2443.4304 | 6.8596
100 | 6 | 40x5.5 | 29 | 40x3.7 | 32.6 |  |  | 42.4x2.6 | 37.2 | 38.1x1.2 | 35.7 | 1887.366 | 6.6824 | 2203.2497 | 6.6304 |  |  | 3266.6094 | 6.7178 | 2942.139 | 6.702
100 | 6 | 50x6.9 | 36.2 | 50x4.6 | 40.8 |  |  | 48.3x2.6 | 43.1 | 50.8x1.2 | 48.4 | 2158.9309 | 6.501 | 2587.3128 | 6.4726 |  |  | 3734.1904 | 6.6113 | 3946.2805 | 6.5123
100 | 6 | 63x8.6 | 45.8 | 63x5.8 | 51.4 |  |  | 60.3x2.9 | 54.5 | 63.5x1.2 | 61.1 | 2466.2733 | 6.3575 | 3010.6455 | 6.3465 |  |  | 4680.9645 | 6.4792 | 4949.6606 | 6.4032
100 | 6 | 75x10.3 | 54.4 | 75x6.8 | 61.4 |  |  | 76.1x2.9 | 70.3 | 76.2x1.6 | 73 | 2678.7791 | 6.2753 | 3370.2073 | 6.2718 |  |  | 5930.8262 | 6.3588 | 5950.3178 | 6.3395
100 | 6 | 90x12.3 | 65.4 | 90x8.2 | 73.6 |  |  | 88.9x3.2 | 82.5 | 88.9x1.6 | 85.7 | 2916.1833 | 6.2073 | 3725.315 | 6.2091 |  |  | 6938.2843 | 6.31 | 6953.3174 | 6.2879
100 | 6 | 110x15.1 | 79.8 | 110x10.0 | 90 |  |  | 114.3x3.6 | 107.1 | 101.6x1.6 | 98.4 | 3149.2125 | 6.1504 | 4133.9231 | 6.1552 |  |  | 8940.2018 | 6.237 | 7956.1367 | 6.2499
100 | 6 | 125x17.1 | 90.8 | 125x11.4 | 102.2 |  |  | 127.0x4.0 | 119 | 127.0x1.6 | 123.8 | 3305.7004 | 6.1219 | 4381.4867 | 6.1276 |  |  | 9939.4003 | 6.2134 | 9961.6076 | 6.1976
100 | 6 | 160x21.9 | 116.2 | 160x14.6 | 130.8 | 160x9.1 | 141.8 | 168.3x4.5 | 159.3 | 152.4x2.0 | 148.4 | 3572.4224 | 6.0805 | 4860.6656 | 6.0864 | 6445.5032 | 6.0975 | 13193.4688 | 6.1581 | 11965.1229 | 6.1652
100 | 6 | 200x27.4 | 145.2 | 200x18.2 | 163.6 | 200x11.4 | 177.2 | 219.1x5.9 | 207.3 | 203.2x2.0 | 199.2 | 3788.2284 | 6.0546 | 5283.3427 | 6.06 | 7178.8965 | 6.0695 | 17187.0505 | 6.1216 | 15975.3904 | 6.1224
0 | 6 | 250x34.2 | 181.6 | 250x22.7 | 204.6 | 250x14.2 | 221.6 | 273.0x6.3 | 260.4 |  |  | 0 | 6 | 0 | 6 | 0 | 6 | 0 | 6
0 | 6 | 315x42.6 | 229.8 | 315x28.6 | 257.8 | 315x17.9 | 279.2 | 323.9x7.1 | 309.7 |  |  | 0 | 6 | 0 | 6 | 0 | 6 | 0 | 6
0 | 6 | 355x48.0 | 259 | 355x32.2 | 290.6 | 355x20.1 | 314.8 | 355.6x8.0 | 339.6 |  |  | 0 | 6 | 0 | 6 | 0 | 6 | 0 | 6
0 | 6 |  |  | 400x36.3 | 327.6 | 400x22.7 | 354.6 | 406.4x8.8 | 388.8 |  |  |  |  | 0 | 6 | 0 | 6 | 0 | 6
0 | 6 |  |  | 450x40.9 | 368.2 | 450x25.5 | 399 | 457.0x10.0 | 437 |  |  |  |  | 0 | 6 | 0 | 6 | 0 | 6
0 | 6 |  |  |  |  | 500x28.4 | 443.2 | 508.0x11.0 | 486 | [6 empty] | 0 | 6 | 0 | 6
0 | 6 |  |  |  |  | 560x31.7 | 496.6 | 559.0x12.5 | 534 | [6 empty] | 0 | 6 | 0 | 6
0 | 6 |  |  |  |  | 630x35.7 | 558.6 | 610.0x12.5 | 585 | [6 empty] | 0 | 6 | 0 | 6
[12 empty] | 30023.9583 | Watt Total | 37901.2194 | Watt Total | 13624.3997 | Watt Total | 80017.7443 | Watt Total | 76417.6395 | Watt Total
The user of this program ultimately remains responsible for the interpretation of the data.
Aquatherm Pipe Systems Pty Ltd can in no way be held liable for the incorrect interpretation of these data.
aquatherm Pipe Systems
The Professional Plumbers Alternative
www.aquatherm.com.au
aquatherm@aquatherm.com.au
Note on B45: Max. 236 meter without decimals.

## Costs for Heat exchange
aquatherm Pipe Systems Pty Limited
Ecological pipe systems: just say yes to a better world!
Heat exchange and costs [$]
in combination with
aquatherm green pipe SDR7.4 MF, aquatherm blue pipe SDR7.4 MF / SDR11 MF and SDR17.6 MF,
Seamless Carbon Steel DIN 2448 and Copper AS 1432 : 2000 type B pipes
Only the green cells and column B "pipe length" can be edited
Ambient temperature |  | 23 | ⁰C |  | α Air | W/m²K
α Air |  | 15 | W/m²K |  | still air | 8 |  | Cost 1 kWh |  | 0.24 |  | ⁰C | ⁰F | K | ⁰R
[5 empty] | fast moving air | 30 | [5 empty] | 20 | 68 | 293.16 | 527.67
Insulation Copper |  | 0 | mm |  | default | 15 |  | Cost per annum [$] |  |  |  | 0 | 32 | 273.16 | 491.67
Insulation Steel |  | 0 | mm |  |  |  |  | ? kWh x $ 1 kWh x 24 hours x 365 days |  |  |  | 16.84 | 62.312 | 290 | 521.982
Insulation PP-R |  | 0 | mm |  | Armaflex | 0.037 W/mK | [5 empty] | 60.1833 | 140.33 | 333.3433 | 600
λ Insulation |  | 0.025 | W/mK |  | Rockwool | 0.025 W/mK
[12 empty] | aquatherm green pipe |  | aquatherm blue pipe |  | aquatherm blue pipe |  | Seamless Steel |  | Copper
Pipe | Starting | aquatherm green pipe |  | aquatherm blue pipe |  | aquatherm blue pipe |  | Seamless Steel |  | Copper |  | SDR7.4 MF |  | SDR7.4 MF / SDR11 MF |  | SDR17.6 MF |  | DIN 2448 |  | AS 1432:2000 type B
length | Temperature | SDR7.4 MF |  | SDR7.4 MF / SDR11 MF |  | SDR17.6 MF |  | DIN 2448 |  | AS 1432:2000 type B |  | Heat exchange | Cost per Annum | Heat exchange | Cost per Annum | Heat exchange | Cost per Annum | Heat exchange | Cost per Annum | Heat exchange | Cost per Annum
[m] | ⁰C | Dimension | dh | Dimension | dh | Dimension | dh | Dimension | dh | Dimension | dh | W | $ | W | $ | W | $ | W | $ | W | $
100 | 6 | 20x2.8 | 14.4 | 20x2.8 | 14.4 |  |  | 21.3x2.0 | 17.3 | 19.1x1.0 | 17.1 | 1129.1656 | 2373.9577 | 1129.1656 | 2373.9577 |  |  | 1594.0299 | 3351.2884 | 1438.2811 | 3023.8421
100 | 6 | 25x3.5 | 18 | 25x3.5 | 18 |  |  | 26.9x2.3 | 22.3 | 25.4x1.2 | 23 | 1346.9316 | 2831.7891 | 1346.9316 | 2831.7891 |  |  | 2037.3902 | 4283.4091 | 1935.955 | 4070.1518
100 | 6 | 32x4.4 | 23.2 | 32x2.9 | 26.2 |  |  | 33.7x2.6 | 28.5 | 31.8x1.2 | 29.4 | 1624.7649 | 3415.9057 | 1868.9738 | 3929.3305 |  |  | 2575.3281 | 5414.3697 | 2443.4304 | 5137.0681
100 | 6 | 40x5.5 | 29 | 40x3.7 | 32.6 |  |  | 42.4x2.6 | 37.2 | 38.1x1.2 | 35.7 | 1887.366 | 3967.9984 | 2203.2497 | 4632.1121 |  |  | 3266.6094 | 6867.7195 | 2942.139 | 6185.5529
100 | 6 | 50x6.9 | 36.2 | 50x4.6 | 40.8 |  |  | 48.3x2.6 | 43.1 | 50.8x1.2 | 48.4 | 2158.9309 | 4538.9362 | 2587.3128 | 5439.5665 |  |  | 3734.1904 | 7850.7618 | 3946.2805 | 8296.6602
100 | 6 | 63x8.6 | 45.8 | 63x5.8 | 51.4 |  |  | 60.3x2.9 | 54.5 | 63.5x1.2 | 61.1 | 2466.2733 | 5185.0929 | 3010.6455 | 6329.5812 |  |  | 4680.9645 | 9841.2598 | 4949.6606 | 10406.1664
100 | 6 | 75x10.3 | 54.4 | 75x6.8 | 61.4 |  |  | 76.1x2.9 | 70.3 | 76.2x1.6 | 73 | 2678.7791 | 5631.8652 | 3370.2073 | 7085.5239 |  |  | 5930.8262 | 12468.969 | 5950.3178 | 12509.9482
100 | 6 | 90x12.3 | 65.4 | 90x8.2 | 73.6 |  |  | 88.9x3.2 | 82.5 | 88.9x1.6 | 85.7 | 2916.1833 | 6130.9838 | 3725.315 | 7832.1022 |  |  | 6938.2843 | 14587.0489 | 6953.3174 | 14618.6546
100 | 6 | 110x15.1 | 79.8 | 110x10.0 | 90 |  |  | 114.3x3.6 | 107.1 | 101.6x1.6 | 98.4 | 3149.2125 | 6620.9043 | 4133.9231 | 8691.16 |  |  | 8940.2018 | 18795.8803 | 7956.1367 | 16726.9818
100 | 6 | 125x17.1 | 90.8 | 125x11.4 | 102.2 |  |  | 127.0x4.0 | 119 | 127.0x1.6 | 123.8 | 3305.7004 | 6949.9044 | 4381.4867 | 9211.6375 |  |  | 9939.4003 | 20896.5951 | 9961.6076 | 20943.2839
100 | 6 | 160x21.9 | 116.2 | 160x14.6 | 130.8 | 160x9.1 | 141.8 | 168.3x4.5 | 159.3 | 152.4x2.0 | 148.4 | 3572.4224 | 7510.6609 | 4860.6656 | 10219.0633 | 6445.5032 | 13551.0259 | 13193.4688 | 27737.9489 | 11965.1229 | 25155.4744
100 | 6 | 200x27.4 | 145.2 | 200x18.2 | 163.6 | 200x11.4 | 177.2 | 219.1x5.9 | 207.3 | 203.2x2.0 | 199.2 | 3788.2284 | 7964.3713 | 5283.3427 | 11107.6996 | 7178.8965 | 15092.912 | 17187.0505 | 36134.055 | 15975.3904 | 33586.6608
0 | 6 | 250x34.2 | 181.6 | 250x22.7 | 204.6 | 250x14.2 | 221.6 | 273.0x6.3 | 260.4 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 6 | 315x42.6 | 229.8 | 315x28.6 | 257.8 | 315x17.9 | 279.2 | 323.9x7.1 | 309.7 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 6 | 355x48.0 | 259 | 355x32.2 | 290.6 | 355x20.1 | 314.8 | 355.6x8.0 | 339.6 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 6 |  |  | 400x36.3 | 327.6 | 400x22.7 | 354.6 | 406.4x8.8 | 388.8 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0
0 | 6 |  |  | 450x40.9 | 368.2 | 450x25.5 | 399 | 457.0x10.0 | 437 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0
0 | 6 |  |  |  |  | 500x28.4 | 443.2 | 508.0x11.0 | 486 | [6 empty] | 0 | 0 | 0 | 0
0 | 6 |  |  |  |  | 560x31.7 | 496.6 | 559.0x12.5 | 534 | [6 empty] | 0 | 0 | 0 | 0
0 | 6 |  |  |  |  | 630x35.7 | 558.6 | 610.0x12.5 | 585 | [6 empty] | 0 | 0 | 0 | 0
[12 empty] | 30023.9583 | 63122.3698 | 37901.2194 | 79683.5237 | 13624.3997 | 28643.9379 | 80017.7443 | 168229.3057 | 76417.6395 | 160660.4452
The user of this program ultimately remains responsible for the interpretation of the data.
Aquatherm Pipe Systems Pty Ltd can in no way be held liable for the incorrect interpretation of these data.
aquatherm Pipe Systems
The Professional Plumbers Alternative
www.aquatherm.com.au
aquatherm@aquatherm.com.au
Note on B26: Max. 236 meter without decimals.

## 1°C
Heat exchange per meter at T
Ambient temperature |  | 23 | ⁰C |  | λ Fusiolen PP-R | 0.15 W/mK
α Air |  | 15 | W/m²K |  | λ Steel | 50 W/mK
[5 empty] | λ Copper | 384 W/mK
Insulation Copper |  | 0 | mm
Insulation Steel |  | 0 | mm
Insulation PP-R |  | 0 | mm |  | Armaflex | 0.037 W/mK
λ Insulation |  | 0.025 | W/mK |  | Rockwool | 0.025 W/mK
|  | Fusiotherm Faser SDR7.4 |  |  | Climatherm Faser SDR7.4/SDR11 |  |  | Climatherm Faser SDR17.6 |  |  | Seamless Steel |  |  | Copper
Pipe length | Start temp. | Dimension | End temp. | Total | Dimension | End temp. | Total | Dimension | End temp. | Total | Dimension | End temp. | Total | Dimension | End temp. | Total
m | ⁰C | mm | ⁰C | W | mm | ⁰C | W | mm | ⁰C | W | mm | ⁰C | W | mm | ⁰C | W
100 | 6 | 20x2.8 | 7.6559 | 1129.1656 | 20 x 2,8 | 7.6559 | 1129.1656 |  |  |  | 21.3x2.0 | 7.6196 | 1594.0299 | 19.1x1.0 | 7.4957 | 1438.2811
100 | 6 | 25x3.5 | 7.2642 | 1346.9316 | 25 x 3,5 | 7.2642 | 1346.9316 |  |  |  | 26.9x2.3 | 7.2459 | 2037.3902 | 25.4x1.2 | 7.1129 | 1935.955
100 | 6 | 32x4.4 | 6.918 | 1624.7649 | 32 x 4,4 | 6.828 | 1868.9738 |  |  |  | 33.7x2.6 | 6.9642 | 2575.3281 | 31.8x1.2 | 6.8596 | 2443.4304
100 | 6 | 40x5.5 | 6.6824 | 1887.366 | 40 x 5,5 | 6.6304 | 2203.2497 |  |  |  | 42.4x2.6 | 6.7178 | 3266.6094 | 38.1x1.2 | 6.702 | 2942.139
100 | 6 | 50x6.9 | 6.501 | 2158.9309 | 50 x 6,9 | 6.4726 | 2587.3128 |  |  |  | 48.3x2.6 | 6.6113 | 3734.1904 | 50.8x1.2 | 6.5123 | 3946.2805
100 | 6 | 63x8.6 | 6.3575 | 2466.2733 | 63 x 8,6 | 6.3465 | 3010.6455 |  |  |  | 60.3x2.9 | 6.4792 | 4680.9645 | 63.5x1.2 | 6.4032 | 4949.6606
100 | 6 | 75x10.3 | 6.2753 | 2678.7791 | 75 x 10,3 | 6.2718 | 3370.2073 |  |  |  | 76.1x2.9 | 6.3588 | 5930.8262 | 76.2x1.6 | 6.3395 | 5950.3178
100 | 6 | 90x12.3 | 6.2073 | 2916.1833 | 90 x 12,3 | 6.2091 | 3725.315 |  |  |  | 88.9x3.2 | 6.31 | 6938.2843 | 88.9x1.6 | 6.2879 | 6953.3174
100 | 6 | 110x15.1 | 6.1504 | 3149.2125 | 110 x 15,1 | 6.1552 | 4133.9231 |  |  |  | 114.3x3.6 | 6.237 | 8940.2018 | 101.6x1.6 | 6.2499 | 7956.1367
100 | 6 | 125x17.1 | 6.1219 | 3305.7004 | 125 x 11,4 | 6.1276 | 4381.4867 |  |  |  | 127.0x4.0 | 6.2134 | 9939.4003 | 127.0x1.6 | 6.1976 | 9961.6076
100 | 6 | 160x21.9 | 6.0805 | 3572.4224 | 160 x 14,6 | 6.0864 | 4860.6656 | 160 x 9,1 | 6.0975 | 6445.5032 | 168.3x4.5 | 6.1581 | 13193.4688 | 152.4x2.0 | 6.1652 | 11965.1229
100 | 6 | 200x27.4 | 6.0546 | 3788.2284 | 200 x 18,2 | 6.06 | 5283.3427 | 200 x 11,4 | 6.0695 | 7178.8965 | 219.1x5.9 | 6.1216 | 17187.0505 | 203.2x2.0 | 6.1224 | 15975.3904
0 | 6 | 250x34.2 | 6 | 0 | 250 x 22,7 | 6 | 0 | 250 x 14,2 | 6 | 0 | 273.0x6.3 | 6 | 0
0 | 6 | 315x42.6 | 6 | 0 | 315 x 28,6 | 6 | 0 | 315 x 17,9 | 6 | 0 | 323.9x7.1 | 6 | 0
0 | 6 | 355x48.0 | 6 | 0 | 355 x 32,2 | 6 | 0 | 355 x 20,1 | 6 | 0 | 355.6x8.0 | 6 | 0
0 | 6 |  |  |  | 400 x 36,3 | 6 | 0 | 400 x 22,7 | 6 | 0 | 406.4x8.8 | 6 | 0
0 | 6 |  |  |  | 450 x 40,9 | 6 | 0 | 450 x 25,5 | 6 | 0 | 457.0x10.0 | 6 | 0
0 | 6 | [6 empty] | 500 x 28,4 | 6 | 0 | 508.0x11.0 | 6 | 0
0 | 6 | [6 empty] | 560 x 31,7 | 6 | 0 | 559.0x12.5 | 6 | 0
0 | 6 | [6 empty] | 630 x 35,7 | 6 | 0 | 610.0x12.5 | 6 | 0
| Q = (W/mtr) |  | Q = (W/mtr) |  | Q = (W/mtr) |  | Q = (W/mtr) |  | Q = (W/mtr)
| at T |  | at T |  | at T |  | at T |  | at T
Fusiotherm SDR7.4 | Fusiotherm SDR7.4 | Climatherm SDR7.4/11 | Climatherm SDR7.4/11 | Climatherm SDR17.6 | Climatherm SDR17.6 | Steel | Steel | Copper | Copper
20x2.8 | 11.8741 | 20 x 2,8 | 11.8741 |  |  | 21,3 x 2.0 | 16.7432 | 19.1x1.0 | 15.0484
25x3.5 | 13.991 | 25 x 3,5 | 13.991 |  |  | 26,9 x 2,3 | 21.151 | 25.4x1.2 | 20.0155
32x4.4 | 16.6981 | 32 x 2,9 | 19.1554 |  |  | 33,7 x 2,6 | 26.5047 | 31.8x1.2 | 25.0672
40x5.5 | 19.259 | 40 x 3,7 | 22.4472 |  |  | 42,4 x 2,6 | 33.3686 | 38.1x1.2 | 30.0398
50x6.9 | 21.9105 | 50 x 4,6 | 26.2359 |  |  | 48,3 x 2,6 | 38.0229 | 50.8x1.2 | 40.0635
63x8.6 | 24.9231 | 63 x 5,8 | 30.4144 |  |  | 60.3 x 2,9 | 47.4753 | 63.5x1.2 | 50.087
75x10.3 | 27.0048 | 75 x 6,8 | 33.9717 |  |  | 76,1 x 2,9 | 59.9367 | 76.2x1.6 | 60.0994
90x12.3 | 29.3393 | 90 x 8,2 | 37.4819 |  |  | 88,9 x 3,2 | 70.0168 | 88.9x1.6 | 70.1227
110x15.1 | 31.6308 | 110 x 10,0 | 41.5272 |  |  | 114,3 x 3,6 | 90.0248 | 101.6x1.6 | 80.1459
125x17.1 | 33.1749 | 125 x 11,4 | 43.9784 |  |  | 127,0 x 4,0 | 100.0169 | 127.0x1.6 | 100.1938
160x21.9 | 35.8082 | 160 x 14,6 | 48.7293 | 160 x 9,1 | 64.6387 | 168,3 x 4,5 | 132.5458 | 152.4x2.0 | 120.2306
200x27.4 | 37.9427 | 200 x 18,2 | 52.926 | 200 x 11,4 | 71.9347 | 219,1 x 5,9 | 172.4821 | 203.2x2.0 | 160.3261
250x34.2 | 39.9249 | 250 x 22,7 | 56.8421 | 250 x 14,2 | 79.3406 | 273,0 x 6,3 | 214.9196
315x42.6 | 42.1458 | 315 x 28,6 | 60.4509 | 315 x 17,9 | 86.5074 | 323,9 x 7,1 | 254.9432
355x48.0 | 42.9796 | 355 x 32,2 | 62.2125 | 355 x 20,1 | 90.28 | 355,6 x 8,0 | 279.8172
|  | 400 x 36,3 | 63.7834 | 400 x 22,7 | 93.5214 | 406,4 x 8,8 | 319.7282
|  | 450 x 40,9 | 65.163 | 450 x 25,5 | 96.8206 | 457,0 x 10,0 | 359.4095
|  |  |  | 500 x 28,4 | 99.3534 | 508,0 x 11,0 | 399.4077
|  |  |  | 560 x 31,7 | 102.3971 | 559,0 x 12,5 | 439.3028
|  |  |  | 630 x 35,7 | 105.0153 | 610,0 x 12,5 | 479.4216
| ΔQ = (W/m) |  | ΔQ = (W/m) |  | ΔQ = (W/m) |  | ΔQ = (W/m) |  | ΔQ = (W/m)
| ΔT = 1°C |  | ΔT = 1°C |  | ΔT = 1°C |  | ΔT = 1°C |  | ΔT = 1°C
Fusiotherm SDR7.4 | Fusiotherm SDR7.4 | Climatherm SDR7.4/11 | Climatherm SDR7.4/11 | Climatherm SDR17.6 | Climatherm SDR17.6 | Steel | Steel | Copper | Copper
20x2.8 | -0.69847 | 20 x 2,8 | -0.69847 |  |  | 21,3 x 2.0 | -0.98489 | 19.1x1.0 | -0.8852
25x3.5 | -0.823 | 25 x 3,5 | -0.823 |  |  | 26,9 x 2,3 | -1.2442 | 25.4x1.2 | -1.1774
32x4.4 | -0.98224 | 32 x 2,9 | -1.1268 |  |  | 33,7 x 2,6 | -1.5591 | 31.8x1.2 | -1.4745
40x5.5 | -1.1329 | 40 x 3,7 | -1.3204 |  |  | 42,4 x 2,6 | -1.9629 | 38.1x1.2 | -1.767
50x6.9 | -1.2889 | 50 x 4,6 | -1.5433 |  |  | 48,3 x 2,6 | -2.2366 | 50.8x1.2 | -2.3567
63x8.6 | -1.4661 | 63 x 5,8 | -1.7891 |  |  | 60.3 x 2,9 | -2.7927 | 63.5x1.2 | -2.9463
75x10.3 | -1.5885 | 75 x 6,8 | -1.9983 |  |  | 76,1 x 2,9 | -3.5257 | 76.2x1.6 | -3.5353
90x12.3 | -1.7258 | 90 x 8,2 | -2.2048 |  |  | 88,9 x 3,2 | -4.1186 | 88.9x1.6 | -4.1249
110x15.1 | -1.8606 | 110 x 10,0 | -2.4428 |  |  | 114,3 x 3,6 | -5.2956 | 101.6x1.6 | -4.7145
125x17.1 | -1.9515 | 125 x 11,4 | -2.587 |  |  | 127,0 x 4,0 | -5.8833 | 127.0x1.6 | -5.8938
160x21.9 | -2.1064 | 160 x 14,6 | -2.8664 | 160 x 9,1 | -3.8023 | 168,3 x 4,5 | -7.7968 | 152.4x2.0 | -7.0724
200x27.4 | -2.2319 | 200 x 18,2 | -3.1133 | 200 x 11,4 | -4.2315 | 219,1 x 5,9 | -10.146 | 203.2x2.0 | -9.4309
250x34.2 | -2.3485 | 250 x 22,7 | -3.3437 | 250 x 14,2 | -4.6671 | 273,0 x 6,3 | -12.6423
315x42.6 | -2.4792 | 315 x 28,6 | -3.5559 | 315 x 17,9 | -5.0887 | 323,9 x 7,1 | -14.9967
355x48.0 | -2.5282 | 355 x 32,2 | -3.6596 | 355 x 20,1 | -5.3106 | 355,6 x 8,0 | -16.4598
|  | 400 x 36,3 | -3.752 | 400 x 22,7 | -5.5013 | 406,4 x 8,8 | -18.8075
|  | 450 x 40,9 | -3.8331 | 450 x 25,5 | -5.6953 | 457,0 x 10,0 | -21.1417
|  |  |  | 500 x 28,4 | -5.8443 | 508,0 x 11,0 | -23.4946
|  |  |  | 560 x 31,7 | -6.0234 | 559,0 x 12,5 | -25.8413
|  |  |  | 630 x 35,7 | -6.1774 | 610,0 x 12,5 | -28.2013
Fusiotherm PP-R Faser SDR7.4
Diameter (mm) | Wanddikte (mm) | Binnendiam. (mm) | Omgevingstemp. (°C) | Medium temp. (°C) | Delta T (°C) | Alfa water (W/m2°C) | Alfa lucht (W/m2°C) | Lambda Staal (W/m°C) | 1/(alfaWxd1) | 1/(alfaLxd2) | 1/(2xLambda)xLn(d2/d1) | Dikte Isolatie (mm) | Lambda Isolatie (W/m°C) | 1/(2xLambda)xLn(d2/d1) | Axk=pi/(H+I+J+M) | Q = (W/mtr) | Delta T = Q/(1/(Alfa2xd2)) | Temp. buiswand (°C)
20 | 2.8 | 14.4 | 23 | 6 | 17 | 1000 | 15 | 0.15 | 0.069444 | 3.3333 | 1.095 | 0 | 0.025 | 0 | 0.69847 | 11.8741 | 12.5987 | 10.4013
25 | 3.5 | 18 | 23 | 6 | 17 | 1000 | 15 | 0.15 | 0.055556 | 2.6667 | 1.095 | 0 | 0.025 | 0 | 0.823 | 13.991 | 11.8759 | 11.1241
32 | 4.4 | 23.2 | 23 | 6 | 17 | 1000 | 15 | 0.15 | 0.043103 | 2.0833 | 1.0719 | 0 | 0.025 | 0 | 0.98224 | 16.6981 | 11.0733 | 11.9267
40 | 5.5 | 29 | 23 | 6 | 17 | 1000 | 15 | 0.15 | 0.034483 | 1.6667 | 1.0719 | 0 | 0.025 | 0 | 1.1329 | 19.259 | 10.2172 | 12.7828
50 | 6.9 | 36.2 | 23 | 6 | 17 | 1000 | 15 | 0.15 | 0.027624 | 1.3333 | 1.0765 | 0 | 0.025 | 0 | 1.2889 | 21.9105 | 9.2991 | 13.7009
63 | 8.6 | 45.8 | 23 | 6 | 17 | 1000 | 15 | 0.15 | 0.021834 | 1.0582 | 1.0628 | 0 | 0.025 | 0 | 1.4661 | 24.9231 | 8.395 | 14.605
75 | 10.3 | 54.4 | 23 | 6 | 17 | 1000 | 15 | 0.15 | 0.018382 | 0.88889 | 1.0704 | 0 | 0.025 | 0 | 1.5885 | 27.0048 | 7.6408 | 15.3592
90 | 12.3 | 65.4 | 23 | 6 | 17 | 1000 | 15 | 0.15 | 0.015291 | 0.74074 | 1.0643 | 0 | 0.025 | 0 | 1.7258 | 29.3393 | 6.9178 | 16.0822
110 | 15.1 | 79.8 | 23 | 6 | 17 | 1000 | 15 | 0.15 | 0.012531 | 0.60606 | 1.0699 | 0 | 0.025 | 0 | 1.8606 | 31.6308 | 6.1021 | 16.8979
125 | 17.1 | 90.8 | 23 | 6 | 17 | 1000 | 15 | 0.15 | 0.011013 | 0.53333 | 1.0655 | 0 | 0.025 | 0 | 1.9515 | 33.1749 | 5.6319 | 17.3681
160 | 21.9 | 116.2 | 23 | 6 | 17 | 1000 | 15 | 0.15 | 0.0086059 | 0.41667 | 1.0662 | 0 | 0.025 | 0 | 2.1064 | 35.8082 | 4.7492 | 18.2508
200 | 27.4 | 145.2 | 23 | 6 | 17 | 1000 | 15 | 0.15 | 0.0068871 | 0.33333 | 1.0674 | 0 | 0.025 | 0 | 2.2319 | 37.9427 | 4.0258 | 18.9742
250 | 34.2 | 181.6 | 23 | 6 | 17 | 1000 | 15 | 0.15 | 0.0055066 | 0.26667 | 1.0655 | 0 | 0.025 | 0 | 2.3485 | 39.9249 | 3.3889 | 19.6111
315 | 42.6 | 229.8 | 23 | 6 | 17 | 1001 | 15 | 0.15 | 0.0043473 | 0.21164 | 1.0512 | 0 | 0.025 | 0 | 2.4792 | 42.1458 | 2.8392 | 20.1608
355 | 48 | 259 | 23 | 6 | 17 | 1002 | 15 | 0.15 | 0.0038533 | 0.18779 | 1.051 | 0 | 0.025 | 0 | 2.5282 | 42.9796 | 2.5692 | 20.4308
Climatherm PP-R Faser SDR7.4/SDR11
Diameter (mm) | Wanddikte (mm) | Binnendiam. (mm) | Omgevingstemp. (°C) | Medium temp. (°C) | Delta T (°C) | Alfa water (W/m2°C) | Alfa lucht (W/m2°C) | Lambda Staal (W/m°C) | 1/(alfaWxd1) | 1/(alfaLxd2) | 1/(2xLambda)xLn(d2/d1) | Dikte Isolatie (mm) | Lambda Isolatie (W/m°C) | 1/(2xLambda)xLn(d2/d1) | Axk=pi/(H+I+J+M) | Q = (W/mtr) | Delta T = Q/(1/(Alfa2xd2)) | Temp. buiswand (°C)
20 | 2.8 | 14.4 | 23 | 6 | 17 | 1000 | 15 | 0.15 | 0.069444 | 3.3333 | 1.095 | 0 | 0.025 | 0 | 0.69847 | 11.8741 | 12.5987 | 10.4013
25 | 3.5 | 18 | 23 | 6 | 17 | 1000 | 15 | 0.15 | 0.055556 | 2.6667 | 1.095 | 0 | 0.025 | 0 | 0.823 | 13.991 | 11.8759 | 11.1241
32 | 2.9 | 26.2 | 23 | 6 | 17 | 1000 | 15 | 0.15 | 0.038168 | 2.0833 | 0.66659 | 0 | 0.025 | 0 | 1.1268 | 19.1554 | 12.7028 | 10.2972
40 | 3.7 | 32.6 | 23 | 6 | 17 | 1000 | 15 | 0.15 | 0.030675 | 1.6667 | 0.68189 | 0 | 0.025 | 0 | 1.3204 | 22.4472 | 11.9086 | 11.0914
50 | 4.6 | 40.8 | 23 | 6 | 17 | 1000 | 15 | 0.15 | 0.02451 | 1.3333 | 0.6778 | 0 | 0.025 | 0 | 1.5433 | 26.2359 | 11.1348 | 11.8652
63 | 5.8 | 51.4 | 23 | 6 | 17 | 1000 | 15 | 0.15 | 0.019455 | 1.0582 | 0.67832 | 0 | 0.025 | 0 | 1.7891 | 30.4144 | 10.2446 | 12.7554
75 | 6.8 | 61.4 | 23 | 6 | 17 | 1000 | 15 | 0.15 | 0.016287 | 0.88889 | 0.66693 | 0 | 0.025 | 0 | 1.9983 | 33.9717 | 9.612 | 13.388
90 | 8.2 | 73.6 | 23 | 6 | 17 | 1000 | 15 | 0.15 | 0.013587 | 0.74074 | 0.67055 | 0 | 0.025 | 0 | 2.2048 | 37.4819 | 8.8376 | 14.1624
110 | 10 | 90 | 23 | 6 | 17 | 1000 | 15 | 0.15 | 0.011111 | 0.60606 | 0.6689 | 0 | 0.025 | 0 | 2.4428 | 41.5272 | 8.0112 | 14.9888
125 | 11.4 | 102.2 | 23 | 6 | 17 | 1000 | 15 | 0.15 | 0.0097847 | 0.53333 | 0.67127 | 0 | 0.025 | 0 | 2.587 | 43.9784 | 7.466 | 15.534
160 | 14.6 | 130.8 | 23 | 6 | 17 | 1000 | 15 | 0.15 | 0.0076453 | 0.41667 | 0.67168 | 0 | 0.025 | 0 | 2.8664 | 48.7293 | 6.4629 | 16.5371
200 | 18.2 | 163.6 | 23 | 6 | 17 | 1000 | 15 | 0.15 | 0.0061125 | 0.33333 | 0.66964 | 0 | 0.025 | 0 | 3.1133 | 52.926 | 5.6156 | 17.3844
250 | 22.7 | 204.6 | 23 | 6 | 17 | 1000 | 15 | 0.15 | 0.0048876 | 0.26667 | 0.66801 | 0 | 0.025 | 0 | 3.3437 | 56.8421 | 4.8249 | 18.1751
315 | 28.6 | 257.8 | 23 | 6 | 17 | 1001 | 15 | 0.15 | 0.0038751 | 0.21164 | 0.66796 | 0 | 0.025 | 0 | 3.5559 | 60.4509 | 4.0724 | 18.9276
355 | 32.2 | 290.6 | 23 | 6 | 17 | 1002 | 15 | 0.15 | 0.0034343 | 0.18779 | 0.66723 | 0 | 0.025 | 0 | 3.6596 | 62.2125 | 3.7188 | 19.2812
400 | 36.3 | 327.4 | 23 | 6 | 17 | 1003 | 15 | 0.15 | 0.0030452 | 0.16667 | 0.66761 | 0 | 0.025 | 0 | 3.752 | 63.7834 | 3.3838 | 19.6162
450 | 40.9 | 368.2 | 23 | 6 | 17 | 1004 | 15 | 0.15 | 0.0027051 | 0.14815 | 0.66874 | 0 | 0.025 | 0 | 3.8331 | 65.163 | 3.0729 | 19.9271
Climatherm PP-R Faser SDR17.6
Diameter (mm) | Wanddikte (mm) | Binnendiam. (mm) | Omgevingstemp. (°C) | Medium temp. (°C) | Delta T (°C) | Alfa water (W/m2°C) | Alfa lucht (W/m2°C) | Lambda Staal (W/m°C) | 1/(alfaWxd1) | 1/(alfaLxd2) | 1/(2xLambda)xLn(d2/d1) | Dikte Isolatie (mm) | Lambda Isolatie (W/m°C) | 1/(2xLambda)xLn(d2/d1) | Axk=pi/(H+I+J+M) | Q = (W/mtr) | Delta T = Q/(1/(Alfa2xd2)) | Temp. buiswand (°C)
160 | 9.1 | 141.8 | 23 | 6 | 17 | 1000 | 15 | 0.15 | 0.0070522 | 0.41667 | 0.40252 | 0 | 0.025 | 0 | 3.8023 | 64.6387 | 8.573 | 14.427
200 | 11.4 | 177.2 | 23 | 6 | 17 | 1000 | 15 | 0.15 | 0.0056433 | 0.33333 | 0.40346 | 0 | 0.025 | 0 | 4.2315 | 71.9347 | 7.6325 | 15.3675
250 | 14.2 | 221.6 | 23 | 6 | 17 | 1000 | 15 | 0.15 | 0.0045126 | 0.26667 | 0.40196 | 0 | 0.025 | 0 | 4.6671 | 79.3406 | 6.7346 | 16.2654
315 | 17.9 | 279.2 | 23 | 6 | 17 | 1000 | 15 | 0.15 | 0.0035817 | 0.21164 | 0.40215 | 0 | 0.025 | 0 | 5.0887 | 86.5074 | 5.8277 | 17.1723
355 | 20.1 | 314.8 | 23 | 6 | 17 | 1000 | 15 | 0.15 | 0.0031766 | 0.18779 | 0.4006 | 0 | 0.025 | 0 | 5.3106 | 90.28 | 5.3966 | 17.6034
400 | 22.7 | 354.6 | 23 | 6 | 17 | 1000 | 15 | 0.15 | 0.0028201 | 0.16667 | 0.40158 | 0 | 0.025 | 0 | 5.5013 | 93.5214 | 4.9615 | 18.0385
450 | 25.5 | 399 | 23 | 6 | 17 | 1000 | 15 | 0.15 | 0.0025063 | 0.14815 | 0.40095 | 0 | 0.025 | 0 | 5.6953 | 96.8206 | 4.5658 | 18.4342
500 | 28.4 | 443.2 | 23 | 6 | 17 | 1000 | 15 | 0.15 | 0.0022563 | 0.13333 | 0.40196 | 0 | 0.025 | 0 | 5.8443 | 99.3534 | 4.2167 | 18.7833
560 | 31.7 | 496.6 | 23 | 6 | 17 | 1000 | 15 | 0.15 | 0.0020137 | 0.11905 | 0.40051 | 0 | 0.025 | 0 | 6.0234 | 102.3971 | 3.8802 | 19.1198
630 | 35.7 | 558.6 | 23 | 6 | 17 | 1000 | 15 | 0.15 | 0.0017902 | 0.10582 | 0.40095 | 0 | 0.025 | 0 | 6.1774 | 105.0153 | 3.5373 | 19.4627
Seamless Steel
Diameter (mm) | Wanddikte (mm) | Binnendiam. (mm) | Omgevingstemp. (°C) | Medium temp. (°C) | Delta T (°C) | Alfa water (W/m2°C) | Alfa lucht (W/m2°C) | Lambda Staal (W/m°C) | 1/(alfaWxd1) | 1/(alfaLxd2) | 1/(2xLambda)xLn(d2/d1) | Dikte Isolatie (mm) | Lambda Isolatie (W/m°C) | 1/(2xLambda)xLn(d2/d1) | Axk=pi/(H+I+J+M) | Q = (W/mtr) | Delta T = Q/(1/(Alfa2xd2)) | Temp. buiswand (°C)
21.3 | 2 | 17.3 | 23 | 6 | 17 | 1000 | 15 | 50 | 0.057803 | 3.1299 | 0.00208 | 0 | 0.025 | 0 | 0.98489 | 16.7432 | 16.6808 | 6.3192
26.9 | 2.3 | 22.3 | 23 | 6 | 17 | 1000 | 15 | 50 | 0.044843 | 2.4783 | 0.0018754 | 0 | 0.025 | 0 | 1.2442 | 21.151 | 16.6854 | 6.3146
33.7 | 2.6 | 28.5 | 23 | 6 | 17 | 1000 | 15 | 50 | 0.035088 | 1.9782 | 0.0016759 | 0 | 0.025 | 0 | 1.5591 | 26.5047 | 16.6898 | 6.3102
42.4 | 2.6 | 37.2 | 23 | 6 | 17 | 1000 | 15 | 50 | 0.026882 | 1.5723 | 0.0013084 | 0 | 0.025 | 0 | 1.9629 | 33.3686 | 16.7005 | 6.2995
48.3 | 2.6 | 43.1 | 23 | 6 | 17 | 1000 | 15 | 50 | 0.023202 | 1.3803 | 0.0011391 | 0 | 0.025 | 0 | 2.2366 | 38.0229 | 16.7053 | 6.2947
60.3 | 2.9 | 54.5 | 23 | 6 | 17 | 1000 | 15 | 50 | 0.018349 | 1.1056 | 0.0010113 | 0 | 0.025 | 0 | 2.7927 | 47.4753 | 16.7074 | 6.2926
76.1 | 2.9 | 70.3 | 23 | 6 | 17 | 1000 | 15 | 50 | 0.014225 | 0.87604 | 0.00079276 | 0 | 0.025 | 0 | 3.5257 | 59.9367 | 16.7134 | 6.2866
88.9 | 3.2 | 82.5 | 23 | 6 | 17 | 1000 | 15 | 50 | 0.012121 | 0.74991 | 0.00074714 | 0 | 0.025 | 0 | 4.1186 | 70.0168 | 16.7131 | 6.2869
114.3 | 3.6 | 107.1 | 23 | 6 | 17 | 1000 | 15 | 50 | 0.0093371 | 0.58326 | 0.00065064 | 0 | 0.025 | 0 | 5.2956 | 90.0248 | 16.7137 | 6.2863
127 | 4 | 119 | 23 | 6 | 17 | 1001 | 15 | 50 | 0.008395 | 0.52493 | 0.00065064 | 0 | 0.025 | 0 | 5.8833 | 100.0169 | 16.712 | 6.288
168.3 | 4.5 | 159.3 | 23 | 6 | 17 | 1002 | 15 | 50 | 0.0062649 | 0.39612 | 0.00054959 | 0 | 0.025 | 0 | 7.7968 | 132.5458 | 16.7124 | 6.2876
219.1 | 5.9 | 207.3 | 23 | 6 | 17 | 1003 | 15 | 50 | 0.0048095 | 0.30428 | 0.00055361 | 0 | 0.025 | 0 | 10.146 | 172.4821 | 16.7055 | 6.2945
273 | 6.3 | 260.4 | 23 | 6 | 17 | 1004 | 15 | 50 | 0.0038249 | 0.2442 | 0.00047253 | 0 | 0.025 | 0 | 12.6423 | 214.9196 | 16.706 | 6.294
323.9 | 7.1 | 309.7 | 23 | 6 | 17 | 1005 | 15 | 50 | 0.0032129 | 0.20582 | 0.00044831 | 0 | 0.025 | 0 | 14.9967 | 254.9432 | 16.7028 | 6.2972
355.6 | 8 | 339.6 | 23 | 6 | 17 | 1006 | 15 | 50 | 0.0029271 | 0.18748 | 0.00046038 | 0 | 0.025 | 0 | 16.4598 | 279.8172 | 16.6982 | 6.3018
406.4 | 8.8 | 388.8 | 23 | 6 | 17 | 1007 | 15 | 50 | 0.0025541 | 0.16404 | 0.00044273 | 0 | 0.025 | 0 | 18.8075 | 319.7282 | 16.6949 | 6.3051
457 | 10 | 437 | 23 | 6 | 17 | 1008 | 15 | 50 | 0.0022702 | 0.14588 | 0.0004475 | 0 | 0.025 | 0 | 21.1417 | 359.4095 | 16.689 | 6.311
508 | 11 | 486 | 23 | 6 | 17 | 1009 | 15 | 50 | 0.0020393 | 0.13123 | 0.00044273 | 0 | 0.025 | 0 | 23.4946 | 399.4077 | 16.6844 | 6.3156
559 | 12.5 | 534 | 23 | 6 | 17 | 1010 | 15 | 50 | 0.0018541 | 0.11926 | 0.00045754 | 0 | 0.025 | 0 | 25.8413 | 439.3028 | 16.6767 | 6.3233
610 | 12.5 | 585 | 23 | 6 | 17 | 1011 | 15 | 50 | 0.0016908 | 0.10929 | 0.00041847 | 0 | 0.025 | 0 | 28.2013 | 479.4216 | 16.6781 | 6.3219
Copper
Diameter (mm) | Wanddikte (mm) | Binnendiam. (mm) | Omgevingstemp. (°C) | Medium temp. (°C) | Delta T (°C) | Alfa water (W/m2°C) | Alfa lucht (W/m2°C) | Lambda Copper (W/m°C) | 1/(alfaWxd1) | 1/(alfaLxd2) | 1/(2xLambda)xLn(d2/d1) | Dikte Isolatie (mm) | Lambda Isolatie (W/m°C) | 1/(2xLambda)xLn(d2/d1) | Axk=pi/(H+I+J+M) | Q = (W/mtr) | Delta T = Q/(1/(Alfa2xd2)) | Temp. buiswand (°C)
19.1 | 1 | 17.1 | 23 | 6 | 17 | 1000 | 15 | 384 | 0.05848 | 3.4904 | 0.00014402 | 0 | 0.025 | 0 | 0.8852 | 15.0484 | 16.7191 | 6.2809
25.4 | 1.2 | 23 | 23 | 6 | 17 | 1000 | 15 | 384 | 0.043478 | 2.6247 | 0.00012924 | 0 | 0.025 | 0 | 1.1774 | 20.0155 | 16.7221 | 6.2779
31.8 | 1.2 | 29.4 | 23 | 6 | 17 | 1000 | 15 | 384 | 0.034014 | 2.0964 | 0.00010218 | 0 | 0.025 | 0 | 1.4745 | 25.0672 | 16.7277 | 6.2723
38.1 | 1.2 | 35.7 | 23 | 6 | 17 | 1000 | 15 | 384 | 0.028011 | 1.7498 | 8.4718e-05 | 0 | 0.025 | 0 | 1.767 | 30.0398 | 16.7313 | 6.2687
50.8 | 1.2 | 48.4 | 23 | 6 | 17 | 1000 | 15 | 384 | 0.020661 | 1.3123 | 6.3016e-05 | 0 | 0.025 | 0 | 2.3567 | 40.0635 | 16.7357 | 6.2643
63.5 | 1.2 | 61.1 | 23 | 6 | 17 | 1000 | 15 | 384 | 0.016367 | 1.0499 | 5.0167e-05 | 0 | 0.025 | 0 | 2.9463 | 50.087 | 16.7382 | 6.2618
76.2 | 1.6 | 73 | 23 | 6 | 17 | 1000 | 15 | 384 | 0.013699 | 0.87489 | 5.5862e-05 | 0 | 0.025 | 0 | 3.5353 | 60.0994 | 16.7368 | 6.2632
88.9 | 1.6 | 85.7 | 23 | 6 | 17 | 1000 | 15 | 384 | 0.011669 | 0.74991 | 4.7733e-05 | 0 | 0.025 | 0 | 4.1249 | 70.1227 | 16.7384 | 6.2616
101.6 | 1.6 | 98.4 | 23 | 6 | 17 | 1000 | 15 | 384 | 0.010163 | 0.65617 | 4.167e-05 | 0 | 0.025 | 0 | 4.7145 | 80.1459 | 16.7396 | 6.2604
127 | 1.6 | 123.8 | 23 | 6 | 17 | 1001 | 15 | 384 | 0.0080695 | 0.52493 | 3.3229e-05 | 0 | 0.025 | 0 | 5.8938 | 100.1938 | 16.7415 | 6.2585
152.4 | 2 | 148.4 | 23 | 6 | 17 | 1002 | 15 | 384 | 0.0067251 | 0.43745 | 3.4632e-05 | 0 | 0.025 | 0 | 7.0724 | 120.2306 | 16.7412 | 6.2588
203.2 | 2 | 199.2 | 23 | 6 | 17 | 1003 | 15 | 384 | 0.0050051 | 0.32808 | 2.5887e-05 | 0 | 0.025 | 0 | 9.4309 | 160.3261 | 16.7432 | 6.2568

## 0°C
Heat exchange per meter at T -1⁰C
Ambient temperature |  | 23 | ⁰C |  | λ Fusiolen PP-R | 0.15 W/mK
α Air |  | 15 | W/m²K |  | λ Steel | 50 W/mK
[5 empty] | λ Copper | 384 W/mK
Insulation Copper |  | 0 | mm
Insulation Steel |  | 0 | mm
Insulation PP-R |  | 0 | mm |  | Armaflex | 0.037 W/mK
λ Insulation |  | 0.025 | W/mK |  | Rockwool | 0.025 W/mK
| Q = (W/mtr) |  | Q = (W/mtr) |  | Q = (W/mtr) |  | Q = (W/mtr) |  | Q = (W/mtr)
| T -1⁰C |  | T -1⁰C |  | T -1⁰C |  | T -1⁰C |  | T -1⁰C
Fusiotherm SDR7.4 | Fusiotherm SDR7.4 | Climatherm SDR7.4/11 | Climatherm SDR7.4/11 | Climatherm SDR17.6 | Climatherm SDR17.6 | Steel | Steel | Copper | Copper
20x2.8 | 12.5725 | 20 x 2,8 | 12.5725 |  |  | 21,3 x 2.0 | 17.7281 | 19.1x1.0 | 15.9336
25x3.5 | 14.814 | 25 x 3,5 | 14.814 |  |  | 26,9 x 2,3 | 22.3952 | 25.4x1.2 | 21.1929
32x4.4 | 17.6804 | 32 x 2,9 | 20.2822 |  |  | 33,7 x 2,6 | 28.0638 | 31.8x1.2 | 26.5418
40x5.5 | 20.3919 | 40 x 3,7 | 23.7676 |  |  | 42,4 x 2,6 | 35.3315 | 38.1x1.2 | 31.8068
50x6.9 | 23.1994 | 50 x 4,6 | 27.7792 |  |  | 48,3 x 2,6 | 40.2595 | 50.8x1.2 | 42.4202
63x8.6 | 26.3892 | 63 x 5,8 | 32.2035 |  |  | 60.3 x 2,9 | 50.268 | 63.5x1.2 | 53.0333
75x10.3 | 28.5933 | 75 x 6,8 | 35.97 |  |  | 76,1 x 2,9 | 63.4623 | 76.2x1.6 | 63.6346
90x12.3 | 31.0652 | 90 x 8,2 | 39.6867 |  |  | 88,9 x 3,2 | 74.1354 | 88.9x1.6 | 74.2476
110x15.1 | 33.4915 | 110 x 10,0 | 43.97 |  |  | 114,3 x 3,6 | 95.3204 | 101.6x1.6 | 84.8604
125x17.1 | 35.1264 | 125 x 11,4 | 46.5654 |  |  | 127,0 x 4,0 | 105.9003 | 127.0x1.6 | 106.0876
160x21.9 | 37.9145 | 160 x 14,6 | 51.5958 | 160 x 9,1 | 68.441 | 168,3 x 4,5 | 140.3426 | 152.4x2.0 | 127.303
200x27.4 | 40.1746 | 200 x 18,2 | 56.0393 | 200 x 11,4 | 76.1661 | 219,1 x 5,9 | 182.6281 | 203.2x2.0 | 169.7571
250x34.2 | 42.2734 | 250 x 22,7 | 60.1858 | 250 x 14,2 | 84.0077 | 273,0 x 6,3 | 227.5619
315x42.6 | 44.6249 | 315 x 28,6 | 64.0069 | 315 x 17,9 | 91.5961 | 323,9 x 7,1 | 269.9398
355x48.0 | 45.5078 | 355 x 32,2 | 65.8721 | 355 x 20,1 | 95.5906 | 355,6 x 8,0 | 296.277
|  | 400 x 36,3 | 67.5354 | 400 x 22,7 | 99.0227 | 406,4 x 8,8 | 338.5357
|  | 450 x 40,9 | 68.9961 | 450 x 25,5 | 102.5159 | 457,0 x 10,0 | 380.5513
|  |  |  | 500 x 28,4 | 105.1977 | 508,0 x 11,0 | 422.9022
|  |  |  | 560 x 31,7 | 108.4205 | 559,0 x 12,5 | 465.1442
|  |  |  | 630 x 35,7 | 111.1927 | 610,0 x 12,5 | 507.6228
Fusiotherm PP-R Faser SDR7.4
Diameter (mm) | Wanddikte (mm) | Binnendiam. (mm) | Omgevingstemp. (°C) | Medium temp. (°C) | Delta T (°C) | Alfa water (W/m2°C) | Alfa lucht (W/m2°C) | Lambda Staal (W/m°C) | 1/(alfaWxd1) | 1/(alfaLxd2) | 1/(2xLambda)xLn(d2/d1) | Dikte Isolatie (mm) | Lambda Isolatie (W/m°C) | 1/(2xLambda)xLn(d2/d1) | Axk=pi/(H+I+J+M) | Q = (W/mtr) | Delta T = Q/(1/(Alfa2xd2)) | Temp. buiswand (°C)
20 | 2.8 | 14.4 | 23 | 5 | 18 | 1000 | 15 | 0.15 | 0.069444 | 3.3333 | 1.095 | 0 | 0.025 | 0 | 0.69847 | 12.5725 | 13.3398 | 9.6602
25 | 3.5 | 18 | 23 | 5 | 18 | 1000 | 15 | 0.15 | 0.055556 | 2.6667 | 1.095 | 0 | 0.025 | 0 | 0.823 | 14.814 | 12.5745 | 10.4255
32 | 4.4 | 23.2 | 23 | 5 | 18 | 1000 | 15 | 0.15 | 0.043103 | 2.0833 | 1.0719 | 0 | 0.025 | 0 | 0.98224 | 17.6804 | 11.7246 | 11.2754
40 | 5.5 | 29 | 23 | 5 | 18 | 1000 | 15 | 0.15 | 0.034483 | 1.6667 | 1.0719 | 0 | 0.025 | 0 | 1.1329 | 20.3919 | 10.8182 | 12.1818
50 | 6.9 | 36.2 | 23 | 5 | 18 | 1000 | 15 | 0.15 | 0.027624 | 1.3333 | 1.0765 | 0 | 0.025 | 0 | 1.2889 | 23.1994 | 9.8461 | 13.1539
63 | 8.6 | 45.8 | 23 | 5 | 18 | 1000 | 15 | 0.15 | 0.021834 | 1.0582 | 1.0628 | 0 | 0.025 | 0 | 1.4661 | 26.3892 | 8.8888 | 14.1112
75 | 10.3 | 54.4 | 23 | 5 | 18 | 1000 | 15 | 0.15 | 0.018382 | 0.88889 | 1.0704 | 0 | 0.025 | 0 | 1.5885 | 28.5933 | 8.0902 | 14.9098
90 | 12.3 | 65.4 | 23 | 5 | 18 | 1000 | 15 | 0.15 | 0.015291 | 0.74074 | 1.0643 | 0 | 0.025 | 0 | 1.7258 | 31.0652 | 7.3247 | 15.6753
110 | 15.1 | 79.8 | 23 | 5 | 18 | 1000 | 15 | 0.15 | 0.012531 | 0.60606 | 1.0699 | 0 | 0.025 | 0 | 1.8606 | 33.4915 | 6.461 | 16.539
125 | 17.1 | 90.8 | 23 | 5 | 18 | 1000 | 15 | 0.15 | 0.011013 | 0.53333 | 1.0655 | 0 | 0.025 | 0 | 1.9515 | 35.1264 | 5.9632 | 17.0368
160 | 21.9 | 116.2 | 23 | 5 | 18 | 1000 | 15 | 0.15 | 0.0086059 | 0.41667 | 1.0662 | 0 | 0.025 | 0 | 2.1064 | 37.9145 | 5.0286 | 17.9714
200 | 27.4 | 145.2 | 23 | 5 | 18 | 1000 | 15 | 0.15 | 0.0068871 | 0.33333 | 1.0674 | 0 | 0.025 | 0 | 2.2319 | 40.1746 | 4.2626 | 18.7374
250 | 34.2 | 181.6 | 23 | 5 | 18 | 1000 | 15 | 0.15 | 0.0055066 | 0.26667 | 1.0655 | 0 | 0.025 | 0 | 2.3485 | 42.2734 | 3.5883 | 19.4117
315 | 42.6 | 229.8 | 23 | 5 | 18 | 1001 | 15 | 0.15 | 0.0043473 | 0.21164 | 1.0512 | 0 | 0.025 | 0 | 2.4792 | 44.6249 | 3.0062 | 19.9938
355 | 48 | 259 | 23 | 5 | 18 | 1002 | 15 | 0.15 | 0.0038533 | 0.18779 | 1.051 | 0 | 0.025 | 0 | 2.5282 | 45.5078 | 2.7203 | 20.2797
Climatherm PP-R Faser SDR7.4/SDR11
Diameter (mm) | Wanddikte (mm) | Binnendiam. (mm) | Omgevingstemp. (°C) | Medium temp. (°C) | Delta T (°C) | Alfa water (W/m2°C) | Alfa lucht (W/m2°C) | Lambda Staal (W/m°C) | 1/(alfaWxd1) | 1/(alfaLxd2) | 1/(2xLambda)xLn(d2/d1) | Dikte Isolatie (mm) | Lambda Isolatie (W/m°C) | 1/(2xLambda)xLn(d2/d1) | Axk=pi/(H+I+J+M) | Q = (W/mtr) | Delta T = Q/(1/(Alfa2xd2)) | Temp. buiswand (°C)
20 | 2.8 | 14.4 | 23 | 5 | 18 | 1000 | 15 | 0.15 | 0.069444 | 3.3333 | 1.095 | 0 | 0.025 | 0 | 0.69847 | 12.5725 | 13.3398 | 9.6602
25 | 3.5 | 18 | 23 | 5 | 18 | 1000 | 15 | 0.15 | 0.055556 | 2.6667 | 1.095 | 0 | 0.025 | 0 | 0.823 | 14.814 | 12.5745 | 10.4255
32 | 2.9 | 26.2 | 23 | 5 | 18 | 1000 | 15 | 0.15 | 0.038168 | 2.0833 | 0.66659 | 0 | 0.025 | 0 | 1.1268 | 20.2822 | 13.45 | 9.55
40 | 3.7 | 32.6 | 23 | 5 | 18 | 1000 | 15 | 0.15 | 0.030675 | 1.6667 | 0.68189 | 0 | 0.025 | 0 | 1.3204 | 23.7676 | 12.6091 | 10.3909
50 | 4.6 | 40.8 | 23 | 5 | 18 | 1000 | 15 | 0.15 | 0.02451 | 1.3333 | 0.6778 | 0 | 0.025 | 0 | 1.5433 | 27.7792 | 11.7898 | 11.2102
63 | 5.8 | 51.4 | 23 | 5 | 18 | 1000 | 15 | 0.15 | 0.019455 | 1.0582 | 0.67832 | 0 | 0.025 | 0 | 1.7891 | 32.2035 | 10.8473 | 12.1527
75 | 6.8 | 61.4 | 23 | 5 | 18 | 1000 | 15 | 0.15 | 0.016287 | 0.88889 | 0.66693 | 0 | 0.025 | 0 | 1.9983 | 35.97 | 10.1774 | 12.8226
90 | 8.2 | 73.6 | 23 | 5 | 18 | 1000 | 15 | 0.15 | 0.013587 | 0.74074 | 0.67055 | 0 | 0.025 | 0 | 2.2048 | 39.6867 | 9.3575 | 13.6425
110 | 10 | 90 | 23 | 5 | 18 | 1000 | 15 | 0.15 | 0.011111 | 0.60606 | 0.6689 | 0 | 0.025 | 0 | 2.4428 | 43.97 | 8.4824 | 14.5176
125 | 11.4 | 102.2 | 23 | 5 | 18 | 1000 | 15 | 0.15 | 0.0097847 | 0.53333 | 0.67127 | 0 | 0.025 | 0 | 2.587 | 46.5654 | 7.9052 | 15.0948
160 | 14.6 | 130.8 | 23 | 5 | 18 | 1000 | 15 | 0.15 | 0.0076453 | 0.41667 | 0.67168 | 0 | 0.025 | 0 | 2.8664 | 51.5958 | 6.8431 | 16.1569
200 | 18.2 | 163.6 | 23 | 5 | 18 | 1000 | 15 | 0.15 | 0.0061125 | 0.33333 | 0.66964 | 0 | 0.025 | 0 | 3.1133 | 56.0393 | 5.9459 | 17.0541
250 | 22.7 | 204.6 | 23 | 5 | 18 | 1000 | 15 | 0.15 | 0.0048876 | 0.26667 | 0.66801 | 0 | 0.025 | 0 | 3.3437 | 60.1858 | 5.1087 | 17.8913
315 | 28.6 | 257.8 | 23 | 5 | 18 | 1001 | 15 | 0.15 | 0.0038751 | 0.21164 | 0.66796 | 0 | 0.025 | 0 | 3.5559 | 64.0069 | 4.312 | 18.688
355 | 32.2 | 290.6 | 23 | 5 | 18 | 1002 | 15 | 0.15 | 0.0034343 | 0.18779 | 0.66723 | 0 | 0.025 | 0 | 3.6596 | 65.8721 | 3.9376 | 19.0624
400 | 36.3 | 327.4 | 23 | 5 | 18 | 1003 | 15 | 0.15 | 0.0030452 | 0.16667 | 0.66761 | 0 | 0.025 | 0 | 3.752 | 67.5354 | 3.5829 | 19.4171
450 | 40.9 | 368.2 | 23 | 5 | 18 | 1004 | 15 | 0.15 | 0.0027051 | 0.14815 | 0.66874 | 0 | 0.025 | 0 | 3.8331 | 68.9961 | 3.2536 | 19.7464
Climatherm PP-R Faser SDR17.6
Diameter (mm) | Wanddikte (mm) | Binnendiam. (mm) | Omgevingstemp. (°C) | Medium temp. (°C) | Delta T (°C) | Alfa water (W/m2°C) | Alfa lucht (W/m2°C) | Lambda Staal (W/m°C) | 1/(alfaWxd1) | 1/(alfaLxd2) | 1/(2xLambda)xLn(d2/d1) | Dikte Isolatie (mm) | Lambda Isolatie (W/m°C) | 1/(2xLambda)xLn(d2/d1) | Axk=pi/(H+I+J+M) | Q = (W/mtr) | Delta T = Q/(1/(Alfa2xd2)) | Temp. buiswand (°C)
160 | 9.1 | 141.8 | 23 | 5 | 18 | 1000 | 15 | 0.15 | 0.0070522 | 0.41667 | 0.40252 | 0 | 0.025 | 0 | 3.8023 | 68.441 | 9.0772 | 13.9228
200 | 11.4 | 177.2 | 23 | 5 | 18 | 1000 | 15 | 0.15 | 0.0056433 | 0.33333 | 0.40346 | 0 | 0.025 | 0 | 4.2315 | 76.1661 | 8.0815 | 14.9185
250 | 14.2 | 221.6 | 23 | 5 | 18 | 1000 | 15 | 0.15 | 0.0045126 | 0.26667 | 0.40196 | 0 | 0.025 | 0 | 4.6671 | 84.0077 | 7.1308 | 15.8692
315 | 17.9 | 279.2 | 23 | 5 | 18 | 1000 | 15 | 0.15 | 0.0035817 | 0.21164 | 0.40215 | 0 | 0.025 | 0 | 5.0887 | 91.5961 | 6.1706 | 16.8294
355 | 20.1 | 314.8 | 23 | 5 | 18 | 1000 | 15 | 0.15 | 0.0031766 | 0.18779 | 0.4006 | 0 | 0.025 | 0 | 5.3106 | 95.5906 | 5.7141 | 17.2859
400 | 22.7 | 354.6 | 23 | 5 | 18 | 1000 | 15 | 0.15 | 0.0028201 | 0.16667 | 0.40158 | 0 | 0.025 | 0 | 5.5013 | 99.0227 | 5.2533 | 17.7467
450 | 25.5 | 399 | 23 | 5 | 18 | 1000 | 15 | 0.15 | 0.0025063 | 0.14815 | 0.40095 | 0 | 0.025 | 0 | 5.6953 | 102.5159 | 4.8343 | 18.1657
500 | 28.4 | 443.2 | 23 | 5 | 18 | 1000 | 15 | 0.15 | 0.0022563 | 0.13333 | 0.40196 | 0 | 0.025 | 0 | 5.8443 | 105.1977 | 4.4647 | 18.5353
560 | 31.7 | 496.6 | 23 | 5 | 18 | 1000 | 15 | 0.15 | 0.0020137 | 0.11905 | 0.40051 | 0 | 0.025 | 0 | 6.0234 | 108.4205 | 4.1085 | 18.8915
630 | 35.7 | 558.6 | 23 | 5 | 18 | 1000 | 15 | 0.15 | 0.0017902 | 0.10582 | 0.40095 | 0 | 0.025 | 0 | 6.1774 | 111.1927 | 3.7454 | 19.2546
Seamless Steel
Diameter (mm) | Wanddikte (mm) | Binnendiam. (mm) | Omgevingstemp. (°C) | Medium temp. (°C) | Delta T (°C) | Alfa water (W/m2°C) | Alfa lucht (W/m2°C) | Lambda Staal (W/m°C) | 1/(alfaWxd1) | 1/(alfaLxd2) | 1/(2xLambda)xLn(d2/d1) | Dikte Isolatie (mm) | Lambda Isolatie (W/m°C) | 1/(2xLambda)xLn(d2/d1) | Axk=pi/(H+I+J+M) | Q = (W/mtr) | Delta T = Q/(1/(Alfa2xd2)) | Temp. buiswand (°C)
21.3 | 2 | 17.3 | 23 | 5 | 18 | 1000 | 15 | 50 | 0.057803 | 3.1299 | 0.00208 | 0 | 0.025 | 0 | 0.98489 | 17.7281 | 17.662 | 5.338
26.9 | 2.3 | 22.3 | 23 | 5 | 18 | 1000 | 15 | 50 | 0.044843 | 2.4783 | 0.0018754 | 0 | 0.025 | 0 | 1.2442 | 22.3952 | 17.6669 | 5.3331
33.7 | 2.6 | 28.5 | 23 | 5 | 18 | 1000 | 15 | 50 | 0.035088 | 1.9782 | 0.0016759 | 0 | 0.025 | 0 | 1.5591 | 28.0638 | 17.6715 | 5.3285
42.4 | 2.6 | 37.2 | 23 | 5 | 18 | 1000 | 15 | 50 | 0.026882 | 1.5723 | 0.0013084 | 0 | 0.025 | 0 | 1.9629 | 35.3315 | 17.6829 | 5.3171
48.3 | 2.6 | 43.1 | 23 | 5 | 18 | 1000 | 15 | 50 | 0.023202 | 1.3803 | 0.0011391 | 0 | 0.025 | 0 | 2.2366 | 40.2595 | 17.688 | 5.312
60.3 | 2.9 | 54.5 | 23 | 5 | 18 | 1000 | 15 | 50 | 0.018349 | 1.1056 | 0.0010113 | 0 | 0.025 | 0 | 2.7927 | 50.268 | 17.6902 | 5.3098
76.1 | 2.9 | 70.3 | 23 | 5 | 18 | 1000 | 15 | 50 | 0.014225 | 0.87604 | 0.00079276 | 0 | 0.025 | 0 | 3.5257 | 63.4623 | 17.6966 | 5.3034
88.9 | 3.2 | 82.5 | 23 | 5 | 18 | 1000 | 15 | 50 | 0.012121 | 0.74991 | 0.00074714 | 0 | 0.025 | 0 | 4.1186 | 74.1354 | 17.6963 | 5.3037
114.3 | 3.6 | 107.1 | 23 | 5 | 18 | 1000 | 15 | 50 | 0.0093371 | 0.58326 | 0.00065064 | 0 | 0.025 | 0 | 5.2956 | 95.3204 | 17.6969 | 5.3031
127 | 4 | 119 | 23 | 5 | 18 | 1001 | 15 | 50 | 0.008395 | 0.52493 | 0.00065064 | 0 | 0.025 | 0 | 5.8833 | 105.9003 | 17.695 | 5.305
168.3 | 4.5 | 159.3 | 23 | 5 | 18 | 1002 | 15 | 50 | 0.0062649 | 0.39612 | 0.00054959 | 0 | 0.025 | 0 | 7.7968 | 140.3426 | 17.6955 | 5.3045
219.1 | 5.9 | 207.3 | 23 | 5 | 18 | 1003 | 15 | 50 | 0.0048095 | 0.30428 | 0.00055361 | 0 | 0.025 | 0 | 10.146 | 182.6281 | 17.6882 | 5.3118
273 | 6.3 | 260.4 | 23 | 5 | 18 | 1004 | 15 | 50 | 0.0038249 | 0.2442 | 0.00047253 | 0 | 0.025 | 0 | 12.6423 | 227.5619 | 17.6887 | 5.3113
323.9 | 7.1 | 309.7 | 23 | 5 | 18 | 1005 | 15 | 50 | 0.0032129 | 0.20582 | 0.00044831 | 0 | 0.025 | 0 | 14.9967 | 269.9398 | 17.6854 | 5.3146
355.6 | 8 | 339.6 | 23 | 5 | 18 | 1006 | 15 | 50 | 0.0029271 | 0.18748 | 0.00046038 | 0 | 0.025 | 0 | 16.4598 | 296.277 | 17.6805 | 5.3195
406.4 | 8.8 | 388.8 | 23 | 5 | 18 | 1007 | 15 | 50 | 0.0025541 | 0.16404 | 0.00044273 | 0 | 0.025 | 0 | 18.8075 | 338.5357 | 17.677 | 5.323
457 | 10 | 437 | 23 | 5 | 18 | 1008 | 15 | 50 | 0.0022702 | 0.14588 | 0.0004475 | 0 | 0.025 | 0 | 21.1417 | 380.5513 | 17.6707 | 5.3293
508 | 11 | 486 | 23 | 5 | 18 | 1009 | 15 | 50 | 0.0020393 | 0.13123 | 0.00044273 | 0 | 0.025 | 0 | 23.4946 | 422.9022 | 17.6658 | 5.3342
559 | 12.5 | 534 | 23 | 5 | 18 | 1010 | 15 | 50 | 0.0018541 | 0.11926 | 0.00045754 | 0 | 0.025 | 0 | 25.8413 | 465.1442 | 17.6577 | 5.3423
610 | 12.5 | 585 | 23 | 5 | 18 | 1011 | 15 | 50 | 0.0016908 | 0.10929 | 0.00041847 | 0 | 0.025 | 0 | 28.2013 | 507.6228 | 17.6591 | 5.3409
Copper
Diameter (mm) | Wanddikte (mm) | Binnendiam. (mm) | Omgevingstemp. (°C) | Medium temp. (°C) | Delta T (°C) | Alfa water (W/m2°C) | Alfa lucht (W/m2°C) | Lambda Copper (W/m°C) | 1/(alfaWxd1) | 1/(alfaLxd2) | 1/(2xLambda)xLn(d2/d1) | Dikte Isolatie (mm) | Lambda Isolatie (W/m°C) | 1/(2xLambda)xLn(d2/d1) | Axk=pi/(H+I+J+M) | Q = (W/mtr) | Delta T = Q/(1/(Alfa2xd2)) | Temp. buiswand (°C)
19.1 | 1 | 17.1 | 23 | 5 | 18 | 1000 | 15 | 384 | 0.05848 | 3.4904 | 0.00014402 | 0 | 0.025 | 0 | 0.8852 | 15.9336 | 17.7026 | 5.2974
25.4 | 1.2 | 23 | 23 | 5 | 18 | 1000 | 15 | 384 | 0.043478 | 2.6247 | 0.00012924 | 0 | 0.025 | 0 | 1.1774 | 21.1929 | 17.7058 | 5.2942
31.8 | 1.2 | 29.4 | 23 | 5 | 18 | 1000 | 15 | 384 | 0.034014 | 2.0964 | 0.00010218 | 0 | 0.025 | 0 | 1.4745 | 26.5418 | 17.7117 | 5.2883
38.1 | 1.2 | 35.7 | 23 | 5 | 18 | 1000 | 15 | 384 | 0.028011 | 1.7498 | 8.4718e-05 | 0 | 0.025 | 0 | 1.767 | 31.8068 | 17.7155 | 5.2845
50.8 | 1.2 | 48.4 | 23 | 5 | 18 | 1000 | 15 | 384 | 0.020661 | 1.3123 | 6.3016e-05 | 0 | 0.025 | 0 | 2.3567 | 42.4202 | 17.7201 | 5.2799
63.5 | 1.2 | 61.1 | 23 | 5 | 18 | 1000 | 15 | 384 | 0.016367 | 1.0499 | 5.0167e-05 | 0 | 0.025 | 0 | 2.9463 | 53.0333 | 17.7228 | 5.2772
76.2 | 1.6 | 73 | 23 | 5 | 18 | 1000 | 15 | 384 | 0.013699 | 0.87489 | 5.5862e-05 | 0 | 0.025 | 0 | 3.5353 | 63.6346 | 17.7213 | 5.2787
88.9 | 1.6 | 85.7 | 23 | 5 | 18 | 1000 | 15 | 384 | 0.011669 | 0.74991 | 4.7733e-05 | 0 | 0.025 | 0 | 4.1249 | 74.2476 | 17.723 | 5.277
101.6 | 1.6 | 98.4 | 23 | 5 | 18 | 1000 | 15 | 384 | 0.010163 | 0.65617 | 4.167e-05 | 0 | 0.025 | 0 | 4.7145 | 84.8604 | 17.7243 | 5.2757
127 | 1.6 | 123.8 | 23 | 5 | 18 | 1001 | 15 | 384 | 0.0080695 | 0.52493 | 3.3229e-05 | 0 | 0.025 | 0 | 5.8938 | 106.0876 | 17.7263 | 5.2737
152.4 | 2 | 148.4 | 23 | 5 | 18 | 1002 | 15 | 384 | 0.0067251 | 0.43745 | 3.4632e-05 | 0 | 0.025 | 0 | 7.0724 | 127.303 | 17.726 | 5.274
203.2 | 2 | 199.2 | 23 | 5 | 18 | 1003 | 15 | 384 | 0.0050051 | 0.32808 | 2.5887e-05 | 0 | 0.025 | 0 | 9.4309 | 169.7571 | 17.7281 | 5.2719

## Fus20
|  |  | buis | verlies W/M | L /°C/sec
diam | wandikte |  | inhoud l/m |  | W/M
20 | 2.8 | 3.1416 | 0.16286 | 11.8741 | 4187
[8 empty] | J/sec/mtr | aantal mtr. | verlies
|  | buis | verlies W/M | L /°C/sec | verlies temp | begintemp | eindtemp | verlies | bij 1°C | totaal J/sec
|  | inhoud L |  | W/M | °C per M | °C | °C | per m°C | daling | aantal mtr
1 | 20 | 0.16286 | 11.8741 | 4187 | 0.017413 | 6 | 6.0174 | -0.69847 | 57.4273 | 11.8741 | -0.012163
2 |  | 0.16286 | 11.8619 | 4187 | 0.017395 | 6.0174 | 6.0348 | -0.69847 | 57.4862 | 23.736 | -0.01215
3 |  | 0.16286 | 11.8497 | 4187 | 0.017378 | 6.0348 | 6.0522 | -0.69847 | 57.5452 | 35.5857 | -0.012138
4 |  | 0.16286 | 11.8376 | 4187 | 0.01736 | 6.0522 | 6.0695 | -0.69847 | 57.6042 | 47.4233 | -0.012125
5 |  | 0.16286 | 11.8255 | 4187 | 0.017342 | 6.0695 | 6.0869 | -0.69847 | 57.6632 | 59.2488 | -0.012113
6 |  | 0.16286 | 11.8134 | 4187 | 0.017324 | 6.0869 | 6.1042 | -0.69847 | 57.7224 | 71.0621 | -0.012101
7 |  | 0.16286 | 11.8013 | 4187 | 0.017307 | 6.1042 | 6.1215 | -0.69847 | 57.7816 | 82.8634 | -0.012088
8 |  | 0.16286 | 11.7892 | 4187 | 0.017289 | 6.1215 | 6.1388 | -0.69847 | 57.8408 | 94.6526 | -0.012076
9 |  | 0.16286 | 11.7771 | 4187 | 0.017271 | 6.1388 | 6.1561 | -0.69847 | 57.9001 | 106.4297 | -0.012063
10 |  | 0.16286 | 11.765 | 4187 | 0.017253 | 6.1561 | 6.1733 | -0.69847 | 57.9595 | 118.1947 | -0.012051
11 |  | 0.16286 | 11.753 | 4187 | 0.017236 | 6.1733 | 6.1906 | -0.69847 | 58.0189 | 129.9477 | -0.012039
12 |  | 0.16286 | 11.7409 | 4187 | 0.017218 | 6.1906 | 6.2078 | -0.69847 | 58.0784 | 141.6887 | -0.012026
13 |  | 0.16286 | 11.7289 | 4187 | 0.0172 | 6.2078 | 6.225 | -0.69847 | 58.1379 | 153.4176 | -0.012014
14 |  | 0.16286 | 11.7169 | 4187 | 0.017183 | 6.225 | 6.2422 | -0.69847 | 58.1976 | 165.1345 | -0.012002
15 |  | 0.16286 | 11.7049 | 4187 | 0.017165 | 6.2422 | 6.2593 | -0.69847 | 58.2572 | 176.8394 | -0.011989
16 |  | 0.16286 | 11.6929 | 4187 | 0.017148 | 6.2593 | 6.2765 | -0.69847 | 58.317 | 188.5323 | -0.011977
17 |  | 0.16286 | 11.6809 | 4187 | 0.01713 | 6.2765 | 6.2936 | -0.69847 | 58.3768 | 200.2133 | -0.011965
18 |  | 0.16286 | 11.669 | 4187 | 0.017113 | 6.2936 | 6.3107 | -0.69847 | 58.4366 | 211.8823 | -0.011953
19 |  | 0.16286 | 11.657 | 4187 | 0.017095 | 6.3107 | 6.3278 | -0.69847 | 58.4965 | 223.5393 | -0.01194
20 |  | 0.16286 | 11.6451 | 4187 | 0.017078 | 6.3278 | 6.3449 | -0.69847 | 58.5565 | 235.1844 | -0.011928
21 |  | 0.16286 | 11.6332 | 4187 | 0.01706 | 6.3449 | 6.362 | -0.69847 | 58.6166 | 246.8175 | -0.011916
22 |  | 0.16286 | 11.6212 | 4187 | 0.017043 | 6.362 | 6.379 | -0.69847 | 58.6767 | 258.4388 | -0.011904
23 |  | 0.16286 | 11.6093 | 4187 | 0.017025 | 6.379 | 6.396 | -0.69847 | 58.7368 | 270.0481 | -0.011892
24 |  | 0.16286 | 11.5974 | 4187 | 0.017008 | 6.396 | 6.413 | -0.69847 | 58.7971 | 281.6455 | -0.011879
25 |  | 0.16286 | 11.5856 | 4187 | 0.01699 | 6.413 | 6.43 | -0.69847 | 58.8573 | 293.2311 | -0.011867
26 |  | 0.16286 | 11.5737 | 4187 | 0.016973 | 6.43 | 6.447 | -0.69847 | 58.9177 | 304.8048 | -0.011855
27 |  | 0.16286 | 11.5618 | 4187 | 0.016955 | 6.447 | 6.464 | -0.69847 | 58.9781 | 316.3666 | -0.011843
28 |  | 0.16286 | 11.55 | 4187 | 0.016938 | 6.464 | 6.4809 | -0.69847 | 59.0386 | 327.9166 | -0.011831
29 |  | 0.16286 | 11.5382 | 4187 | 0.016921 | 6.4809 | 6.4978 | -0.69847 | 59.0991 | 339.4548 | -0.011819
30 |  | 0.16286 | 11.5263 | 4187 | 0.016903 | 6.4978 | 6.5147 | -0.69847 | 59.1597 | 350.9811 | -0.011807
31 |  | 0.16286 | 11.5145 | 4187 | 0.016886 | 6.5147 | 6.5316 | -0.69847 | 59.2204 | 362.4957 | -0.011794
32 |  | 0.16286 | 11.5027 | 4187 | 0.016869 | 6.5316 | 6.5485 | -0.69847 | 59.2811 | 373.9984 | -0.011782
33 |  | 0.16286 | 11.491 | 4187 | 0.016852 | 6.5485 | 6.5653 | -0.69847 | 59.3419 | 385.4894 | -0.01177
34 |  | 0.16286 | 11.4792 | 4187 | 0.016834 | 6.5653 | 6.5822 | -0.69847 | 59.4027 | 396.9686 | -0.011758
35 |  | 0.16286 | 11.4674 | 4187 | 0.016817 | 6.5822 | 6.599 | -0.69847 | 59.4636 | 408.436 | -0.011746
36 |  | 0.16286 | 11.4557 | 4187 | 0.0168 | 6.599 | 6.6158 | -0.69847 | 59.5246 | 419.8917 | -0.011734
37 |  | 0.16286 | 11.444 | 4187 | 0.016783 | 6.6158 | 6.6326 | -0.69847 | 59.5856 | 431.3357 | -0.011722
38 |  | 0.16286 | 11.4322 | 4187 | 0.016765 | 6.6326 | 6.6493 | -0.69847 | 59.6467 | 442.7679 | -0.01171
39 |  | 0.16286 | 11.4205 | 4187 | 0.016748 | 6.6493 | 6.6661 | -0.69847 | 59.7079 | 454.1884 | -0.011698
40 |  | 0.16286 | 11.4088 | 4187 | 0.016731 | 6.6661 | 6.6828 | -0.69847 | 59.7691 | 465.5973 | -0.011686
41 |  | 0.16286 | 11.3971 | 4187 | 0.016714 | 6.6828 | 6.6995 | -0.69847 | 59.8304 | 476.9944 | -0.011674
42 |  | 0.16286 | 11.3855 | 4187 | 0.016697 | 6.6995 | 6.7162 | -0.69847 | 59.8918 | 488.3799 | -0.011662
43 |  | 0.16286 | 11.3738 | 4187 | 0.01668 | 6.7162 | 6.7329 | -0.69847 | 59.9532 | 499.7537 | -0.01165
44 |  | 0.16286 | 11.3622 | 4187 | 0.016663 | 6.7329 | 6.7496 | -0.69847 | 60.0146 | 511.1158 | -0.011638
45 |  | 0.16286 | 11.3505 | 4187 | 0.016646 | 6.7496 | 6.7662 | -0.69847 | 60.0762 | 522.4663 | -0.011626
46 |  | 0.16286 | 11.3389 | 4187 | 0.016628 | 6.7662 | 6.7828 | -0.69847 | 60.1378 | 533.8052 | -0.011615
47 |  | 0.16286 | 11.3273 | 4187 | 0.016611 | 6.7828 | 6.7994 | -0.69847 | 60.1994 | 545.1325 | -0.011603
48 |  | 0.16286 | 11.3157 | 4187 | 0.016594 | 6.7994 | 6.816 | -0.69847 | 60.2612 | 556.4482 | -0.011591
49 |  | 0.16286 | 11.3041 | 4187 | 0.016577 | 6.816 | 6.8326 | -0.69847 | 60.323 | 567.7523 | -0.011579
50 |  | 0.16286 | 11.2925 | 4187 | 0.01656 | 6.8326 | 6.8492 | -0.69847 | 60.3848 | 579.0448 | -0.011567
51 |  | 0.16286 | 11.2809 | 4187 | 0.016543 | 6.8492 | 6.8657 | -0.69847 | 60.4467 | 590.3257 | -0.011555
52 |  | 0.16286 | 11.2694 | 4187 | 0.016527 | 6.8657 | 6.8822 | -0.69847 | 60.5087 | 601.5951 | -0.011543
53 |  | 0.16286 | 11.2578 | 4187 | 0.01651 | 6.8822 | 6.8987 | -0.69847 | 60.5707 | 612.8529 | -0.011532
54 |  | 0.16286 | 11.2463 | 4187 | 0.016493 | 6.8987 | 6.9152 | -0.69847 | 60.6329 | 624.0992 | -0.01152
55 |  | 0.16286 | 11.2348 | 4187 | 0.016476 | 6.9152 | 6.9317 | -0.69847 | 60.695 | 635.334 | -0.011508
56 |  | 0.16286 | 11.2233 | 4187 | 0.016459 | 6.9317 | 6.9482 | -0.69847 | 60.7573 | 646.5573 | -0.011496
57 |  | 0.16286 | 11.2118 | 4187 | 0.016442 | 6.9482 | 6.9646 | -0.69847 | 60.8196 | 657.7691 | -0.011484
58 |  | 0.16286 | 11.2003 | 4187 | 0.016425 | 6.9646 | 6.981 | -0.69847 | 60.8819 | 668.9693 | -0.011473
59 |  | 0.16286 | 11.1888 | 4187 | 0.016408 | 6.981 | 6.9975 | -0.69847 | 60.9443 | 680.1582 | -0.011461
60 |  | 0.16286 | 11.1774 | 4187 | 0.016392 | 6.9975 | 7.0138 | -0.69847 | 61.0068 | 691.3355 | -0.011449
61 |  | 0.16286 | 11.1659 | 4187 | 0.016375 | 7.0138 | 7.0302 | -0.69847 | 61.0694 | 702.5014 | -0.011437
62 |  | 0.16286 | 11.1545 | 4187 | 0.016358 | 7.0302 | 7.0466 | -0.69847 | 61.132 | 713.6559 | -0.011426
63 |  | 0.16286 | 11.1431 | 4187 | 0.016341 | 7.0466 | 7.0629 | -0.69847 | 61.1947 | 724.799 | -0.011414
64 |  | 0.16286 | 11.1316 | 4187 | 0.016325 | 7.0629 | 7.0792 | -0.69847 | 61.2574 | 735.9306 | -0.011402
65 |  | 0.16286 | 11.1202 | 4187 | 0.016308 | 7.0792 | 7.0956 | -0.69847 | 61.3202 | 747.0508 | -0.011391
66 |  | 0.16286 | 11.1088 | 4187 | 0.016291 | 7.0956 | 7.1118 | -0.69847 | 61.3831 | 758.1597 | -0.011379
67 |  | 0.16286 | 11.0975 | 4187 | 0.016274 | 7.1118 | 7.1281 | -0.69847 | 61.4461 | 769.2572 | -0.011367
68 |  | 0.16286 | 11.0861 | 4187 | 0.016258 | 7.1281 | 7.1444 | -0.69847 | 61.5091 | 780.3432 | -0.011356
69 |  | 0.16286 | 11.0747 | 4187 | 0.016241 | 7.1444 | 7.1606 | -0.69847 | 61.5721 | 791.418 | -0.011344
70 |  | 0.16286 | 11.0634 | 4187 | 0.016224 | 7.1606 | 7.1768 | -0.69847 | 61.6353 | 802.4814 | -0.011332
71 |  | 0.16286 | 11.0521 | 4187 | 0.016208 | 7.1768 | 7.193 | -0.69847 | 61.6985 | 813.5335 | -0.011321
72 |  | 0.16286 | 11.0407 | 4187 | 0.016191 | 7.193 | 7.2092 | -0.69847 | 61.7617 | 824.5742 | -0.011309
73 |  | 0.16286 | 11.0294 | 4187 | 0.016175 | 7.2092 | 7.2254 | -0.69847 | 61.8251 | 835.6036 | -0.011298
74 |  | 0.16286 | 11.0181 | 4187 | 0.016158 | 7.2254 | 7.2416 | -0.69847 | 61.8885 | 846.6218 | -0.011286
75 |  | 0.16286 | 11.0069 | 4187 | 0.016142 | 7.2416 | 7.2577 | -0.69847 | 61.9519 | 857.6286 | -0.011274
76 |  | 0.16286 | 10.9956 | 4187 | 0.016125 | 7.2577 | 7.2738 | -0.69847 | 62.0154 | 868.6242 | -0.011263
77 |  | 0.16286 | 10.9843 | 4187 | 0.016109 | 7.2738 | 7.2899 | -0.69847 | 62.079 | 879.6085 | -0.011251
78 |  | 0.16286 | 10.9731 | 4187 | 0.016092 | 7.2899 | 7.306 | -0.69847 | 62.1427 | 890.5816 | -0.01124
79 |  | 0.16286 | 10.9618 | 4187 | 0.016076 | 7.306 | 7.3221 | -0.69847 | 62.2064 | 901.5434 | -0.011228
80 |  | 0.16286 | 10.9506 | 4187 | 0.016059 | 7.3221 | 7.3382 | -0.69847 | 62.2702 | 912.494 | -0.011217
81 |  | 0.16286 | 10.9394 | 4187 | 0.016043 | 7.3382 | 7.3542 | -0.69847 | 62.334 | 923.4334 | -0.011205
82 |  | 0.16286 | 10.9282 | 4187 | 0.016026 | 7.3542 | 7.3702 | -0.69847 | 62.3979 | 934.3615 | -0.011194
83 |  | 0.16286 | 10.917 | 4187 | 0.01601 | 7.3702 | 7.3863 | -0.69847 | 62.4619 | 945.2785 | -0.011182
84 |  | 0.16286 | 10.9058 | 4187 | 0.015993 | 7.3863 | 7.4022 | -0.69847 | 62.526 | 956.1843 | -0.011171
85 |  | 0.16286 | 10.8946 | 4187 | 0.015977 | 7.4022 | 7.4182 | -0.69847 | 62.5901 | 967.0789 | -0.011159
86 |  | 0.16286 | 10.8835 | 4187 | 0.015961 | 7.4182 | 7.4342 | -0.69847 | 62.6543 | 977.9624 | -0.011148
87 |  | 0.16286 | 10.8723 | 4187 | 0.015944 | 7.4342 | 7.4501 | -0.69847 | 62.7185 | 988.8347 | -0.011137
88 |  | 0.16286 | 10.8612 | 4187 | 0.015928 | 7.4501 | 7.4661 | -0.69847 | 62.7828 | 999.6959 | -0.011125
89 |  | 0.16286 | 10.8501 | 4187 | 0.015912 | 7.4661 | 7.482 | -0.69847 | 62.8472 | 1010.546 | -0.011114
90 |  | 0.16286 | 10.8389 | 4187 | 0.015895 | 7.482 | 7.4979 | -0.69847 | 62.9116 | 1021.3849 | -0.011102
91 |  | 0.16286 | 10.8278 | 4187 | 0.015879 | 7.4979 | 7.5137 | -0.69847 | 62.9761 | 1032.2128 | -0.011091
92 |  | 0.16286 | 10.8167 | 4187 | 0.015863 | 7.5137 | 7.5296 | -0.69847 | 63.0407 | 1043.0295 | -0.01108
93 |  | 0.16286 | 10.8057 | 4187 | 0.015847 | 7.5296 | 7.5454 | -0.69847 | 63.1053 | 1053.8352 | -0.011068
94 |  | 0.16286 | 10.7946 | 4187 | 0.01583 | 7.5454 | 7.5613 | -0.69847 | 63.1701 | 1064.6298 | -0.011057
95 |  | 0.16286 | 10.7835 | 4187 | 0.015814 | 7.5613 | 7.5771 | -0.69847 | 63.2348 | 1075.4133 | -0.011046
96 |  | 0.16286 | 10.7725 | 4187 | 0.015798 | 7.5771 | 7.5929 | -0.69847 | 63.2997 | 1086.1858 | -0.011034
97 |  | 0.16286 | 10.7615 | 4187 | 0.015782 | 7.5929 | 7.6087 | -0.69847 | 63.3646 | 1096.9473 | -0.011023
98 |  | 0.16286 | 10.7504 | 4187 | 0.015766 | 7.6087 | 7.6244 | -0.69847 | 63.4295 | 1107.6977 | -0.011012
99 |  | 0.16286 | 10.7394 | 4187 | 0.015749 | 7.6244 | 7.6402 | -0.69847 | 63.4946 | 1118.4371 | -0.011001
100 |  | 0.16286 | 10.7284 | 4187 | 0.015733 | 7.6402 | 7.6559 | -0.69847 | 63.5597 | 1129.1656 | -0.010989
101 |  | 0.16286 | 10.7174 | 4187 | 0.015717 | 7.6559 | 7.6716 | -0.69847 | 63.6249 | 1139.883 | -0.010978
102 |  | 0.16286 | 10.7065 | 4187 | 0.015701 | 7.6716 | 7.6873 | -0.69847 | 63.6901 | 1150.5895 | -0.010967
103 |  | 0.16286 | 10.6955 | 4187 | 0.015685 | 7.6873 | 7.703 | -0.69847 | 63.7554 | 1161.285 | -0.010956
104 |  | 0.16286 | 10.6845 | 4187 | 0.015669 | 7.703 | 7.7187 | -0.69847 | 63.8208 | 1171.9695 | -0.010944
105 |  | 0.16286 | 10.6736 | 4187 | 0.015653 | 7.7187 | 7.7343 | -0.69847 | 63.8862 | 1182.6431 | -0.010933
106 |  | 0.16286 | 10.6627 | 4187 | 0.015637 | 7.7343 | 7.75 | -0.69847 | 63.9517 | 1193.3058 | -0.010922
107 |  | 0.16286 | 10.6517 | 4187 | 0.015621 | 7.75 | 7.7656 | -0.69847 | 64.0173 | 1203.9575 | -0.010911
108 |  | 0.16286 | 10.6408 | 4187 | 0.015605 | 7.7656 | 7.7812 | -0.69847 | 64.0829 | 1214.5983 | -0.0109
109 |  | 0.16286 | 10.6299 | 4187 | 0.015589 | 7.7812 | 7.7968 | -0.69847 | 64.1486 | 1225.2283 | -0.010888
110 |  | 0.16286 | 10.619 | 4187 | 0.015573 | 7.7968 | 7.8124 | -0.69847 | 64.2144 | 1235.8473 | -0.010877
111 |  | 0.16286 | 10.6082 | 4187 | 0.015557 | 7.8124 | 7.8279 | -0.69847 | 64.2803 | 1246.4555 | -0.010866
112 |  | 0.16286 | 10.5973 | 4187 | 0.015541 | 7.8279 | 7.8435 | -0.69847 | 64.3462 | 1257.0528 | -0.010855
113 |  | 0.16286 | 10.5864 | 4187 | 0.015525 | 7.8435 | 7.859 | -0.69847 | 64.4121 | 1267.6392 | -0.010844
114 |  | 0.16286 | 10.5756 | 4187 | 0.015509 | 7.859 | 7.8745 | -0.69847 | 64.4782 | 1278.2148 | -0.010833
115 |  | 0.16286 | 10.5648 | 4187 | 0.015493 | 7.8745 | 7.89 | -0.69847 | 64.5443 | 1288.7796 | -0.010822
116 |  | 0.16286 | 10.5539 | 4187 | 0.015477 | 7.89 | 7.9055 | -0.69847 | 64.6105 | 1299.3335 | -0.010811
117 |  | 0.16286 | 10.5431 | 4187 | 0.015462 | 7.9055 | 7.9209 | -0.69847 | 64.6767 | 1309.8766 | -0.010799
118 |  | 0.16286 | 10.5323 | 4187 | 0.015446 | 7.9209 | 7.9364 | -0.69847 | 64.7431 | 1320.409 | -0.010788
119 |  | 0.16286 | 10.5215 | 4187 | 0.01543 | 7.9364 | 7.9518 | -0.69847 | 64.8094 | 1330.9305 | -0.010777
120 |  | 0.16286 | 10.5108 | 4187 | 0.015414 | 7.9518 | 7.9672 | -0.69847 | 64.8759 | 1341.4413 | -0.010766
121 |  | 0.16286 | 10.5 | 4187 | 0.015398 | 7.9672 | 7.9826 | -0.69847 | 64.9424 | 1351.9413 | -0.010755
122 |  | 0.16286 | 10.4892 | 4187 | 0.015382 | 7.9826 | 7.998 | -0.69847 | 65.009 | 1362.4305 | -0.010744
123 |  | 0.16286 | 10.4785 | 4187 | 0.015367 | 7.998 | 8.0134 | -0.69847 | 65.0757 | 1372.909 | -0.010733
124 |  | 0.16286 | 10.4678 | 4187 | 0.015351 | 8.0134 | 8.0287 | -0.69847 | 65.1424 | 1383.3768 | -0.010722
125 |  | 0.16286 | 10.457 | 4187 | 0.015335 | 8.0287 | 8.0441 | -0.69847 | 65.2092 | 1393.8339 | -0.010711
126 |  | 0.16286 | 10.4463 | 4187 | 0.01532 | 8.0441 | 8.0594 | -0.69847 | 65.276 | 1404.2802 | -0.0107
127 |  | 0.16286 | 10.4356 | 4187 | 0.015304 | 8.0594 | 8.0747 | -0.69847 | 65.343 | 1414.7158 | -0.010689
128 |  | 0.16286 | 10.4249 | 4187 | 0.015288 | 8.0747 | 8.09 | -0.69847 | 65.41 | 1425.1408 | -0.010678
129 |  | 0.16286 | 10.4143 | 4187 | 0.015273 | 8.09 | 8.1052 | -0.69847 | 65.477 | 1435.555 | -0.010667
130 |  | 0.16286 | 10.4036 | 4187 | 0.015257 | 8.1052 | 8.1205 | -0.69847 | 65.5442 | 1445.9586 | -0.010657
131 |  | 0.16286 | 10.3929 | 4187 | 0.015241 | 8.1205 | 8.1357 | -0.69847 | 65.6114 | 1456.3516 | -0.010646
132 |  | 0.16286 | 10.3823 | 4187 | 0.015226 | 8.1357 | 8.151 | -0.69847 | 65.6787 | 1466.7339 | -0.010635
133 |  | 0.16286 | 10.3717 | 4187 | 0.01521 | 8.151 | 8.1662 | -0.69847 | 65.746 | 1477.1055 | -0.010624
134 |  | 0.16286 | 10.361 | 4187 | 0.015194 | 8.1662 | 8.1814 | -0.69847 | 65.8134 | 1487.4666 | -0.010613
135 |  | 0.16286 | 10.3504 | 4187 | 0.015179 | 8.1814 | 8.1965 | -0.69847 | 65.8809 | 1497.817 | -0.010602
136 |  | 0.16286 | 10.3398 | 4187 | 0.015163 | 8.1965 | 8.2117 | -0.69847 | 65.9485 | 1508.1568 | -0.010591
137 |  | 0.16286 | 10.3292 | 4187 | 0.015148 | 8.2117 | 8.2269 | -0.69847 | 66.0161 | 1518.4861 | -0.01058
138 |  | 0.16286 | 10.3187 | 4187 | 0.015132 | 8.2269 | 8.242 | -0.69847 | 66.0838 | 1528.8047 | -0.01057
139 |  | 0.16286 | 10.3081 | 4187 | 0.015117 | 8.242 | 8.2571 | -0.69847 | 66.1515 | 1539.1128 | -0.010559
140 |  | 0.16286 | 10.2975 | 4187 | 0.015101 | 8.2571 | 8.2722 | -0.69847 | 66.2194 | 1549.4103 | -0.010548
141 |  | 0.16286 | 10.287 | 4187 | 0.015086 | 8.2722 | 8.2873 | -0.69847 | 66.2873 | 1559.6973 | -0.010537
142 |  | 0.16286 | 10.2764 | 4187 | 0.01507 | 8.2873 | 8.3024 | -0.69847 | 66.3552 | 1569.9737 | -0.010526
143 |  | 0.16286 | 10.2659 | 4187 | 0.015055 | 8.3024 | 8.3174 | -0.69847 | 66.4233 | 1580.2397 | -0.010516
144 |  | 0.16286 | 10.2554 | 4187 | 0.01504 | 8.3174 | 8.3325 | -0.69847 | 66.4914 | 1590.4951 | -0.010505
145 |  | 0.16286 | 10.2449 | 4187 | 0.015024 | 8.3325 | 8.3475 | -0.69847 | 66.5596 | 1600.74 | -0.010494
146 |  | 0.16286 | 10.2344 | 4187 | 0.015009 | 8.3475 | 8.3625 | -0.69847 | 66.6278 | 1610.9744 | -0.010483
147 |  | 0.16286 | 10.2239 | 4187 | 0.014993 | 8.3625 | 8.3775 | -0.69847 | 66.6961 | 1621.1983 | -0.010472
148 |  | 0.16286 | 10.2134 | 4187 | 0.014978 | 8.3775 | 8.3925 | -0.69847 | 66.7645 | 1631.4117 | -0.010462
149 |  | 0.16286 | 10.203 | 4187 | 0.014963 | 8.3925 | 8.4074 | -0.69847 | 66.833 | 1641.6147 | -0.010451
150 |  | 0.16286 | 10.1925 | 4187 | 0.014947 | 8.4074 | 8.4224 | -0.69847 | 66.9015 | 1651.8072 | -0.01044
151 |  | 0.16286 | 10.1821 | 4187 | 0.014932 | 8.4224 | 8.4373 | -0.69847 | 66.9701 | 1661.9893 | -0.01043
152 |  | 0.16286 | 10.1717 | 4187 | 0.014917 | 8.4373 | 8.4522 | -0.69847 | 67.0388 | 1672.161 | -0.010419
153 |  | 0.16286 | 10.1612 | 4187 | 0.014901 | 8.4522 | 8.4671 | -0.69847 | 67.1075 | 1682.3222 | -0.010408
154 |  | 0.16286 | 10.1508 | 4187 | 0.014886 | 8.4671 | 8.482 | -0.69847 | 67.1763 | 1692.473 | -0.010398
155 |  | 0.16286 | 10.1404 | 4187 | 0.014871 | 8.482 | 8.4969 | -0.69847 | 67.2452 | 1702.6135 | -0.010387
156 |  | 0.16286 | 10.13 | 4187 | 0.014856 | 8.4969 | 8.5117 | -0.69847 | 67.3141 | 1712.7435 | -0.010376
157 |  | 0.16286 | 10.1197 | 4187 | 0.014841 | 8.5117 | 8.5266 | -0.69847 | 67.3832 | 1722.8632 | -0.010366
158 |  | 0.16286 | 10.1093 | 4187 | 0.014825 | 8.5266 | 8.5414 | -0.69847 | 67.4523 | 1732.9725 | -0.010355
159 |  | 0.16286 | 10.099 | 4187 | 0.01481 | 8.5414 | 8.5562 | -0.69847 | 67.5214 | 1743.0715 | -0.010344
160 |  | 0.16286 | 10.0886 | 4187 | 0.014795 | 8.5562 | 8.571 | -0.69847 | 67.5906 | 1753.1601 | -0.010334
161 |  | 0.16286 | 10.0783 | 4187 | 0.01478 | 8.571 | 8.5858 | -0.69847 | 67.66 | 1763.2383 | -0.010323
162 |  | 0.16286 | 10.068 | 4187 | 0.014765 | 8.5858 | 8.6006 | -0.69847 | 67.7293 | 1773.3063 | -0.010313
163 |  | 0.16286 | 10.0576 | 4187 | 0.01475 | 8.6006 | 8.6153 | -0.69847 | 67.7988 | 1783.3639 | -0.010302
164 |  | 0.16286 | 10.0473 | 4187 | 0.014734 | 8.6153 | 8.63 | -0.69847 | 67.8683 | 1793.4113 | -0.010292
165 |  | 0.16286 | 10.037 | 4187 | 0.014719 | 8.63 | 8.6448 | -0.69847 | 67.9379 | 1803.4483 | -0.010281
166 |  | 0.16286 | 10.0268 | 4187 | 0.014704 | 8.6448 | 8.6595 | -0.69847 | 68.0075 | 1813.4751 | -0.010271
167 |  | 0.16286 | 10.0165 | 4187 | 0.014689 | 8.6595 | 8.6742 | -0.69847 | 68.0773 | 1823.4916 | -0.01026
168 |  | 0.16286 | 10.0062 | 4187 | 0.014674 | 8.6742 | 8.6888 | -0.69847 | 68.1471 | 1833.4978 | -0.01025
169 |  | 0.16286 | 9.996 | 4187 | 0.014659 | 8.6888 | 8.7035 | -0.69847 | 68.217 | 1843.4938 | -0.010239
170 |  | 0.16286 | 9.9857 | 4187 | 0.014644 | 8.7035 | 8.7181 | -0.69847 | 68.2869 | 1853.4795 | -0.010229
171 |  | 0.16286 | 9.9755 | 4187 | 0.014629 | 8.7181 | 8.7328 | -0.69847 | 68.3569 | 1863.455 | -0.010218
172 |  | 0.16286 | 9.9653 | 4187 | 0.014614 | 8.7328 | 8.7474 | -0.69847 | 68.427 | 1873.4203 | -0.010208
173 |  | 0.16286 | 9.9551 | 4187 | 0.014599 | 8.7474 | 8.762 | -0.69847 | 68.4972 | 1883.3754 | -0.010197
174 |  | 0.16286 | 9.9449 | 4187 | 0.014584 | 8.762 | 8.7766 | -0.69847 | 68.5674 | 1893.3203 | -0.010187
175 |  | 0.16286 | 9.9347 | 4187 | 0.014569 | 8.7766 | 8.7911 | -0.69847 | 68.6377 | 1903.255 | -0.010176
176 |  | 0.16286 | 9.9245 | 4187 | 0.014554 | 8.7911 | 8.8057 | -0.69847 | 68.7081 | 1913.1796 | -0.010166
177 |  | 0.16286 | 9.9144 | 4187 | 0.014539 | 8.8057 | 8.8202 | -0.69847 | 68.7785 | 1923.0939 | -0.010155
178 |  | 0.16286 | 9.9042 | 4187 | 0.014525 | 8.8202 | 8.8347 | -0.69847 | 68.8491 | 1932.9981 | -0.010145
179 |  | 0.16286 | 9.8941 | 4187 | 0.01451 | 8.8347 | 8.8493 | -0.69847 | 68.9197 | 1942.8922 | -0.010135
180 |  | 0.16286 | 9.8839 | 4187 | 0.014495 | 8.8493 | 8.8637 | -0.69847 | 68.9903 | 1952.7761 | -0.010124
181 |  | 0.16286 | 9.8738 | 4187 | 0.01448 | 8.8637 | 8.8782 | -0.69847 | 69.0611 | 1962.6499 | -0.010114
182 |  | 0.16286 | 9.8637 | 4187 | 0.014465 | 8.8782 | 8.8927 | -0.69847 | 69.1319 | 1972.5136 | -0.010103
183 |  | 0.16286 | 9.8536 | 4187 | 0.01445 | 8.8927 | 8.9071 | -0.69847 | 69.2028 | 1982.3672 | -0.010093
184 |  | 0.16286 | 9.8435 | 4187 | 0.014435 | 8.9071 | 8.9216 | -0.69847 | 69.2737 | 1992.2107 | -0.010083
185 |  | 0.16286 | 9.8334 | 4187 | 0.014421 | 8.9216 | 8.936 | -0.69847 | 69.3448 | 2002.0441 | -0.010072
186 |  | 0.16286 | 9.8233 | 4187 | 0.014406 | 8.936 | 8.9504 | -0.69847 | 69.4159 | 2011.8674 | -0.010062
187 |  | 0.16286 | 9.8133 | 4187 | 0.014391 | 8.9504 | 8.9648 | -0.69847 | 69.487 | 2021.6807 | -0.010052
188 |  | 0.16286 | 9.8032 | 4187 | 0.014376 | 8.9648 | 8.9792 | -0.69847 | 69.5583 | 2031.4839 | -0.010042
189 |  | 0.16286 | 9.7932 | 4187 | 0.014362 | 8.9792 | 8.9935 | -0.69847 | 69.6296 | 2041.2771 | -0.010031
190 |  | 0.16286 | 9.7832 | 4187 | 0.014347 | 8.9935 | 9.0079 | -0.69847 | 69.701 | 2051.0603 | -0.010021
191 |  | 0.16286 | 9.7731 | 4187 | 0.014332 | 9.0079 | 9.0222 | -0.69847 | 69.7725 | 2060.8334 | -0.010011
192 |  | 0.16286 | 9.7631 | 4187 | 0.014318 | 9.0222 | 9.0365 | -0.69847 | 69.844 | 2070.5965 | -0.01
193 |  | 0.16286 | 9.7531 | 4187 | 0.014303 | 9.0365 | 9.0508 | -0.69847 | 69.9156 | 2080.3496 | -0.0099902
194 |  | 0.16286 | 9.7431 | 4187 | 0.014288 | 9.0508 | 9.0651 | -0.69847 | 69.9873 | 2090.0928 | -0.00998
195 |  | 0.16286 | 9.7331 | 4187 | 0.014274 | 9.0651 | 9.0794 | -0.69847 | 70.0591 | 2099.8259 | -0.0099698
196 |  | 0.16286 | 9.7232 | 4187 | 0.014259 | 9.0794 | 9.0937 | -0.69847 | 70.1309 | 2109.5491 | -0.0099596
197 |  | 0.16286 | 9.7132 | 4187 | 0.014244 | 9.0937 | 9.1079 | -0.69847 | 70.2028 | 2119.2623 | -0.0099494
198 |  | 0.16286 | 9.7033 | 4187 | 0.01423 | 9.1079 | 9.1221 | -0.69847 | 70.2748 | 2128.9656 | -0.0099392
199 |  | 0.16286 | 9.6933 | 4187 | 0.014215 | 9.1221 | 9.1363 | -0.69847 | 70.3469 | 2138.6589 | -0.009929
200 |  | 0.16286 | 9.6834 | 4187 | 0.014201 | 9.1363 | 9.1505 | -0.69847 | 70.419 | 2148.3423 | -0.0099188
201 |  | 0.16286 | 9.6735 | 4187 | 0.014186 | 9.1505 | 9.1647 | -0.69847 | 70.4912 | 2158.0158 | -0.0099087
202 |  | 0.16286 | 9.6636 | 4187 | 0.014172 | 9.1647 | 9.1789 | -0.69847 | 70.5635 | 2167.6794 | -0.0098985
203 |  | 0.16286 | 9.6537 | 4187 | 0.014157 | 9.1789 | 9.1931 | -0.69847 | 70.6358 | 2177.3331 | -0.0098884
204 |  | 0.16286 | 9.6438 | 4187 | 0.014143 | 9.1931 | 9.2072 | -0.69847 | 70.7083 | 2186.9769 | -0.0098783
205 |  | 0.16286 | 9.6339 | 4187 | 0.014128 | 9.2072 | 9.2213 | -0.69847 | 70.7808 | 2196.6108 | -0.0098681
206 |  | 0.16286 | 9.624 | 4187 | 0.014114 | 9.2213 | 9.2354 | -0.69847 | 70.8533 | 2206.2348 | -0.009858
207 |  | 0.16286 | 9.6142 | 4187 | 0.014099 | 9.2354 | 9.2495 | -0.69847 | 70.926 | 2215.849 | -0.0098479
208 |  | 0.16286 | 9.6043 | 4187 | 0.014085 | 9.2495 | 9.2636 | -0.69847 | 70.9987 | 2225.4533 | -0.0098378
209 |  | 0.16286 | 9.5945 | 4187 | 0.01407 | 9.2636 | 9.2777 | -0.69847 | 71.0715 | 2235.0478 | -0.0098278
210 |  | 0.16286 | 9.5847 | 4187 | 0.014056 | 9.2777 | 9.2918 | -0.69847 | 71.1444 | 2244.6325 | -0.0098177
211 |  | 0.16286 | 9.5749 | 4187 | 0.014042 | 9.2918 | 9.3058 | -0.69847 | 71.2173 | 2254.2073 | -0.0098076
212 |  | 0.16286 | 9.565 | 4187 | 0.014027 | 9.3058 | 9.3198 | -0.69847 | 71.2904 | 2263.7724 | -0.0097976
213 |  | 0.16286 | 9.5552 | 4187 | 0.014013 | 9.3198 | 9.3338 | -0.69847 | 71.3635 | 2273.3276 | -0.0097876
214 |  | 0.16286 | 9.5455 | 4187 | 0.013998 | 9.3338 | 9.3478 | -0.69847 | 71.4366 | 2282.8731 | -0.0097775
215 |  | 0.16286 | 9.5357 | 4187 | 0.013984 | 9.3478 | 9.3618 | -0.69847 | 71.5099 | 2292.4088 | -0.0097675
216 |  | 0.16286 | 9.5259 | 4187 | 0.01397 | 9.3618 | 9.3758 | -0.69847 | 71.5832 | 2301.9347 | -0.0097575
217 |  | 0.16286 | 9.5162 | 4187 | 0.013955 | 9.3758 | 9.3897 | -0.69847 | 71.6566 | 2311.4508 | -0.0097475
218 |  | 0.16286 | 9.5064 | 4187 | 0.013941 | 9.3897 | 9.4037 | -0.69847 | 71.7301 | 2320.9573 | -0.0097375
219 |  | 0.16286 | 9.4967 | 4187 | 0.013927 | 9.4037 | 9.4176 | -0.69847 | 71.8036 | 2330.4539 | -0.0097276
220 |  | 0.16286 | 9.4869 | 4187 | 0.013913 | 9.4176 | 9.4315 | -0.69847 | 71.8773 | 2339.9409 | -0.0097176
221 |  | 0.16286 | 9.4772 | 4187 | 0.013898 | 9.4315 | 9.4454 | -0.69847 | 71.951 | 2349.4181 | -0.0097076
222 |  | 0.16286 | 9.4675 | 4187 | 0.013884 | 9.4454 | 9.4593 | -0.69847 | 72.0247 | 2358.8856 | -0.0096977
223 |  | 0.16286 | 9.4578 | 4187 | 0.01387 | 9.4593 | 9.4732 | -0.69847 | 72.0986 | 2368.3434 | -0.0096878
224 |  | 0.16286 | 9.4481 | 4187 | 0.013856 | 9.4732 | 9.487 | -0.69847 | 72.1725 | 2377.7916 | -0.0096778
225 |  | 0.16286 | 9.4385 | 4187 | 0.013841 | 9.487 | 9.5009 | -0.69847 | 72.2465 | 2387.23 | -0.0096679
226 |  | 0.16286 | 9.4288 | 4187 | 0.013827 | 9.5009 | 9.5147 | -0.69847 | 72.3206 | 2396.6588 | -0.009658
227 |  | 0.16286 | 9.4191 | 4187 | 0.013813 | 9.5147 | 9.5285 | -0.69847 | 72.3947 | 2406.0779 | -0.0096481
228 |  | 0.16286 | 9.4095 | 4187 | 0.013799 | 9.5285 | 9.5423 | -0.69847 | 72.469 | 2415.4874 | -0.0096382
229 |  | 0.16286 | 9.3998 | 4187 | 0.013785 | 9.5423 | 9.5561 | -0.69847 | 72.5433 | 2424.8873 | -0.0096284
230 |  | 0.16286 | 9.3902 | 4187 | 0.013771 | 9.5561 | 9.5699 | -0.69847 | 72.6177 | 2434.2775 | -0.0096185
231 |  | 0.16286 | 9.3806 | 4187 | 0.013757 | 9.5699 | 9.5836 | -0.69847 | 72.6921 | 2443.6581 | -0.0096087
232 |  | 0.16286 | 9.371 | 4187 | 0.013743 | 9.5836 | 9.5974 | -0.69847 | 72.7667 | 2453.0291 | -0.0095988
233 |  | 0.16286 | 9.3614 | 4187 | 0.013728 | 9.5974 | 9.6111 | -0.69847 | 72.8413 | 2462.3905 | -0.009589
234 |  | 0.16286 | 9.3518 | 4187 | 0.013714 | 9.6111 | 9.6248 | -0.69847 | 72.916 | 2471.7423 | -0.0095792
235 |  | 0.16286 | 9.3422 | 4187 | 0.0137 | 9.6248 | 9.6385 | -0.69847 | 72.9907 | 2481.0845 | -0.0095694
236 |  | 0.16286 | 9.3327 | 4187 | 0.013686 | 9.6385 | 9.6522 | -0.69847 | 73.0656 | 2490.4171 | -0.0095595

## Fus25
|  |  | buis | verlies W/M | L /°C/sec
diam | wandikte |  | inhoud l/m |  | W/M
25 | 3.5 | 3.1416 | 0.25447 | 13.991 | 4187
[8 empty] | J/sec/mtr | aantal mtr. | verlies
|  | buis | verlies W/M | L /°C/sec | verlies temp | begintemp | eindtemp | verlies | bij 1°C | totaal J/sec
|  | inhoud L |  | W/M | °C per M | °C | °C | per m°C | daling | aantal mtr
1 | 25 | 0.25447 | 13.991 | 4187 | 0.013131 | 6 | 6.0131 | -0.823 | 76.1532 | 13.991 | -0.010807
2 |  | 0.25447 | 13.9802 | 4187 | 0.013121 | 6.0131 | 6.0263 | -0.823 | 76.2121 | 27.9712 | -0.010799
3 |  | 0.25447 | 13.9694 | 4187 | 0.013111 | 6.0263 | 6.0394 | -0.823 | 76.271 | 41.9407 | -0.01079
4 |  | 0.25447 | 13.9586 | 4187 | 0.013101 | 6.0394 | 6.0525 | -0.823 | 76.33 | 55.8993 | -0.010782
5 |  | 0.25447 | 13.9478 | 4187 | 0.013091 | 6.0525 | 6.0656 | -0.823 | 76.389 | 69.8471 | -0.010774
6 |  | 0.25447 | 13.9371 | 4187 | 0.013081 | 6.0656 | 6.0786 | -0.823 | 76.448 | 83.7842 | -0.010765
7 |  | 0.25447 | 13.9263 | 4187 | 0.013071 | 6.0786 | 6.0917 | -0.823 | 76.5071 | 97.7105 | -0.010757
8 |  | 0.25447 | 13.9155 | 4187 | 0.013061 | 6.0917 | 6.1048 | -0.823 | 76.5663 | 111.626 | -0.010749
9 |  | 0.25447 | 13.9048 | 4187 | 0.01305 | 6.1048 | 6.1178 | -0.823 | 76.6255 | 125.5308 | -0.010741
10 |  | 0.25447 | 13.8941 | 4187 | 0.01304 | 6.1178 | 6.1309 | -0.823 | 76.6847 | 139.4249 | -0.010732
11 |  | 0.25447 | 13.8833 | 4187 | 0.01303 | 6.1309 | 6.1439 | -0.823 | 76.744 | 153.3082 | -0.010724
12 |  | 0.25447 | 13.8726 | 4187 | 0.01302 | 6.1439 | 6.1569 | -0.823 | 76.8033 | 167.1808 | -0.010716
13 |  | 0.25447 | 13.8619 | 4187 | 0.01301 | 6.1569 | 6.1699 | -0.823 | 76.8627 | 181.0427 | -0.010707
14 |  | 0.25447 | 13.8512 | 4187 | 0.013 | 6.1699 | 6.1829 | -0.823 | 76.9221 | 194.8939 | -0.010699
15 |  | 0.25447 | 13.8405 | 4187 | 0.01299 | 6.1829 | 6.1959 | -0.823 | 76.9816 | 208.7344 | -0.010691
16 |  | 0.25447 | 13.8298 | 4187 | 0.01298 | 6.1959 | 6.2089 | -0.823 | 77.0411 | 222.5642 | -0.010683
17 |  | 0.25447 | 13.8191 | 4187 | 0.01297 | 6.2089 | 6.2219 | -0.823 | 77.1006 | 236.3833 | -0.010674
18 |  | 0.25447 | 13.8084 | 4187 | 0.01296 | 6.2219 | 6.2348 | -0.823 | 77.1602 | 250.1917 | -0.010666
19 |  | 0.25447 | 13.7978 | 4187 | 0.01295 | 6.2348 | 6.2478 | -0.823 | 77.2199 | 263.9895 | -0.010658
20 |  | 0.25447 | 13.7871 | 4187 | 0.01294 | 6.2478 | 6.2607 | -0.823 | 77.2796 | 277.7766 | -0.01065
21 |  | 0.25447 | 13.7765 | 4187 | 0.01293 | 6.2607 | 6.2736 | -0.823 | 77.3393 | 291.553 | -0.010641
22 |  | 0.25447 | 13.7658 | 4187 | 0.01292 | 6.2736 | 6.2866 | -0.823 | 77.3991 | 305.3188 | -0.010633
23 |  | 0.25447 | 13.7552 | 4187 | 0.01291 | 6.2866 | 6.2995 | -0.823 | 77.4589 | 319.074 | -0.010625
24 |  | 0.25447 | 13.7446 | 4187 | 0.0129 | 6.2995 | 6.3124 | -0.823 | 77.5188 | 332.8186 | -0.010617
25 |  | 0.25447 | 13.7339 | 4187 | 0.01289 | 6.3124 | 6.3253 | -0.823 | 77.5787 | 346.5525 | -0.010609
26 |  | 0.25447 | 13.7233 | 4187 | 0.01288 | 6.3253 | 6.3381 | -0.823 | 77.6387 | 360.2759 | -0.0106
27 |  | 0.25447 | 13.7127 | 4187 | 0.01287 | 6.3381 | 6.351 | -0.823 | 77.6987 | 373.9886 | -0.010592
28 |  | 0.25447 | 13.7021 | 4187 | 0.01286 | 6.351 | 6.3639 | -0.823 | 77.7588 | 387.6907 | -0.010584
29 |  | 0.25447 | 13.6916 | 4187 | 0.01285 | 6.3639 | 6.3767 | -0.823 | 77.8189 | 401.3823 | -0.010576
30 |  | 0.25447 | 13.681 | 4187 | 0.01284 | 6.3767 | 6.3896 | -0.823 | 77.8791 | 415.0633 | -0.010568
31 |  | 0.25447 | 13.6704 | 4187 | 0.012831 | 6.3896 | 6.4024 | -0.823 | 77.9393 | 428.7337 | -0.01056
32 |  | 0.25447 | 13.6599 | 4187 | 0.012821 | 6.4024 | 6.4152 | -0.823 | 77.9995 | 442.3935 | -0.010551
33 |  | 0.25447 | 13.6493 | 4187 | 0.012811 | 6.4152 | 6.428 | -0.823 | 78.0598 | 456.0428 | -0.010543
34 |  | 0.25447 | 13.6388 | 4187 | 0.012801 | 6.428 | 6.4408 | -0.823 | 78.1201 | 469.6816 | -0.010535
35 |  | 0.25447 | 13.6282 | 4187 | 0.012791 | 6.4408 | 6.4536 | -0.823 | 78.1805 | 483.3098 | -0.010527
36 |  | 0.25447 | 13.6177 | 4187 | 0.012781 | 6.4536 | 6.4664 | -0.823 | 78.241 | 496.9275 | -0.010519
37 |  | 0.25447 | 13.6072 | 4187 | 0.012771 | 6.4664 | 6.4792 | -0.823 | 78.3015 | 510.5347 | -0.010511
38 |  | 0.25447 | 13.5967 | 4187 | 0.012761 | 6.4792 | 6.4919 | -0.823 | 78.362 | 524.1313 | -0.010503
39 |  | 0.25447 | 13.5862 | 4187 | 0.012751 | 6.4919 | 6.5047 | -0.823 | 78.4226 | 537.7175 | -0.010494
40 |  | 0.25447 | 13.5757 | 4187 | 0.012742 | 6.5047 | 6.5174 | -0.823 | 78.4832 | 551.2932 | -0.010486
41 |  | 0.25447 | 13.5652 | 4187 | 0.012732 | 6.5174 | 6.5302 | -0.823 | 78.5439 | 564.8584 | -0.010478
42 |  | 0.25447 | 13.5547 | 4187 | 0.012722 | 6.5302 | 6.5429 | -0.823 | 78.6046 | 578.4131 | -0.01047
43 |  | 0.25447 | 13.5442 | 4187 | 0.012712 | 6.5429 | 6.5556 | -0.823 | 78.6653 | 591.9573 | -0.010462
44 |  | 0.25447 | 13.5338 | 4187 | 0.012702 | 6.5556 | 6.5683 | -0.823 | 78.7261 | 605.4911 | -0.010454
45 |  | 0.25447 | 13.5233 | 4187 | 0.012692 | 6.5683 | 6.581 | -0.823 | 78.787 | 619.0144 | -0.010446
46 |  | 0.25447 | 13.5129 | 4187 | 0.012683 | 6.581 | 6.5937 | -0.823 | 78.8479 | 632.5273 | -0.010438
47 |  | 0.25447 | 13.5024 | 4187 | 0.012673 | 6.5937 | 6.6063 | -0.823 | 78.9089 | 646.0297 | -0.01043
48 |  | 0.25447 | 13.492 | 4187 | 0.012663 | 6.6063 | 6.619 | -0.823 | 78.9699 | 659.5217 | -0.010422
49 |  | 0.25447 | 13.4816 | 4187 | 0.012653 | 6.619 | 6.6317 | -0.823 | 79.0309 | 673.0033 | -0.010414
50 |  | 0.25447 | 13.4712 | 4187 | 0.012644 | 6.6317 | 6.6443 | -0.823 | 79.092 | 686.4745 | -0.010406
51 |  | 0.25447 | 13.4608 | 4187 | 0.012634 | 6.6443 | 6.6569 | -0.823 | 79.1531 | 699.9352 | -0.010398
52 |  | 0.25447 | 13.4504 | 4187 | 0.012624 | 6.6569 | 6.6696 | -0.823 | 79.2143 | 713.3856 | -0.01039
53 |  | 0.25447 | 13.44 | 4187 | 0.012614 | 6.6696 | 6.6822 | -0.823 | 79.2756 | 726.8256 | -0.010382
54 |  | 0.25447 | 13.4296 | 4187 | 0.012604 | 6.6822 | 6.6948 | -0.823 | 79.3368 | 740.2552 | -0.010374
55 |  | 0.25447 | 13.4192 | 4187 | 0.012595 | 6.6948 | 6.7074 | -0.823 | 79.3982 | 753.6744 | -0.010365
56 |  | 0.25447 | 13.4089 | 4187 | 0.012585 | 6.7074 | 6.72 | -0.823 | 79.4596 | 767.0832 | -0.010357
57 |  | 0.25447 | 13.3985 | 4187 | 0.012575 | 6.72 | 6.7325 | -0.823 | 79.521 | 780.4817 | -0.010349
58 |  | 0.25447 | 13.3881 | 4187 | 0.012566 | 6.7325 | 6.7451 | -0.823 | 79.5824 | 793.8699 | -0.010341
59 |  | 0.25447 | 13.3778 | 4187 | 0.012556 | 6.7451 | 6.7577 | -0.823 | 79.644 | 807.2477 | -0.010334
60 |  | 0.25447 | 13.3675 | 4187 | 0.012546 | 6.7577 | 6.7702 | -0.823 | 79.7055 | 820.6152 | -0.010326
61 |  | 0.25447 | 13.3571 | 4187 | 0.012536 | 6.7702 | 6.7827 | -0.823 | 79.7672 | 833.9723 | -0.010318
62 |  | 0.25447 | 13.3468 | 4187 | 0.012527 | 6.7827 | 6.7953 | -0.823 | 79.8288 | 847.3192 | -0.01031
63 |  | 0.25447 | 13.3365 | 4187 | 0.012517 | 6.7953 | 6.8078 | -0.823 | 79.8905 | 860.6557 | -0.010302
64 |  | 0.25447 | 13.3262 | 4187 | 0.012507 | 6.8078 | 6.8203 | -0.823 | 79.9523 | 873.9819 | -0.010294
65 |  | 0.25447 | 13.3159 | 4187 | 0.012498 | 6.8203 | 6.8328 | -0.823 | 80.0141 | 887.2978 | -0.010286
66 |  | 0.25447 | 13.3056 | 4187 | 0.012488 | 6.8328 | 6.8453 | -0.823 | 80.0759 | 900.6035 | -0.010278
67 |  | 0.25447 | 13.2954 | 4187 | 0.012478 | 6.8453 | 6.8577 | -0.823 | 80.1378 | 913.8988 | -0.01027
68 |  | 0.25447 | 13.2851 | 4187 | 0.012469 | 6.8577 | 6.8702 | -0.823 | 80.1998 | 927.1839 | -0.010262
69 |  | 0.25447 | 13.2748 | 4187 | 0.012459 | 6.8702 | 6.8827 | -0.823 | 80.2618 | 940.4588 | -0.010254
70 |  | 0.25447 | 13.2646 | 4187 | 0.01245 | 6.8827 | 6.8951 | -0.823 | 80.3238 | 953.7233 | -0.010246
71 |  | 0.25447 | 13.2543 | 4187 | 0.01244 | 6.8951 | 6.9076 | -0.823 | 80.3859 | 966.9777 | -0.010238
72 |  | 0.25447 | 13.2441 | 4187 | 0.01243 | 6.9076 | 6.92 | -0.823 | 80.4481 | 980.2218 | -0.01023
73 |  | 0.25447 | 13.2339 | 4187 | 0.012421 | 6.92 | 6.9324 | -0.823 | 80.5103 | 993.4556 | -0.010222
74 |  | 0.25447 | 13.2236 | 4187 | 0.012411 | 6.9324 | 6.9448 | -0.823 | 80.5725 | 1006.6793 | -0.010214
75 |  | 0.25447 | 13.2134 | 4187 | 0.012402 | 6.9448 | 6.9572 | -0.823 | 80.6348 | 1019.8927 | -0.010207
76 |  | 0.25447 | 13.2032 | 4187 | 0.012392 | 6.9572 | 6.9696 | -0.823 | 80.6971 | 1033.0959 | -0.010199
77 |  | 0.25447 | 13.193 | 4187 | 0.012382 | 6.9696 | 6.982 | -0.823 | 80.7595 | 1046.2889 | -0.010191
78 |  | 0.25447 | 13.1828 | 4187 | 0.012373 | 6.982 | 6.9944 | -0.823 | 80.8219 | 1059.4718 | -0.010183
79 |  | 0.25447 | 13.1726 | 4187 | 0.012363 | 6.9944 | 7.0067 | -0.823 | 80.8844 | 1072.6444 | -0.010175
80 |  | 0.25447 | 13.1625 | 4187 | 0.012354 | 7.0067 | 7.0191 | -0.823 | 80.9469 | 1085.8069 | -0.010167
81 |  | 0.25447 | 13.1523 | 4187 | 0.012344 | 7.0191 | 7.0314 | -0.823 | 81.0095 | 1098.9592 | -0.010159
82 |  | 0.25447 | 13.1421 | 4187 | 0.012335 | 7.0314 | 7.0438 | -0.823 | 81.0721 | 1112.1013 | -0.010151
83 |  | 0.25447 | 13.132 | 4187 | 0.012325 | 7.0438 | 7.0561 | -0.823 | 81.1348 | 1125.2333 | -0.010144
84 |  | 0.25447 | 13.1219 | 4187 | 0.012316 | 7.0561 | 7.0684 | -0.823 | 81.1975 | 1138.3552 | -0.010136
85 |  | 0.25447 | 13.1117 | 4187 | 0.012306 | 7.0684 | 7.0807 | -0.823 | 81.2603 | 1151.4669 | -0.010128
86 |  | 0.25447 | 13.1016 | 4187 | 0.012297 | 7.0807 | 7.093 | -0.823 | 81.3231 | 1164.5685 | -0.01012
87 |  | 0.25447 | 13.0915 | 4187 | 0.012287 | 7.093 | 7.1053 | -0.823 | 81.386 | 1177.6599 | -0.010112
88 |  | 0.25447 | 13.0814 | 4187 | 0.012278 | 7.1053 | 7.1176 | -0.823 | 81.4489 | 1190.7413 | -0.010105
89 |  | 0.25447 | 13.0713 | 4187 | 0.012268 | 7.1176 | 7.1299 | -0.823 | 81.5118 | 1203.8125 | -0.010097
90 |  | 0.25447 | 13.0612 | 4187 | 0.012259 | 7.1299 | 7.1421 | -0.823 | 81.5749 | 1216.8737 | -0.010089
91 |  | 0.25447 | 13.0511 | 4187 | 0.012249 | 7.1421 | 7.1544 | -0.823 | 81.6379 | 1229.9248 | -0.010081
92 |  | 0.25447 | 13.041 | 4187 | 0.01224 | 7.1544 | 7.1666 | -0.823 | 81.701 | 1242.9658 | -0.010073
93 |  | 0.25447 | 13.0309 | 4187 | 0.01223 | 7.1666 | 7.1788 | -0.823 | 81.7642 | 1255.9967 | -0.010066
94 |  | 0.25447 | 13.0208 | 4187 | 0.012221 | 7.1788 | 7.191 | -0.823 | 81.8274 | 1269.0175 | -0.010058
95 |  | 0.25447 | 13.0108 | 4187 | 0.012211 | 7.191 | 7.2033 | -0.823 | 81.8906 | 1282.0283 | -0.01005
96 |  | 0.25447 | 13.0007 | 4187 | 0.012202 | 7.2033 | 7.2155 | -0.823 | 81.9539 | 1295.029 | -0.010042
97 |  | 0.25447 | 12.9907 | 4187 | 0.012193 | 7.2155 | 7.2277 | -0.823 | 82.0173 | 1308.0197 | -0.010034
98 |  | 0.25447 | 12.9807 | 4187 | 0.012183 | 7.2277 | 7.2398 | -0.823 | 82.0807 | 1321.0004 | -0.010027
99 |  | 0.25447 | 12.9706 | 4187 | 0.012174 | 7.2398 | 7.252 | -0.823 | 82.1442 | 1333.971 | -0.010019
100 |  | 0.25447 | 12.9606 | 4187 | 0.012164 | 7.252 | 7.2642 | -0.823 | 82.2077 | 1346.9316 | -0.010011
101 |  | 0.25447 | 12.9506 | 4187 | 0.012155 | 7.2642 | 7.2763 | -0.823 | 82.2712 | 1359.8822 | -0.010004
102 |  | 0.25447 | 12.9406 | 4187 | 0.012146 | 7.2763 | 7.2885 | -0.823 | 82.3348 | 1372.8228 | -0.0099958
103 |  | 0.25447 | 12.9306 | 4187 | 0.012136 | 7.2885 | 7.3006 | -0.823 | 82.3985 | 1385.7534 | -0.0099881
104 |  | 0.25447 | 12.9206 | 4187 | 0.012127 | 7.3006 | 7.3127 | -0.823 | 82.4621 | 1398.6741 | -0.0099804
105 |  | 0.25447 | 12.9106 | 4187 | 0.012117 | 7.3127 | 7.3249 | -0.823 | 82.5259 | 1411.5847 | -0.0099726
106 |  | 0.25447 | 12.9007 | 4187 | 0.012108 | 7.3249 | 7.337 | -0.823 | 82.5897 | 1424.4854 | -0.0099649
107 |  | 0.25447 | 12.8907 | 4187 | 0.012099 | 7.337 | 7.3491 | -0.823 | 82.6535 | 1437.3761 | -0.0099572
108 |  | 0.25447 | 12.8807 | 4187 | 0.012089 | 7.3491 | 7.3612 | -0.823 | 82.7174 | 1450.2568 | -0.0099496
109 |  | 0.25447 | 12.8708 | 4187 | 0.01208 | 7.3612 | 7.3732 | -0.823 | 82.7814 | 1463.1276 | -0.0099419
110 |  | 0.25447 | 12.8608 | 4187 | 0.012071 | 7.3732 | 7.3853 | -0.823 | 82.8454 | 1475.9884 | -0.0099342
111 |  | 0.25447 | 12.8509 | 4187 | 0.012061 | 7.3853 | 7.3974 | -0.823 | 82.9094 | 1488.8393 | -0.0099265
112 |  | 0.25447 | 12.841 | 4187 | 0.012052 | 7.3974 | 7.4094 | -0.823 | 82.9735 | 1501.6803 | -0.0099188
113 |  | 0.25447 | 12.8311 | 4187 | 0.012043 | 7.4094 | 7.4215 | -0.823 | 83.0376 | 1514.5114 | -0.0099112
114 |  | 0.25447 | 12.8212 | 4187 | 0.012033 | 7.4215 | 7.4335 | -0.823 | 83.1018 | 1527.3326 | -0.0099035
115 |  | 0.25447 | 12.8113 | 4187 | 0.012024 | 7.4335 | 7.4455 | -0.823 | 83.1661 | 1540.1438 | -0.0098959
116 |  | 0.25447 | 12.8014 | 4187 | 0.012015 | 7.4455 | 7.4575 | -0.823 | 83.2304 | 1552.9452 | -0.0098882
117 |  | 0.25447 | 12.7915 | 4187 | 0.012006 | 7.4575 | 7.4695 | -0.823 | 83.2947 | 1565.7366 | -0.0098806
118 |  | 0.25447 | 12.7816 | 4187 | 0.011996 | 7.4695 | 7.4815 | -0.823 | 83.3591 | 1578.5182 | -0.009873
119 |  | 0.25447 | 12.7717 | 4187 | 0.011987 | 7.4815 | 7.4935 | -0.823 | 83.4235 | 1591.29 | -0.0098653
120 |  | 0.25447 | 12.7619 | 4187 | 0.011978 | 7.4935 | 7.5055 | -0.823 | 83.488 | 1604.0518 | -0.0098577
121 |  | 0.25447 | 12.752 | 4187 | 0.011969 | 7.5055 | 7.5175 | -0.823 | 83.5526 | 1616.8038 | -0.0098501
122 |  | 0.25447 | 12.7421 | 4187 | 0.011959 | 7.5175 | 7.5294 | -0.823 | 83.6171 | 1629.5459 | -0.0098425
123 |  | 0.25447 | 12.7323 | 4187 | 0.01195 | 7.5294 | 7.5414 | -0.823 | 83.6818 | 1642.2782 | -0.0098349
124 |  | 0.25447 | 12.7225 | 4187 | 0.011941 | 7.5414 | 7.5533 | -0.823 | 83.7465 | 1655.0007 | -0.0098273
125 |  | 0.25447 | 12.7126 | 4187 | 0.011932 | 7.5533 | 7.5652 | -0.823 | 83.8112 | 1667.7134 | -0.0098197
126 |  | 0.25447 | 12.7028 | 4187 | 0.011922 | 7.5652 | 7.5772 | -0.823 | 83.876 | 1680.4162 | -0.0098121
127 |  | 0.25447 | 12.693 | 4187 | 0.011913 | 7.5772 | 7.5891 | -0.823 | 83.9408 | 1693.1092 | -0.0098045
128 |  | 0.25447 | 12.6832 | 4187 | 0.011904 | 7.5891 | 7.601 | -0.823 | 84.0057 | 1705.7924 | -0.009797
129 |  | 0.25447 | 12.6734 | 4187 | 0.011895 | 7.601 | 7.6129 | -0.823 | 84.0707 | 1718.4658 | -0.0097894
130 |  | 0.25447 | 12.6636 | 4187 | 0.011886 | 7.6129 | 7.6248 | -0.823 | 84.1357 | 1731.1294 | -0.0097818
131 |  | 0.25447 | 12.6538 | 4187 | 0.011876 | 7.6248 | 7.6366 | -0.823 | 84.2007 | 1743.7832 | -0.0097743
132 |  | 0.25447 | 12.6441 | 4187 | 0.011867 | 7.6366 | 7.6485 | -0.823 | 84.2658 | 1756.4273 | -0.0097667
133 |  | 0.25447 | 12.6343 | 4187 | 0.011858 | 7.6485 | 7.6604 | -0.823 | 84.3309 | 1769.0616 | -0.0097592
134 |  | 0.25447 | 12.6245 | 4187 | 0.011849 | 7.6604 | 7.6722 | -0.823 | 84.3961 | 1781.6861 | -0.0097516
135 |  | 0.25447 | 12.6148 | 4187 | 0.01184 | 7.6722 | 7.6841 | -0.823 | 84.4614 | 1794.3009 | -0.0097441
136 |  | 0.25447 | 12.605 | 4187 | 0.011831 | 7.6841 | 7.6959 | -0.823 | 84.5267 | 1806.906 | -0.0097366
137 |  | 0.25447 | 12.5953 | 4187 | 0.011821 | 7.6959 | 7.7077 | -0.823 | 84.592 | 1819.5013 | -0.0097291
138 |  | 0.25447 | 12.5856 | 4187 | 0.011812 | 7.7077 | 7.7195 | -0.823 | 84.6574 | 1832.0868 | -0.0097216
139 |  | 0.25447 | 12.5759 | 4187 | 0.011803 | 7.7195 | 7.7313 | -0.823 | 84.7228 | 1844.6627 | -0.009714
140 |  | 0.25447 | 12.5661 | 4187 | 0.011794 | 7.7313 | 7.7431 | -0.823 | 84.7883 | 1857.2288 | -0.0097065
141 |  | 0.25447 | 12.5564 | 4187 | 0.011785 | 7.7431 | 7.7549 | -0.823 | 84.8539 | 1869.7853 | -0.009699
142 |  | 0.25447 | 12.5467 | 4187 | 0.011776 | 7.7549 | 7.7667 | -0.823 | 84.9195 | 1882.332 | -0.0096916
143 |  | 0.25447 | 12.537 | 4187 | 0.011767 | 7.7667 | 7.7784 | -0.823 | 84.9851 | 1894.869 | -0.0096841
144 |  | 0.25447 | 12.5274 | 4187 | 0.011758 | 7.7784 | 7.7902 | -0.823 | 85.0508 | 1907.3964 | -0.0096766
145 |  | 0.25447 | 12.5177 | 4187 | 0.011749 | 7.7902 | 7.802 | -0.823 | 85.1165 | 1919.9141 | -0.0096691
146 |  | 0.25447 | 12.508 | 4187 | 0.01174 | 7.802 | 7.8137 | -0.823 | 85.1823 | 1932.4221 | -0.0096616
147 |  | 0.25447 | 12.4983 | 4187 | 0.01173 | 7.8137 | 7.8254 | -0.823 | 85.2482 | 1944.9204 | -0.0096542
148 |  | 0.25447 | 12.4887 | 4187 | 0.011721 | 7.8254 | 7.8371 | -0.823 | 85.3141 | 1957.4091 | -0.0096467
149 |  | 0.25447 | 12.479 | 4187 | 0.011712 | 7.8371 | 7.8489 | -0.823 | 85.38 | 1969.8882 | -0.0096393
150 |  | 0.25447 | 12.4694 | 4187 | 0.011703 | 7.8489 | 7.8606 | -0.823 | 85.446 | 1982.3576 | -0.0096318
151 |  | 0.25447 | 12.4598 | 4187 | 0.011694 | 7.8606 | 7.8723 | -0.823 | 85.5121 | 1994.8173 | -0.0096244
152 |  | 0.25447 | 12.4502 | 4187 | 0.011685 | 7.8723 | 7.8839 | -0.823 | 85.5782 | 2007.2675 | -0.0096169
153 |  | 0.25447 | 12.4405 | 4187 | 0.011676 | 7.8839 | 7.8956 | -0.823 | 85.6444 | 2019.708 | -0.0096095
154 |  | 0.25447 | 12.4309 | 4187 | 0.011667 | 7.8956 | 7.9073 | -0.823 | 85.7106 | 2032.139 | -0.0096021
155 |  | 0.25447 | 12.4213 | 4187 | 0.011658 | 7.9073 | 7.9189 | -0.823 | 85.7768 | 2044.5603 | -0.0095947
156 |  | 0.25447 | 12.4117 | 4187 | 0.011649 | 7.9189 | 7.9306 | -0.823 | 85.8431 | 2056.972 | -0.0095873
157 |  | 0.25447 | 12.4021 | 4187 | 0.01164 | 7.9306 | 7.9422 | -0.823 | 85.9095 | 2069.3742 | -0.0095799
158 |  | 0.25447 | 12.3926 | 4187 | 0.011631 | 7.9422 | 7.9539 | -0.823 | 85.9759 | 2081.7667 | -0.0095725
159 |  | 0.25447 | 12.383 | 4187 | 0.011622 | 7.9539 | 7.9655 | -0.823 | 86.0424 | 2094.1497 | -0.0095651
160 |  | 0.25447 | 12.3734 | 4187 | 0.011613 | 7.9655 | 7.9771 | -0.823 | 86.1089 | 2106.5231 | -0.0095577
161 |  | 0.25447 | 12.3639 | 4187 | 0.011604 | 7.9771 | 7.9887 | -0.823 | 86.1754 | 2118.887 | -0.0095503
162 |  | 0.25447 | 12.3543 | 4187 | 0.011595 | 7.9887 | 8.0003 | -0.823 | 86.2421 | 2131.2413 | -0.0095429
163 |  | 0.25447 | 12.3448 | 4187 | 0.011586 | 8.0003 | 8.0119 | -0.823 | 86.3087 | 2143.5861 | -0.0095356
164 |  | 0.25447 | 12.3352 | 4187 | 0.011577 | 8.0119 | 8.0235 | -0.823 | 86.3754 | 2155.9213 | -0.0095282
165 |  | 0.25447 | 12.3257 | 4187 | 0.011568 | 8.0235 | 8.035 | -0.823 | 86.4422 | 2168.247 | -0.0095208
166 |  | 0.25447 | 12.3162 | 4187 | 0.011559 | 8.035 | 8.0466 | -0.823 | 86.509 | 2180.5632 | -0.0095135
167 |  | 0.25447 | 12.3067 | 4187 | 0.011551 | 8.0466 | 8.0581 | -0.823 | 86.5759 | 2192.8699 | -0.0095061
168 |  | 0.25447 | 12.2972 | 4187 | 0.011542 | 8.0581 | 8.0697 | -0.823 | 86.6428 | 2205.1671 | -0.0094988
169 |  | 0.25447 | 12.2877 | 4187 | 0.011533 | 8.0697 | 8.0812 | -0.823 | 86.7098 | 2217.4547 | -0.0094914
170 |  | 0.25447 | 12.2782 | 4187 | 0.011524 | 8.0812 | 8.0927 | -0.823 | 86.7768 | 2229.7329 | -0.0094841
171 |  | 0.25447 | 12.2687 | 4187 | 0.011515 | 8.0927 | 8.1043 | -0.823 | 86.8439 | 2242.0016 | -0.0094768
172 |  | 0.25447 | 12.2592 | 4187 | 0.011506 | 8.1043 | 8.1158 | -0.823 | 86.9111 | 2254.2608 | -0.0094695
173 |  | 0.25447 | 12.2497 | 4187 | 0.011497 | 8.1158 | 8.1273 | -0.823 | 86.9782 | 2266.5106 | -0.0094622
174 |  | 0.25447 | 12.2403 | 4187 | 0.011488 | 8.1273 | 8.1387 | -0.823 | 87.0455 | 2278.7509 | -0.0094548
175 |  | 0.25447 | 12.2308 | 4187 | 0.011479 | 8.1387 | 8.1502 | -0.823 | 87.1128 | 2290.9817 | -0.0094475
176 |  | 0.25447 | 12.2214 | 4187 | 0.011471 | 8.1502 | 8.1617 | -0.823 | 87.1801 | 2303.2031 | -0.0094402
177 |  | 0.25447 | 12.2119 | 4187 | 0.011462 | 8.1617 | 8.1732 | -0.823 | 87.2475 | 2315.415 | -0.0094329
178 |  | 0.25447 | 12.2025 | 4187 | 0.011453 | 8.1732 | 8.1846 | -0.823 | 87.315 | 2327.6176 | -0.0094257
179 |  | 0.25447 | 12.1931 | 4187 | 0.011444 | 8.1846 | 8.1961 | -0.823 | 87.3825 | 2339.8106 | -0.0094184
180 |  | 0.25447 | 12.1837 | 4187 | 0.011435 | 8.1961 | 8.2075 | -0.823 | 87.45 | 2351.9943 | -0.0094111
181 |  | 0.25447 | 12.1743 | 4187 | 0.011426 | 8.2075 | 8.2189 | -0.823 | 87.5176 | 2364.1686 | -0.0094038
182 |  | 0.25447 | 12.1649 | 4187 | 0.011417 | 8.2189 | 8.2303 | -0.823 | 87.5853 | 2376.3334 | -0.0093966
183 |  | 0.25447 | 12.1555 | 4187 | 0.011409 | 8.2303 | 8.2417 | -0.823 | 87.653 | 2388.4889 | -0.0093893
184 |  | 0.25447 | 12.1461 | 4187 | 0.0114 | 8.2417 | 8.2531 | -0.823 | 87.7207 | 2400.6349 | -0.0093821
185 |  | 0.25447 | 12.1367 | 4187 | 0.011391 | 8.2531 | 8.2645 | -0.823 | 87.7885 | 2412.7716 | -0.0093748
186 |  | 0.25447 | 12.1273 | 4187 | 0.011382 | 8.2645 | 8.2759 | -0.823 | 87.8564 | 2424.8989 | -0.0093676
187 |  | 0.25447 | 12.1179 | 4187 | 0.011373 | 8.2759 | 8.2873 | -0.823 | 87.9243 | 2437.0169 | -0.0093603
188 |  | 0.25447 | 12.1086 | 4187 | 0.011365 | 8.2873 | 8.2987 | -0.823 | 87.9923 | 2449.1255 | -0.0093531
189 |  | 0.25447 | 12.0992 | 4187 | 0.011356 | 8.2987 | 8.31 | -0.823 | 88.0603 | 2461.2247 | -0.0093459
190 |  | 0.25447 | 12.0899 | 4187 | 0.011347 | 8.31 | 8.3214 | -0.823 | 88.1284 | 2473.3146 | -0.0093387
191 |  | 0.25447 | 12.0805 | 4187 | 0.011338 | 8.3214 | 8.3327 | -0.823 | 88.1965 | 2485.3951 | -0.0093315
192 |  | 0.25447 | 12.0712 | 4187 | 0.01133 | 8.3327 | 8.344 | -0.823 | 88.2647 | 2497.4663 | -0.0093242
193 |  | 0.25447 | 12.0619 | 4187 | 0.011321 | 8.344 | 8.3553 | -0.823 | 88.3329 | 2509.5282 | -0.009317
194 |  | 0.25447 | 12.0526 | 4187 | 0.011312 | 8.3553 | 8.3667 | -0.823 | 88.4012 | 2521.5808 | -0.0093098
195 |  | 0.25447 | 12.0433 | 4187 | 0.011303 | 8.3667 | 8.378 | -0.823 | 88.4695 | 2533.624 | -0.0093027
196 |  | 0.25447 | 12.034 | 4187 | 0.011295 | 8.378 | 8.3893 | -0.823 | 88.5379 | 2545.658 | -0.0092955
197 |  | 0.25447 | 12.0247 | 4187 | 0.011286 | 8.3893 | 8.4005 | -0.823 | 88.6064 | 2557.6827 | -0.0092883
198 |  | 0.25447 | 12.0154 | 4187 | 0.011277 | 8.4005 | 8.4118 | -0.823 | 88.6749 | 2569.698 | -0.0092811
199 |  | 0.25447 | 12.0061 | 4187 | 0.011268 | 8.4118 | 8.4231 | -0.823 | 88.7434 | 2581.7041 | -0.0092739
200 |  | 0.25447 | 11.9968 | 4187 | 0.01126 | 8.4231 | 8.4343 | -0.823 | 88.812 | 2593.701 | -0.0092668
201 |  | 0.25447 | 11.9876 | 4187 | 0.011251 | 8.4343 | 8.4456 | -0.823 | 88.8807 | 2605.6885 | -0.0092596
202 |  | 0.25447 | 11.9783 | 4187 | 0.011242 | 8.4456 | 8.4568 | -0.823 | 88.9494 | 2617.6668 | -0.0092525
203 |  | 0.25447 | 11.969 | 4187 | 0.011234 | 8.4568 | 8.4681 | -0.823 | 89.0181 | 2629.6358 | -0.0092453
204 |  | 0.25447 | 11.9598 | 4187 | 0.011225 | 8.4681 | 8.4793 | -0.823 | 89.0869 | 2641.5956 | -0.0092382
205 |  | 0.25447 | 11.9506 | 4187 | 0.011216 | 8.4793 | 8.4905 | -0.823 | 89.1558 | 2653.5462 | -0.009231
206 |  | 0.25447 | 11.9413 | 4187 | 0.011208 | 8.4905 | 8.5017 | -0.823 | 89.2247 | 2665.4875 | -0.0092239
207 |  | 0.25447 | 11.9321 | 4187 | 0.011199 | 8.5017 | 8.5129 | -0.823 | 89.2937 | 2677.4196 | -0.0092168
208 |  | 0.25447 | 11.9229 | 4187 | 0.01119 | 8.5129 | 8.5241 | -0.823 | 89.3627 | 2689.3425 | -0.0092097
209 |  | 0.25447 | 11.9137 | 4187 | 0.011182 | 8.5241 | 8.5353 | -0.823 | 89.4318 | 2701.2562 | -0.0092026
210 |  | 0.25447 | 11.9045 | 4187 | 0.011173 | 8.5353 | 8.5465 | -0.823 | 89.501 | 2713.1607 | -0.0091954
211 |  | 0.25447 | 11.8953 | 4187 | 0.011164 | 8.5465 | 8.5576 | -0.823 | 89.5701 | 2725.0559 | -0.0091883
212 |  | 0.25447 | 11.8861 | 4187 | 0.011156 | 8.5576 | 8.5688 | -0.823 | 89.6394 | 2736.942 | -0.0091812
213 |  | 0.25447 | 11.8769 | 4187 | 0.011147 | 8.5688 | 8.5799 | -0.823 | 89.7087 | 2748.8189 | -0.0091742
214 |  | 0.25447 | 11.8677 | 4187 | 0.011139 | 8.5799 | 8.5911 | -0.823 | 89.778 | 2760.6867 | -0.0091671
215 |  | 0.25447 | 11.8586 | 4187 | 0.01113 | 8.5911 | 8.6022 | -0.823 | 89.8474 | 2772.5452 | -0.00916
216 |  | 0.25447 | 11.8494 | 4187 | 0.011121 | 8.6022 | 8.6133 | -0.823 | 89.9169 | 2784.3946 | -0.0091529
217 |  | 0.25447 | 11.8403 | 4187 | 0.011113 | 8.6133 | 8.6244 | -0.823 | 89.9864 | 2796.2349 | -0.0091458
218 |  | 0.25447 | 11.8311 | 4187 | 0.011104 | 8.6244 | 8.6355 | -0.823 | 90.0559 | 2808.066 | -0.0091388
219 |  | 0.25447 | 11.822 | 4187 | 0.011096 | 8.6355 | 8.6466 | -0.823 | 90.1256 | 2819.888 | -0.0091317
220 |  | 0.25447 | 11.8128 | 4187 | 0.011087 | 8.6466 | 8.6577 | -0.823 | 90.1952 | 2831.7008 | -0.0091247
221 |  | 0.25447 | 11.8037 | 4187 | 0.011078 | 8.6577 | 8.6688 | -0.823 | 90.265 | 2843.5045 | -0.0091176
222 |  | 0.25447 | 11.7946 | 4187 | 0.01107 | 8.6688 | 8.6799 | -0.823 | 90.3347 | 2855.2991 | -0.0091106
223 |  | 0.25447 | 11.7855 | 4187 | 0.011061 | 8.6799 | 8.6909 | -0.823 | 90.4046 | 2867.0846 | -0.0091035
224 |  | 0.25447 | 11.7764 | 4187 | 0.011053 | 8.6909 | 8.702 | -0.823 | 90.4745 | 2878.861 | -0.0090965
225 |  | 0.25447 | 11.7673 | 4187 | 0.011044 | 8.702 | 8.713 | -0.823 | 90.5444 | 2890.6283 | -0.0090895
226 |  | 0.25447 | 11.7582 | 4187 | 0.011036 | 8.713 | 8.7241 | -0.823 | 90.6144 | 2902.3865 | -0.0090825
227 |  | 0.25447 | 11.7491 | 4187 | 0.011027 | 8.7241 | 8.7351 | -0.823 | 90.6844 | 2914.1356 | -0.0090754
228 |  | 0.25447 | 11.74 | 4187 | 0.011019 | 8.7351 | 8.7461 | -0.823 | 90.7545 | 2925.8756 | -0.0090684
229 |  | 0.25447 | 11.731 | 4187 | 0.01101 | 8.7461 | 8.7571 | -0.823 | 90.8247 | 2937.6066 | -0.0090614
230 |  | 0.25447 | 11.7219 | 4187 | 0.011002 | 8.7571 | 8.7681 | -0.823 | 90.8949 | 2949.3285 | -0.0090544
231 |  | 0.25447 | 11.7129 | 4187 | 0.010993 | 8.7681 | 8.7791 | -0.823 | 90.9652 | 2961.0414 | -0.0090474
232 |  | 0.25447 | 11.7038 | 4187 | 0.010985 | 8.7791 | 8.7901 | -0.823 | 91.0355 | 2972.7452 | -0.0090404
233 |  | 0.25447 | 11.6948 | 4187 | 0.010976 | 8.7901 | 8.8011 | -0.823 | 91.1059 | 2984.4399 | -0.0090335
234 |  | 0.25447 | 11.6857 | 4187 | 0.010968 | 8.8011 | 8.812 | -0.823 | 91.1763 | 2996.1257 | -0.0090265
235 |  | 0.25447 | 11.6767 | 4187 | 0.010959 | 8.812 | 8.823 | -0.823 | 91.2468 | 3007.8024 | -0.0090195
236 |  | 0.25447 | 11.6677 | 4187 | 0.010951 | 8.823 | 8.834 | -0.823 | 91.3173 | 3019.4701 | -0.0090125

## Fus32
|  |  | buis | verlies W/M | L /°C/sec
diam | wandikte |  | inhoud l/m |  | W/M
32 | 4.4 | 3.1416 | 0.42273 | 16.6981 | 4187
[8 empty] | J/sec/mtr | aantal mtr. | verlies
|  | buis | verlies W/M | L /°C/sec | verlies temp | begintemp | eindtemp | verlies | bij 1°C | totaal J/sec
|  | inhoud L |  | W/M | °C per M | °C | °C | per m°C | daling | aantal mtr
1 | 32 | 0.42273 | 16.6981 | 4187 | 0.0094341 | 6 | 6.0094 | -0.98224 | 105.9988 | 16.6981 | -0.0092666
2 |  | 0.42273 | 16.6889 | 4187 | 0.0094288 | 6.0094 | 6.0189 | -0.98224 | 106.0576 | 33.387 | -0.0092614
3 |  | 0.42273 | 16.6796 | 4187 | 0.0094236 | 6.0189 | 6.0283 | -0.98224 | 106.1165 | 50.0666 | -0.0092563
4 |  | 0.42273 | 16.6704 | 4187 | 0.0094184 | 6.0283 | 6.0377 | -0.98224 | 106.1754 | 66.737 | -0.0092511
5 |  | 0.42273 | 16.6611 | 4187 | 0.0094131 | 6.0377 | 6.0471 | -0.98224 | 106.2344 | 83.3981 | -0.009246
6 |  | 0.42273 | 16.6519 | 4187 | 0.0094079 | 6.0471 | 6.0565 | -0.98224 | 106.2934 | 100.0499 | -0.0092409
7 |  | 0.42273 | 16.6426 | 4187 | 0.0094027 | 6.0565 | 6.0659 | -0.98224 | 106.3524 | 116.6926 | -0.0092357
8 |  | 0.42273 | 16.6334 | 4187 | 0.0093975 | 6.0659 | 6.0753 | -0.98224 | 106.4114 | 133.3259 | -0.0092306
9 |  | 0.42273 | 16.6242 | 4187 | 0.0093923 | 6.0753 | 6.0847 | -0.98224 | 106.4705 | 149.9501 | -0.0092255
10 |  | 0.42273 | 16.6149 | 4187 | 0.0093871 | 6.0847 | 6.0941 | -0.98224 | 106.5296 | 166.565 | -0.0092204
11 |  | 0.42273 | 16.6057 | 4187 | 0.0093819 | 6.0941 | 6.1035 | -0.98224 | 106.5888 | 183.1707 | -0.0092153
12 |  | 0.42273 | 16.5965 | 4187 | 0.0093766 | 6.1035 | 6.1129 | -0.98224 | 106.648 | 199.7672 | -0.0092101
13 |  | 0.42273 | 16.5873 | 4187 | 0.0093714 | 6.1129 | 6.1222 | -0.98224 | 106.7072 | 216.3545 | -0.009205
14 |  | 0.42273 | 16.5781 | 4187 | 0.0093662 | 6.1222 | 6.1316 | -0.98224 | 106.7664 | 232.9326 | -0.0091999
15 |  | 0.42273 | 16.5689 | 4187 | 0.009361 | 6.1316 | 6.141 | -0.98224 | 106.8257 | 249.5014 | -0.0091948
16 |  | 0.42273 | 16.5597 | 4187 | 0.0093558 | 6.141 | 6.1503 | -0.98224 | 106.885 | 266.0611 | -0.0091897
17 |  | 0.42273 | 16.5505 | 4187 | 0.0093507 | 6.1503 | 6.1597 | -0.98224 | 106.9444 | 282.6116 | -0.0091846
18 |  | 0.42273 | 16.5413 | 4187 | 0.0093455 | 6.1597 | 6.169 | -0.98224 | 107.0038 | 299.1529 | -0.0091795
19 |  | 0.42273 | 16.5321 | 4187 | 0.0093403 | 6.169 | 6.1784 | -0.98224 | 107.0632 | 315.685 | -0.0091744
20 |  | 0.42273 | 16.523 | 4187 | 0.0093351 | 6.1784 | 6.1877 | -0.98224 | 107.1226 | 332.208 | -0.0091693
21 |  | 0.42273 | 16.5138 | 4187 | 0.0093299 | 6.1877 | 6.197 | -0.98224 | 107.1821 | 348.7218 | -0.0091642
22 |  | 0.42273 | 16.5046 | 4187 | 0.0093247 | 6.197 | 6.2063 | -0.98224 | 107.2416 | 365.2264 | -0.0091592
23 |  | 0.42273 | 16.4955 | 4187 | 0.0093196 | 6.2063 | 6.2157 | -0.98224 | 107.3012 | 381.7218 | -0.0091541
24 |  | 0.42273 | 16.4863 | 4187 | 0.0093144 | 6.2157 | 6.225 | -0.98224 | 107.3607 | 398.2081 | -0.009149
25 |  | 0.42273 | 16.4772 | 4187 | 0.0093092 | 6.225 | 6.2343 | -0.98224 | 107.4204 | 414.6853 | -0.0091439
26 |  | 0.42273 | 16.468 | 4187 | 0.0093041 | 6.2343 | 6.2436 | -0.98224 | 107.48 | 431.1533 | -0.0091388
27 |  | 0.42273 | 16.4589 | 4187 | 0.0092989 | 6.2436 | 6.2529 | -0.98224 | 107.5397 | 447.6122 | -0.0091338
28 |  | 0.42273 | 16.4497 | 4187 | 0.0092937 | 6.2529 | 6.2622 | -0.98224 | 107.5994 | 464.0619 | -0.0091287
29 |  | 0.42273 | 16.4406 | 4187 | 0.0092886 | 6.2622 | 6.2715 | -0.98224 | 107.6591 | 480.5025 | -0.0091236
30 |  | 0.42273 | 16.4315 | 4187 | 0.0092834 | 6.2715 | 6.2808 | -0.98224 | 107.7189 | 496.934 | -0.0091186
31 |  | 0.42273 | 16.4224 | 4187 | 0.0092783 | 6.2808 | 6.29 | -0.98224 | 107.7787 | 513.3564 | -0.0091135
32 |  | 0.42273 | 16.4133 | 4187 | 0.0092731 | 6.29 | 6.2993 | -0.98224 | 107.8386 | 529.7696 | -0.0091085
33 |  | 0.42273 | 16.4041 | 4187 | 0.009268 | 6.2993 | 6.3086 | -0.98224 | 107.8984 | 546.1738 | -0.0091034
34 |  | 0.42273 | 16.395 | 4187 | 0.0092628 | 6.3086 | 6.3178 | -0.98224 | 107.9584 | 562.5688 | -0.0090984
35 |  | 0.42273 | 16.3859 | 4187 | 0.0092577 | 6.3178 | 6.3271 | -0.98224 | 108.0183 | 578.9548 | -0.0090933
36 |  | 0.42273 | 16.3769 | 4187 | 0.0092526 | 6.3271 | 6.3363 | -0.98224 | 108.0783 | 595.3316 | -0.0090883
37 |  | 0.42273 | 16.3678 | 4187 | 0.0092474 | 6.3363 | 6.3456 | -0.98224 | 108.1383 | 611.6994 | -0.0090832
38 |  | 0.42273 | 16.3587 | 4187 | 0.0092423 | 6.3456 | 6.3548 | -0.98224 | 108.1983 | 628.0581 | -0.0090782
39 |  | 0.42273 | 16.3496 | 4187 | 0.0092372 | 6.3548 | 6.3641 | -0.98224 | 108.2584 | 644.4077 | -0.0090731
40 |  | 0.42273 | 16.3405 | 4187 | 0.009232 | 6.3641 | 6.3733 | -0.98224 | 108.3185 | 660.7482 | -0.0090681
41 |  | 0.42273 | 16.3315 | 4187 | 0.0092269 | 6.3733 | 6.3825 | -0.98224 | 108.3787 | 677.0796 | -0.0090631
42 |  | 0.42273 | 16.3224 | 4187 | 0.0092218 | 6.3825 | 6.3918 | -0.98224 | 108.4388 | 693.402 | -0.009058
43 |  | 0.42273 | 16.3133 | 4187 | 0.0092167 | 6.3918 | 6.401 | -0.98224 | 108.4991 | 709.7154 | -0.009053
44 |  | 0.42273 | 16.3043 | 4187 | 0.0092116 | 6.401 | 6.4102 | -0.98224 | 108.5593 | 726.0197 | -0.009048
45 |  | 0.42273 | 16.2952 | 4187 | 0.0092064 | 6.4102 | 6.4194 | -0.98224 | 108.6196 | 742.3149 | -0.009043
46 |  | 0.42273 | 16.2862 | 4187 | 0.0092013 | 6.4194 | 6.4286 | -0.98224 | 108.6799 | 758.6011 | -0.009038
47 |  | 0.42273 | 16.2772 | 4187 | 0.0091962 | 6.4286 | 6.4378 | -0.98224 | 108.7402 | 774.8783 | -0.0090329
48 |  | 0.42273 | 16.2681 | 4187 | 0.0091911 | 6.4378 | 6.447 | -0.98224 | 108.8006 | 791.1464 | -0.0090279
49 |  | 0.42273 | 16.2591 | 4187 | 0.009186 | 6.447 | 6.4562 | -0.98224 | 108.861 | 807.4055 | -0.0090229
50 |  | 0.42273 | 16.2501 | 4187 | 0.0091809 | 6.4562 | 6.4653 | -0.98224 | 108.9215 | 823.6555 | -0.0090179
51 |  | 0.42273 | 16.2411 | 4187 | 0.0091758 | 6.4653 | 6.4745 | -0.98224 | 108.982 | 839.8966 | -0.0090129
52 |  | 0.42273 | 16.232 | 4187 | 0.0091707 | 6.4745 | 6.4837 | -0.98224 | 109.0425 | 856.1286 | -0.0090079
53 |  | 0.42273 | 16.223 | 4187 | 0.0091657 | 6.4837 | 6.4929 | -0.98224 | 109.103 | 872.3517 | -0.0090029
54 |  | 0.42273 | 16.214 | 4187 | 0.0091606 | 6.4929 | 6.502 | -0.98224 | 109.1636 | 888.5657 | -0.0089979
55 |  | 0.42273 | 16.205 | 4187 | 0.0091555 | 6.502 | 6.5112 | -0.98224 | 109.2242 | 904.7707 | -0.0089929
56 |  | 0.42273 | 16.196 | 4187 | 0.0091504 | 6.5112 | 6.5203 | -0.98224 | 109.2849 | 920.9668 | -0.0089879
57 |  | 0.42273 | 16.1871 | 4187 | 0.0091453 | 6.5203 | 6.5295 | -0.98224 | 109.3455 | 937.1538 | -0.0089829
58 |  | 0.42273 | 16.1781 | 4187 | 0.0091402 | 6.5295 | 6.5386 | -0.98224 | 109.4062 | 953.3319 | -0.0089779
59 |  | 0.42273 | 16.1691 | 4187 | 0.0091352 | 6.5386 | 6.5477 | -0.98224 | 109.467 | 969.501 | -0.008973
60 |  | 0.42273 | 16.1601 | 4187 | 0.0091301 | 6.5477 | 6.5569 | -0.98224 | 109.5278 | 985.6611 | -0.008968
61 |  | 0.42273 | 16.1512 | 4187 | 0.009125 | 6.5569 | 6.566 | -0.98224 | 109.5886 | 1001.8123 | -0.008963
62 |  | 0.42273 | 16.1422 | 4187 | 0.00912 | 6.566 | 6.5751 | -0.98224 | 109.6494 | 1017.9545 | -0.008958
63 |  | 0.42273 | 16.1332 | 4187 | 0.0091149 | 6.5751 | 6.5842 | -0.98224 | 109.7103 | 1034.0877 | -0.0089531
64 |  | 0.42273 | 16.1243 | 4187 | 0.0091099 | 6.5842 | 6.5933 | -0.98224 | 109.7712 | 1050.212 | -0.0089481
65 |  | 0.42273 | 16.1153 | 4187 | 0.0091048 | 6.5933 | 6.6025 | -0.98224 | 109.8322 | 1066.3273 | -0.0089431
66 |  | 0.42273 | 16.1064 | 4187 | 0.0090997 | 6.6025 | 6.6116 | -0.98224 | 109.8932 | 1082.4337 | -0.0089382
67 |  | 0.42273 | 16.0974 | 4187 | 0.0090947 | 6.6116 | 6.6206 | -0.98224 | 109.9542 | 1098.5311 | -0.0089332
68 |  | 0.42273 | 16.0885 | 4187 | 0.0090896 | 6.6206 | 6.6297 | -0.98224 | 110.0152 | 1114.6196 | -0.0089282
69 |  | 0.42273 | 16.0796 | 4187 | 0.0090846 | 6.6297 | 6.6388 | -0.98224 | 110.0763 | 1130.6992 | -0.0089233
70 |  | 0.42273 | 16.0707 | 4187 | 0.0090796 | 6.6388 | 6.6479 | -0.98224 | 110.1375 | 1146.7699 | -0.0089183
71 |  | 0.42273 | 16.0617 | 4187 | 0.0090745 | 6.6479 | 6.657 | -0.98224 | 110.1986 | 1162.8316 | -0.0089134
72 |  | 0.42273 | 16.0528 | 4187 | 0.0090695 | 6.657 | 6.666 | -0.98224 | 110.2598 | 1178.8845 | -0.0089084
73 |  | 0.42273 | 16.0439 | 4187 | 0.0090645 | 6.666 | 6.6751 | -0.98224 | 110.321 | 1194.9284 | -0.0089035
74 |  | 0.42273 | 16.035 | 4187 | 0.0090594 | 6.6751 | 6.6842 | -0.98224 | 110.3823 | 1210.9634 | -0.0088986
75 |  | 0.42273 | 16.0261 | 4187 | 0.0090544 | 6.6842 | 6.6932 | -0.98224 | 110.4436 | 1226.9895 | -0.0088936
76 |  | 0.42273 | 16.0172 | 4187 | 0.0090494 | 6.6932 | 6.7023 | -0.98224 | 110.5049 | 1243.0067 | -0.0088887
77 |  | 0.42273 | 16.0083 | 4187 | 0.0090444 | 6.7023 | 6.7113 | -0.98224 | 110.5662 | 1259.0151 | -0.0088838
78 |  | 0.42273 | 15.9995 | 4187 | 0.0090393 | 6.7113 | 6.7204 | -0.98224 | 110.6276 | 1275.0145 | -0.0088788
79 |  | 0.42273 | 15.9906 | 4187 | 0.0090343 | 6.7204 | 6.7294 | -0.98224 | 110.6891 | 1291.0051 | -0.0088739
80 |  | 0.42273 | 15.9817 | 4187 | 0.0090293 | 6.7294 | 6.7384 | -0.98224 | 110.7505 | 1306.9868 | -0.008869
81 |  | 0.42273 | 15.9728 | 4187 | 0.0090243 | 6.7384 | 6.7474 | -0.98224 | 110.812 | 1322.9596 | -0.0088641
82 |  | 0.42273 | 15.964 | 4187 | 0.0090193 | 6.7474 | 6.7565 | -0.98224 | 110.8736 | 1338.9236 | -0.0088591
83 |  | 0.42273 | 15.9551 | 4187 | 0.0090143 | 6.7565 | 6.7655 | -0.98224 | 110.9351 | 1354.8787 | -0.0088542
84 |  | 0.42273 | 15.9463 | 4187 | 0.0090093 | 6.7655 | 6.7745 | -0.98224 | 110.9967 | 1370.825 | -0.0088493
85 |  | 0.42273 | 15.9374 | 4187 | 0.0090043 | 6.7745 | 6.7835 | -0.98224 | 111.0583 | 1386.7624 | -0.0088444
86 |  | 0.42273 | 15.9286 | 4187 | 0.0089993 | 6.7835 | 6.7925 | -0.98224 | 111.12 | 1402.6909 | -0.0088395
87 |  | 0.42273 | 15.9197 | 4187 | 0.0089943 | 6.7925 | 6.8015 | -0.98224 | 111.1817 | 1418.6107 | -0.0088346
88 |  | 0.42273 | 15.9109 | 4187 | 0.0089893 | 6.8015 | 6.8105 | -0.98224 | 111.2434 | 1434.5216 | -0.0088297
89 |  | 0.42273 | 15.9021 | 4187 | 0.0089843 | 6.8105 | 6.8195 | -0.98224 | 111.3052 | 1450.4236 | -0.0088248
90 |  | 0.42273 | 15.8932 | 4187 | 0.0089793 | 6.8195 | 6.8284 | -0.98224 | 111.367 | 1466.3168 | -0.0088199
91 |  | 0.42273 | 15.8844 | 4187 | 0.0089743 | 6.8284 | 6.8374 | -0.98224 | 111.4288 | 1482.2013 | -0.008815
92 |  | 0.42273 | 15.8756 | 4187 | 0.0089694 | 6.8374 | 6.8464 | -0.98224 | 111.4907 | 1498.0769 | -0.0088101
93 |  | 0.42273 | 15.8668 | 4187 | 0.0089644 | 6.8464 | 6.8553 | -0.98224 | 111.5526 | 1513.9436 | -0.0088052
94 |  | 0.42273 | 15.858 | 4187 | 0.0089594 | 6.8553 | 6.8643 | -0.98224 | 111.6146 | 1529.8016 | -0.0088003
95 |  | 0.42273 | 15.8492 | 4187 | 0.0089544 | 6.8643 | 6.8733 | -0.98224 | 111.6765 | 1545.6508 | -0.0087954
96 |  | 0.42273 | 15.8404 | 4187 | 0.0089495 | 6.8733 | 6.8822 | -0.98224 | 111.7385 | 1561.4912 | -0.0087906
97 |  | 0.42273 | 15.8316 | 4187 | 0.0089445 | 6.8822 | 6.8912 | -0.98224 | 111.8006 | 1577.3228 | -0.0087857
98 |  | 0.42273 | 15.8228 | 4187 | 0.0089395 | 6.8912 | 6.9001 | -0.98224 | 111.8627 | 1593.1456 | -0.0087808
99 |  | 0.42273 | 15.814 | 4187 | 0.0089346 | 6.9001 | 6.909 | -0.98224 | 111.9248 | 1608.9596 | -0.0087759
100 |  | 0.42273 | 15.8053 | 4187 | 0.0089296 | 6.909 | 6.918 | -0.98224 | 111.9869 | 1624.7649 | -0.0087711
101 |  | 0.42273 | 15.7965 | 4187 | 0.0089247 | 6.918 | 6.9269 | -0.98224 | 112.0491 | 1640.5614 | -0.0087662
102 |  | 0.42273 | 15.7877 | 4187 | 0.0089197 | 6.9269 | 6.9358 | -0.98224 | 112.1113 | 1656.3491 | -0.0087613
103 |  | 0.42273 | 15.779 | 4187 | 0.0089148 | 6.9358 | 6.9447 | -0.98224 | 112.1736 | 1672.128 | -0.0087565
104 |  | 0.42273 | 15.7702 | 4187 | 0.0089098 | 6.9447 | 6.9536 | -0.98224 | 112.2359 | 1687.8982 | -0.0087516
105 |  | 0.42273 | 15.7614 | 4187 | 0.0089049 | 6.9536 | 6.9625 | -0.98224 | 112.2982 | 1703.6597 | -0.0087467
106 |  | 0.42273 | 15.7527 | 4187 | 0.0088999 | 6.9625 | 6.9714 | -0.98224 | 112.3605 | 1719.4124 | -0.0087419
107 |  | 0.42273 | 15.744 | 4187 | 0.008895 | 6.9714 | 6.9803 | -0.98224 | 112.4229 | 1735.1563 | -0.008737
108 |  | 0.42273 | 15.7352 | 4187 | 0.00889 | 6.9803 | 6.9892 | -0.98224 | 112.4853 | 1750.8916 | -0.0087322
109 |  | 0.42273 | 15.7265 | 4187 | 0.0088851 | 6.9892 | 6.9981 | -0.98224 | 112.5478 | 1766.6181 | -0.0087273
110 |  | 0.42273 | 15.7178 | 4187 | 0.0088802 | 6.9981 | 7.007 | -0.98224 | 112.6103 | 1782.3358 | -0.0087225
111 |  | 0.42273 | 15.709 | 4187 | 0.0088753 | 7.007 | 7.0159 | -0.98224 | 112.6728 | 1798.0449 | -0.0087177
112 |  | 0.42273 | 15.7003 | 4187 | 0.0088703 | 7.0159 | 7.0247 | -0.98224 | 112.7354 | 1813.7452 | -0.0087128
113 |  | 0.42273 | 15.6916 | 4187 | 0.0088654 | 7.0247 | 7.0336 | -0.98224 | 112.798 | 1829.4368 | -0.008708
114 |  | 0.42273 | 15.6829 | 4187 | 0.0088605 | 7.0336 | 7.0425 | -0.98224 | 112.8606 | 1845.1197 | -0.0087032
115 |  | 0.42273 | 15.6742 | 4187 | 0.0088556 | 7.0425 | 7.0513 | -0.98224 | 112.9233 | 1860.7939 | -0.0086983
116 |  | 0.42273 | 15.6655 | 4187 | 0.0088507 | 7.0513 | 7.0602 | -0.98224 | 112.986 | 1876.4594 | -0.0086935
117 |  | 0.42273 | 15.6568 | 4187 | 0.0088457 | 7.0602 | 7.069 | -0.98224 | 113.0487 | 1892.1162 | -0.0086887
118 |  | 0.42273 | 15.6481 | 4187 | 0.0088408 | 7.069 | 7.0778 | -0.98224 | 113.1115 | 1907.7643 | -0.0086839
119 |  | 0.42273 | 15.6394 | 4187 | 0.0088359 | 7.0778 | 7.0867 | -0.98224 | 113.1743 | 1923.4037 | -0.008679
120 |  | 0.42273 | 15.6308 | 4187 | 0.008831 | 7.0867 | 7.0955 | -0.98224 | 113.2371 | 1939.0345 | -0.0086742
121 |  | 0.42273 | 15.6221 | 4187 | 0.0088261 | 7.0955 | 7.1043 | -0.98224 | 113.3 | 1954.6566 | -0.0086694
122 |  | 0.42273 | 15.6134 | 4187 | 0.0088212 | 7.1043 | 7.1132 | -0.98224 | 113.3629 | 1970.27 | -0.0086646
123 |  | 0.42273 | 15.6047 | 4187 | 0.0088163 | 7.1132 | 7.122 | -0.98224 | 113.4259 | 1985.8747 | -0.0086598
124 |  | 0.42273 | 15.5961 | 4187 | 0.0088114 | 7.122 | 7.1308 | -0.98224 | 113.4888 | 2001.4708 | -0.008655
125 |  | 0.42273 | 15.5874 | 4187 | 0.0088065 | 7.1308 | 7.1396 | -0.98224 | 113.5519 | 2017.0583 | -0.0086502
126 |  | 0.42273 | 15.5788 | 4187 | 0.0088017 | 7.1396 | 7.1484 | -0.98224 | 113.6149 | 2032.637 | -0.0086454
127 |  | 0.42273 | 15.5701 | 4187 | 0.0087968 | 7.1484 | 7.1572 | -0.98224 | 113.678 | 2048.2072 | -0.0086406
128 |  | 0.42273 | 15.5615 | 4187 | 0.0087919 | 7.1572 | 7.166 | -0.98224 | 113.7411 | 2063.7687 | -0.0086358
129 |  | 0.42273 | 15.5529 | 4187 | 0.008787 | 7.166 | 7.1748 | -0.98224 | 113.8043 | 2079.3215 | -0.008631
130 |  | 0.42273 | 15.5442 | 4187 | 0.0087821 | 7.1748 | 7.1836 | -0.98224 | 113.8675 | 2094.8658 | -0.0086262
131 |  | 0.42273 | 15.5356 | 4187 | 0.0087773 | 7.1836 | 7.1923 | -0.98224 | 113.9307 | 2110.4014 | -0.0086214
132 |  | 0.42273 | 15.527 | 4187 | 0.0087724 | 7.1923 | 7.2011 | -0.98224 | 113.9939 | 2125.9283 | -0.0086166
133 |  | 0.42273 | 15.5184 | 4187 | 0.0087675 | 7.2011 | 7.2099 | -0.98224 | 114.0572 | 2141.4467 | -0.0086118
134 |  | 0.42273 | 15.5098 | 4187 | 0.0087627 | 7.2099 | 7.2186 | -0.98224 | 114.1206 | 2156.9565 | -0.0086071
135 |  | 0.42273 | 15.5011 | 4187 | 0.0087578 | 7.2186 | 7.2274 | -0.98224 | 114.1839 | 2172.4576 | -0.0086023
136 |  | 0.42273 | 15.4925 | 4187 | 0.0087529 | 7.2274 | 7.2361 | -0.98224 | 114.2473 | 2187.9501 | -0.0085975
137 |  | 0.42273 | 15.4839 | 4187 | 0.0087481 | 7.2361 | 7.2449 | -0.98224 | 114.3108 | 2203.4341 | -0.0085927
138 |  | 0.42273 | 15.4754 | 4187 | 0.0087432 | 7.2449 | 7.2536 | -0.98224 | 114.3742 | 2218.9094 | -0.008588
139 |  | 0.42273 | 15.4668 | 4187 | 0.0087384 | 7.2536 | 7.2624 | -0.98224 | 114.4378 | 2234.3762 | -0.0085832
140 |  | 0.42273 | 15.4582 | 4187 | 0.0087335 | 7.2624 | 7.2711 | -0.98224 | 114.5013 | 2249.8344 | -0.0085784
141 |  | 0.42273 | 15.4496 | 4187 | 0.0087287 | 7.2711 | 7.2798 | -0.98224 | 114.5649 | 2265.284 | -0.0085737
142 |  | 0.42273 | 15.441 | 4187 | 0.0087238 | 7.2798 | 7.2886 | -0.98224 | 114.6285 | 2280.725 | -0.0085689
143 |  | 0.42273 | 15.4325 | 4187 | 0.008719 | 7.2886 | 7.2973 | -0.98224 | 114.6921 | 2296.1575 | -0.0085642
144 |  | 0.42273 | 15.4239 | 4187 | 0.0087142 | 7.2973 | 7.306 | -0.98224 | 114.7558 | 2311.5814 | -0.0085594
145 |  | 0.42273 | 15.4153 | 4187 | 0.0087093 | 7.306 | 7.3147 | -0.98224 | 114.8195 | 2326.9967 | -0.0085547
146 |  | 0.42273 | 15.4068 | 4187 | 0.0087045 | 7.3147 | 7.3234 | -0.98224 | 114.8833 | 2342.4035 | -0.0085499
147 |  | 0.42273 | 15.3982 | 4187 | 0.0086997 | 7.3234 | 7.3321 | -0.98224 | 114.9471 | 2357.8017 | -0.0085452
148 |  | 0.42273 | 15.3897 | 4187 | 0.0086948 | 7.3321 | 7.3408 | -0.98224 | 115.0109 | 2373.1914 | -0.0085404
149 |  | 0.42273 | 15.3811 | 4187 | 0.00869 | 7.3408 | 7.3495 | -0.98224 | 115.0748 | 2388.5726 | -0.0085357
150 |  | 0.42273 | 15.3726 | 4187 | 0.0086852 | 7.3495 | 7.3582 | -0.98224 | 115.1387 | 2403.9452 | -0.008531
151 |  | 0.42273 | 15.3641 | 4187 | 0.0086804 | 7.3582 | 7.3669 | -0.98224 | 115.2026 | 2419.3093 | -0.0085262
152 |  | 0.42273 | 15.3556 | 4187 | 0.0086755 | 7.3669 | 7.3755 | -0.98224 | 115.2666 | 2434.6648 | -0.0085215
153 |  | 0.42273 | 15.347 | 4187 | 0.0086707 | 7.3755 | 7.3842 | -0.98224 | 115.3306 | 2450.0119 | -0.0085168
154 |  | 0.42273 | 15.3385 | 4187 | 0.0086659 | 7.3842 | 7.3929 | -0.98224 | 115.3946 | 2465.3504 | -0.008512
155 |  | 0.42273 | 15.33 | 4187 | 0.0086611 | 7.3929 | 7.4015 | -0.98224 | 115.4587 | 2480.6804 | -0.0085073
156 |  | 0.42273 | 15.3215 | 4187 | 0.0086563 | 7.4015 | 7.4102 | -0.98224 | 115.5228 | 2496.0019 | -0.0085026
157 |  | 0.42273 | 15.313 | 4187 | 0.0086515 | 7.4102 | 7.4188 | -0.98224 | 115.5869 | 2511.3149 | -0.0084979
158 |  | 0.42273 | 15.3045 | 4187 | 0.0086467 | 7.4188 | 7.4275 | -0.98224 | 115.6511 | 2526.6194 | -0.0084932
159 |  | 0.42273 | 15.296 | 4187 | 0.0086419 | 7.4275 | 7.4361 | -0.98224 | 115.7153 | 2541.9154 | -0.0084884
160 |  | 0.42273 | 15.2875 | 4187 | 0.0086371 | 7.4361 | 7.4448 | -0.98224 | 115.7796 | 2557.2029 | -0.0084837
161 |  | 0.42273 | 15.279 | 4187 | 0.0086323 | 7.4448 | 7.4534 | -0.98224 | 115.8439 | 2572.4819 | -0.008479
162 |  | 0.42273 | 15.2706 | 4187 | 0.0086275 | 7.4534 | 7.462 | -0.98224 | 115.9082 | 2587.7525 | -0.0084743
163 |  | 0.42273 | 15.2621 | 4187 | 0.0086227 | 7.462 | 7.4706 | -0.98224 | 115.9725 | 2603.0145 | -0.0084696
164 |  | 0.42273 | 15.2536 | 4187 | 0.0086179 | 7.4706 | 7.4793 | -0.98224 | 116.0369 | 2618.2681 | -0.0084649
165 |  | 0.42273 | 15.2451 | 4187 | 0.0086132 | 7.4793 | 7.4879 | -0.98224 | 116.1014 | 2633.5133 | -0.0084602
166 |  | 0.42273 | 15.2367 | 4187 | 0.0086084 | 7.4879 | 7.4965 | -0.98224 | 116.1658 | 2648.75 | -0.0084555
167 |  | 0.42273 | 15.2282 | 4187 | 0.0086036 | 7.4965 | 7.5051 | -0.98224 | 116.2303 | 2663.9782 | -0.0084508
168 |  | 0.42273 | 15.2198 | 4187 | 0.0085988 | 7.5051 | 7.5137 | -0.98224 | 116.2949 | 2679.198 | -0.0084461
169 |  | 0.42273 | 15.2113 | 4187 | 0.0085941 | 7.5137 | 7.5223 | -0.98224 | 116.3594 | 2694.4093 | -0.0084415
170 |  | 0.42273 | 15.2029 | 4187 | 0.0085893 | 7.5223 | 7.5309 | -0.98224 | 116.424 | 2709.6122 | -0.0084368
171 |  | 0.42273 | 15.1945 | 4187 | 0.0085845 | 7.5309 | 7.5395 | -0.98224 | 116.4887 | 2724.8066 | -0.0084321
172 |  | 0.42273 | 15.186 | 4187 | 0.0085798 | 7.5395 | 7.548 | -0.98224 | 116.5534 | 2739.9927 | -0.0084274
173 |  | 0.42273 | 15.1776 | 4187 | 0.008575 | 7.548 | 7.5566 | -0.98224 | 116.6181 | 2755.1703 | -0.0084227
174 |  | 0.42273 | 15.1692 | 4187 | 0.0085702 | 7.5566 | 7.5652 | -0.98224 | 116.6828 | 2770.3394 | -0.0084181
175 |  | 0.42273 | 15.1608 | 4187 | 0.0085655 | 7.5652 | 7.5737 | -0.98224 | 116.7476 | 2785.5002 | -0.0084134
176 |  | 0.42273 | 15.1523 | 4187 | 0.0085607 | 7.5737 | 7.5823 | -0.98224 | 116.8125 | 2800.6525 | -0.0084087
177 |  | 0.42273 | 15.1439 | 4187 | 0.008556 | 7.5823 | 7.5909 | -0.98224 | 116.8773 | 2815.7964 | -0.0084041
178 |  | 0.42273 | 15.1355 | 4187 | 0.0085512 | 7.5909 | 7.5994 | -0.98224 | 116.9422 | 2830.932 | -0.0083994
179 |  | 0.42273 | 15.1271 | 4187 | 0.0085465 | 7.5994 | 7.608 | -0.98224 | 117.0071 | 2846.0591 | -0.0083947
180 |  | 0.42273 | 15.1187 | 4187 | 0.0085417 | 7.608 | 7.6165 | -0.98224 | 117.0721 | 2861.1778 | -0.0083901
181 |  | 0.42273 | 15.1103 | 4187 | 0.008537 | 7.6165 | 7.625 | -0.98224 | 117.1371 | 2876.2882 | -0.0083854
182 |  | 0.42273 | 15.102 | 4187 | 0.0085323 | 7.625 | 7.6336 | -0.98224 | 117.2022 | 2891.3901 | -0.0083808
183 |  | 0.42273 | 15.0936 | 4187 | 0.0085275 | 7.6336 | 7.6421 | -0.98224 | 117.2672 | 2906.4837 | -0.0083761
184 |  | 0.42273 | 15.0852 | 4187 | 0.0085228 | 7.6421 | 7.6506 | -0.98224 | 117.3324 | 2921.5689 | -0.0083715
185 |  | 0.42273 | 15.0768 | 4187 | 0.0085181 | 7.6506 | 7.6591 | -0.98224 | 117.3975 | 2936.6457 | -0.0083668
186 |  | 0.42273 | 15.0685 | 4187 | 0.0085133 | 7.6591 | 7.6677 | -0.98224 | 117.4627 | 2951.7142 | -0.0083622
187 |  | 0.42273 | 15.0601 | 4187 | 0.0085086 | 7.6677 | 7.6762 | -0.98224 | 117.5279 | 2966.7743 | -0.0083575
188 |  | 0.42273 | 15.0517 | 4187 | 0.0085039 | 7.6762 | 7.6847 | -0.98224 | 117.5932 | 2981.826 | -0.0083529
189 |  | 0.42273 | 15.0434 | 4187 | 0.0084992 | 7.6847 | 7.6932 | -0.98224 | 117.6585 | 2996.8694 | -0.0083483
190 |  | 0.42273 | 15.035 | 4187 | 0.0084945 | 7.6932 | 7.7017 | -0.98224 | 117.7238 | 3011.9044 | -0.0083436
191 |  | 0.42273 | 15.0267 | 4187 | 0.0084897 | 7.7017 | 7.7101 | -0.98224 | 117.7892 | 3026.9311 | -0.008339
192 |  | 0.42273 | 15.0184 | 4187 | 0.008485 | 7.7101 | 7.7186 | -0.98224 | 117.8546 | 3041.9495 | -0.0083344
193 |  | 0.42273 | 15.01 | 4187 | 0.0084803 | 7.7186 | 7.7271 | -0.98224 | 117.92 | 3056.9595 | -0.0083297
194 |  | 0.42273 | 15.0017 | 4187 | 0.0084756 | 7.7271 | 7.7356 | -0.98224 | 117.9855 | 3071.9612 | -0.0083251
195 |  | 0.42273 | 14.9934 | 4187 | 0.0084709 | 7.7356 | 7.7441 | -0.98224 | 118.051 | 3086.9546 | -0.0083205
196 |  | 0.42273 | 14.985 | 4187 | 0.0084662 | 7.7441 | 7.7525 | -0.98224 | 118.1165 | 3101.9396 | -0.0083159
197 |  | 0.42273 | 14.9767 | 4187 | 0.0084615 | 7.7525 | 7.761 | -0.98224 | 118.1821 | 3116.9164 | -0.0083113
198 |  | 0.42273 | 14.9684 | 4187 | 0.0084568 | 7.761 | 7.7694 | -0.98224 | 118.2477 | 3131.8848 | -0.0083067
199 |  | 0.42273 | 14.9601 | 4187 | 0.0084521 | 7.7694 | 7.7779 | -0.98224 | 118.3134 | 3146.8449 | -0.008302
200 |  | 0.42273 | 14.9518 | 4187 | 0.0084474 | 7.7779 | 7.7863 | -0.98224 | 118.3791 | 3161.7967 | -0.0082974
201 |  | 0.42273 | 14.9435 | 4187 | 0.0084427 | 7.7863 | 7.7948 | -0.98224 | 118.4448 | 3176.7402 | -0.0082928
202 |  | 0.42273 | 14.9352 | 4187 | 0.0084381 | 7.7948 | 7.8032 | -0.98224 | 118.5106 | 3191.6754 | -0.0082882
203 |  | 0.42273 | 14.9269 | 4187 | 0.0084334 | 7.8032 | 7.8117 | -0.98224 | 118.5764 | 3206.6024 | -0.0082836
204 |  | 0.42273 | 14.9186 | 4187 | 0.0084287 | 7.8117 | 7.8201 | -0.98224 | 118.6422 | 3221.521 | -0.008279
205 |  | 0.42273 | 14.9104 | 4187 | 0.008424 | 7.8201 | 7.8285 | -0.98224 | 118.7081 | 3236.4314 | -0.0082744
206 |  | 0.42273 | 14.9021 | 4187 | 0.0084193 | 7.8285 | 7.8369 | -0.98224 | 118.774 | 3251.3335 | -0.0082699
207 |  | 0.42273 | 14.8938 | 4187 | 0.0084147 | 7.8369 | 7.8453 | -0.98224 | 118.84 | 3266.2273 | -0.0082653
208 |  | 0.42273 | 14.8856 | 4187 | 0.00841 | 7.8453 | 7.8538 | -0.98224 | 118.906 | 3281.1129 | -0.0082607
209 |  | 0.42273 | 14.8773 | 4187 | 0.0084053 | 7.8538 | 7.8622 | -0.98224 | 118.972 | 3295.9902 | -0.0082561
210 |  | 0.42273 | 14.869 | 4187 | 0.0084007 | 7.8622 | 7.8706 | -0.98224 | 119.038 | 3310.8592 | -0.0082515
211 |  | 0.42273 | 14.8608 | 4187 | 0.008396 | 7.8706 | 7.879 | -0.98224 | 119.1041 | 3325.72 | -0.0082469
212 |  | 0.42273 | 14.8525 | 4187 | 0.0083914 | 7.879 | 7.8873 | -0.98224 | 119.1703 | 3340.5726 | -0.0082424
213 |  | 0.42273 | 14.8443 | 4187 | 0.0083867 | 7.8873 | 7.8957 | -0.98224 | 119.2364 | 3355.4169 | -0.0082378
214 |  | 0.42273 | 14.8361 | 4187 | 0.008382 | 7.8957 | 7.9041 | -0.98224 | 119.3026 | 3370.2529 | -0.0082332
215 |  | 0.42273 | 14.8278 | 4187 | 0.0083774 | 7.9041 | 7.9125 | -0.98224 | 119.3689 | 3385.0808 | -0.0082286
216 |  | 0.42273 | 14.8196 | 4187 | 0.0083727 | 7.9125 | 7.9209 | -0.98224 | 119.4352 | 3399.9004 | -0.0082241
217 |  | 0.42273 | 14.8114 | 4187 | 0.0083681 | 7.9209 | 7.9292 | -0.98224 | 119.5015 | 3414.7117 | -0.0082195
218 |  | 0.42273 | 14.8032 | 4187 | 0.0083635 | 7.9292 | 7.9376 | -0.98224 | 119.5678 | 3429.5149 | -0.0082149
219 |  | 0.42273 | 14.7949 | 4187 | 0.0083588 | 7.9376 | 7.946 | -0.98224 | 119.6342 | 3444.3098 | -0.0082104
220 |  | 0.42273 | 14.7867 | 4187 | 0.0083542 | 7.946 | 7.9543 | -0.98224 | 119.7007 | 3459.0966 | -0.0082058
221 |  | 0.42273 | 14.7785 | 4187 | 0.0083495 | 7.9543 | 7.9627 | -0.98224 | 119.7671 | 3473.8751 | -0.0082013
222 |  | 0.42273 | 14.7703 | 4187 | 0.0083449 | 7.9627 | 7.971 | -0.98224 | 119.8336 | 3488.6454 | -0.0081967
223 |  | 0.42273 | 14.7621 | 4187 | 0.0083403 | 7.971 | 7.9793 | -0.98224 | 119.9002 | 3503.4076 | -0.0081922
224 |  | 0.42273 | 14.7539 | 4187 | 0.0083356 | 7.9793 | 7.9877 | -0.98224 | 119.9667 | 3518.1615 | -0.0081876
225 |  | 0.42273 | 14.7458 | 4187 | 0.008331 | 7.9877 | 7.996 | -0.98224 | 120.0333 | 3532.9073 | -0.0081831
226 |  | 0.42273 | 14.7376 | 4187 | 0.0083264 | 7.996 | 8.0043 | -0.98224 | 120.1 | 3547.6448 | -0.0081785
227 |  | 0.42273 | 14.7294 | 4187 | 0.0083218 | 8.0043 | 8.0127 | -0.98224 | 120.1667 | 3562.3742 | -0.008174
228 |  | 0.42273 | 14.7212 | 4187 | 0.0083172 | 8.0127 | 8.021 | -0.98224 | 120.2334 | 3577.0954 | -0.0081695
229 |  | 0.42273 | 14.713 | 4187 | 0.0083125 | 8.021 | 8.0293 | -0.98224 | 120.3002 | 3591.8085 | -0.0081649
230 |  | 0.42273 | 14.7049 | 4187 | 0.0083079 | 8.0293 | 8.0376 | -0.98224 | 120.367 | 3606.5134 | -0.0081604
231 |  | 0.42273 | 14.6967 | 4187 | 0.0083033 | 8.0376 | 8.0459 | -0.98224 | 120.4338 | 3621.2101 | -0.0081559
232 |  | 0.42273 | 14.6886 | 4187 | 0.0082987 | 8.0459 | 8.0542 | -0.98224 | 120.5007 | 3635.8986 | -0.0081514
233 |  | 0.42273 | 14.6804 | 4187 | 0.0082941 | 8.0542 | 8.0625 | -0.98224 | 120.5676 | 3650.5791 | -0.0081468
234 |  | 0.42273 | 14.6723 | 4187 | 0.0082895 | 8.0625 | 8.0708 | -0.98224 | 120.6345 | 3665.2513 | -0.0081423
235 |  | 0.42273 | 14.6641 | 4187 | 0.0082849 | 8.0708 | 8.0791 | -0.98224 | 120.7015 | 3679.9154 | -0.0081378
236 |  | 0.42273 | 14.656 | 4187 | 0.0082803 | 8.0791 | 8.0873 | -0.98224 | 120.7685 | 3694.5714 | -0.0081333

## Fus40
|  |  | buis | verlies W/M | L /°C/sec
diam | wandikte |  | inhoud l/m |  | W/M
40 | 5.5 | 3.1416 | 0.66052 | 19.259 | 4187
[8 empty] | J/sec/mtr | aantal mtr. | verlies
|  | buis | verlies W/M | L /°C/sec | verlies temp | begintemp | eindtemp | verlies | bij 1°C | totaal J/sec
|  | inhoud L |  | W/M | °C per M | °C | °C | per m°C | daling | aantal mtr
1 | 40 | 0.66052 | 19.259 | 4187 | 0.0069638 | 6 | 6.007 | -1.1329 | 143.6002 | 19.259 | -0.0078891
2 |  | 0.66052 | 19.2511 | 4187 | 0.0069609 | 6.007 | 6.0139 | -1.1329 | 143.6591 | 38.5101 | -0.0078859
3 |  | 0.66052 | 19.2432 | 4187 | 0.0069581 | 6.0139 | 6.0209 | -1.1329 | 143.7179 | 57.7533 | -0.0078827
4 |  | 0.66052 | 19.2353 | 4187 | 0.0069552 | 6.0209 | 6.0278 | -1.1329 | 143.7768 | 76.9887 | -0.0078794
5 |  | 0.66052 | 19.2275 | 4187 | 0.0069524 | 6.0278 | 6.0348 | -1.1329 | 143.8358 | 96.2161 | -0.0078762
6 |  | 0.66052 | 19.2196 | 4187 | 0.0069495 | 6.0348 | 6.0417 | -1.1329 | 143.8947 | 115.4357 | -0.007873
7 |  | 0.66052 | 19.2117 | 4187 | 0.0069467 | 6.0417 | 6.0487 | -1.1329 | 143.9537 | 134.6474 | -0.0078698
8 |  | 0.66052 | 19.2038 | 4187 | 0.0069438 | 6.0487 | 6.0556 | -1.1329 | 144.0127 | 153.8513 | -0.0078665
9 |  | 0.66052 | 19.196 | 4187 | 0.006941 | 6.0556 | 6.0626 | -1.1329 | 144.0717 | 173.0473 | -0.0078633
10 |  | 0.66052 | 19.1881 | 4187 | 0.0069381 | 6.0626 | 6.0695 | -1.1329 | 144.1307 | 192.2354 | -0.0078601
11 |  | 0.66052 | 19.1803 | 4187 | 0.0069353 | 6.0695 | 6.0764 | -1.1329 | 144.1898 | 211.4156 | -0.0078569
12 |  | 0.66052 | 19.1724 | 4187 | 0.0069325 | 6.0764 | 6.0834 | -1.1329 | 144.2489 | 230.588 | -0.0078537
13 |  | 0.66052 | 19.1645 | 4187 | 0.0069296 | 6.0834 | 6.0903 | -1.1329 | 144.308 | 249.7526 | -0.0078504
14 |  | 0.66052 | 19.1567 | 4187 | 0.0069268 | 6.0903 | 6.0972 | -1.1329 | 144.3671 | 268.9092 | -0.0078472
15 |  | 0.66052 | 19.1488 | 4187 | 0.0069239 | 6.0972 | 6.1042 | -1.1329 | 144.4263 | 288.0581 | -0.007844
16 |  | 0.66052 | 19.141 | 4187 | 0.0069211 | 6.1042 | 6.1111 | -1.1329 | 144.4855 | 307.1991 | -0.0078408
17 |  | 0.66052 | 19.1332 | 4187 | 0.0069183 | 6.1111 | 6.118 | -1.1329 | 144.5447 | 326.3322 | -0.0078376
18 |  | 0.66052 | 19.1253 | 4187 | 0.0069154 | 6.118 | 6.1249 | -1.1329 | 144.6039 | 345.4576 | -0.0078344
19 |  | 0.66052 | 19.1175 | 4187 | 0.0069126 | 6.1249 | 6.1318 | -1.1329 | 144.6632 | 364.5751 | -0.0078312
20 |  | 0.66052 | 19.1097 | 4187 | 0.0069098 | 6.1318 | 6.1387 | -1.1329 | 144.7225 | 383.6847 | -0.007828
21 |  | 0.66052 | 19.1018 | 4187 | 0.0069069 | 6.1387 | 6.1456 | -1.1329 | 144.7818 | 402.7865 | -0.0078248
22 |  | 0.66052 | 19.094 | 4187 | 0.0069041 | 6.1456 | 6.1525 | -1.1329 | 144.8411 | 421.8805 | -0.0078216
23 |  | 0.66052 | 19.0862 | 4187 | 0.0069013 | 6.1525 | 6.1594 | -1.1329 | 144.9005 | 440.9667 | -0.0078183
24 |  | 0.66052 | 19.0784 | 4187 | 0.0068985 | 6.1594 | 6.1663 | -1.1329 | 144.9598 | 460.0451 | -0.0078151
25 |  | 0.66052 | 19.0705 | 4187 | 0.0068956 | 6.1663 | 6.1732 | -1.1329 | 145.0192 | 479.1156 | -0.0078119
26 |  | 0.66052 | 19.0627 | 4187 | 0.0068928 | 6.1732 | 6.1801 | -1.1329 | 145.0787 | 498.1784 | -0.0078087
27 |  | 0.66052 | 19.0549 | 4187 | 0.00689 | 6.1801 | 6.187 | -1.1329 | 145.1381 | 517.2333 | -0.0078055
28 |  | 0.66052 | 19.0471 | 4187 | 0.0068872 | 6.187 | 6.1939 | -1.1329 | 145.1976 | 536.2804 | -0.0078023
29 |  | 0.66052 | 19.0393 | 4187 | 0.0068843 | 6.1939 | 6.2008 | -1.1329 | 145.2571 | 555.3197 | -0.0077992
30 |  | 0.66052 | 19.0315 | 4187 | 0.0068815 | 6.2008 | 6.2077 | -1.1329 | 145.3166 | 574.3513 | -0.007796
31 |  | 0.66052 | 19.0237 | 4187 | 0.0068787 | 6.2077 | 6.2146 | -1.1329 | 145.3762 | 593.375 | -0.0077928
32 |  | 0.66052 | 19.0159 | 4187 | 0.0068759 | 6.2146 | 6.2214 | -1.1329 | 145.4358 | 612.3909 | -0.0077896
33 |  | 0.66052 | 19.0081 | 4187 | 0.0068731 | 6.2214 | 6.2283 | -1.1329 | 145.4954 | 631.3991 | -0.0077864
34 |  | 0.66052 | 19.0004 | 4187 | 0.0068703 | 6.2283 | 6.2352 | -1.1329 | 145.555 | 650.3994 | -0.0077832
35 |  | 0.66052 | 18.9926 | 4187 | 0.0068674 | 6.2352 | 6.242 | -1.1329 | 145.6146 | 669.392 | -0.00778
36 |  | 0.66052 | 18.9848 | 4187 | 0.0068646 | 6.242 | 6.2489 | -1.1329 | 145.6743 | 688.3768 | -0.0077768
37 |  | 0.66052 | 18.977 | 4187 | 0.0068618 | 6.2489 | 6.2558 | -1.1329 | 145.734 | 707.3538 | -0.0077736
38 |  | 0.66052 | 18.9692 | 4187 | 0.006859 | 6.2558 | 6.2626 | -1.1329 | 145.7937 | 726.3231 | -0.0077704
39 |  | 0.66052 | 18.9615 | 4187 | 0.0068562 | 6.2626 | 6.2695 | -1.1329 | 145.8535 | 745.2845 | -0.0077673
40 |  | 0.66052 | 18.9537 | 4187 | 0.0068534 | 6.2695 | 6.2763 | -1.1329 | 145.9132 | 764.2382 | -0.0077641
41 |  | 0.66052 | 18.9459 | 4187 | 0.0068506 | 6.2763 | 6.2832 | -1.1329 | 145.973 | 783.1842 | -0.0077609
42 |  | 0.66052 | 18.9382 | 4187 | 0.0068478 | 6.2832 | 6.29 | -1.1329 | 146.0329 | 802.1223 | -0.0077577
43 |  | 0.66052 | 18.9304 | 4187 | 0.006845 | 6.29 | 6.2969 | -1.1329 | 146.0927 | 821.0528 | -0.0077545
44 |  | 0.66052 | 18.9227 | 4187 | 0.0068422 | 6.2969 | 6.3037 | -1.1329 | 146.1526 | 839.9754 | -0.0077514
45 |  | 0.66052 | 18.9149 | 4187 | 0.0068394 | 6.3037 | 6.3106 | -1.1329 | 146.2125 | 858.8904 | -0.0077482
46 |  | 0.66052 | 18.9072 | 4187 | 0.0068366 | 6.3106 | 6.3174 | -1.1329 | 146.2724 | 877.7975 | -0.007745
47 |  | 0.66052 | 18.8994 | 4187 | 0.0068338 | 6.3174 | 6.3242 | -1.1329 | 146.3323 | 896.6969 | -0.0077418
48 |  | 0.66052 | 18.8917 | 4187 | 0.006831 | 6.3242 | 6.3311 | -1.1329 | 146.3923 | 915.5886 | -0.0077387
49 |  | 0.66052 | 18.8839 | 4187 | 0.0068282 | 6.3311 | 6.3379 | -1.1329 | 146.4523 | 934.4726 | -0.0077355
50 |  | 0.66052 | 18.8762 | 4187 | 0.0068254 | 6.3379 | 6.3447 | -1.1329 | 146.5123 | 953.3488 | -0.0077323
51 |  | 0.66052 | 18.8685 | 4187 | 0.0068226 | 6.3447 | 6.3515 | -1.1329 | 146.5723 | 972.2173 | -0.0077292
52 |  | 0.66052 | 18.8607 | 4187 | 0.0068198 | 6.3515 | 6.3584 | -1.1329 | 146.6324 | 991.078 | -0.007726
53 |  | 0.66052 | 18.853 | 4187 | 0.006817 | 6.3584 | 6.3652 | -1.1329 | 146.6925 | 1009.931 | -0.0077228
54 |  | 0.66052 | 18.8453 | 4187 | 0.0068142 | 6.3652 | 6.372 | -1.1329 | 146.7526 | 1028.7763 | -0.0077197
55 |  | 0.66052 | 18.8376 | 4187 | 0.0068114 | 6.372 | 6.3788 | -1.1329 | 146.8128 | 1047.6139 | -0.0077165
56 |  | 0.66052 | 18.8299 | 4187 | 0.0068086 | 6.3788 | 6.3856 | -1.1329 | 146.8729 | 1066.4438 | -0.0077134
57 |  | 0.66052 | 18.8221 | 4187 | 0.0068058 | 6.3856 | 6.3924 | -1.1329 | 146.9331 | 1085.2659 | -0.0077102
58 |  | 0.66052 | 18.8144 | 4187 | 0.006803 | 6.3924 | 6.3992 | -1.1329 | 146.9933 | 1104.0803 | -0.007707
59 |  | 0.66052 | 18.8067 | 4187 | 0.0068002 | 6.3992 | 6.406 | -1.1329 | 147.0536 | 1122.8871 | -0.0077039
60 |  | 0.66052 | 18.799 | 4187 | 0.0067975 | 6.406 | 6.4128 | -1.1329 | 147.1138 | 1141.6861 | -0.0077007
61 |  | 0.66052 | 18.7913 | 4187 | 0.0067947 | 6.4128 | 6.4196 | -1.1329 | 147.1741 | 1160.4774 | -0.0076976
62 |  | 0.66052 | 18.7836 | 4187 | 0.0067919 | 6.4196 | 6.4264 | -1.1329 | 147.2344 | 1179.261 | -0.0076944
63 |  | 0.66052 | 18.7759 | 4187 | 0.0067891 | 6.4264 | 6.4332 | -1.1329 | 147.2948 | 1198.037 | -0.0076913
64 |  | 0.66052 | 18.7682 | 4187 | 0.0067863 | 6.4332 | 6.44 | -1.1329 | 147.3551 | 1216.8052 | -0.0076881
65 |  | 0.66052 | 18.7606 | 4187 | 0.0067835 | 6.44 | 6.4468 | -1.1329 | 147.4155 | 1235.5658 | -0.007685
66 |  | 0.66052 | 18.7529 | 4187 | 0.0067808 | 6.4468 | 6.4535 | -1.1329 | 147.4759 | 1254.3186 | -0.0076818
67 |  | 0.66052 | 18.7452 | 4187 | 0.006778 | 6.4535 | 6.4603 | -1.1329 | 147.5364 | 1273.0638 | -0.0076787
68 |  | 0.66052 | 18.7375 | 4187 | 0.0067752 | 6.4603 | 6.4671 | -1.1329 | 147.5968 | 1291.8013 | -0.0076755
69 |  | 0.66052 | 18.7298 | 4187 | 0.0067724 | 6.4671 | 6.4739 | -1.1329 | 147.6573 | 1310.5312 | -0.0076724
70 |  | 0.66052 | 18.7222 | 4187 | 0.0067697 | 6.4739 | 6.4806 | -1.1329 | 147.7178 | 1329.2533 | -0.0076692
71 |  | 0.66052 | 18.7145 | 4187 | 0.0067669 | 6.4806 | 6.4874 | -1.1329 | 147.7783 | 1347.9678 | -0.0076661
72 |  | 0.66052 | 18.7068 | 4187 | 0.0067641 | 6.4874 | 6.4942 | -1.1329 | 147.8389 | 1366.6746 | -0.007663
73 |  | 0.66052 | 18.6992 | 4187 | 0.0067613 | 6.4942 | 6.5009 | -1.1329 | 147.8995 | 1385.3738 | -0.0076598
74 |  | 0.66052 | 18.6915 | 4187 | 0.0067586 | 6.5009 | 6.5077 | -1.1329 | 147.9601 | 1404.0653 | -0.0076567
75 |  | 0.66052 | 18.6838 | 4187 | 0.0067558 | 6.5077 | 6.5144 | -1.1329 | 148.0207 | 1422.7492 | -0.0076535
76 |  | 0.66052 | 18.6762 | 4187 | 0.006753 | 6.5144 | 6.5212 | -1.1329 | 148.0814 | 1441.4254 | -0.0076504
77 |  | 0.66052 | 18.6685 | 4187 | 0.0067503 | 6.5212 | 6.5279 | -1.1329 | 148.1421 | 1460.0939 | -0.0076473
78 |  | 0.66052 | 18.6609 | 4187 | 0.0067475 | 6.5279 | 6.5347 | -1.1329 | 148.2028 | 1478.7548 | -0.0076441
79 |  | 0.66052 | 18.6533 | 4187 | 0.0067447 | 6.5347 | 6.5414 | -1.1329 | 148.2635 | 1497.408 | -0.007641
80 |  | 0.66052 | 18.6456 | 4187 | 0.006742 | 6.5414 | 6.5482 | -1.1329 | 148.3243 | 1516.0536 | -0.0076379
81 |  | 0.66052 | 18.638 | 4187 | 0.0067392 | 6.5482 | 6.5549 | -1.1329 | 148.3851 | 1534.6916 | -0.0076347
82 |  | 0.66052 | 18.6303 | 4187 | 0.0067365 | 6.5549 | 6.5617 | -1.1329 | 148.4459 | 1553.322 | -0.0076316
83 |  | 0.66052 | 18.6227 | 4187 | 0.0067337 | 6.5617 | 6.5684 | -1.1329 | 148.5067 | 1571.9447 | -0.0076285
84 |  | 0.66052 | 18.6151 | 4187 | 0.0067309 | 6.5684 | 6.5751 | -1.1329 | 148.5676 | 1590.5597 | -0.0076254
85 |  | 0.66052 | 18.6075 | 4187 | 0.0067282 | 6.5751 | 6.5819 | -1.1329 | 148.6284 | 1609.1672 | -0.0076222
86 |  | 0.66052 | 18.5998 | 4187 | 0.0067254 | 6.5819 | 6.5886 | -1.1329 | 148.6894 | 1627.767 | -0.0076191
87 |  | 0.66052 | 18.5922 | 4187 | 0.0067227 | 6.5886 | 6.5953 | -1.1329 | 148.7503 | 1646.3592 | -0.007616
88 |  | 0.66052 | 18.5846 | 4187 | 0.0067199 | 6.5953 | 6.602 | -1.1329 | 148.8112 | 1664.9438 | -0.0076129
89 |  | 0.66052 | 18.577 | 4187 | 0.0067172 | 6.602 | 6.6087 | -1.1329 | 148.8722 | 1683.5208 | -0.0076098
90 |  | 0.66052 | 18.5694 | 4187 | 0.0067144 | 6.6087 | 6.6155 | -1.1329 | 148.9332 | 1702.0902 | -0.0076066
91 |  | 0.66052 | 18.5618 | 4187 | 0.0067117 | 6.6155 | 6.6222 | -1.1329 | 148.9943 | 1720.6519 | -0.0076035
92 |  | 0.66052 | 18.5542 | 4187 | 0.0067089 | 6.6222 | 6.6289 | -1.1329 | 149.0553 | 1739.2061 | -0.0076004
93 |  | 0.66052 | 18.5466 | 4187 | 0.0067062 | 6.6289 | 6.6356 | -1.1329 | 149.1164 | 1757.7527 | -0.0075973
94 |  | 0.66052 | 18.539 | 4187 | 0.0067034 | 6.6356 | 6.6423 | -1.1329 | 149.1775 | 1776.2916 | -0.0075942
95 |  | 0.66052 | 18.5314 | 4187 | 0.0067007 | 6.6423 | 6.649 | -1.1329 | 149.2387 | 1794.823 | -0.0075911
96 |  | 0.66052 | 18.5238 | 4187 | 0.0066979 | 6.649 | 6.6557 | -1.1329 | 149.2998 | 1813.3468 | -0.007588
97 |  | 0.66052 | 18.5162 | 4187 | 0.0066952 | 6.6557 | 6.6624 | -1.1329 | 149.361 | 1831.863 | -0.0075849
98 |  | 0.66052 | 18.5086 | 4187 | 0.0066924 | 6.6624 | 6.6691 | -1.1329 | 149.4222 | 1850.3716 | -0.0075818
99 |  | 0.66052 | 18.501 | 4187 | 0.0066897 | 6.6691 | 6.6758 | -1.1329 | 149.4834 | 1868.8726 | -0.0075786
100 |  | 0.66052 | 18.4934 | 4187 | 0.006687 | 6.6758 | 6.6824 | -1.1329 | 149.5447 | 1887.366 | -0.0075755
101 |  | 0.66052 | 18.4859 | 4187 | 0.0066842 | 6.6824 | 6.6891 | -1.1329 | 149.606 | 1905.8519 | -0.0075724
102 |  | 0.66052 | 18.4783 | 4187 | 0.0066815 | 6.6891 | 6.6958 | -1.1329 | 149.6673 | 1924.3302 | -0.0075693
103 |  | 0.66052 | 18.4707 | 4187 | 0.0066787 | 6.6958 | 6.7025 | -1.1329 | 149.7286 | 1942.8009 | -0.0075662
104 |  | 0.66052 | 18.4632 | 4187 | 0.006676 | 6.7025 | 6.7092 | -1.1329 | 149.79 | 1961.2641 | -0.0075631
105 |  | 0.66052 | 18.4556 | 4187 | 0.0066733 | 6.7092 | 6.7158 | -1.1329 | 149.8514 | 1979.7197 | -0.00756
106 |  | 0.66052 | 18.448 | 4187 | 0.0066705 | 6.7158 | 6.7225 | -1.1329 | 149.9128 | 1998.1677 | -0.0075569
107 |  | 0.66052 | 18.4405 | 4187 | 0.0066678 | 6.7225 | 6.7292 | -1.1329 | 149.9742 | 2016.6082 | -0.0075538
108 |  | 0.66052 | 18.4329 | 4187 | 0.0066651 | 6.7292 | 6.7358 | -1.1329 | 150.0357 | 2035.0411 | -0.0075508
109 |  | 0.66052 | 18.4254 | 4187 | 0.0066624 | 6.7358 | 6.7425 | -1.1329 | 150.0972 | 2053.4665 | -0.0075477
110 |  | 0.66052 | 18.4178 | 4187 | 0.0066596 | 6.7425 | 6.7492 | -1.1329 | 150.1587 | 2071.8843 | -0.0075446
111 |  | 0.66052 | 18.4103 | 4187 | 0.0066569 | 6.7492 | 6.7558 | -1.1329 | 150.2202 | 2090.2946 | -0.0075415
112 |  | 0.66052 | 18.4027 | 4187 | 0.0066542 | 6.7558 | 6.7625 | -1.1329 | 150.2818 | 2108.6974 | -0.0075384
113 |  | 0.66052 | 18.3952 | 4187 | 0.0066514 | 6.7625 | 6.7691 | -1.1329 | 150.3433 | 2127.0926 | -0.0075353
114 |  | 0.66052 | 18.3877 | 4187 | 0.0066487 | 6.7691 | 6.7758 | -1.1329 | 150.405 | 2145.4802 | -0.0075322
115 |  | 0.66052 | 18.3801 | 4187 | 0.006646 | 6.7758 | 6.7824 | -1.1329 | 150.4666 | 2163.8604 | -0.0075291
116 |  | 0.66052 | 18.3726 | 4187 | 0.0066433 | 6.7824 | 6.7891 | -1.1329 | 150.5283 | 2182.233 | -0.007526
117 |  | 0.66052 | 18.3651 | 4187 | 0.0066405 | 6.7891 | 6.7957 | -1.1329 | 150.5899 | 2200.5981 | -0.007523
118 |  | 0.66052 | 18.3576 | 4187 | 0.0066378 | 6.7957 | 6.8023 | -1.1329 | 150.6517 | 2218.9556 | -0.0075199
119 |  | 0.66052 | 18.35 | 4187 | 0.0066351 | 6.8023 | 6.809 | -1.1329 | 150.7134 | 2237.3057 | -0.0075168
120 |  | 0.66052 | 18.3425 | 4187 | 0.0066324 | 6.809 | 6.8156 | -1.1329 | 150.7752 | 2255.6482 | -0.0075137
121 |  | 0.66052 | 18.335 | 4187 | 0.0066297 | 6.8156 | 6.8222 | -1.1329 | 150.8369 | 2273.9832 | -0.0075106
122 |  | 0.66052 | 18.3275 | 4187 | 0.006627 | 6.8222 | 6.8289 | -1.1329 | 150.8988 | 2292.3107 | -0.0075076
123 |  | 0.66052 | 18.32 | 4187 | 0.0066242 | 6.8289 | 6.8355 | -1.1329 | 150.9606 | 2310.6307 | -0.0075045
124 |  | 0.66052 | 18.3125 | 4187 | 0.0066215 | 6.8355 | 6.8421 | -1.1329 | 151.0225 | 2328.9432 | -0.0075014
125 |  | 0.66052 | 18.305 | 4187 | 0.0066188 | 6.8421 | 6.8487 | -1.1329 | 151.0843 | 2347.2482 | -0.0074983
126 |  | 0.66052 | 18.2975 | 4187 | 0.0066161 | 6.8487 | 6.8553 | -1.1329 | 151.1463 | 2365.5457 | -0.0074953
127 |  | 0.66052 | 18.29 | 4187 | 0.0066134 | 6.8553 | 6.862 | -1.1329 | 151.2082 | 2383.8356 | -0.0074922
128 |  | 0.66052 | 18.2825 | 4187 | 0.0066107 | 6.862 | 6.8686 | -1.1329 | 151.2702 | 2402.1181 | -0.0074891
129 |  | 0.66052 | 18.275 | 4187 | 0.006608 | 6.8686 | 6.8752 | -1.1329 | 151.3322 | 2420.3932 | -0.0074861
130 |  | 0.66052 | 18.2675 | 4187 | 0.0066053 | 6.8752 | 6.8818 | -1.1329 | 151.3942 | 2438.6607 | -0.007483
131 |  | 0.66052 | 18.26 | 4187 | 0.0066026 | 6.8818 | 6.8884 | -1.1329 | 151.4562 | 2456.9207 | -0.0074799
132 |  | 0.66052 | 18.2526 | 4187 | 0.0065999 | 6.8884 | 6.895 | -1.1329 | 151.5183 | 2475.1733 | -0.0074769
133 |  | 0.66052 | 18.2451 | 4187 | 0.0065972 | 6.895 | 6.9016 | -1.1329 | 151.5804 | 2493.4184 | -0.0074738
134 |  | 0.66052 | 18.2376 | 4187 | 0.0065945 | 6.9016 | 6.9082 | -1.1329 | 151.6425 | 2511.656 | -0.0074707
135 |  | 0.66052 | 18.2301 | 4187 | 0.0065918 | 6.9082 | 6.9148 | -1.1329 | 151.7046 | 2529.8861 | -0.0074677
136 |  | 0.66052 | 18.2227 | 4187 | 0.0065891 | 6.9148 | 6.9214 | -1.1329 | 151.7668 | 2548.1088 | -0.0074646
137 |  | 0.66052 | 18.2152 | 4187 | 0.0065864 | 6.9214 | 6.9279 | -1.1329 | 151.829 | 2566.324 | -0.0074616
138 |  | 0.66052 | 18.2077 | 4187 | 0.0065837 | 6.9279 | 6.9345 | -1.1329 | 151.8912 | 2584.5317 | -0.0074585
139 |  | 0.66052 | 18.2003 | 4187 | 0.006581 | 6.9345 | 6.9411 | -1.1329 | 151.9535 | 2602.732 | -0.0074555
140 |  | 0.66052 | 18.1928 | 4187 | 0.0065783 | 6.9411 | 6.9477 | -1.1329 | 152.0157 | 2620.9249 | -0.0074524
141 |  | 0.66052 | 18.1854 | 4187 | 0.0065756 | 6.9477 | 6.9543 | -1.1329 | 152.078 | 2639.1102 | -0.0074493
142 |  | 0.66052 | 18.1779 | 4187 | 0.0065729 | 6.9543 | 6.9608 | -1.1329 | 152.1404 | 2657.2882 | -0.0074463
143 |  | 0.66052 | 18.1705 | 4187 | 0.0065702 | 6.9608 | 6.9674 | -1.1329 | 152.2027 | 2675.4586 | -0.0074432
144 |  | 0.66052 | 18.163 | 4187 | 0.0065675 | 6.9674 | 6.974 | -1.1329 | 152.2651 | 2693.6217 | -0.0074402
145 |  | 0.66052 | 18.1556 | 4187 | 0.0065648 | 6.974 | 6.9805 | -1.1329 | 152.3275 | 2711.7773 | -0.0074372
146 |  | 0.66052 | 18.1482 | 4187 | 0.0065621 | 6.9805 | 6.9871 | -1.1329 | 152.3899 | 2729.9254 | -0.0074341
147 |  | 0.66052 | 18.1407 | 4187 | 0.0065594 | 6.9871 | 6.9937 | -1.1329 | 152.4523 | 2748.0662 | -0.0074311
148 |  | 0.66052 | 18.1333 | 4187 | 0.0065567 | 6.9937 | 7.0002 | -1.1329 | 152.5148 | 2766.1995 | -0.007428
149 |  | 0.66052 | 18.1259 | 4187 | 0.0065541 | 7.0002 | 7.0068 | -1.1329 | 152.5773 | 2784.3253 | -0.007425
150 |  | 0.66052 | 18.1184 | 4187 | 0.0065514 | 7.0068 | 7.0133 | -1.1329 | 152.6398 | 2802.4438 | -0.0074219
151 |  | 0.66052 | 18.111 | 4187 | 0.0065487 | 7.0133 | 7.0199 | -1.1329 | 152.7024 | 2820.5548 | -0.0074189
152 |  | 0.66052 | 18.1036 | 4187 | 0.006546 | 7.0199 | 7.0264 | -1.1329 | 152.765 | 2838.6584 | -0.0074159
153 |  | 0.66052 | 18.0962 | 4187 | 0.0065433 | 7.0264 | 7.033 | -1.1329 | 152.8276 | 2856.7546 | -0.0074128
154 |  | 0.66052 | 18.0888 | 4187 | 0.0065406 | 7.033 | 7.0395 | -1.1329 | 152.8902 | 2874.8434 | -0.0074098
155 |  | 0.66052 | 18.0814 | 4187 | 0.006538 | 7.0395 | 7.046 | -1.1329 | 152.9529 | 2892.9247 | -0.0074067
156 |  | 0.66052 | 18.074 | 4187 | 0.0065353 | 7.046 | 7.0526 | -1.1329 | 153.0155 | 2910.9987 | -0.0074037
157 |  | 0.66052 | 18.0666 | 4187 | 0.0065326 | 7.0526 | 7.0591 | -1.1329 | 153.0783 | 2929.0653 | -0.0074007
158 |  | 0.66052 | 18.0592 | 4187 | 0.0065299 | 7.0591 | 7.0656 | -1.1329 | 153.141 | 2947.1244 | -0.0073976
159 |  | 0.66052 | 18.0518 | 4187 | 0.0065273 | 7.0656 | 7.0722 | -1.1329 | 153.2037 | 2965.1762 | -0.0073946
160 |  | 0.66052 | 18.0444 | 4187 | 0.0065246 | 7.0722 | 7.0787 | -1.1329 | 153.2665 | 2983.2205 | -0.0073916
161 |  | 0.66052 | 18.037 | 4187 | 0.0065219 | 7.0787 | 7.0852 | -1.1329 | 153.3293 | 3001.2575 | -0.0073886
162 |  | 0.66052 | 18.0296 | 4187 | 0.0065192 | 7.0852 | 7.0917 | -1.1329 | 153.3922 | 3019.2871 | -0.0073855
163 |  | 0.66052 | 18.0222 | 4187 | 0.0065166 | 7.0917 | 7.0982 | -1.1329 | 153.455 | 3037.3093 | -0.0073825
164 |  | 0.66052 | 18.0148 | 4187 | 0.0065139 | 7.0982 | 7.1048 | -1.1329 | 153.5179 | 3055.3241 | -0.0073795
165 |  | 0.66052 | 18.0074 | 4187 | 0.0065112 | 7.1048 | 7.1113 | -1.1329 | 153.5808 | 3073.3315 | -0.0073765
166 |  | 0.66052 | 18.0001 | 4187 | 0.0065086 | 7.1113 | 7.1178 | -1.1329 | 153.6438 | 3091.3316 | -0.0073734
167 |  | 0.66052 | 17.9927 | 4187 | 0.0065059 | 7.1178 | 7.1243 | -1.1329 | 153.7067 | 3109.3243 | -0.0073704
168 |  | 0.66052 | 17.9853 | 4187 | 0.0065032 | 7.1243 | 7.1308 | -1.1329 | 153.7697 | 3127.3096 | -0.0073674
169 |  | 0.66052 | 17.9779 | 4187 | 0.0065006 | 7.1308 | 7.1373 | -1.1329 | 153.8327 | 3145.2875 | -0.0073644
170 |  | 0.66052 | 17.9706 | 4187 | 0.0064979 | 7.1373 | 7.1438 | -1.1329 | 153.8958 | 3163.2581 | -0.0073614
171 |  | 0.66052 | 17.9632 | 4187 | 0.0064952 | 7.1438 | 7.1503 | -1.1329 | 153.9588 | 3181.2213 | -0.0073583
172 |  | 0.66052 | 17.9559 | 4187 | 0.0064926 | 7.1503 | 7.1568 | -1.1329 | 154.0219 | 3199.1772 | -0.0073553
173 |  | 0.66052 | 17.9485 | 4187 | 0.0064899 | 7.1568 | 7.1633 | -1.1329 | 154.0851 | 3217.1257 | -0.0073523
174 |  | 0.66052 | 17.9412 | 4187 | 0.0064873 | 7.1633 | 7.1698 | -1.1329 | 154.1482 | 3235.0669 | -0.0073493
175 |  | 0.66052 | 17.9338 | 4187 | 0.0064846 | 7.1698 | 7.1762 | -1.1329 | 154.2114 | 3253.0007 | -0.0073463
176 |  | 0.66052 | 17.9265 | 4187 | 0.006482 | 7.1762 | 7.1827 | -1.1329 | 154.2746 | 3270.9271 | -0.0073433
177 |  | 0.66052 | 17.9191 | 4187 | 0.0064793 | 7.1827 | 7.1892 | -1.1329 | 154.3378 | 3288.8462 | -0.0073403
178 |  | 0.66052 | 17.9118 | 4187 | 0.0064766 | 7.1892 | 7.1957 | -1.1329 | 154.401 | 3306.758 | -0.0073373
179 |  | 0.66052 | 17.9044 | 4187 | 0.006474 | 7.1957 | 7.2022 | -1.1329 | 154.4643 | 3324.6624 | -0.0073343
180 |  | 0.66052 | 17.8971 | 4187 | 0.0064713 | 7.2022 | 7.2086 | -1.1329 | 154.5276 | 3342.5596 | -0.0073313
181 |  | 0.66052 | 17.8898 | 4187 | 0.0064687 | 7.2086 | 7.2151 | -1.1329 | 154.5909 | 3360.4493 | -0.0073283
182 |  | 0.66052 | 17.8824 | 4187 | 0.006466 | 7.2151 | 7.2216 | -1.1329 | 154.6543 | 3378.3318 | -0.0073253
183 |  | 0.66052 | 17.8751 | 4187 | 0.0064634 | 7.2216 | 7.228 | -1.1329 | 154.7177 | 3396.2069 | -0.0073223
184 |  | 0.66052 | 17.8678 | 4187 | 0.0064607 | 7.228 | 7.2345 | -1.1329 | 154.7811 | 3414.0747 | -0.0073193
185 |  | 0.66052 | 17.8605 | 4187 | 0.0064581 | 7.2345 | 7.2409 | -1.1329 | 154.8445 | 3431.9352 | -0.0073163
186 |  | 0.66052 | 17.8532 | 4187 | 0.0064554 | 7.2409 | 7.2474 | -1.1329 | 154.9079 | 3449.7883 | -0.0073133
187 |  | 0.66052 | 17.8458 | 4187 | 0.0064528 | 7.2474 | 7.2538 | -1.1329 | 154.9714 | 3467.6342 | -0.0073103
188 |  | 0.66052 | 17.8385 | 4187 | 0.0064502 | 7.2538 | 7.2603 | -1.1329 | 155.0349 | 3485.4727 | -0.0073073
189 |  | 0.66052 | 17.8312 | 4187 | 0.0064475 | 7.2603 | 7.2667 | -1.1329 | 155.0985 | 3503.3039 | -0.0073043
190 |  | 0.66052 | 17.8239 | 4187 | 0.0064449 | 7.2667 | 7.2732 | -1.1329 | 155.162 | 3521.1279 | -0.0073013
191 |  | 0.66052 | 17.8166 | 4187 | 0.0064422 | 7.2732 | 7.2796 | -1.1329 | 155.2256 | 3538.9445 | -0.0072983
192 |  | 0.66052 | 17.8093 | 4187 | 0.0064396 | 7.2796 | 7.2861 | -1.1329 | 155.2892 | 3556.7538 | -0.0072953
193 |  | 0.66052 | 17.802 | 4187 | 0.006437 | 7.2861 | 7.2925 | -1.1329 | 155.3529 | 3574.5559 | -0.0072923
194 |  | 0.66052 | 17.7947 | 4187 | 0.0064343 | 7.2925 | 7.2989 | -1.1329 | 155.4165 | 3592.3506 | -0.0072893
195 |  | 0.66052 | 17.7874 | 4187 | 0.0064317 | 7.2989 | 7.3054 | -1.1329 | 155.4802 | 3610.138 | -0.0072863
196 |  | 0.66052 | 17.7802 | 4187 | 0.0064291 | 7.3054 | 7.3118 | -1.1329 | 155.5439 | 3627.9182 | -0.0072834
197 |  | 0.66052 | 17.7729 | 4187 | 0.0064264 | 7.3118 | 7.3182 | -1.1329 | 155.6077 | 3645.6911 | -0.0072804
198 |  | 0.66052 | 17.7656 | 4187 | 0.0064238 | 7.3182 | 7.3247 | -1.1329 | 155.6714 | 3663.4567 | -0.0072774
199 |  | 0.66052 | 17.7583 | 4187 | 0.0064212 | 7.3247 | 7.3311 | -1.1329 | 155.7352 | 3681.215 | -0.0072744
200 |  | 0.66052 | 17.751 | 4187 | 0.0064185 | 7.3311 | 7.3375 | -1.1329 | 155.7991 | 3698.9661 | -0.0072714
201 |  | 0.66052 | 17.7438 | 4187 | 0.0064159 | 7.3375 | 7.3439 | -1.1329 | 155.8629 | 3716.7098 | -0.0072685
202 |  | 0.66052 | 17.7365 | 4187 | 0.0064133 | 7.3439 | 7.3503 | -1.1329 | 155.9268 | 3734.4463 | -0.0072655
203 |  | 0.66052 | 17.7292 | 4187 | 0.0064106 | 7.3503 | 7.3567 | -1.1329 | 155.9907 | 3752.1756 | -0.0072625
204 |  | 0.66052 | 17.722 | 4187 | 0.006408 | 7.3567 | 7.3631 | -1.1329 | 156.0546 | 3769.8976 | -0.0072595
205 |  | 0.66052 | 17.7147 | 4187 | 0.0064054 | 7.3631 | 7.3695 | -1.1329 | 156.1186 | 3787.6123 | -0.0072566
206 |  | 0.66052 | 17.7075 | 4187 | 0.0064028 | 7.3695 | 7.3759 | -1.1329 | 156.1825 | 3805.3197 | -0.0072536
207 |  | 0.66052 | 17.7002 | 4187 | 0.0064001 | 7.3759 | 7.3823 | -1.1329 | 156.2465 | 3823.02 | -0.0072506
208 |  | 0.66052 | 17.693 | 4187 | 0.0063975 | 7.3823 | 7.3887 | -1.1329 | 156.3106 | 3840.7129 | -0.0072476
209 |  | 0.66052 | 17.6857 | 4187 | 0.0063949 | 7.3887 | 7.3951 | -1.1329 | 156.3746 | 3858.3986 | -0.0072447
210 |  | 0.66052 | 17.6785 | 4187 | 0.0063923 | 7.3951 | 7.4015 | -1.1329 | 156.4387 | 3876.0771 | -0.0072417
211 |  | 0.66052 | 17.6712 | 4187 | 0.0063897 | 7.4015 | 7.4079 | -1.1329 | 156.5028 | 3893.7483 | -0.0072387
212 |  | 0.66052 | 17.664 | 4187 | 0.006387 | 7.4079 | 7.4143 | -1.1329 | 156.567 | 3911.4123 | -0.0072358
213 |  | 0.66052 | 17.6568 | 4187 | 0.0063844 | 7.4143 | 7.4207 | -1.1329 | 156.6311 | 3929.0691 | -0.0072328
214 |  | 0.66052 | 17.6495 | 4187 | 0.0063818 | 7.4207 | 7.4271 | -1.1329 | 156.6953 | 3946.7186 | -0.0072298
215 |  | 0.66052 | 17.6423 | 4187 | 0.0063792 | 7.4271 | 7.4335 | -1.1329 | 156.7595 | 3964.3609 | -0.0072269
216 |  | 0.66052 | 17.6351 | 4187 | 0.0063766 | 7.4335 | 7.4398 | -1.1329 | 156.8238 | 3981.9959 | -0.0072239
217 |  | 0.66052 | 17.6278 | 4187 | 0.006374 | 7.4398 | 7.4462 | -1.1329 | 156.888 | 3999.6238 | -0.007221
218 |  | 0.66052 | 17.6206 | 4187 | 0.0063714 | 7.4462 | 7.4526 | -1.1329 | 156.9523 | 4017.2444 | -0.007218
219 |  | 0.66052 | 17.6134 | 4187 | 0.0063688 | 7.4526 | 7.4589 | -1.1329 | 157.0166 | 4034.8578 | -0.007215
220 |  | 0.66052 | 17.6062 | 4187 | 0.0063661 | 7.4589 | 7.4653 | -1.1329 | 157.081 | 4052.464 | -0.0072121
221 |  | 0.66052 | 17.599 | 4187 | 0.0063635 | 7.4653 | 7.4717 | -1.1329 | 157.1454 | 4070.0629 | -0.0072091
222 |  | 0.66052 | 17.5918 | 4187 | 0.0063609 | 7.4717 | 7.478 | -1.1329 | 157.2098 | 4087.6547 | -0.0072062
223 |  | 0.66052 | 17.5846 | 4187 | 0.0063583 | 7.478 | 7.4844 | -1.1329 | 157.2742 | 4105.2393 | -0.0072032
224 |  | 0.66052 | 17.5774 | 4187 | 0.0063557 | 7.4844 | 7.4908 | -1.1329 | 157.3386 | 4122.8166 | -0.0072003
225 |  | 0.66052 | 17.5702 | 4187 | 0.0063531 | 7.4908 | 7.4971 | -1.1329 | 157.4031 | 4140.3868 | -0.0071973
226 |  | 0.66052 | 17.563 | 4187 | 0.0063505 | 7.4971 | 7.5035 | -1.1329 | 157.4676 | 4157.9497 | -0.0071944
227 |  | 0.66052 | 17.5558 | 4187 | 0.0063479 | 7.5035 | 7.5098 | -1.1329 | 157.5321 | 4175.5055 | -0.0071914
228 |  | 0.66052 | 17.5486 | 4187 | 0.0063453 | 7.5098 | 7.5161 | -1.1329 | 157.5967 | 4193.0541 | -0.0071885
229 |  | 0.66052 | 17.5414 | 4187 | 0.0063427 | 7.5161 | 7.5225 | -1.1329 | 157.6613 | 4210.5954 | -0.0071855
230 |  | 0.66052 | 17.5342 | 4187 | 0.0063401 | 7.5225 | 7.5288 | -1.1329 | 157.7259 | 4228.1296 | -0.0071826
231 |  | 0.66052 | 17.527 | 4187 | 0.0063375 | 7.5288 | 7.5352 | -1.1329 | 157.7905 | 4245.6566 | -0.0071797
232 |  | 0.66052 | 17.5198 | 4187 | 0.0063349 | 7.5352 | 7.5415 | -1.1329 | 157.8552 | 4263.1765 | -0.0071767
233 |  | 0.66052 | 17.5127 | 4187 | 0.0063323 | 7.5415 | 7.5478 | -1.1329 | 157.9199 | 4280.6891 | -0.0071738
234 |  | 0.66052 | 17.5055 | 4187 | 0.0063297 | 7.5478 | 7.5542 | -1.1329 | 157.9846 | 4298.1946 | -0.0071708
235 |  | 0.66052 | 17.4983 | 4187 | 0.0063271 | 7.5542 | 7.5605 | -1.1329 | 158.0493 | 4315.6929 | -0.0071679
236 |  | 0.66052 | 17.4911 | 4187 | 0.0063245 | 7.5605 | 7.5668 | -1.1329 | 158.1141 | 4333.1841 | -0.007165

## Fus50
|  |  | buis | verlies W/M | L /°C/sec
diam | wandikte |  | inhoud l/m |  | W/M
50 | 6.9 | 3.1416 | 1.0292 | 21.9105 | 4187
[8 empty] | J/sec/mtr | aantal mtr. | verlies
|  | buis | verlies W/M | L /°C/sec | verlies temp | begintemp | eindtemp | verlies | bij 1°C | totaal J/sec
|  | inhoud L |  | W/M | °C per M | °C | °C | per m°C | daling | aantal mtr
1 | 50 | 1.0292 | 21.9105 | 4187 | 0.0050844 | 6 | 6.0051 | -1.2889 | 196.6785 | 21.9105 | -0.0065531
2 |  | 1.0292 | 21.904 | 4187 | 0.0050829 | 6.0051 | 6.0102 | -1.2889 | 196.7373 | 43.8145 | -0.0065511
3 |  | 1.0292 | 21.8974 | 4187 | 0.0050814 | 6.0102 | 6.0152 | -1.2889 | 196.7962 | 65.712 | -0.0065492
4 |  | 1.0292 | 21.8909 | 4187 | 0.0050799 | 6.0152 | 6.0203 | -1.2889 | 196.8551 | 87.6029 | -0.0065472
5 |  | 1.0292 | 21.8843 | 4187 | 0.0050784 | 6.0203 | 6.0254 | -1.2889 | 196.914 | 109.4872 | -0.0065453
6 |  | 1.0292 | 21.8778 | 4187 | 0.0050768 | 6.0254 | 6.0305 | -1.2889 | 196.9729 | 131.365 | -0.0065433
7 |  | 1.0292 | 21.8713 | 4187 | 0.0050753 | 6.0305 | 6.0356 | -1.2889 | 197.0318 | 153.2362 | -0.0065414
8 |  | 1.0292 | 21.8647 | 4187 | 0.0050738 | 6.0356 | 6.0406 | -1.2889 | 197.0908 | 175.101 | -0.0065394
9 |  | 1.0292 | 21.8582 | 4187 | 0.0050723 | 6.0406 | 6.0457 | -1.2889 | 197.1497 | 196.9591 | -0.0065374
10 |  | 1.0292 | 21.8516 | 4187 | 0.0050708 | 6.0457 | 6.0508 | -1.2889 | 197.2087 | 218.8108 | -0.0065355
11 |  | 1.0292 | 21.8451 | 4187 | 0.0050693 | 6.0508 | 6.0558 | -1.2889 | 197.2677 | 240.6559 | -0.0065335
12 |  | 1.0292 | 21.8386 | 4187 | 0.0050677 | 6.0558 | 6.0609 | -1.2889 | 197.3267 | 262.4944 | -0.0065316
13 |  | 1.0292 | 21.832 | 4187 | 0.0050662 | 6.0609 | 6.066 | -1.2889 | 197.3858 | 284.3265 | -0.0065296
14 |  | 1.0292 | 21.8255 | 4187 | 0.0050647 | 6.066 | 6.071 | -1.2889 | 197.4448 | 306.152 | -0.0065277
15 |  | 1.0292 | 21.819 | 4187 | 0.0050632 | 6.071 | 6.0761 | -1.2889 | 197.5039 | 327.9709 | -0.0065257
16 |  | 1.0292 | 21.8124 | 4187 | 0.0050617 | 6.0761 | 6.0812 | -1.2889 | 197.563 | 349.7834 | -0.0065238
17 |  | 1.0292 | 21.8059 | 4187 | 0.0050602 | 6.0812 | 6.0862 | -1.2889 | 197.6221 | 371.5893 | -0.0065218
18 |  | 1.0292 | 21.7994 | 4187 | 0.0050587 | 6.0862 | 6.0913 | -1.2889 | 197.6812 | 393.3887 | -0.0065199
19 |  | 1.0292 | 21.7929 | 4187 | 0.0050571 | 6.0913 | 6.0963 | -1.2889 | 197.7403 | 415.1816 | -0.0065179
20 |  | 1.0292 | 21.7864 | 4187 | 0.0050556 | 6.0963 | 6.1014 | -1.2889 | 197.7995 | 436.968 | -0.006516
21 |  | 1.0292 | 21.7799 | 4187 | 0.0050541 | 6.1014 | 6.1065 | -1.2889 | 197.8587 | 458.7478 | -0.006514
22 |  | 1.0292 | 21.7733 | 4187 | 0.0050526 | 6.1065 | 6.1115 | -1.2889 | 197.9179 | 480.5211 | -0.0065121
23 |  | 1.0292 | 21.7668 | 4187 | 0.0050511 | 6.1115 | 6.1166 | -1.2889 | 197.9771 | 502.288 | -0.0065101
24 |  | 1.0292 | 21.7603 | 4187 | 0.0050496 | 6.1166 | 6.1216 | -1.2889 | 198.0363 | 524.0483 | -0.0065082
25 |  | 1.0292 | 21.7538 | 4187 | 0.0050481 | 6.1216 | 6.1267 | -1.2889 | 198.0956 | 545.8021 | -0.0065062
26 |  | 1.0292 | 21.7473 | 4187 | 0.0050466 | 6.1267 | 6.1317 | -1.2889 | 198.1548 | 567.5494 | -0.0065043
27 |  | 1.0292 | 21.7408 | 4187 | 0.005045 | 6.1317 | 6.1367 | -1.2889 | 198.2141 | 589.2902 | -0.0065023
28 |  | 1.0292 | 21.7343 | 4187 | 0.0050435 | 6.1367 | 6.1418 | -1.2889 | 198.2734 | 611.0245 | -0.0065004
29 |  | 1.0292 | 21.7278 | 4187 | 0.005042 | 6.1418 | 6.1468 | -1.2889 | 198.3327 | 632.7523 | -0.0064985
30 |  | 1.0292 | 21.7213 | 4187 | 0.0050405 | 6.1468 | 6.1519 | -1.2889 | 198.3921 | 654.4736 | -0.0064965
31 |  | 1.0292 | 21.7148 | 4187 | 0.005039 | 6.1519 | 6.1569 | -1.2889 | 198.4514 | 676.1884 | -0.0064946
32 |  | 1.0292 | 21.7083 | 4187 | 0.0050375 | 6.1569 | 6.162 | -1.2889 | 198.5108 | 697.8967 | -0.0064926
33 |  | 1.0292 | 21.7018 | 4187 | 0.005036 | 6.162 | 6.167 | -1.2889 | 198.5702 | 719.5985 | -0.0064907
34 |  | 1.0292 | 21.6953 | 4187 | 0.0050345 | 6.167 | 6.172 | -1.2889 | 198.6296 | 741.2938 | -0.0064887
35 |  | 1.0292 | 21.6888 | 4187 | 0.005033 | 6.172 | 6.1771 | -1.2889 | 198.689 | 762.9826 | -0.0064868
36 |  | 1.0292 | 21.6823 | 4187 | 0.0050315 | 6.1771 | 6.1821 | -1.2889 | 198.7484 | 784.665 | -0.0064849
37 |  | 1.0292 | 21.6759 | 4187 | 0.00503 | 6.1821 | 6.1871 | -1.2889 | 198.8079 | 806.3408 | -0.0064829
38 |  | 1.0292 | 21.6694 | 4187 | 0.0050285 | 6.1871 | 6.1921 | -1.2889 | 198.8674 | 828.0102 | -0.006481
39 |  | 1.0292 | 21.6629 | 4187 | 0.005027 | 6.1921 | 6.1972 | -1.2889 | 198.9269 | 849.6731 | -0.006479
40 |  | 1.0292 | 21.6564 | 4187 | 0.0050255 | 6.1972 | 6.2022 | -1.2889 | 198.9864 | 871.3295 | -0.0064771
41 |  | 1.0292 | 21.6499 | 4187 | 0.005024 | 6.2022 | 6.2072 | -1.2889 | 199.0459 | 892.9795 | -0.0064752
42 |  | 1.0292 | 21.6435 | 4187 | 0.0050225 | 6.2072 | 6.2122 | -1.2889 | 199.1055 | 914.6229 | -0.0064732
43 |  | 1.0292 | 21.637 | 4187 | 0.005021 | 6.2122 | 6.2173 | -1.2889 | 199.165 | 936.2599 | -0.0064713
44 |  | 1.0292 | 21.6305 | 4187 | 0.0050195 | 6.2173 | 6.2223 | -1.2889 | 199.2246 | 957.8904 | -0.0064694
45 |  | 1.0292 | 21.6241 | 4187 | 0.005018 | 6.2223 | 6.2273 | -1.2889 | 199.2842 | 979.5145 | -0.0064674
46 |  | 1.0292 | 21.6176 | 4187 | 0.0050165 | 6.2273 | 6.2323 | -1.2889 | 199.3439 | 1001.1321 | -0.0064655
47 |  | 1.0292 | 21.6111 | 4187 | 0.005015 | 6.2323 | 6.2373 | -1.2889 | 199.4035 | 1022.7432 | -0.0064636
48 |  | 1.0292 | 21.6047 | 4187 | 0.0050135 | 6.2373 | 6.2423 | -1.2889 | 199.4631 | 1044.3479 | -0.0064616
49 |  | 1.0292 | 21.5982 | 4187 | 0.005012 | 6.2423 | 6.2474 | -1.2889 | 199.5228 | 1065.946 | -0.0064597
50 |  | 1.0292 | 21.5917 | 4187 | 0.0050105 | 6.2474 | 6.2524 | -1.2889 | 199.5825 | 1087.5378 | -0.0064578
51 |  | 1.0292 | 21.5853 | 4187 | 0.005009 | 6.2524 | 6.2574 | -1.2889 | 199.6422 | 1109.1231 | -0.0064558
52 |  | 1.0292 | 21.5788 | 4187 | 0.0050075 | 6.2574 | 6.2624 | -1.2889 | 199.7019 | 1130.7019 | -0.0064539
53 |  | 1.0292 | 21.5724 | 4187 | 0.005006 | 6.2624 | 6.2674 | -1.2889 | 199.7617 | 1152.2742 | -0.006452
54 |  | 1.0292 | 21.5659 | 4187 | 0.0050045 | 6.2674 | 6.2724 | -1.2889 | 199.8215 | 1173.8402 | -0.00645
55 |  | 1.0292 | 21.5595 | 4187 | 0.005003 | 6.2724 | 6.2774 | -1.2889 | 199.8812 | 1195.3996 | -0.0064481
56 |  | 1.0292 | 21.553 | 4187 | 0.0050015 | 6.2774 | 6.2824 | -1.2889 | 199.941 | 1216.9526 | -0.0064462
57 |  | 1.0292 | 21.5466 | 4187 | 0.005 | 6.2824 | 6.2874 | -1.2889 | 200.0009 | 1238.4992 | -0.0064442
58 |  | 1.0292 | 21.5401 | 4187 | 0.0049985 | 6.2874 | 6.2924 | -1.2889 | 200.0607 | 1260.0393 | -0.0064423
59 |  | 1.0292 | 21.5337 | 4187 | 0.004997 | 6.2924 | 6.2974 | -1.2889 | 200.1205 | 1281.573 | -0.0064404
60 |  | 1.0292 | 21.5272 | 4187 | 0.0049955 | 6.2974 | 6.3024 | -1.2889 | 200.1804 | 1303.1002 | -0.0064385
61 |  | 1.0292 | 21.5208 | 4187 | 0.004994 | 6.3024 | 6.3074 | -1.2889 | 200.2403 | 1324.6211 | -0.0064365
62 |  | 1.0292 | 21.5144 | 4187 | 0.0049925 | 6.3074 | 6.3124 | -1.2889 | 200.3002 | 1346.1354 | -0.0064346
63 |  | 1.0292 | 21.5079 | 4187 | 0.004991 | 6.3124 | 6.3174 | -1.2889 | 200.3601 | 1367.6434 | -0.0064327
64 |  | 1.0292 | 21.5015 | 4187 | 0.0049895 | 6.3174 | 6.3224 | -1.2889 | 200.4201 | 1389.1449 | -0.0064308
65 |  | 1.0292 | 21.4951 | 4187 | 0.004988 | 6.3224 | 6.3273 | -1.2889 | 200.48 | 1410.6399 | -0.0064288
66 |  | 1.0292 | 21.4886 | 4187 | 0.0049865 | 6.3273 | 6.3323 | -1.2889 | 200.54 | 1432.1286 | -0.0064269
67 |  | 1.0292 | 21.4822 | 4187 | 0.004985 | 6.3323 | 6.3373 | -1.2889 | 200.6 | 1453.6108 | -0.006425
68 |  | 1.0292 | 21.4758 | 4187 | 0.0049836 | 6.3373 | 6.3423 | -1.2889 | 200.66 | 1475.0866 | -0.0064231
69 |  | 1.0292 | 21.4694 | 4187 | 0.0049821 | 6.3423 | 6.3473 | -1.2889 | 200.7201 | 1496.5559 | -0.0064212
70 |  | 1.0292 | 21.4629 | 4187 | 0.0049806 | 6.3473 | 6.3523 | -1.2889 | 200.7801 | 1518.0189 | -0.0064192
71 |  | 1.0292 | 21.4565 | 4187 | 0.0049791 | 6.3523 | 6.3572 | -1.2889 | 200.8402 | 1539.4754 | -0.0064173
72 |  | 1.0292 | 21.4501 | 4187 | 0.0049776 | 6.3572 | 6.3622 | -1.2889 | 200.9003 | 1560.9255 | -0.0064154
73 |  | 1.0292 | 21.4437 | 4187 | 0.0049761 | 6.3622 | 6.3672 | -1.2889 | 200.9604 | 1582.3692 | -0.0064135
74 |  | 1.0292 | 21.4373 | 4187 | 0.0049746 | 6.3672 | 6.3722 | -1.2889 | 201.0205 | 1603.8065 | -0.0064116
75 |  | 1.0292 | 21.4309 | 4187 | 0.0049731 | 6.3722 | 6.3771 | -1.2889 | 201.0806 | 1625.2373 | -0.0064096
76 |  | 1.0292 | 21.4245 | 4187 | 0.0049716 | 6.3771 | 6.3821 | -1.2889 | 201.1408 | 1646.6618 | -0.0064077
77 |  | 1.0292 | 21.418 | 4187 | 0.0049702 | 6.3821 | 6.3871 | -1.2889 | 201.201 | 1668.0798 | -0.0064058
78 |  | 1.0292 | 21.4116 | 4187 | 0.0049687 | 6.3871 | 6.3921 | -1.2889 | 201.2612 | 1689.4915 | -0.0064039
79 |  | 1.0292 | 21.4052 | 4187 | 0.0049672 | 6.3921 | 6.397 | -1.2889 | 201.3214 | 1710.8967 | -0.006402
80 |  | 1.0292 | 21.3988 | 4187 | 0.0049657 | 6.397 | 6.402 | -1.2889 | 201.3816 | 1732.2956 | -0.0064001
81 |  | 1.0292 | 21.3924 | 4187 | 0.0049642 | 6.402 | 6.407 | -1.2889 | 201.4419 | 1753.688 | -0.0063982
82 |  | 1.0292 | 21.386 | 4187 | 0.0049627 | 6.407 | 6.4119 | -1.2889 | 201.5021 | 1775.074 | -0.0063962
83 |  | 1.0292 | 21.3796 | 4187 | 0.0049612 | 6.4119 | 6.4169 | -1.2889 | 201.5624 | 1796.4537 | -0.0063943
84 |  | 1.0292 | 21.3732 | 4187 | 0.0049598 | 6.4169 | 6.4218 | -1.2889 | 201.6227 | 1817.8269 | -0.0063924
85 |  | 1.0292 | 21.3669 | 4187 | 0.0049583 | 6.4218 | 6.4268 | -1.2889 | 201.683 | 1839.1938 | -0.0063905
86 |  | 1.0292 | 21.3605 | 4187 | 0.0049568 | 6.4268 | 6.4318 | -1.2889 | 201.7434 | 1860.5543 | -0.0063886
87 |  | 1.0292 | 21.3541 | 4187 | 0.0049553 | 6.4318 | 6.4367 | -1.2889 | 201.8037 | 1881.9083 | -0.0063867
88 |  | 1.0292 | 21.3477 | 4187 | 0.0049538 | 6.4367 | 6.4417 | -1.2889 | 201.8641 | 1903.256 | -0.0063848
89 |  | 1.0292 | 21.3413 | 4187 | 0.0049523 | 6.4417 | 6.4466 | -1.2889 | 201.9245 | 1924.5973 | -0.0063829
90 |  | 1.0292 | 21.3349 | 4187 | 0.0049509 | 6.4466 | 6.4516 | -1.2889 | 201.9849 | 1945.9323 | -0.0063809
91 |  | 1.0292 | 21.3285 | 4187 | 0.0049494 | 6.4516 | 6.4565 | -1.2889 | 202.0453 | 1967.2608 | -0.006379
92 |  | 1.0292 | 21.3222 | 4187 | 0.0049479 | 6.4565 | 6.4615 | -1.2889 | 202.1058 | 1988.583 | -0.0063771
93 |  | 1.0292 | 21.3158 | 4187 | 0.0049464 | 6.4615 | 6.4664 | -1.2889 | 202.1662 | 2009.8988 | -0.0063752
94 |  | 1.0292 | 21.3094 | 4187 | 0.0049449 | 6.4664 | 6.4714 | -1.2889 | 202.2267 | 2031.2082 | -0.0063733
95 |  | 1.0292 | 21.303 | 4187 | 0.0049435 | 6.4714 | 6.4763 | -1.2889 | 202.2872 | 2052.5112 | -0.0063714
96 |  | 1.0292 | 21.2967 | 4187 | 0.004942 | 6.4763 | 6.4812 | -1.2889 | 202.3477 | 2073.8079 | -0.0063695
97 |  | 1.0292 | 21.2903 | 4187 | 0.0049405 | 6.4812 | 6.4862 | -1.2889 | 202.4083 | 2095.0982 | -0.0063676
98 |  | 1.0292 | 21.2839 | 4187 | 0.004939 | 6.4862 | 6.4911 | -1.2889 | 202.4688 | 2116.3821 | -0.0063657
99 |  | 1.0292 | 21.2776 | 4187 | 0.0049376 | 6.4911 | 6.4961 | -1.2889 | 202.5294 | 2137.6597 | -0.0063638
100 |  | 1.0292 | 21.2712 | 4187 | 0.0049361 | 6.4961 | 6.501 | -1.2889 | 202.59 | 2158.9309 | -0.0063619
101 |  | 1.0292 | 21.2648 | 4187 | 0.0049346 | 6.501 | 6.5059 | -1.2889 | 202.6506 | 2180.1957 | -0.00636
102 |  | 1.0292 | 21.2585 | 4187 | 0.0049331 | 6.5059 | 6.5109 | -1.2889 | 202.7112 | 2201.4542 | -0.0063581
103 |  | 1.0292 | 21.2521 | 4187 | 0.0049317 | 6.5109 | 6.5158 | -1.2889 | 202.7719 | 2222.7063 | -0.0063562
104 |  | 1.0292 | 21.2458 | 4187 | 0.0049302 | 6.5158 | 6.5207 | -1.2889 | 202.8325 | 2243.9521 | -0.0063543
105 |  | 1.0292 | 21.2394 | 4187 | 0.0049287 | 6.5207 | 6.5256 | -1.2889 | 202.8932 | 2265.1915 | -0.0063524
106 |  | 1.0292 | 21.2331 | 4187 | 0.0049272 | 6.5256 | 6.5306 | -1.2889 | 202.9539 | 2286.4245 | -0.0063505
107 |  | 1.0292 | 21.2267 | 4187 | 0.0049258 | 6.5306 | 6.5355 | -1.2889 | 203.0146 | 2307.6512 | -0.0063486
108 |  | 1.0292 | 21.2204 | 4187 | 0.0049243 | 6.5355 | 6.5404 | -1.2889 | 203.0754 | 2328.8716 | -0.0063467
109 |  | 1.0292 | 21.214 | 4187 | 0.0049228 | 6.5404 | 6.5453 | -1.2889 | 203.1361 | 2350.0856 | -0.0063448
110 |  | 1.0292 | 21.2077 | 4187 | 0.0049213 | 6.5453 | 6.5503 | -1.2889 | 203.1969 | 2371.2933 | -0.0063429
111 |  | 1.0292 | 21.2013 | 4187 | 0.0049199 | 6.5503 | 6.5552 | -1.2889 | 203.2577 | 2392.4946 | -0.006341
112 |  | 1.0292 | 21.195 | 4187 | 0.0049184 | 6.5552 | 6.5601 | -1.2889 | 203.3185 | 2413.6896 | -0.0063391
113 |  | 1.0292 | 21.1886 | 4187 | 0.0049169 | 6.5601 | 6.565 | -1.2889 | 203.3793 | 2434.8782 | -0.0063372
114 |  | 1.0292 | 21.1823 | 4187 | 0.0049154 | 6.565 | 6.5699 | -1.2889 | 203.4402 | 2456.0605 | -0.0063353
115 |  | 1.0292 | 21.176 | 4187 | 0.004914 | 6.5699 | 6.5749 | -1.2889 | 203.501 | 2477.2365 | -0.0063334
116 |  | 1.0292 | 21.1696 | 4187 | 0.0049125 | 6.5749 | 6.5798 | -1.2889 | 203.5619 | 2498.4061 | -0.0063315
117 |  | 1.0292 | 21.1633 | 4187 | 0.004911 | 6.5798 | 6.5847 | -1.2889 | 203.6228 | 2519.5694 | -0.0063296
118 |  | 1.0292 | 21.157 | 4187 | 0.0049096 | 6.5847 | 6.5896 | -1.2889 | 203.6837 | 2540.7264 | -0.0063277
119 |  | 1.0292 | 21.1506 | 4187 | 0.0049081 | 6.5896 | 6.5945 | -1.2889 | 203.7447 | 2561.8771 | -0.0063258
120 |  | 1.0292 | 21.1443 | 4187 | 0.0049066 | 6.5945 | 6.5994 | -1.2889 | 203.8056 | 2583.0214 | -0.0063239
121 |  | 1.0292 | 21.138 | 4187 | 0.0049052 | 6.5994 | 6.6043 | -1.2889 | 203.8666 | 2604.1594 | -0.0063221
122 |  | 1.0292 | 21.1317 | 4187 | 0.0049037 | 6.6043 | 6.6092 | -1.2889 | 203.9276 | 2625.2911 | -0.0063202
123 |  | 1.0292 | 21.1254 | 4187 | 0.0049022 | 6.6092 | 6.6141 | -1.2889 | 203.9886 | 2646.4164 | -0.0063183
124 |  | 1.0292 | 21.119 | 4187 | 0.0049008 | 6.6141 | 6.619 | -1.2889 | 204.0496 | 2667.5355 | -0.0063164
125 |  | 1.0292 | 21.1127 | 4187 | 0.0048993 | 6.619 | 6.6239 | -1.2889 | 204.1107 | 2688.6482 | -0.0063145
126 |  | 1.0292 | 21.1064 | 4187 | 0.0048978 | 6.6239 | 6.6288 | -1.2889 | 204.1718 | 2709.7546 | -0.0063126
127 |  | 1.0292 | 21.1001 | 4187 | 0.0048964 | 6.6288 | 6.6337 | -1.2889 | 204.2328 | 2730.8547 | -0.0063107
128 |  | 1.0292 | 21.0938 | 4187 | 0.0048949 | 6.6337 | 6.6386 | -1.2889 | 204.2939 | 2751.9485 | -0.0063088
129 |  | 1.0292 | 21.0875 | 4187 | 0.0048934 | 6.6386 | 6.6435 | -1.2889 | 204.3551 | 2773.0359 | -0.0063069
130 |  | 1.0292 | 21.0812 | 4187 | 0.004892 | 6.6435 | 6.6484 | -1.2889 | 204.4162 | 2794.1171 | -0.0063051
131 |  | 1.0292 | 21.0749 | 4187 | 0.0048905 | 6.6484 | 6.6533 | -1.2889 | 204.4774 | 2815.192 | -0.0063032
132 |  | 1.0292 | 21.0686 | 4187 | 0.0048891 | 6.6533 | 6.6582 | -1.2889 | 204.5385 | 2836.2605 | -0.0063013
133 |  | 1.0292 | 21.0623 | 4187 | 0.0048876 | 6.6582 | 6.6631 | -1.2889 | 204.5997 | 2857.3228 | -0.0062994
134 |  | 1.0292 | 21.056 | 4187 | 0.0048861 | 6.6631 | 6.6679 | -1.2889 | 204.6609 | 2878.3788 | -0.0062975
135 |  | 1.0292 | 21.0497 | 4187 | 0.0048847 | 6.6679 | 6.6728 | -1.2889 | 204.7222 | 2899.4284 | -0.0062956
136 |  | 1.0292 | 21.0434 | 4187 | 0.0048832 | 6.6728 | 6.6777 | -1.2889 | 204.7834 | 2920.4718 | -0.0062937
137 |  | 1.0292 | 21.0371 | 4187 | 0.0048817 | 6.6777 | 6.6826 | -1.2889 | 204.8447 | 2941.5089 | -0.0062919
138 |  | 1.0292 | 21.0308 | 4187 | 0.0048803 | 6.6826 | 6.6875 | -1.2889 | 204.906 | 2962.5396 | -0.00629
139 |  | 1.0292 | 21.0245 | 4187 | 0.0048788 | 6.6875 | 6.6923 | -1.2889 | 204.9673 | 2983.5641 | -0.0062881
140 |  | 1.0292 | 21.0182 | 4187 | 0.0048774 | 6.6923 | 6.6972 | -1.2889 | 205.0286 | 3004.5823 | -0.0062862
141 |  | 1.0292 | 21.0119 | 4187 | 0.0048759 | 6.6972 | 6.7021 | -1.2889 | 205.0899 | 3025.5942 | -0.0062843
142 |  | 1.0292 | 21.0056 | 4187 | 0.0048745 | 6.7021 | 6.707 | -1.2889 | 205.1513 | 3046.5999 | -0.0062825
143 |  | 1.0292 | 20.9993 | 4187 | 0.004873 | 6.707 | 6.7119 | -1.2889 | 205.2127 | 3067.5992 | -0.0062806
144 |  | 1.0292 | 20.9931 | 4187 | 0.0048715 | 6.7119 | 6.7167 | -1.2889 | 205.274 | 3088.5923 | -0.0062787
145 |  | 1.0292 | 20.9868 | 4187 | 0.0048701 | 6.7167 | 6.7216 | -1.2889 | 205.3355 | 3109.5791 | -0.0062768
146 |  | 1.0292 | 20.9805 | 4187 | 0.0048686 | 6.7216 | 6.7265 | -1.2889 | 205.3969 | 3130.5596 | -0.006275
147 |  | 1.0292 | 20.9742 | 4187 | 0.0048672 | 6.7265 | 6.7313 | -1.2889 | 205.4583 | 3151.5338 | -0.0062731
148 |  | 1.0292 | 20.968 | 4187 | 0.0048657 | 6.7313 | 6.7362 | -1.2889 | 205.5198 | 3172.5018 | -0.0062712
149 |  | 1.0292 | 20.9617 | 4187 | 0.0048643 | 6.7362 | 6.7411 | -1.2889 | 205.5813 | 3193.4635 | -0.0062693
150 |  | 1.0292 | 20.9554 | 4187 | 0.0048628 | 6.7411 | 6.7459 | -1.2889 | 205.6428 | 3214.4189 | -0.0062674
151 |  | 1.0292 | 20.9492 | 4187 | 0.0048613 | 6.7459 | 6.7508 | -1.2889 | 205.7043 | 3235.3681 | -0.0062656
152 |  | 1.0292 | 20.9429 | 4187 | 0.0048599 | 6.7508 | 6.7556 | -1.2889 | 205.7659 | 3256.311 | -0.0062637
153 |  | 1.0292 | 20.9366 | 4187 | 0.0048584 | 6.7556 | 6.7605 | -1.2889 | 205.8274 | 3277.2476 | -0.0062618
154 |  | 1.0292 | 20.9304 | 4187 | 0.004857 | 6.7605 | 6.7654 | -1.2889 | 205.889 | 3298.178 | -0.00626
155 |  | 1.0292 | 20.9241 | 4187 | 0.0048555 | 6.7654 | 6.7702 | -1.2889 | 205.9506 | 3319.1021 | -0.0062581
156 |  | 1.0292 | 20.9178 | 4187 | 0.0048541 | 6.7702 | 6.7751 | -1.2889 | 206.0122 | 3340.0199 | -0.0062562
157 |  | 1.0292 | 20.9116 | 4187 | 0.0048526 | 6.7751 | 6.7799 | -1.2889 | 206.0738 | 3360.9315 | -0.0062543
158 |  | 1.0292 | 20.9053 | 4187 | 0.0048512 | 6.7799 | 6.7848 | -1.2889 | 206.1355 | 3381.8369 | -0.0062525
159 |  | 1.0292 | 20.8991 | 4187 | 0.0048497 | 6.7848 | 6.7896 | -1.2889 | 206.1972 | 3402.7359 | -0.0062506
160 |  | 1.0292 | 20.8928 | 4187 | 0.0048483 | 6.7896 | 6.7945 | -1.2889 | 206.2589 | 3423.6288 | -0.0062487
161 |  | 1.0292 | 20.8866 | 4187 | 0.0048468 | 6.7945 | 6.7993 | -1.2889 | 206.3206 | 3444.5154 | -0.0062469
162 |  | 1.0292 | 20.8803 | 4187 | 0.0048454 | 6.7993 | 6.8042 | -1.2889 | 206.3823 | 3465.3957 | -0.006245
163 |  | 1.0292 | 20.8741 | 4187 | 0.0048439 | 6.8042 | 6.809 | -1.2889 | 206.444 | 3486.2698 | -0.0062431
164 |  | 1.0292 | 20.8679 | 4187 | 0.0048425 | 6.809 | 6.8138 | -1.2889 | 206.5058 | 3507.1376 | -0.0062413
165 |  | 1.0292 | 20.8616 | 4187 | 0.004841 | 6.8138 | 6.8187 | -1.2889 | 206.5676 | 3527.9993 | -0.0062394
166 |  | 1.0292 | 20.8554 | 4187 | 0.0048396 | 6.8187 | 6.8235 | -1.2889 | 206.6294 | 3548.8546 | -0.0062375
167 |  | 1.0292 | 20.8491 | 4187 | 0.0048381 | 6.8235 | 6.8284 | -1.2889 | 206.6912 | 3569.7038 | -0.0062357
168 |  | 1.0292 | 20.8429 | 4187 | 0.0048367 | 6.8284 | 6.8332 | -1.2889 | 206.753 | 3590.5467 | -0.0062338
169 |  | 1.0292 | 20.8367 | 4187 | 0.0048352 | 6.8332 | 6.838 | -1.2889 | 206.8149 | 3611.3833 | -0.0062319
170 |  | 1.0292 | 20.8304 | 4187 | 0.0048338 | 6.838 | 6.8429 | -1.2889 | 206.8768 | 3632.2137 | -0.0062301
171 |  | 1.0292 | 20.8242 | 4187 | 0.0048323 | 6.8429 | 6.8477 | -1.2889 | 206.9387 | 3653.0379 | -0.0062282
172 |  | 1.0292 | 20.818 | 4187 | 0.0048309 | 6.8477 | 6.8525 | -1.2889 | 207.0006 | 3673.8559 | -0.0062263
173 |  | 1.0292 | 20.8117 | 4187 | 0.0048295 | 6.8525 | 6.8574 | -1.2889 | 207.0625 | 3694.6677 | -0.0062245
174 |  | 1.0292 | 20.8055 | 4187 | 0.004828 | 6.8574 | 6.8622 | -1.2889 | 207.1244 | 3715.4732 | -0.0062226
175 |  | 1.0292 | 20.7993 | 4187 | 0.0048266 | 6.8622 | 6.867 | -1.2889 | 207.1864 | 3736.2725 | -0.0062208
176 |  | 1.0292 | 20.7931 | 4187 | 0.0048251 | 6.867 | 6.8718 | -1.2889 | 207.2484 | 3757.0656 | -0.0062189
177 |  | 1.0292 | 20.7869 | 4187 | 0.0048237 | 6.8718 | 6.8767 | -1.2889 | 207.3104 | 3777.8524 | -0.006217
178 |  | 1.0292 | 20.7806 | 4187 | 0.0048222 | 6.8767 | 6.8815 | -1.2889 | 207.3724 | 3798.6331 | -0.0062152
179 |  | 1.0292 | 20.7744 | 4187 | 0.0048208 | 6.8815 | 6.8863 | -1.2889 | 207.4345 | 3819.4075 | -0.0062133
180 |  | 1.0292 | 20.7682 | 4187 | 0.0048194 | 6.8863 | 6.8911 | -1.2889 | 207.4965 | 3840.1757 | -0.0062115
181 |  | 1.0292 | 20.762 | 4187 | 0.0048179 | 6.8911 | 6.8959 | -1.2889 | 207.5586 | 3860.9377 | -0.0062096
182 |  | 1.0292 | 20.7558 | 4187 | 0.0048165 | 6.8959 | 6.9008 | -1.2889 | 207.6207 | 3881.6935 | -0.0062077
183 |  | 1.0292 | 20.7496 | 4187 | 0.004815 | 6.9008 | 6.9056 | -1.2889 | 207.6828 | 3902.4431 | -0.0062059
184 |  | 1.0292 | 20.7434 | 4187 | 0.0048136 | 6.9056 | 6.9104 | -1.2889 | 207.7449 | 3923.1865 | -0.006204
185 |  | 1.0292 | 20.7372 | 4187 | 0.0048122 | 6.9104 | 6.9152 | -1.2889 | 207.8071 | 3943.9237 | -0.0062022
186 |  | 1.0292 | 20.731 | 4187 | 0.0048107 | 6.9152 | 6.92 | -1.2889 | 207.8693 | 3964.6546 | -0.0062003
187 |  | 1.0292 | 20.7248 | 4187 | 0.0048093 | 6.92 | 6.9248 | -1.2889 | 207.9315 | 3985.3794 | -0.0061985
188 |  | 1.0292 | 20.7186 | 4187 | 0.0048078 | 6.9248 | 6.9296 | -1.2889 | 207.9937 | 4006.098 | -0.0061966
189 |  | 1.0292 | 20.7124 | 4187 | 0.0048064 | 6.9296 | 6.9344 | -1.2889 | 208.0559 | 4026.8104 | -0.0061948
190 |  | 1.0292 | 20.7062 | 4187 | 0.004805 | 6.9344 | 6.9392 | -1.2889 | 208.1181 | 4047.5165 | -0.0061929
191 |  | 1.0292 | 20.7 | 4187 | 0.0048035 | 6.9392 | 6.944 | -1.2889 | 208.1804 | 4068.2165 | -0.0061911
192 |  | 1.0292 | 20.6938 | 4187 | 0.0048021 | 6.944 | 6.9489 | -1.2889 | 208.2427 | 4088.9103 | -0.0061892
193 |  | 1.0292 | 20.6876 | 4187 | 0.0048007 | 6.9489 | 6.9537 | -1.2889 | 208.305 | 4109.5979 | -0.0061873
194 |  | 1.0292 | 20.6814 | 4187 | 0.0047992 | 6.9537 | 6.9584 | -1.2889 | 208.3673 | 4130.2794 | -0.0061855
195 |  | 1.0292 | 20.6752 | 4187 | 0.0047978 | 6.9584 | 6.9632 | -1.2889 | 208.4296 | 4150.9546 | -0.0061836
196 |  | 1.0292 | 20.6691 | 4187 | 0.0047963 | 6.9632 | 6.968 | -1.2889 | 208.492 | 4171.6237 | -0.0061818
197 |  | 1.0292 | 20.6629 | 4187 | 0.0047949 | 6.968 | 6.9728 | -1.2889 | 208.5544 | 4192.2865 | -0.0061799
198 |  | 1.0292 | 20.6567 | 4187 | 0.0047935 | 6.9728 | 6.9776 | -1.2889 | 208.6168 | 4212.9432 | -0.0061781
199 |  | 1.0292 | 20.6505 | 4187 | 0.004792 | 6.9776 | 6.9824 | -1.2889 | 208.6792 | 4233.5937 | -0.0061763
200 |  | 1.0292 | 20.6443 | 4187 | 0.0047906 | 6.9824 | 6.9872 | -1.2889 | 208.7416 | 4254.2381 | -0.0061744
201 |  | 1.0292 | 20.6382 | 4187 | 0.0047892 | 6.9872 | 6.992 | -1.2889 | 208.8041 | 4274.8762 | -0.0061726
202 |  | 1.0292 | 20.632 | 4187 | 0.0047877 | 6.992 | 6.9968 | -1.2889 | 208.8665 | 4295.5082 | -0.0061707
203 |  | 1.0292 | 20.6258 | 4187 | 0.0047863 | 6.9968 | 7.0016 | -1.2889 | 208.929 | 4316.134 | -0.0061689
204 |  | 1.0292 | 20.6197 | 4187 | 0.0047849 | 7.0016 | 7.0064 | -1.2889 | 208.9915 | 4336.7537 | -0.006167
205 |  | 1.0292 | 20.6135 | 4187 | 0.0047835 | 7.0064 | 7.0111 | -1.2889 | 209.054 | 4357.3672 | -0.0061652
206 |  | 1.0292 | 20.6073 | 4187 | 0.004782 | 7.0111 | 7.0159 | -1.2889 | 209.1166 | 4377.9745 | -0.0061633
207 |  | 1.0292 | 20.6012 | 4187 | 0.0047806 | 7.0159 | 7.0207 | -1.2889 | 209.1792 | 4398.5757 | -0.0061615
208 |  | 1.0292 | 20.595 | 4187 | 0.0047792 | 7.0207 | 7.0255 | -1.2889 | 209.2417 | 4419.1707 | -0.0061596
209 |  | 1.0292 | 20.5888 | 4187 | 0.0047777 | 7.0255 | 7.0303 | -1.2889 | 209.3043 | 4439.7595 | -0.0061578
210 |  | 1.0292 | 20.5827 | 4187 | 0.0047763 | 7.0303 | 7.035 | -1.2889 | 209.3669 | 4460.3422 | -0.006156
211 |  | 1.0292 | 20.5765 | 4187 | 0.0047749 | 7.035 | 7.0398 | -1.2889 | 209.4296 | 4480.9187 | -0.0061541
212 |  | 1.0292 | 20.5704 | 4187 | 0.0047734 | 7.0398 | 7.0446 | -1.2889 | 209.4922 | 4501.4891 | -0.0061523
213 |  | 1.0292 | 20.5642 | 4187 | 0.004772 | 7.0446 | 7.0494 | -1.2889 | 209.5549 | 4522.0533 | -0.0061504
214 |  | 1.0292 | 20.5581 | 4187 | 0.0047706 | 7.0494 | 7.0541 | -1.2889 | 209.6176 | 4542.6113 | -0.0061486
215 |  | 1.0292 | 20.5519 | 4187 | 0.0047692 | 7.0541 | 7.0589 | -1.2889 | 209.6803 | 4563.1632 | -0.0061468
216 |  | 1.0292 | 20.5458 | 4187 | 0.0047677 | 7.0589 | 7.0637 | -1.2889 | 209.7431 | 4583.709 | -0.0061449
217 |  | 1.0292 | 20.5396 | 4187 | 0.0047663 | 7.0637 | 7.0684 | -1.2889 | 209.8058 | 4604.2486 | -0.0061431
218 |  | 1.0292 | 20.5335 | 4187 | 0.0047649 | 7.0684 | 7.0732 | -1.2889 | 209.8686 | 4624.7821 | -0.0061412
219 |  | 1.0292 | 20.5273 | 4187 | 0.0047635 | 7.0732 | 7.078 | -1.2889 | 209.9314 | 4645.3095 | -0.0061394
220 |  | 1.0292 | 20.5212 | 4187 | 0.004762 | 7.078 | 7.0827 | -1.2889 | 209.9942 | 4665.8307 | -0.0061376
221 |  | 1.0292 | 20.5151 | 4187 | 0.0047606 | 7.0827 | 7.0875 | -1.2889 | 210.057 | 4686.3457 | -0.0061357
222 |  | 1.0292 | 20.5089 | 4187 | 0.0047592 | 7.0875 | 7.0922 | -1.2889 | 210.1198 | 4706.8546 | -0.0061339
223 |  | 1.0292 | 20.5028 | 4187 | 0.0047578 | 7.0922 | 7.097 | -1.2889 | 210.1827 | 4727.3574 | -0.0061321
224 |  | 1.0292 | 20.4967 | 4187 | 0.0047563 | 7.097 | 7.1018 | -1.2889 | 210.2456 | 4747.8541 | -0.0061302
225 |  | 1.0292 | 20.4905 | 4187 | 0.0047549 | 7.1018 | 7.1065 | -1.2889 | 210.3085 | 4768.3446 | -0.0061284
226 |  | 1.0292 | 20.4844 | 4187 | 0.0047535 | 7.1065 | 7.1113 | -1.2889 | 210.3714 | 4788.829 | -0.0061266
227 |  | 1.0292 | 20.4783 | 4187 | 0.0047521 | 7.1113 | 7.116 | -1.2889 | 210.4343 | 4809.3073 | -0.0061247
228 |  | 1.0292 | 20.4722 | 4187 | 0.0047507 | 7.116 | 7.1208 | -1.2889 | 210.4973 | 4829.7795 | -0.0061229
229 |  | 1.0292 | 20.466 | 4187 | 0.0047492 | 7.1208 | 7.1255 | -1.2889 | 210.5603 | 4850.2455 | -0.0061211
230 |  | 1.0292 | 20.4599 | 4187 | 0.0047478 | 7.1255 | 7.1303 | -1.2889 | 210.6233 | 4870.7054 | -0.0061192
231 |  | 1.0292 | 20.4538 | 4187 | 0.0047464 | 7.1303 | 7.135 | -1.2889 | 210.6863 | 4891.1592 | -0.0061174
232 |  | 1.0292 | 20.4477 | 4187 | 0.004745 | 7.135 | 7.1398 | -1.2889 | 210.7493 | 4911.6069 | -0.0061156
233 |  | 1.0292 | 20.4416 | 4187 | 0.0047436 | 7.1398 | 7.1445 | -1.2889 | 210.8124 | 4932.0484 | -0.0061138
234 |  | 1.0292 | 20.4354 | 4187 | 0.0047421 | 7.1445 | 7.1492 | -1.2889 | 210.8754 | 4952.4838 | -0.0061119
235 |  | 1.0292 | 20.4293 | 4187 | 0.0047407 | 7.1492 | 7.154 | -1.2889 | 210.9385 | 4972.9132 | -0.0061101
236 |  | 1.0292 | 20.4232 | 4187 | 0.0047393 | 7.154 | 7.1587 | -1.2889 | 211.0016 | 4993.3364 | -0.0061083

## Fus63
|  |  | buis | verlies W/M | L /°C/sec
diam | wandikte |  | inhoud l/m |  | W/M
63 | 8.6 | 3.1416 | 1.6475 | 24.9231 | 4187
|  |  |  | 6 |  |  |  | J/sec/mtr | aantal mtr. | verlies
|  | buis | verlies W/M | L /°C/sec | verlies temp | begintemp | eindtemp | verlies | bij 1°C | totaal J/sec
|  | inhoud L |  | W/M | °C per M | °C | °C | per m°C | daling | aantal mtr
1 | 63 | 1.6475 | 24.9231 | 4187 | 0.0036131 | 6 | 6.0036 | -1.4661 | 276.7715 | 24.9231 | -0.005297
2 |  | 1.6475 | 24.9178 | 4187 | 0.0036123 | 6.0036 | 6.0072 | -1.4661 | 276.8303 | 49.841 | -0.0052959
3 |  | 1.6475 | 24.9125 | 4187 | 0.0036116 | 6.0072 | 6.0108 | -1.4661 | 276.8891 | 74.7535 | -0.0052948
4 |  | 1.6475 | 24.9072 | 4187 | 0.0036108 | 6.0108 | 6.0144 | -1.4661 | 276.948 | 99.6607 | -0.0052937
5 |  | 1.6475 | 24.9019 | 4187 | 0.00361 | 6.0144 | 6.0181 | -1.4661 | 277.0069 | 124.5627 | -0.0052925
6 |  | 1.6475 | 24.8967 | 4187 | 0.0036093 | 6.0181 | 6.0217 | -1.4661 | 277.0658 | 149.4593 | -0.0052914
7 |  | 1.6475 | 24.8914 | 4187 | 0.0036085 | 6.0217 | 6.0253 | -1.4661 | 277.1247 | 174.3507 | -0.0052903
8 |  | 1.6475 | 24.8861 | 4187 | 0.0036077 | 6.0253 | 6.0289 | -1.4661 | 277.1836 | 199.2367 | -0.0052892
9 |  | 1.6475 | 24.8808 | 4187 | 0.003607 | 6.0289 | 6.0325 | -1.4661 | 277.2425 | 224.1175 | -0.005288
10 |  | 1.6475 | 24.8755 | 4187 | 0.0036062 | 6.0325 | 6.0361 | -1.4661 | 277.3014 | 248.993 | -0.0052869
11 |  | 1.6475 | 24.8702 | 4187 | 0.0036054 | 6.0361 | 6.0397 | -1.4661 | 277.3604 | 273.8632 | -0.0052858
12 |  | 1.6475 | 24.8649 | 4187 | 0.0036047 | 6.0397 | 6.0433 | -1.4661 | 277.4193 | 298.7281 | -0.0052847
13 |  | 1.6475 | 24.8596 | 4187 | 0.0036039 | 6.0433 | 6.0469 | -1.4661 | 277.4783 | 323.5878 | -0.0052835
14 |  | 1.6475 | 24.8544 | 4187 | 0.0036031 | 6.0469 | 6.0505 | -1.4661 | 277.5373 | 348.4421 | -0.0052824
15 |  | 1.6475 | 24.8491 | 4187 | 0.0036024 | 6.0505 | 6.0541 | -1.4661 | 277.5963 | 373.2912 | -0.0052813
16 |  | 1.6475 | 24.8438 | 4187 | 0.0036016 | 6.0541 | 6.0577 | -1.4661 | 277.6553 | 398.135 | -0.0052802
17 |  | 1.6475 | 24.8385 | 4187 | 0.0036008 | 6.0577 | 6.0613 | -1.4661 | 277.7143 | 422.9735 | -0.005279
18 |  | 1.6475 | 24.8332 | 4187 | 0.0036001 | 6.0613 | 6.0649 | -1.4661 | 277.7734 | 447.8067 | -0.0052779
19 |  | 1.6475 | 24.828 | 4187 | 0.0035993 | 6.0649 | 6.0685 | -1.4661 | 277.8324 | 472.6347 | -0.0052768
20 |  | 1.6475 | 24.8227 | 4187 | 0.0035985 | 6.0685 | 6.0721 | -1.4661 | 277.8915 | 497.4573 | -0.0052757
21 |  | 1.6475 | 24.8174 | 4187 | 0.0035978 | 6.0721 | 6.0757 | -1.4661 | 277.9506 | 522.2747 | -0.0052746
22 |  | 1.6475 | 24.8121 | 4187 | 0.003597 | 6.0757 | 6.0793 | -1.4661 | 278.0097 | 547.0869 | -0.0052734
23 |  | 1.6475 | 24.8068 | 4187 | 0.0035962 | 6.0793 | 6.0829 | -1.4661 | 278.0688 | 571.8937 | -0.0052723
24 |  | 1.6475 | 24.8016 | 4187 | 0.0035955 | 6.0829 | 6.0865 | -1.4661 | 278.1279 | 596.6953 | -0.0052712
25 |  | 1.6475 | 24.7963 | 4187 | 0.0035947 | 6.0865 | 6.0901 | -1.4661 | 278.187 | 621.4916 | -0.0052701
26 |  | 1.6475 | 24.791 | 4187 | 0.0035939 | 6.0901 | 6.0937 | -1.4661 | 278.2461 | 646.2826 | -0.005269
27 |  | 1.6475 | 24.7858 | 4187 | 0.0035932 | 6.0937 | 6.0973 | -1.4661 | 278.3053 | 671.0684 | -0.0052678
28 |  | 1.6475 | 24.7805 | 4187 | 0.0035924 | 6.0973 | 6.1009 | -1.4661 | 278.3644 | 695.8489 | -0.0052667
29 |  | 1.6475 | 24.7752 | 4187 | 0.0035916 | 6.1009 | 6.1045 | -1.4661 | 278.4236 | 720.6241 | -0.0052656
30 |  | 1.6475 | 24.77 | 4187 | 0.0035909 | 6.1045 | 6.1081 | -1.4661 | 278.4828 | 745.3941 | -0.0052645
31 |  | 1.6475 | 24.7647 | 4187 | 0.0035901 | 6.1081 | 6.1116 | -1.4661 | 278.542 | 770.1588 | -0.0052634
32 |  | 1.6475 | 24.7594 | 4187 | 0.0035894 | 6.1116 | 6.1152 | -1.4661 | 278.6012 | 794.9182 | -0.0052622
33 |  | 1.6475 | 24.7542 | 4187 | 0.0035886 | 6.1152 | 6.1188 | -1.4661 | 278.6604 | 819.6724 | -0.0052611
34 |  | 1.6475 | 24.7489 | 4187 | 0.0035878 | 6.1188 | 6.1224 | -1.4661 | 278.7197 | 844.4213 | -0.00526
35 |  | 1.6475 | 24.7437 | 4187 | 0.0035871 | 6.1224 | 6.126 | -1.4661 | 278.7789 | 869.165 | -0.0052589
36 |  | 1.6475 | 24.7384 | 4187 | 0.0035863 | 6.126 | 6.1296 | -1.4661 | 278.8382 | 893.9034 | -0.0052578
37 |  | 1.6475 | 24.7331 | 4187 | 0.0035855 | 6.1296 | 6.1332 | -1.4661 | 278.8975 | 918.6365 | -0.0052566
38 |  | 1.6475 | 24.7279 | 4187 | 0.0035848 | 6.1332 | 6.1368 | -1.4661 | 278.9567 | 943.3644 | -0.0052555
39 |  | 1.6475 | 24.7226 | 4187 | 0.003584 | 6.1368 | 6.1403 | -1.4661 | 279.016 | 968.087 | -0.0052544
40 |  | 1.6475 | 24.7174 | 4187 | 0.0035833 | 6.1403 | 6.1439 | -1.4661 | 279.0754 | 992.8044 | -0.0052533
41 |  | 1.6475 | 24.7121 | 4187 | 0.0035825 | 6.1439 | 6.1475 | -1.4661 | 279.1347 | 1017.5165 | -0.0052522
42 |  | 1.6475 | 24.7069 | 4187 | 0.0035817 | 6.1475 | 6.1511 | -1.4661 | 279.194 | 1042.2234 | -0.0052511
43 |  | 1.6475 | 24.7016 | 4187 | 0.003581 | 6.1511 | 6.1547 | -1.4661 | 279.2534 | 1066.925 | -0.0052499
44 |  | 1.6475 | 24.6964 | 4187 | 0.0035802 | 6.1547 | 6.1583 | -1.4661 | 279.3127 | 1091.6214 | -0.0052488
45 |  | 1.6475 | 24.6911 | 4187 | 0.0035795 | 6.1583 | 6.1618 | -1.4661 | 279.3721 | 1116.3125 | -0.0052477
46 |  | 1.6475 | 24.6859 | 4187 | 0.0035787 | 6.1618 | 6.1654 | -1.4661 | 279.4315 | 1140.9984 | -0.0052466
47 |  | 1.6475 | 24.6806 | 4187 | 0.0035779 | 6.1654 | 6.169 | -1.4661 | 279.4909 | 1165.679 | -0.0052455
48 |  | 1.6475 | 24.6754 | 4187 | 0.0035772 | 6.169 | 6.1726 | -1.4661 | 279.5503 | 1190.3544 | -0.0052444
49 |  | 1.6475 | 24.6701 | 4187 | 0.0035764 | 6.1726 | 6.1761 | -1.4661 | 279.6097 | 1215.0245 | -0.0052433
50 |  | 1.6475 | 24.6649 | 4187 | 0.0035757 | 6.1761 | 6.1797 | -1.4661 | 279.6692 | 1239.6894 | -0.0052421
51 |  | 1.6475 | 24.6596 | 4187 | 0.0035749 | 6.1797 | 6.1833 | -1.4661 | 279.7286 | 1264.349 | -0.005241
52 |  | 1.6475 | 24.6544 | 4187 | 0.0035741 | 6.1833 | 6.1869 | -1.4661 | 279.7881 | 1289.0034 | -0.0052399
53 |  | 1.6475 | 24.6492 | 4187 | 0.0035734 | 6.1869 | 6.1904 | -1.4661 | 279.8476 | 1313.6526 | -0.0052388
54 |  | 1.6475 | 24.6439 | 4187 | 0.0035726 | 6.1904 | 6.194 | -1.4661 | 279.9071 | 1338.2965 | -0.0052377
55 |  | 1.6475 | 24.6387 | 4187 | 0.0035719 | 6.194 | 6.1976 | -1.4661 | 279.9666 | 1362.9352 | -0.0052366
56 |  | 1.6475 | 24.6335 | 4187 | 0.0035711 | 6.1976 | 6.2012 | -1.4661 | 280.0261 | 1387.5687 | -0.0052355
57 |  | 1.6475 | 24.6282 | 4187 | 0.0035703 | 6.2012 | 6.2047 | -1.4661 | 280.0856 | 1412.1969 | -0.0052343
58 |  | 1.6475 | 24.623 | 4187 | 0.0035696 | 6.2047 | 6.2083 | -1.4661 | 280.1452 | 1436.8199 | -0.0052332
59 |  | 1.6475 | 24.6178 | 4187 | 0.0035688 | 6.2083 | 6.2119 | -1.4661 | 280.2047 | 1461.4376 | -0.0052321
60 |  | 1.6475 | 24.6125 | 4187 | 0.0035681 | 6.2119 | 6.2154 | -1.4661 | 280.2643 | 1486.0501 | -0.005231
61 |  | 1.6475 | 24.6073 | 4187 | 0.0035673 | 6.2154 | 6.219 | -1.4661 | 280.3239 | 1510.6574 | -0.0052299
62 |  | 1.6475 | 24.6021 | 4187 | 0.0035665 | 6.219 | 6.2226 | -1.4661 | 280.3834 | 1535.2595 | -0.0052288
63 |  | 1.6475 | 24.5968 | 4187 | 0.0035658 | 6.2226 | 6.2261 | -1.4661 | 280.4431 | 1559.8563 | -0.0052277
64 |  | 1.6475 | 24.5916 | 4187 | 0.003565 | 6.2261 | 6.2297 | -1.4661 | 280.5027 | 1584.4479 | -0.0052266
65 |  | 1.6475 | 24.5864 | 4187 | 0.0035643 | 6.2297 | 6.2333 | -1.4661 | 280.5623 | 1609.0343 | -0.0052255
66 |  | 1.6475 | 24.5811 | 4187 | 0.0035635 | 6.2333 | 6.2368 | -1.4661 | 280.6219 | 1633.6154 | -0.0052243
67 |  | 1.6475 | 24.5759 | 4187 | 0.0035628 | 6.2368 | 6.2404 | -1.4661 | 280.6816 | 1658.1914 | -0.0052232
68 |  | 1.6475 | 24.5707 | 4187 | 0.003562 | 6.2404 | 6.2439 | -1.4661 | 280.7413 | 1682.7621 | -0.0052221
69 |  | 1.6475 | 24.5655 | 4187 | 0.0035612 | 6.2439 | 6.2475 | -1.4661 | 280.8009 | 1707.3275 | -0.005221
70 |  | 1.6475 | 24.5603 | 4187 | 0.0035605 | 6.2475 | 6.2511 | -1.4661 | 280.8606 | 1731.8878 | -0.0052199
71 |  | 1.6475 | 24.555 | 4187 | 0.0035597 | 6.2511 | 6.2546 | -1.4661 | 280.9203 | 1756.4428 | -0.0052188
72 |  | 1.6475 | 24.5498 | 4187 | 0.003559 | 6.2546 | 6.2582 | -1.4661 | 280.9801 | 1780.9927 | -0.0052177
73 |  | 1.6475 | 24.5446 | 4187 | 0.0035582 | 6.2582 | 6.2617 | -1.4661 | 281.0398 | 1805.5373 | -0.0052166
74 |  | 1.6475 | 24.5394 | 4187 | 0.0035575 | 6.2617 | 6.2653 | -1.4661 | 281.0995 | 1830.0766 | -0.0052155
75 |  | 1.6475 | 24.5342 | 4187 | 0.0035567 | 6.2653 | 6.2689 | -1.4661 | 281.1593 | 1854.6108 | -0.0052144
76 |  | 1.6475 | 24.529 | 4187 | 0.0035559 | 6.2689 | 6.2724 | -1.4661 | 281.2191 | 1879.1398 | -0.0052133
77 |  | 1.6475 | 24.5237 | 4187 | 0.0035552 | 6.2724 | 6.276 | -1.4661 | 281.2788 | 1903.6635 | -0.0052121
78 |  | 1.6475 | 24.5185 | 4187 | 0.0035544 | 6.276 | 6.2795 | -1.4661 | 281.3386 | 1928.182 | -0.005211
79 |  | 1.6475 | 24.5133 | 4187 | 0.0035537 | 6.2795 | 6.2831 | -1.4661 | 281.3984 | 1952.6954 | -0.0052099
80 |  | 1.6475 | 24.5081 | 4187 | 0.0035529 | 6.2831 | 6.2866 | -1.4661 | 281.4583 | 1977.2035 | -0.0052088
81 |  | 1.6475 | 24.5029 | 4187 | 0.0035522 | 6.2866 | 6.2902 | -1.4661 | 281.5181 | 2001.7064 | -0.0052077
82 |  | 1.6475 | 24.4977 | 4187 | 0.0035514 | 6.2902 | 6.2937 | -1.4661 | 281.5779 | 2026.2041 | -0.0052066
83 |  | 1.6475 | 24.4925 | 4187 | 0.0035507 | 6.2937 | 6.2973 | -1.4661 | 281.6378 | 2050.6965 | -0.0052055
84 |  | 1.6475 | 24.4873 | 4187 | 0.0035499 | 6.2973 | 6.3008 | -1.4661 | 281.6977 | 2075.1838 | -0.0052044
85 |  | 1.6475 | 24.4821 | 4187 | 0.0035492 | 6.3008 | 6.3044 | -1.4661 | 281.7575 | 2099.6659 | -0.0052033
86 |  | 1.6475 | 24.4769 | 4187 | 0.0035484 | 6.3044 | 6.3079 | -1.4661 | 281.8174 | 2124.1428 | -0.0052022
87 |  | 1.6475 | 24.4717 | 4187 | 0.0035476 | 6.3079 | 6.3115 | -1.4661 | 281.8774 | 2148.6144 | -0.0052011
88 |  | 1.6475 | 24.4665 | 4187 | 0.0035469 | 6.3115 | 6.315 | -1.4661 | 281.9373 | 2173.0809 | -0.0052
89 |  | 1.6475 | 24.4613 | 4187 | 0.0035461 | 6.315 | 6.3186 | -1.4661 | 281.9972 | 2197.5422 | -0.0051989
90 |  | 1.6475 | 24.4561 | 4187 | 0.0035454 | 6.3186 | 6.3221 | -1.4661 | 282.0572 | 2221.9983 | -0.0051978
91 |  | 1.6475 | 24.4509 | 4187 | 0.0035446 | 6.3221 | 6.3257 | -1.4661 | 282.1171 | 2246.4491 | -0.0051967
92 |  | 1.6475 | 24.4457 | 4187 | 0.0035439 | 6.3257 | 6.3292 | -1.4661 | 282.1771 | 2270.8948 | -0.0051956
93 |  | 1.6475 | 24.4405 | 4187 | 0.0035431 | 6.3292 | 6.3328 | -1.4661 | 282.2371 | 2295.3353 | -0.0051944
94 |  | 1.6475 | 24.4353 | 4187 | 0.0035424 | 6.3328 | 6.3363 | -1.4661 | 282.2971 | 2319.7706 | -0.0051933
95 |  | 1.6475 | 24.4301 | 4187 | 0.0035416 | 6.3363 | 6.3398 | -1.4661 | 282.3571 | 2344.2007 | -0.0051922
96 |  | 1.6475 | 24.4249 | 4187 | 0.0035409 | 6.3398 | 6.3434 | -1.4661 | 282.4171 | 2368.6256 | -0.0051911
97 |  | 1.6475 | 24.4197 | 4187 | 0.0035401 | 6.3434 | 6.3469 | -1.4661 | 282.4771 | 2393.0453 | -0.00519
98 |  | 1.6475 | 24.4145 | 4187 | 0.0035394 | 6.3469 | 6.3505 | -1.4661 | 282.5372 | 2417.4598 | -0.0051889
99 |  | 1.6475 | 24.4093 | 4187 | 0.0035386 | 6.3505 | 6.354 | -1.4661 | 282.5972 | 2441.8691 | -0.0051878
100 |  | 1.6475 | 24.4041 | 4187 | 0.0035379 | 6.354 | 6.3575 | -1.4661 | 282.6573 | 2466.2733 | -0.0051867
101 |  | 1.6475 | 24.399 | 4187 | 0.0035371 | 6.3575 | 6.3611 | -1.4661 | 282.7174 | 2490.6722 | -0.0051856
102 |  | 1.6475 | 24.3938 | 4187 | 0.0035363 | 6.3611 | 6.3646 | -1.4661 | 282.7775 | 2515.066 | -0.0051845
103 |  | 1.6475 | 24.3886 | 4187 | 0.0035356 | 6.3646 | 6.3681 | -1.4661 | 282.8376 | 2539.4546 | -0.0051834
104 |  | 1.6475 | 24.3834 | 4187 | 0.0035348 | 6.3681 | 6.3717 | -1.4661 | 282.8977 | 2563.838 | -0.0051823
105 |  | 1.6475 | 24.3782 | 4187 | 0.0035341 | 6.3717 | 6.3752 | -1.4661 | 282.9579 | 2588.2162 | -0.0051812
106 |  | 1.6475 | 24.373 | 4187 | 0.0035333 | 6.3752 | 6.3787 | -1.4661 | 283.018 | 2612.5892 | -0.0051801
107 |  | 1.6475 | 24.3679 | 4187 | 0.0035326 | 6.3787 | 6.3823 | -1.4661 | 283.0782 | 2636.9571 | -0.005179
108 |  | 1.6475 | 24.3627 | 4187 | 0.0035318 | 6.3823 | 6.3858 | -1.4661 | 283.1384 | 2661.3198 | -0.0051779
109 |  | 1.6475 | 24.3575 | 4187 | 0.0035311 | 6.3858 | 6.3893 | -1.4661 | 283.1986 | 2685.6773 | -0.0051768
110 |  | 1.6475 | 24.3523 | 4187 | 0.0035303 | 6.3893 | 6.3929 | -1.4661 | 283.2588 | 2710.0296 | -0.0051757
111 |  | 1.6475 | 24.3471 | 4187 | 0.0035296 | 6.3929 | 6.3964 | -1.4661 | 283.319 | 2734.3768 | -0.0051746
112 |  | 1.6475 | 24.342 | 4187 | 0.0035288 | 6.3964 | 6.3999 | -1.4661 | 283.3792 | 2758.7187 | -0.0051735
113 |  | 1.6475 | 24.3368 | 4187 | 0.0035281 | 6.3999 | 6.4035 | -1.4661 | 283.4395 | 2783.0555 | -0.0051724
114 |  | 1.6475 | 24.3316 | 4187 | 0.0035273 | 6.4035 | 6.407 | -1.4661 | 283.4997 | 2807.3872 | -0.0051713
115 |  | 1.6475 | 24.3265 | 4187 | 0.0035266 | 6.407 | 6.4105 | -1.4661 | 283.56 | 2831.7136 | -0.0051702
116 |  | 1.6475 | 24.3213 | 4187 | 0.0035258 | 6.4105 | 6.414 | -1.4661 | 283.6203 | 2856.0349 | -0.0051691
117 |  | 1.6475 | 24.3161 | 4187 | 0.0035251 | 6.414 | 6.4176 | -1.4661 | 283.6805 | 2880.351 | -0.005168
118 |  | 1.6475 | 24.311 | 4187 | 0.0035243 | 6.4176 | 6.4211 | -1.4661 | 283.7409 | 2904.662 | -0.0051669
119 |  | 1.6475 | 24.3058 | 4187 | 0.0035236 | 6.4211 | 6.4246 | -1.4661 | 283.8012 | 2928.9678 | -0.0051658
120 |  | 1.6475 | 24.3006 | 4187 | 0.0035228 | 6.4246 | 6.4281 | -1.4661 | 283.8615 | 2953.2684 | -0.0051647
121 |  | 1.6475 | 24.2955 | 4187 | 0.0035221 | 6.4281 | 6.4317 | -1.4661 | 283.9218 | 2977.5638 | -0.0051636
122 |  | 1.6475 | 24.2903 | 4187 | 0.0035213 | 6.4317 | 6.4352 | -1.4661 | 283.9822 | 3001.8541 | -0.0051625
123 |  | 1.6475 | 24.2851 | 4187 | 0.0035206 | 6.4352 | 6.4387 | -1.4661 | 284.0426 | 3026.1392 | -0.0051614
124 |  | 1.6475 | 24.28 | 4187 | 0.0035199 | 6.4387 | 6.4422 | -1.4661 | 284.1029 | 3050.4192 | -0.0051603
125 |  | 1.6475 | 24.2748 | 4187 | 0.0035191 | 6.4422 | 6.4457 | -1.4661 | 284.1633 | 3074.694 | -0.0051592
126 |  | 1.6475 | 24.2696 | 4187 | 0.0035184 | 6.4457 | 6.4493 | -1.4661 | 284.2238 | 3098.9637 | -0.0051581
127 |  | 1.6475 | 24.2645 | 4187 | 0.0035176 | 6.4493 | 6.4528 | -1.4661 | 284.2842 | 3123.2281 | -0.005157
128 |  | 1.6475 | 24.2593 | 4187 | 0.0035169 | 6.4528 | 6.4563 | -1.4661 | 284.3446 | 3147.4875 | -0.0051559
129 |  | 1.6475 | 24.2542 | 4187 | 0.0035161 | 6.4563 | 6.4598 | -1.4661 | 284.4051 | 3171.7417 | -0.0051549
130 |  | 1.6475 | 24.249 | 4187 | 0.0035154 | 6.4598 | 6.4633 | -1.4661 | 284.4655 | 3195.9907 | -0.0051538
131 |  | 1.6475 | 24.2439 | 4187 | 0.0035146 | 6.4633 | 6.4668 | -1.4661 | 284.526 | 3220.2345 | -0.0051527
132 |  | 1.6475 | 24.2387 | 4187 | 0.0035139 | 6.4668 | 6.4703 | -1.4661 | 284.5865 | 3244.4732 | -0.0051516
133 |  | 1.6475 | 24.2336 | 4187 | 0.0035131 | 6.4703 | 6.4739 | -1.4661 | 284.647 | 3268.7068 | -0.0051505
134 |  | 1.6475 | 24.2284 | 4187 | 0.0035124 | 6.4739 | 6.4774 | -1.4661 | 284.7075 | 3292.9352 | -0.0051494
135 |  | 1.6475 | 24.2233 | 4187 | 0.0035116 | 6.4774 | 6.4809 | -1.4661 | 284.768 | 3317.1585 | -0.0051483
136 |  | 1.6475 | 24.2181 | 4187 | 0.0035109 | 6.4809 | 6.4844 | -1.4661 | 284.8285 | 3341.3766 | -0.0051472
137 |  | 1.6475 | 24.213 | 4187 | 0.0035101 | 6.4844 | 6.4879 | -1.4661 | 284.8891 | 3365.5896 | -0.0051461
138 |  | 1.6475 | 24.2078 | 4187 | 0.0035094 | 6.4879 | 6.4914 | -1.4661 | 284.9496 | 3389.7974 | -0.005145
139 |  | 1.6475 | 24.2027 | 4187 | 0.0035086 | 6.4914 | 6.4949 | -1.4661 | 285.0102 | 3414.0001 | -0.0051439
140 |  | 1.6475 | 24.1975 | 4187 | 0.0035079 | 6.4949 | 6.4984 | -1.4661 | 285.0708 | 3438.1976 | -0.0051428
141 |  | 1.6475 | 24.1924 | 4187 | 0.0035072 | 6.4984 | 6.5019 | -1.4661 | 285.1314 | 3462.39 | -0.0051417
142 |  | 1.6475 | 24.1872 | 4187 | 0.0035064 | 6.5019 | 6.5054 | -1.4661 | 285.192 | 3486.5772 | -0.0051406
143 |  | 1.6475 | 24.1821 | 4187 | 0.0035057 | 6.5054 | 6.509 | -1.4661 | 285.2526 | 3510.7593 | -0.0051395
144 |  | 1.6475 | 24.177 | 4187 | 0.0035049 | 6.509 | 6.5125 | -1.4661 | 285.3133 | 3534.9363 | -0.0051384
145 |  | 1.6475 | 24.1718 | 4187 | 0.0035042 | 6.5125 | 6.516 | -1.4661 | 285.3739 | 3559.1081 | -0.0051374
146 |  | 1.6475 | 24.1667 | 4187 | 0.0035034 | 6.516 | 6.5195 | -1.4661 | 285.4346 | 3583.2748 | -0.0051363
147 |  | 1.6475 | 24.1616 | 4187 | 0.0035027 | 6.5195 | 6.523 | -1.4661 | 285.4953 | 3607.4364 | -0.0051352
148 |  | 1.6475 | 24.1564 | 4187 | 0.0035019 | 6.523 | 6.5265 | -1.4661 | 285.556 | 3631.5928 | -0.0051341
149 |  | 1.6475 | 24.1513 | 4187 | 0.0035012 | 6.5265 | 6.53 | -1.4661 | 285.6167 | 3655.7441 | -0.005133
150 |  | 1.6475 | 24.1462 | 4187 | 0.0035005 | 6.53 | 6.5335 | -1.4661 | 285.6774 | 3679.8902 | -0.0051319
151 |  | 1.6475 | 24.141 | 4187 | 0.0034997 | 6.5335 | 6.537 | -1.4661 | 285.7381 | 3704.0312 | -0.0051308
152 |  | 1.6475 | 24.1359 | 4187 | 0.003499 | 6.537 | 6.5405 | -1.4661 | 285.7989 | 3728.1671 | -0.0051297
153 |  | 1.6475 | 24.1308 | 4187 | 0.0034982 | 6.5405 | 6.544 | -1.4661 | 285.8596 | 3752.2979 | -0.0051286
154 |  | 1.6475 | 24.1256 | 4187 | 0.0034975 | 6.544 | 6.5475 | -1.4661 | 285.9204 | 3776.4235 | -0.0051275
155 |  | 1.6475 | 24.1205 | 4187 | 0.0034967 | 6.5475 | 6.551 | -1.4661 | 285.9812 | 3800.544 | -0.0051264
156 |  | 1.6475 | 24.1154 | 4187 | 0.003496 | 6.551 | 6.5545 | -1.4661 | 286.042 | 3824.6594 | -0.0051254
157 |  | 1.6475 | 24.1103 | 4187 | 0.0034952 | 6.5545 | 6.558 | -1.4661 | 286.1028 | 3848.7697 | -0.0051243
158 |  | 1.6475 | 24.1051 | 4187 | 0.0034945 | 6.558 | 6.5614 | -1.4661 | 286.1636 | 3872.8748 | -0.0051232
159 |  | 1.6475 | 24.1 | 4187 | 0.0034938 | 6.5614 | 6.5649 | -1.4661 | 286.2244 | 3896.9748 | -0.0051221
160 |  | 1.6475 | 24.0949 | 4187 | 0.003493 | 6.5649 | 6.5684 | -1.4661 | 286.2853 | 3921.0697 | -0.005121
161 |  | 1.6475 | 24.0898 | 4187 | 0.0034923 | 6.5684 | 6.5719 | -1.4661 | 286.3461 | 3945.1594 | -0.0051199
162 |  | 1.6475 | 24.0846 | 4187 | 0.0034915 | 6.5719 | 6.5754 | -1.4661 | 286.407 | 3969.2441 | -0.0051188
163 |  | 1.6475 | 24.0795 | 4187 | 0.0034908 | 6.5754 | 6.5789 | -1.4661 | 286.4679 | 3993.3236 | -0.0051177
164 |  | 1.6475 | 24.0744 | 4187 | 0.0034901 | 6.5789 | 6.5824 | -1.4661 | 286.5288 | 4017.398 | -0.0051166
165 |  | 1.6475 | 24.0693 | 4187 | 0.0034893 | 6.5824 | 6.5859 | -1.4661 | 286.5897 | 4041.4673 | -0.0051156
166 |  | 1.6475 | 24.0642 | 4187 | 0.0034886 | 6.5859 | 6.5894 | -1.4661 | 286.6506 | 4065.5315 | -0.0051145
167 |  | 1.6475 | 24.0591 | 4187 | 0.0034878 | 6.5894 | 6.5929 | -1.4661 | 286.7115 | 4089.5905 | -0.0051134
168 |  | 1.6475 | 24.0539 | 4187 | 0.0034871 | 6.5929 | 6.5964 | -1.4661 | 286.7725 | 4113.6445 | -0.0051123
169 |  | 1.6475 | 24.0488 | 4187 | 0.0034863 | 6.5964 | 6.5998 | -1.4661 | 286.8335 | 4137.6933 | -0.0051112
170 |  | 1.6475 | 24.0437 | 4187 | 0.0034856 | 6.5998 | 6.6033 | -1.4661 | 286.8944 | 4161.737 | -0.0051101
171 |  | 1.6475 | 24.0386 | 4187 | 0.0034849 | 6.6033 | 6.6068 | -1.4661 | 286.9554 | 4185.7756 | -0.005109
172 |  | 1.6475 | 24.0335 | 4187 | 0.0034841 | 6.6068 | 6.6103 | -1.4661 | 287.0164 | 4209.8091 | -0.005108
173 |  | 1.6475 | 24.0284 | 4187 | 0.0034834 | 6.6103 | 6.6138 | -1.4661 | 287.0774 | 4233.8375 | -0.0051069
174 |  | 1.6475 | 24.0233 | 4187 | 0.0034826 | 6.6138 | 6.6173 | -1.4661 | 287.1385 | 4257.8608 | -0.0051058
175 |  | 1.6475 | 24.0182 | 4187 | 0.0034819 | 6.6173 | 6.6207 | -1.4661 | 287.1995 | 4281.879 | -0.0051047
176 |  | 1.6475 | 24.0131 | 4187 | 0.0034812 | 6.6207 | 6.6242 | -1.4661 | 287.2606 | 4305.8921 | -0.0051036
177 |  | 1.6475 | 24.008 | 4187 | 0.0034804 | 6.6242 | 6.6277 | -1.4661 | 287.3216 | 4329.9 | -0.0051025
178 |  | 1.6475 | 24.0029 | 4187 | 0.0034797 | 6.6277 | 6.6312 | -1.4661 | 287.3827 | 4353.9029 | -0.0051014
179 |  | 1.6475 | 23.9978 | 4187 | 0.0034789 | 6.6312 | 6.6347 | -1.4661 | 287.4438 | 4377.9007 | -0.0051004
180 |  | 1.6475 | 23.9927 | 4187 | 0.0034782 | 6.6347 | 6.6381 | -1.4661 | 287.5049 | 4401.8934 | -0.0050993
181 |  | 1.6475 | 23.9876 | 4187 | 0.0034775 | 6.6381 | 6.6416 | -1.4661 | 287.566 | 4425.8809 | -0.0050982
182 |  | 1.6475 | 23.9825 | 4187 | 0.0034767 | 6.6416 | 6.6451 | -1.4661 | 287.6271 | 4449.8634 | -0.0050971
183 |  | 1.6475 | 23.9774 | 4187 | 0.003476 | 6.6451 | 6.6486 | -1.4661 | 287.6883 | 4473.8408 | -0.005096
184 |  | 1.6475 | 23.9723 | 4187 | 0.0034752 | 6.6486 | 6.652 | -1.4661 | 287.7494 | 4497.813 | -0.0050949
185 |  | 1.6475 | 23.9672 | 4187 | 0.0034745 | 6.652 | 6.6555 | -1.4661 | 287.8106 | 4521.7802 | -0.0050939
186 |  | 1.6475 | 23.9621 | 4187 | 0.0034738 | 6.6555 | 6.659 | -1.4661 | 287.8718 | 4545.7423 | -0.0050928
187 |  | 1.6475 | 23.957 | 4187 | 0.003473 | 6.659 | 6.6625 | -1.4661 | 287.933 | 4569.6993 | -0.0050917
188 |  | 1.6475 | 23.9519 | 4187 | 0.0034723 | 6.6625 | 6.6659 | -1.4661 | 287.9942 | 4593.6512 | -0.0050906
189 |  | 1.6475 | 23.9468 | 4187 | 0.0034716 | 6.6659 | 6.6694 | -1.4661 | 288.0554 | 4617.598 | -0.0050895
190 |  | 1.6475 | 23.9417 | 4187 | 0.0034708 | 6.6694 | 6.6729 | -1.4661 | 288.1167 | 4641.5398 | -0.0050884
191 |  | 1.6475 | 23.9366 | 4187 | 0.0034701 | 6.6729 | 6.6764 | -1.4661 | 288.1779 | 4665.4764 | -0.0050874
192 |  | 1.6475 | 23.9315 | 4187 | 0.0034693 | 6.6764 | 6.6798 | -1.4661 | 288.2392 | 4689.4079 | -0.0050863
193 |  | 1.6475 | 23.9265 | 4187 | 0.0034686 | 6.6798 | 6.6833 | -1.4661 | 288.3004 | 4713.3344 | -0.0050852
194 |  | 1.6475 | 23.9214 | 4187 | 0.0034679 | 6.6833 | 6.6868 | -1.4661 | 288.3617 | 4737.2558 | -0.0050841
195 |  | 1.6475 | 23.9163 | 4187 | 0.0034671 | 6.6868 | 6.6902 | -1.4661 | 288.423 | 4761.1721 | -0.005083
196 |  | 1.6475 | 23.9112 | 4187 | 0.0034664 | 6.6902 | 6.6937 | -1.4661 | 288.4843 | 4785.0833 | -0.005082
197 |  | 1.6475 | 23.9061 | 4187 | 0.0034657 | 6.6937 | 6.6972 | -1.4661 | 288.5457 | 4808.9894 | -0.0050809
198 |  | 1.6475 | 23.901 | 4187 | 0.0034649 | 6.6972 | 6.7006 | -1.4661 | 288.607 | 4832.8905 | -0.0050798
199 |  | 1.6475 | 23.896 | 4187 | 0.0034642 | 6.7006 | 6.7041 | -1.4661 | 288.6684 | 4856.7864 | -0.0050787
200 |  | 1.6475 | 23.8909 | 4187 | 0.0034634 | 6.7041 | 6.7075 | -1.4661 | 288.7297 | 4880.6773 | -0.0050776
201 |  | 1.6475 | 23.8858 | 4187 | 0.0034627 | 6.7075 | 6.711 | -1.4661 | 288.7911 | 4904.5631 | -0.0050766
202 |  | 1.6475 | 23.8807 | 4187 | 0.003462 | 6.711 | 6.7145 | -1.4661 | 288.8525 | 4928.4439 | -0.0050755
203 |  | 1.6475 | 23.8757 | 4187 | 0.0034612 | 6.7145 | 6.7179 | -1.4661 | 288.9139 | 4952.3195 | -0.0050744
204 |  | 1.6475 | 23.8706 | 4187 | 0.0034605 | 6.7179 | 6.7214 | -1.4661 | 288.9753 | 4976.1901 | -0.0050733
205 |  | 1.6475 | 23.8655 | 4187 | 0.0034598 | 6.7214 | 6.7249 | -1.4661 | 289.0367 | 5000.0556 | -0.0050722
206 |  | 1.6475 | 23.8604 | 4187 | 0.003459 | 6.7249 | 6.7283 | -1.4661 | 289.0982 | 5023.9161 | -0.0050712
207 |  | 1.6475 | 23.8554 | 4187 | 0.0034583 | 6.7283 | 6.7318 | -1.4661 | 289.1596 | 5047.7714 | -0.0050701
208 |  | 1.6475 | 23.8503 | 4187 | 0.0034576 | 6.7318 | 6.7352 | -1.4661 | 289.2211 | 5071.6217 | -0.005069
209 |  | 1.6475 | 23.8452 | 4187 | 0.0034568 | 6.7352 | 6.7387 | -1.4661 | 289.2826 | 5095.467 | -0.0050679
210 |  | 1.6475 | 23.8402 | 4187 | 0.0034561 | 6.7387 | 6.7421 | -1.4661 | 289.3441 | 5119.3071 | -0.0050669
211 |  | 1.6475 | 23.8351 | 4187 | 0.0034554 | 6.7421 | 6.7456 | -1.4661 | 289.4056 | 5143.1422 | -0.0050658
212 |  | 1.6475 | 23.83 | 4187 | 0.0034546 | 6.7456 | 6.7491 | -1.4661 | 289.4671 | 5166.9722 | -0.0050647
213 |  | 1.6475 | 23.825 | 4187 | 0.0034539 | 6.7491 | 6.7525 | -1.4661 | 289.5287 | 5190.7972 | -0.0050636
214 |  | 1.6475 | 23.8199 | 4187 | 0.0034532 | 6.7525 | 6.756 | -1.4661 | 289.5902 | 5214.6171 | -0.0050626
215 |  | 1.6475 | 23.8148 | 4187 | 0.0034524 | 6.756 | 6.7594 | -1.4661 | 289.6518 | 5238.4319 | -0.0050615
216 |  | 1.6475 | 23.8098 | 4187 | 0.0034517 | 6.7594 | 6.7629 | -1.4661 | 289.7133 | 5262.2417 | -0.0050604
217 |  | 1.6475 | 23.8047 | 4187 | 0.003451 | 6.7629 | 6.7663 | -1.4661 | 289.7749 | 5286.0464 | -0.0050593
218 |  | 1.6475 | 23.7997 | 4187 | 0.0034502 | 6.7663 | 6.7698 | -1.4661 | 289.8365 | 5309.8461 | -0.0050583
219 |  | 1.6475 | 23.7946 | 4187 | 0.0034495 | 6.7698 | 6.7732 | -1.4661 | 289.8981 | 5333.6407 | -0.0050572
220 |  | 1.6475 | 23.7895 | 4187 | 0.0034488 | 6.7732 | 6.7767 | -1.4661 | 289.9598 | 5357.4302 | -0.0050561
221 |  | 1.6475 | 23.7845 | 4187 | 0.003448 | 6.7767 | 6.7801 | -1.4661 | 290.0214 | 5381.2147 | -0.005055
222 |  | 1.6475 | 23.7794 | 4187 | 0.0034473 | 6.7801 | 6.7836 | -1.4661 | 290.0831 | 5404.9941 | -0.005054
223 |  | 1.6475 | 23.7744 | 4187 | 0.0034466 | 6.7836 | 6.787 | -1.4661 | 290.1447 | 5428.7685 | -0.0050529
224 |  | 1.6475 | 23.7693 | 4187 | 0.0034458 | 6.787 | 6.7905 | -1.4661 | 290.2064 | 5452.5378 | -0.0050518
225 |  | 1.6475 | 23.7643 | 4187 | 0.0034451 | 6.7905 | 6.7939 | -1.4661 | 290.2681 | 5476.3021 | -0.0050507
226 |  | 1.6475 | 23.7592 | 4187 | 0.0034444 | 6.7939 | 6.7973 | -1.4661 | 290.3298 | 5500.0613 | -0.0050497
227 |  | 1.6475 | 23.7542 | 4187 | 0.0034436 | 6.7973 | 6.8008 | -1.4661 | 290.3915 | 5523.8155 | -0.0050486
228 |  | 1.6475 | 23.7491 | 4187 | 0.0034429 | 6.8008 | 6.8042 | -1.4661 | 290.4532 | 5547.5646 | -0.0050475
229 |  | 1.6475 | 23.7441 | 4187 | 0.0034422 | 6.8042 | 6.8077 | -1.4661 | 290.515 | 5571.3087 | -0.0050464
230 |  | 1.6475 | 23.739 | 4187 | 0.0034414 | 6.8077 | 6.8111 | -1.4661 | 290.5767 | 5595.0477 | -0.0050454
231 |  | 1.6475 | 23.734 | 4187 | 0.0034407 | 6.8111 | 6.8146 | -1.4661 | 290.6385 | 5618.7817 | -0.0050443
232 |  | 1.6475 | 23.7289 | 4187 | 0.00344 | 6.8146 | 6.818 | -1.4661 | 290.7003 | 5642.5107 | -0.0050432
233 |  | 1.6475 | 23.7239 | 4187 | 0.0034392 | 6.818 | 6.8214 | -1.4661 | 290.7621 | 5666.2346 | -0.0050422
234 |  | 1.6475 | 23.7189 | 4187 | 0.0034385 | 6.8214 | 6.8249 | -1.4661 | 290.8239 | 5689.9534 | -0.0050411
235 |  | 1.6475 | 23.7138 | 4187 | 0.0034378 | 6.8249 | 6.8283 | -1.4661 | 290.8857 | 5713.6672 | -0.00504
236 |  | 1.6475 | 23.7088 | 4187 | 0.003437 | 6.8283 | 6.8317 | -1.4661 | 290.9476 | 5737.376 | -0.0050389

## Fus75
|  |  | buis | verlies W/M | L /°C/sec
diam | wandikte |  | inhoud l/m |  | W/M
75 | 10.3 | 3.1416 | 2.3243 | 27.0048 | 4187
[8 empty] | J/sec/mtr | aantal mtr. | verlies
|  | buis | verlies W/M | L /°C/sec | verlies temp | begintemp | eindtemp | verlies | bij 1°C | totaal J/sec
|  | inhoud L |  | W/M | °C per M | °C | °C | per m°C | daling | aantal mtr
1 | 75 | 2.3243 | 27.0048 | 4187 | 0.0027749 | 6 | 6.0028 | -1.5885 | 360.3705 | 27.0048 | -0.004408
2 |  | 2.3243 | 27.0004 | 4187 | 0.0027745 | 6.0028 | 6.0055 | -1.5885 | 360.4293 | 54.0052 | -0.0044073
3 |  | 2.3243 | 26.996 | 4187 | 0.002774 | 6.0055 | 6.0083 | -1.5885 | 360.4882 | 81.0013 | -0.0044066
4 |  | 2.3243 | 26.9916 | 4187 | 0.0027736 | 6.0083 | 6.0111 | -1.5885 | 360.547 | 107.9929 | -0.0044059
5 |  | 2.3243 | 26.9872 | 4187 | 0.0027731 | 6.0111 | 6.0139 | -1.5885 | 360.6059 | 134.9801 | -0.0044051
6 |  | 2.3243 | 26.9828 | 4187 | 0.0027727 | 6.0139 | 6.0166 | -1.5885 | 360.6647 | 161.9629 | -0.0044044
7 |  | 2.3243 | 26.9784 | 4187 | 0.0027722 | 6.0166 | 6.0194 | -1.5885 | 360.7236 | 188.9413 | -0.0044037
8 |  | 2.3243 | 26.974 | 4187 | 0.0027718 | 6.0194 | 6.0222 | -1.5885 | 360.7825 | 215.9152 | -0.004403
9 |  | 2.3243 | 26.9696 | 4187 | 0.0027713 | 6.0222 | 6.025 | -1.5885 | 360.8414 | 242.8848 | -0.0044023
10 |  | 2.3243 | 26.9652 | 4187 | 0.0027708 | 6.025 | 6.0277 | -1.5885 | 360.9003 | 269.85 | -0.0044015
11 |  | 2.3243 | 26.9608 | 4187 | 0.0027704 | 6.0277 | 6.0305 | -1.5885 | 360.9592 | 296.8108 | -0.0044008
12 |  | 2.3243 | 26.9564 | 4187 | 0.0027699 | 6.0305 | 6.0333 | -1.5885 | 361.0182 | 323.7672 | -0.0044001
13 |  | 2.3243 | 26.952 | 4187 | 0.0027695 | 6.0333 | 6.036 | -1.5885 | 361.0771 | 350.7192 | -0.0043994
14 |  | 2.3243 | 26.9476 | 4187 | 0.002769 | 6.036 | 6.0388 | -1.5885 | 361.1361 | 377.6667 | -0.0043987
15 |  | 2.3243 | 26.9432 | 4187 | 0.0027686 | 6.0388 | 6.0416 | -1.5885 | 361.195 | 404.6099 | -0.004398
16 |  | 2.3243 | 26.9388 | 4187 | 0.0027681 | 6.0416 | 6.0443 | -1.5885 | 361.254 | 431.5487 | -0.0043972
17 |  | 2.3243 | 26.9344 | 4187 | 0.0027677 | 6.0443 | 6.0471 | -1.5885 | 361.313 | 458.4831 | -0.0043965
18 |  | 2.3243 | 26.93 | 4187 | 0.0027672 | 6.0471 | 6.0499 | -1.5885 | 361.372 | 485.4131 | -0.0043958
19 |  | 2.3243 | 26.9256 | 4187 | 0.0027668 | 6.0499 | 6.0526 | -1.5885 | 361.4309 | 512.3387 | -0.0043951
20 |  | 2.3243 | 26.9212 | 4187 | 0.0027663 | 6.0526 | 6.0554 | -1.5885 | 361.49 | 539.2599 | -0.0043944
21 |  | 2.3243 | 26.9168 | 4187 | 0.0027659 | 6.0554 | 6.0582 | -1.5885 | 361.549 | 566.1767 | -0.0043936
22 |  | 2.3243 | 26.9124 | 4187 | 0.0027654 | 6.0582 | 6.0609 | -1.5885 | 361.608 | 593.0891 | -0.0043929
23 |  | 2.3243 | 26.908 | 4187 | 0.002765 | 6.0609 | 6.0637 | -1.5885 | 361.667 | 619.9971 | -0.0043922
24 |  | 2.3243 | 26.9036 | 4187 | 0.0027645 | 6.0637 | 6.0665 | -1.5885 | 361.7261 | 646.9007 | -0.0043915
25 |  | 2.3243 | 26.8992 | 4187 | 0.0027641 | 6.0665 | 6.0692 | -1.5885 | 361.7851 | 673.8 | -0.0043908
26 |  | 2.3243 | 26.8948 | 4187 | 0.0027636 | 6.0692 | 6.072 | -1.5885 | 361.8442 | 700.6948 | -0.0043901
27 |  | 2.3243 | 26.8905 | 4187 | 0.0027632 | 6.072 | 6.0748 | -1.5885 | 361.9033 | 727.5853 | -0.0043893
28 |  | 2.3243 | 26.8861 | 4187 | 0.0027627 | 6.0748 | 6.0775 | -1.5885 | 361.9624 | 754.4713 | -0.0043886
29 |  | 2.3243 | 26.8817 | 4187 | 0.0027623 | 6.0775 | 6.0803 | -1.5885 | 362.0214 | 781.353 | -0.0043879
30 |  | 2.3243 | 26.8773 | 4187 | 0.0027618 | 6.0803 | 6.0831 | -1.5885 | 362.0805 | 808.2303 | -0.0043872
31 |  | 2.3243 | 26.8729 | 4187 | 0.0027614 | 6.0831 | 6.0858 | -1.5885 | 362.1397 | 835.1032 | -0.0043865
32 |  | 2.3243 | 26.8685 | 4187 | 0.0027609 | 6.0858 | 6.0886 | -1.5885 | 362.1988 | 861.9717 | -0.0043858
33 |  | 2.3243 | 26.8641 | 4187 | 0.0027605 | 6.0886 | 6.0913 | -1.5885 | 362.2579 | 888.8358 | -0.0043851
34 |  | 2.3243 | 26.8597 | 4187 | 0.00276 | 6.0913 | 6.0941 | -1.5885 | 362.3171 | 915.6956 | -0.0043843
35 |  | 2.3243 | 26.8554 | 4187 | 0.0027596 | 6.0941 | 6.0969 | -1.5885 | 362.3762 | 942.5509 | -0.0043836
36 |  | 2.3243 | 26.851 | 4187 | 0.0027591 | 6.0969 | 6.0996 | -1.5885 | 362.4354 | 969.4019 | -0.0043829
37 |  | 2.3243 | 26.8466 | 4187 | 0.0027587 | 6.0996 | 6.1024 | -1.5885 | 362.4945 | 996.2485 | -0.0043822
38 |  | 2.3243 | 26.8422 | 4187 | 0.0027582 | 6.1024 | 6.1051 | -1.5885 | 362.5537 | 1023.0907 | -0.0043815
39 |  | 2.3243 | 26.8378 | 4187 | 0.0027578 | 6.1051 | 6.1079 | -1.5885 | 362.6129 | 1049.9286 | -0.0043808
40 |  | 2.3243 | 26.8334 | 4187 | 0.0027573 | 6.1079 | 6.1106 | -1.5885 | 362.6721 | 1076.762 | -0.00438
41 |  | 2.3243 | 26.8291 | 4187 | 0.0027569 | 6.1106 | 6.1134 | -1.5885 | 362.7313 | 1103.5911 | -0.0043793
42 |  | 2.3243 | 26.8247 | 4187 | 0.0027564 | 6.1134 | 6.1162 | -1.5885 | 362.7905 | 1130.4158 | -0.0043786
43 |  | 2.3243 | 26.8203 | 4187 | 0.002756 | 6.1162 | 6.1189 | -1.5885 | 362.8498 | 1157.2361 | -0.0043779
44 |  | 2.3243 | 26.8159 | 4187 | 0.0027555 | 6.1189 | 6.1217 | -1.5885 | 362.909 | 1184.052 | -0.0043772
45 |  | 2.3243 | 26.8116 | 4187 | 0.0027551 | 6.1217 | 6.1244 | -1.5885 | 362.9682 | 1210.8636 | -0.0043765
46 |  | 2.3243 | 26.8072 | 4187 | 0.0027546 | 6.1244 | 6.1272 | -1.5885 | 363.0275 | 1237.6707 | -0.0043758
47 |  | 2.3243 | 26.8028 | 4187 | 0.0027542 | 6.1272 | 6.1299 | -1.5885 | 363.0868 | 1264.4735 | -0.004375
48 |  | 2.3243 | 26.7984 | 4187 | 0.0027537 | 6.1299 | 6.1327 | -1.5885 | 363.146 | 1291.272 | -0.0043743
49 |  | 2.3243 | 26.7941 | 4187 | 0.0027533 | 6.1327 | 6.1354 | -1.5885 | 363.2053 | 1318.066 | -0.0043736
50 |  | 2.3243 | 26.7897 | 4187 | 0.0027528 | 6.1354 | 6.1382 | -1.5885 | 363.2646 | 1344.8557 | -0.0043729
51 |  | 2.3243 | 26.7853 | 4187 | 0.0027524 | 6.1382 | 6.1409 | -1.5885 | 363.3239 | 1371.641 | -0.0043722
52 |  | 2.3243 | 26.7809 | 4187 | 0.0027519 | 6.1409 | 6.1437 | -1.5885 | 363.3833 | 1398.4219 | -0.0043715
53 |  | 2.3243 | 26.7766 | 4187 | 0.0027515 | 6.1437 | 6.1464 | -1.5885 | 363.4426 | 1425.1985 | -0.0043708
54 |  | 2.3243 | 26.7722 | 4187 | 0.002751 | 6.1464 | 6.1492 | -1.5885 | 363.5019 | 1451.9707 | -0.00437
55 |  | 2.3243 | 26.7678 | 4187 | 0.0027506 | 6.1492 | 6.152 | -1.5885 | 363.5613 | 1478.7385 | -0.0043693
56 |  | 2.3243 | 26.7635 | 4187 | 0.0027501 | 6.152 | 6.1547 | -1.5885 | 363.6206 | 1505.502 | -0.0043686
57 |  | 2.3243 | 26.7591 | 4187 | 0.0027497 | 6.1547 | 6.1574 | -1.5885 | 363.68 | 1532.2611 | -0.0043679
58 |  | 2.3243 | 26.7547 | 4187 | 0.0027492 | 6.1574 | 6.1602 | -1.5885 | 363.7393 | 1559.0158 | -0.0043672
59 |  | 2.3243 | 26.7503 | 4187 | 0.0027488 | 6.1602 | 6.1629 | -1.5885 | 363.7987 | 1585.7661 | -0.0043665
60 |  | 2.3243 | 26.746 | 4187 | 0.0027483 | 6.1629 | 6.1657 | -1.5885 | 363.8581 | 1612.5121 | -0.0043658
61 |  | 2.3243 | 26.7416 | 4187 | 0.0027479 | 6.1657 | 6.1684 | -1.5885 | 363.9175 | 1639.2537 | -0.0043651
62 |  | 2.3243 | 26.7373 | 4187 | 0.0027474 | 6.1684 | 6.1712 | -1.5885 | 363.9769 | 1665.991 | -0.0043643
63 |  | 2.3243 | 26.7329 | 4187 | 0.002747 | 6.1712 | 6.1739 | -1.5885 | 364.0364 | 1692.7239 | -0.0043636
64 |  | 2.3243 | 26.7285 | 4187 | 0.0027465 | 6.1739 | 6.1767 | -1.5885 | 364.0958 | 1719.4524 | -0.0043629
65 |  | 2.3243 | 26.7242 | 4187 | 0.0027461 | 6.1767 | 6.1794 | -1.5885 | 364.1552 | 1746.1766 | -0.0043622
66 |  | 2.3243 | 26.7198 | 4187 | 0.0027456 | 6.1794 | 6.1822 | -1.5885 | 364.2147 | 1772.8964 | -0.0043615
67 |  | 2.3243 | 26.7154 | 4187 | 0.0027452 | 6.1822 | 6.1849 | -1.5885 | 364.2741 | 1799.6118 | -0.0043608
68 |  | 2.3243 | 26.7111 | 4187 | 0.0027447 | 6.1849 | 6.1877 | -1.5885 | 364.3336 | 1826.3229 | -0.0043601
69 |  | 2.3243 | 26.7067 | 4187 | 0.0027443 | 6.1877 | 6.1904 | -1.5885 | 364.3931 | 1853.0296 | -0.0043594
70 |  | 2.3243 | 26.7024 | 4187 | 0.0027438 | 6.1904 | 6.1932 | -1.5885 | 364.4526 | 1879.7319 | -0.0043586
71 |  | 2.3243 | 26.698 | 4187 | 0.0027434 | 6.1932 | 6.1959 | -1.5885 | 364.5121 | 1906.4299 | -0.0043579
72 |  | 2.3243 | 26.6936 | 4187 | 0.0027429 | 6.1959 | 6.1986 | -1.5885 | 364.5716 | 1933.1236 | -0.0043572
73 |  | 2.3243 | 26.6893 | 4187 | 0.0027425 | 6.1986 | 6.2014 | -1.5885 | 364.6311 | 1959.8129 | -0.0043565
74 |  | 2.3243 | 26.6849 | 4187 | 0.0027421 | 6.2014 | 6.2041 | -1.5885 | 364.6906 | 1986.4978 | -0.0043558
75 |  | 2.3243 | 26.6806 | 4187 | 0.0027416 | 6.2041 | 6.2069 | -1.5885 | 364.7502 | 2013.1784 | -0.0043551
76 |  | 2.3243 | 26.6762 | 4187 | 0.0027412 | 6.2069 | 6.2096 | -1.5885 | 364.8097 | 2039.8546 | -0.0043544
77 |  | 2.3243 | 26.6719 | 4187 | 0.0027407 | 6.2096 | 6.2123 | -1.5885 | 364.8693 | 2066.5264 | -0.0043537
78 |  | 2.3243 | 26.6675 | 4187 | 0.0027403 | 6.2123 | 6.2151 | -1.5885 | 364.9289 | 2093.194 | -0.004353
79 |  | 2.3243 | 26.6632 | 4187 | 0.0027398 | 6.2151 | 6.2178 | -1.5885 | 364.9884 | 2119.8571 | -0.0043522
80 |  | 2.3243 | 26.6588 | 4187 | 0.0027394 | 6.2178 | 6.2206 | -1.5885 | 365.048 | 2146.5159 | -0.0043515
81 |  | 2.3243 | 26.6545 | 4187 | 0.0027389 | 6.2206 | 6.2233 | -1.5885 | 365.1076 | 2173.1704 | -0.0043508
82 |  | 2.3243 | 26.6501 | 4187 | 0.0027385 | 6.2233 | 6.226 | -1.5885 | 365.1672 | 2199.8205 | -0.0043501
83 |  | 2.3243 | 26.6458 | 4187 | 0.002738 | 6.226 | 6.2288 | -1.5885 | 365.2268 | 2226.4662 | -0.0043494
84 |  | 2.3243 | 26.6414 | 4187 | 0.0027376 | 6.2288 | 6.2315 | -1.5885 | 365.2865 | 2253.1076 | -0.0043487
85 |  | 2.3243 | 26.6371 | 4187 | 0.0027371 | 6.2315 | 6.2343 | -1.5885 | 365.3461 | 2279.7447 | -0.004348
86 |  | 2.3243 | 26.6327 | 4187 | 0.0027367 | 6.2343 | 6.237 | -1.5885 | 365.4057 | 2306.3774 | -0.0043473
87 |  | 2.3243 | 26.6284 | 4187 | 0.0027362 | 6.237 | 6.2397 | -1.5885 | 365.4654 | 2333.0057 | -0.0043466
88 |  | 2.3243 | 26.624 | 4187 | 0.0027358 | 6.2397 | 6.2425 | -1.5885 | 365.5251 | 2359.6297 | -0.0043459
89 |  | 2.3243 | 26.6197 | 4187 | 0.0027353 | 6.2425 | 6.2452 | -1.5885 | 365.5847 | 2386.2494 | -0.0043451
90 |  | 2.3243 | 26.6153 | 4187 | 0.0027349 | 6.2452 | 6.2479 | -1.5885 | 365.6444 | 2412.8647 | -0.0043444
91 |  | 2.3243 | 26.611 | 4187 | 0.0027345 | 6.2479 | 6.2507 | -1.5885 | 365.7041 | 2439.4757 | -0.0043437
92 |  | 2.3243 | 26.6066 | 4187 | 0.002734 | 6.2507 | 6.2534 | -1.5885 | 365.7638 | 2466.0823 | -0.004343
93 |  | 2.3243 | 26.6023 | 4187 | 0.0027336 | 6.2534 | 6.2561 | -1.5885 | 365.8235 | 2492.6846 | -0.0043423
94 |  | 2.3243 | 26.5979 | 4187 | 0.0027331 | 6.2561 | 6.2589 | -1.5885 | 365.8833 | 2519.2826 | -0.0043416
95 |  | 2.3243 | 26.5936 | 4187 | 0.0027327 | 6.2589 | 6.2616 | -1.5885 | 365.943 | 2545.8762 | -0.0043409
96 |  | 2.3243 | 26.5893 | 4187 | 0.0027322 | 6.2616 | 6.2643 | -1.5885 | 366.0027 | 2572.4654 | -0.0043402
97 |  | 2.3243 | 26.5849 | 4187 | 0.0027318 | 6.2643 | 6.2671 | -1.5885 | 366.0625 | 2599.0504 | -0.0043395
98 |  | 2.3243 | 26.5806 | 4187 | 0.0027313 | 6.2671 | 6.2698 | -1.5885 | 366.1222 | 2625.6309 | -0.0043388
99 |  | 2.3243 | 26.5762 | 4187 | 0.0027309 | 6.2698 | 6.2725 | -1.5885 | 366.182 | 2652.2072 | -0.0043381
100 |  | 2.3243 | 26.5719 | 4187 | 0.0027304 | 6.2725 | 6.2753 | -1.5885 | 366.2418 | 2678.7791 | -0.0043374
101 |  | 2.3243 | 26.5676 | 4187 | 0.00273 | 6.2753 | 6.278 | -1.5885 | 366.3016 | 2705.3467 | -0.0043366
102 |  | 2.3243 | 26.5632 | 4187 | 0.0027295 | 6.278 | 6.2807 | -1.5885 | 366.3614 | 2731.9099 | -0.0043359
103 |  | 2.3243 | 26.5589 | 4187 | 0.0027291 | 6.2807 | 6.2835 | -1.5885 | 366.4212 | 2758.4688 | -0.0043352
104 |  | 2.3243 | 26.5546 | 4187 | 0.0027287 | 6.2835 | 6.2862 | -1.5885 | 366.481 | 2785.0234 | -0.0043345
105 |  | 2.3243 | 26.5502 | 4187 | 0.0027282 | 6.2862 | 6.2889 | -1.5885 | 366.5409 | 2811.5736 | -0.0043338
106 |  | 2.3243 | 26.5459 | 4187 | 0.0027278 | 6.2889 | 6.2916 | -1.5885 | 366.6007 | 2838.1195 | -0.0043331
107 |  | 2.3243 | 26.5416 | 4187 | 0.0027273 | 6.2916 | 6.2944 | -1.5885 | 366.6605 | 2864.661 | -0.0043324
108 |  | 2.3243 | 26.5372 | 4187 | 0.0027269 | 6.2944 | 6.2971 | -1.5885 | 366.7204 | 2891.1983 | -0.0043317
109 |  | 2.3243 | 26.5329 | 4187 | 0.0027264 | 6.2971 | 6.2998 | -1.5885 | 366.7803 | 2917.7312 | -0.004331
110 |  | 2.3243 | 26.5286 | 4187 | 0.002726 | 6.2998 | 6.3025 | -1.5885 | 366.8402 | 2944.2597 | -0.0043303
111 |  | 2.3243 | 26.5242 | 4187 | 0.0027255 | 6.3025 | 6.3053 | -1.5885 | 366.9 | 2970.784 | -0.0043296
112 |  | 2.3243 | 26.5199 | 4187 | 0.0027251 | 6.3053 | 6.308 | -1.5885 | 366.9599 | 2997.3039 | -0.0043289
113 |  | 2.3243 | 26.5156 | 4187 | 0.0027246 | 6.308 | 6.3107 | -1.5885 | 367.0199 | 3023.8194 | -0.0043282
114 |  | 2.3243 | 26.5112 | 4187 | 0.0027242 | 6.3107 | 6.3134 | -1.5885 | 367.0798 | 3050.3307 | -0.0043274
115 |  | 2.3243 | 26.5069 | 4187 | 0.0027238 | 6.3134 | 6.3162 | -1.5885 | 367.1397 | 3076.8376 | -0.0043267
116 |  | 2.3243 | 26.5026 | 4187 | 0.0027233 | 6.3162 | 6.3189 | -1.5885 | 367.1996 | 3103.3402 | -0.004326
117 |  | 2.3243 | 26.4983 | 4187 | 0.0027229 | 6.3189 | 6.3216 | -1.5885 | 367.2596 | 3129.8385 | -0.0043253
118 |  | 2.3243 | 26.4939 | 4187 | 0.0027224 | 6.3216 | 6.3243 | -1.5885 | 367.3195 | 3156.3324 | -0.0043246
119 |  | 2.3243 | 26.4896 | 4187 | 0.002722 | 6.3243 | 6.3271 | -1.5885 | 367.3795 | 3182.822 | -0.0043239
120 |  | 2.3243 | 26.4853 | 4187 | 0.0027215 | 6.3271 | 6.3298 | -1.5885 | 367.4395 | 3209.3073 | -0.0043232
121 |  | 2.3243 | 26.481 | 4187 | 0.0027211 | 6.3298 | 6.3325 | -1.5885 | 367.4995 | 3235.7883 | -0.0043225
122 |  | 2.3243 | 26.4766 | 4187 | 0.0027206 | 6.3325 | 6.3352 | -1.5885 | 367.5595 | 3262.265 | -0.0043218
123 |  | 2.3243 | 26.4723 | 4187 | 0.0027202 | 6.3352 | 6.3379 | -1.5885 | 367.6195 | 3288.7373 | -0.0043211
124 |  | 2.3243 | 26.468 | 4187 | 0.0027198 | 6.3379 | 6.3407 | -1.5885 | 367.6795 | 3315.2053 | -0.0043204
125 |  | 2.3243 | 26.4637 | 4187 | 0.0027193 | 6.3407 | 6.3434 | -1.5885 | 367.7395 | 3341.669 | -0.0043197
126 |  | 2.3243 | 26.4594 | 4187 | 0.0027189 | 6.3434 | 6.3461 | -1.5885 | 367.7996 | 3368.1283 | -0.004319
127 |  | 2.3243 | 26.455 | 4187 | 0.0027184 | 6.3461 | 6.3488 | -1.5885 | 367.8596 | 3394.5834 | -0.0043183
128 |  | 2.3243 | 26.4507 | 4187 | 0.002718 | 6.3488 | 6.3515 | -1.5885 | 367.9197 | 3421.0341 | -0.0043176
129 |  | 2.3243 | 26.4464 | 4187 | 0.0027175 | 6.3515 | 6.3543 | -1.5885 | 367.9797 | 3447.4805 | -0.0043169
130 |  | 2.3243 | 26.4421 | 4187 | 0.0027171 | 6.3543 | 6.357 | -1.5885 | 368.0398 | 3473.9226 | -0.0043162
131 |  | 2.3243 | 26.4378 | 4187 | 0.0027167 | 6.357 | 6.3597 | -1.5885 | 368.0999 | 3500.3604 | -0.0043155
132 |  | 2.3243 | 26.4335 | 4187 | 0.0027162 | 6.3597 | 6.3624 | -1.5885 | 368.16 | 3526.7939 | -0.0043148
133 |  | 2.3243 | 26.4291 | 4187 | 0.0027158 | 6.3624 | 6.3651 | -1.5885 | 368.2201 | 3553.223 | -0.004314
134 |  | 2.3243 | 26.4248 | 4187 | 0.0027153 | 6.3651 | 6.3678 | -1.5885 | 368.2802 | 3579.6478 | -0.0043133
135 |  | 2.3243 | 26.4205 | 4187 | 0.0027149 | 6.3678 | 6.3705 | -1.5885 | 368.3403 | 3606.0684 | -0.0043126
136 |  | 2.3243 | 26.4162 | 4187 | 0.0027144 | 6.3705 | 6.3733 | -1.5885 | 368.4005 | 3632.4846 | -0.0043119
137 |  | 2.3243 | 26.4119 | 4187 | 0.002714 | 6.3733 | 6.376 | -1.5885 | 368.4606 | 3658.8965 | -0.0043112
138 |  | 2.3243 | 26.4076 | 4187 | 0.0027136 | 6.376 | 6.3787 | -1.5885 | 368.5208 | 3685.3041 | -0.0043105
139 |  | 2.3243 | 26.4033 | 4187 | 0.0027131 | 6.3787 | 6.3814 | -1.5885 | 368.5809 | 3711.7073 | -0.0043098
140 |  | 2.3243 | 26.399 | 4187 | 0.0027127 | 6.3814 | 6.3841 | -1.5885 | 368.6411 | 3738.1063 | -0.0043091
141 |  | 2.3243 | 26.3947 | 4187 | 0.0027122 | 6.3841 | 6.3868 | -1.5885 | 368.7013 | 3764.5009 | -0.0043084
142 |  | 2.3243 | 26.3903 | 4187 | 0.0027118 | 6.3868 | 6.3895 | -1.5885 | 368.7615 | 3790.8913 | -0.0043077
143 |  | 2.3243 | 26.386 | 4187 | 0.0027113 | 6.3895 | 6.3923 | -1.5885 | 368.8217 | 3817.2773 | -0.004307
144 |  | 2.3243 | 26.3817 | 4187 | 0.0027109 | 6.3923 | 6.395 | -1.5885 | 368.8819 | 3843.6591 | -0.0043063
145 |  | 2.3243 | 26.3774 | 4187 | 0.0027105 | 6.395 | 6.3977 | -1.5885 | 368.9421 | 3870.0365 | -0.0043056
146 |  | 2.3243 | 26.3731 | 4187 | 0.00271 | 6.3977 | 6.4004 | -1.5885 | 369.0023 | 3896.4096 | -0.0043049
147 |  | 2.3243 | 26.3688 | 4187 | 0.0027096 | 6.4004 | 6.4031 | -1.5885 | 369.0626 | 3922.7784 | -0.0043042
148 |  | 2.3243 | 26.3645 | 4187 | 0.0027091 | 6.4031 | 6.4058 | -1.5885 | 369.1228 | 3949.1429 | -0.0043035
149 |  | 2.3243 | 26.3602 | 4187 | 0.0027087 | 6.4058 | 6.4085 | -1.5885 | 369.1831 | 3975.5031 | -0.0043028
150 |  | 2.3243 | 26.3559 | 4187 | 0.0027082 | 6.4085 | 6.4112 | -1.5885 | 369.2434 | 4001.8591 | -0.0043021
151 |  | 2.3243 | 26.3516 | 4187 | 0.0027078 | 6.4112 | 6.4139 | -1.5885 | 369.3037 | 4028.2107 | -0.0043014
152 |  | 2.3243 | 26.3473 | 4187 | 0.0027074 | 6.4139 | 6.4166 | -1.5885 | 369.3639 | 4054.558 | -0.0043007
153 |  | 2.3243 | 26.343 | 4187 | 0.0027069 | 6.4166 | 6.4193 | -1.5885 | 369.4243 | 4080.901 | -0.0043
154 |  | 2.3243 | 26.3387 | 4187 | 0.0027065 | 6.4193 | 6.422 | -1.5885 | 369.4846 | 4107.2397 | -0.0042993
155 |  | 2.3243 | 26.3344 | 4187 | 0.002706 | 6.422 | 6.4248 | -1.5885 | 369.5449 | 4133.5741 | -0.0042986
156 |  | 2.3243 | 26.3301 | 4187 | 0.0027056 | 6.4248 | 6.4275 | -1.5885 | 369.6052 | 4159.9042 | -0.0042979
157 |  | 2.3243 | 26.3258 | 4187 | 0.0027051 | 6.4275 | 6.4302 | -1.5885 | 369.6656 | 4186.23 | -0.0042972
158 |  | 2.3243 | 26.3215 | 4187 | 0.0027047 | 6.4302 | 6.4329 | -1.5885 | 369.7259 | 4212.5515 | -0.0042965
159 |  | 2.3243 | 26.3172 | 4187 | 0.0027043 | 6.4329 | 6.4356 | -1.5885 | 369.7863 | 4238.8687 | -0.0042958
160 |  | 2.3243 | 26.3129 | 4187 | 0.0027038 | 6.4356 | 6.4383 | -1.5885 | 369.8466 | 4265.1816 | -0.0042951
161 |  | 2.3243 | 26.3086 | 4187 | 0.0027034 | 6.4383 | 6.441 | -1.5885 | 369.907 | 4291.4902 | -0.0042944
162 |  | 2.3243 | 26.3043 | 4187 | 0.0027029 | 6.441 | 6.4437 | -1.5885 | 369.9674 | 4317.7945 | -0.0042937
163 |  | 2.3243 | 26.3 | 4187 | 0.0027025 | 6.4437 | 6.4464 | -1.5885 | 370.0278 | 4344.0946 | -0.004293
164 |  | 2.3243 | 26.2957 | 4187 | 0.0027021 | 6.4464 | 6.4491 | -1.5885 | 370.0882 | 4370.3903 | -0.0042923
165 |  | 2.3243 | 26.2914 | 4187 | 0.0027016 | 6.4491 | 6.4518 | -1.5885 | 370.1486 | 4396.6818 | -0.0042916
166 |  | 2.3243 | 26.2872 | 4187 | 0.0027012 | 6.4518 | 6.4545 | -1.5885 | 370.2091 | 4422.9689 | -0.0042909
167 |  | 2.3243 | 26.2829 | 4187 | 0.0027007 | 6.4545 | 6.4572 | -1.5885 | 370.2695 | 4449.2518 | -0.0042902
168 |  | 2.3243 | 26.2786 | 4187 | 0.0027003 | 6.4572 | 6.4599 | -1.5885 | 370.33 | 4475.5304 | -0.0042895
169 |  | 2.3243 | 26.2743 | 4187 | 0.0026999 | 6.4599 | 6.4626 | -1.5885 | 370.3904 | 4501.8046 | -0.0042888
170 |  | 2.3243 | 26.27 | 4187 | 0.0026994 | 6.4626 | 6.4653 | -1.5885 | 370.4509 | 4528.0746 | -0.0042881
171 |  | 2.3243 | 26.2657 | 4187 | 0.002699 | 6.4653 | 6.468 | -1.5885 | 370.5114 | 4554.3403 | -0.0042874
172 |  | 2.3243 | 26.2614 | 4187 | 0.0026985 | 6.468 | 6.4707 | -1.5885 | 370.5718 | 4580.6018 | -0.0042867
173 |  | 2.3243 | 26.2571 | 4187 | 0.0026981 | 6.4707 | 6.4734 | -1.5885 | 370.6323 | 4606.8589 | -0.004286
174 |  | 2.3243 | 26.2528 | 4187 | 0.0026977 | 6.4734 | 6.4761 | -1.5885 | 370.6929 | 4633.1117 | -0.0042853
175 |  | 2.3243 | 26.2486 | 4187 | 0.0026972 | 6.4761 | 6.4788 | -1.5885 | 370.7534 | 4659.3603 | -0.0042846
176 |  | 2.3243 | 26.2443 | 4187 | 0.0026968 | 6.4788 | 6.4815 | -1.5885 | 370.8139 | 4685.6046 | -0.0042839
177 |  | 2.3243 | 26.24 | 4187 | 0.0026963 | 6.4815 | 6.4842 | -1.5885 | 370.8744 | 4711.8446 | -0.0042832
178 |  | 2.3243 | 26.2357 | 4187 | 0.0026959 | 6.4842 | 6.4869 | -1.5885 | 370.935 | 4738.0803 | -0.0042825
179 |  | 2.3243 | 26.2314 | 4187 | 0.0026955 | 6.4869 | 6.4896 | -1.5885 | 370.9955 | 4764.3117 | -0.0042818
180 |  | 2.3243 | 26.2271 | 4187 | 0.002695 | 6.4896 | 6.4923 | -1.5885 | 371.0561 | 4790.5389 | -0.0042811
181 |  | 2.3243 | 26.2229 | 4187 | 0.0026946 | 6.4923 | 6.495 | -1.5885 | 371.1167 | 4816.7617 | -0.0042804
182 |  | 2.3243 | 26.2186 | 4187 | 0.0026941 | 6.495 | 6.4976 | -1.5885 | 371.1773 | 4842.9803 | -0.0042797
183 |  | 2.3243 | 26.2143 | 4187 | 0.0026937 | 6.4976 | 6.5003 | -1.5885 | 371.2379 | 4869.1946 | -0.004279
184 |  | 2.3243 | 26.21 | 4187 | 0.0026933 | 6.5003 | 6.503 | -1.5885 | 371.2985 | 4895.4047 | -0.0042783
185 |  | 2.3243 | 26.2057 | 4187 | 0.0026928 | 6.503 | 6.5057 | -1.5885 | 371.3591 | 4921.6104 | -0.0042776
186 |  | 2.3243 | 26.2015 | 4187 | 0.0026924 | 6.5057 | 6.5084 | -1.5885 | 371.4197 | 4947.8119 | -0.0042769
187 |  | 2.3243 | 26.1972 | 4187 | 0.0026919 | 6.5084 | 6.5111 | -1.5885 | 371.4804 | 4974.0091 | -0.0042762
188 |  | 2.3243 | 26.1929 | 4187 | 0.0026915 | 6.5111 | 6.5138 | -1.5885 | 371.541 | 5000.202 | -0.0042755
189 |  | 2.3243 | 26.1886 | 4187 | 0.0026911 | 6.5138 | 6.5165 | -1.5885 | 371.6017 | 5026.3906 | -0.0042748
190 |  | 2.3243 | 26.1844 | 4187 | 0.0026906 | 6.5165 | 6.5192 | -1.5885 | 371.6623 | 5052.575 | -0.0042741
191 |  | 2.3243 | 26.1801 | 4187 | 0.0026902 | 6.5192 | 6.5219 | -1.5885 | 371.723 | 5078.7551 | -0.0042734
192 |  | 2.3243 | 26.1758 | 4187 | 0.0026897 | 6.5219 | 6.5246 | -1.5885 | 371.7837 | 5104.9309 | -0.0042727
193 |  | 2.3243 | 26.1715 | 4187 | 0.0026893 | 6.5246 | 6.5273 | -1.5885 | 371.8444 | 5131.1025 | -0.004272
194 |  | 2.3243 | 26.1673 | 4187 | 0.0026889 | 6.5273 | 6.5299 | -1.5885 | 371.9051 | 5157.2697 | -0.0042713
195 |  | 2.3243 | 26.163 | 4187 | 0.0026884 | 6.5299 | 6.5326 | -1.5885 | 371.9658 | 5183.4327 | -0.0042706
196 |  | 2.3243 | 26.1587 | 4187 | 0.002688 | 6.5326 | 6.5353 | -1.5885 | 372.0265 | 5209.5915 | -0.0042699
197 |  | 2.3243 | 26.1545 | 4187 | 0.0026875 | 6.5353 | 6.538 | -1.5885 | 372.0873 | 5235.7459 | -0.0042692
198 |  | 2.3243 | 26.1502 | 4187 | 0.0026871 | 6.538 | 6.5407 | -1.5885 | 372.148 | 5261.8961 | -0.0042685
199 |  | 2.3243 | 26.1459 | 4187 | 0.0026867 | 6.5407 | 6.5434 | -1.5885 | 372.2088 | 5288.0421 | -0.0042678
200 |  | 2.3243 | 26.1417 | 4187 | 0.0026862 | 6.5434 | 6.5461 | -1.5885 | 372.2695 | 5314.1837 | -0.0042671
201 |  | 2.3243 | 26.1374 | 4187 | 0.0026858 | 6.5461 | 6.5488 | -1.5885 | 372.3303 | 5340.3211 | -0.0042664
202 |  | 2.3243 | 26.1331 | 4187 | 0.0026853 | 6.5488 | 6.5514 | -1.5885 | 372.3911 | 5366.4542 | -0.0042657
203 |  | 2.3243 | 26.1289 | 4187 | 0.0026849 | 6.5514 | 6.5541 | -1.5885 | 372.4519 | 5392.5831 | -0.004265
204 |  | 2.3243 | 26.1246 | 4187 | 0.0026845 | 6.5541 | 6.5568 | -1.5885 | 372.5127 | 5418.7077 | -0.0042643
205 |  | 2.3243 | 26.1203 | 4187 | 0.002684 | 6.5568 | 6.5595 | -1.5885 | 372.5735 | 5444.828 | -0.0042636
206 |  | 2.3243 | 26.1161 | 4187 | 0.0026836 | 6.5595 | 6.5622 | -1.5885 | 372.6344 | 5470.9441 | -0.0042629
207 |  | 2.3243 | 26.1118 | 4187 | 0.0026832 | 6.5622 | 6.5649 | -1.5885 | 372.6952 | 5497.0559 | -0.0042622
208 |  | 2.3243 | 26.1075 | 4187 | 0.0026827 | 6.5649 | 6.5675 | -1.5885 | 372.756 | 5523.1634 | -0.0042616
209 |  | 2.3243 | 26.1033 | 4187 | 0.0026823 | 6.5675 | 6.5702 | -1.5885 | 372.8169 | 5549.2667 | -0.0042609
210 |  | 2.3243 | 26.099 | 4187 | 0.0026818 | 6.5702 | 6.5729 | -1.5885 | 372.8778 | 5575.3657 | -0.0042602
211 |  | 2.3243 | 26.0948 | 4187 | 0.0026814 | 6.5729 | 6.5756 | -1.5885 | 372.9386 | 5601.4605 | -0.0042595
212 |  | 2.3243 | 26.0905 | 4187 | 0.002681 | 6.5756 | 6.5783 | -1.5885 | 372.9995 | 5627.551 | -0.0042588
213 |  | 2.3243 | 26.0862 | 4187 | 0.0026805 | 6.5783 | 6.5809 | -1.5885 | 373.0604 | 5653.6372 | -0.0042581
214 |  | 2.3243 | 26.082 | 4187 | 0.0026801 | 6.5809 | 6.5836 | -1.5885 | 373.1213 | 5679.7192 | -0.0042574
215 |  | 2.3243 | 26.0777 | 4187 | 0.0026797 | 6.5836 | 6.5863 | -1.5885 | 373.1822 | 5705.7969 | -0.0042567
216 |  | 2.3243 | 26.0735 | 4187 | 0.0026792 | 6.5863 | 6.589 | -1.5885 | 373.2432 | 5731.8704 | -0.004256
217 |  | 2.3243 | 26.0692 | 4187 | 0.0026788 | 6.589 | 6.5917 | -1.5885 | 373.3041 | 5757.9396 | -0.0042553
218 |  | 2.3243 | 26.065 | 4187 | 0.0026783 | 6.5917 | 6.5943 | -1.5885 | 373.365 | 5784.0046 | -0.0042546
219 |  | 2.3243 | 26.0607 | 4187 | 0.0026779 | 6.5943 | 6.597 | -1.5885 | 373.426 | 5810.0653 | -0.0042539
220 |  | 2.3243 | 26.0564 | 4187 | 0.0026775 | 6.597 | 6.5997 | -1.5885 | 373.4869 | 5836.1217 | -0.0042532
221 |  | 2.3243 | 26.0522 | 4187 | 0.002677 | 6.5997 | 6.6024 | -1.5885 | 373.5479 | 5862.1739 | -0.0042525
222 |  | 2.3243 | 26.0479 | 4187 | 0.0026766 | 6.6024 | 6.6051 | -1.5885 | 373.6089 | 5888.2218 | -0.0042518
223 |  | 2.3243 | 26.0437 | 4187 | 0.0026762 | 6.6051 | 6.6077 | -1.5885 | 373.6699 | 5914.2655 | -0.0042511
224 |  | 2.3243 | 26.0394 | 4187 | 0.0026757 | 6.6077 | 6.6104 | -1.5885 | 373.7309 | 5940.305 | -0.0042504
225 |  | 2.3243 | 26.0352 | 4187 | 0.0026753 | 6.6104 | 6.6131 | -1.5885 | 373.7919 | 5966.3402 | -0.0042497
226 |  | 2.3243 | 26.0309 | 4187 | 0.0026748 | 6.6131 | 6.6158 | -1.5885 | 373.8529 | 5992.3711 | -0.004249
227 |  | 2.3243 | 26.0267 | 4187 | 0.0026744 | 6.6158 | 6.6184 | -1.5885 | 373.914 | 6018.3978 | -0.0042484
228 |  | 2.3243 | 26.0224 | 4187 | 0.002674 | 6.6184 | 6.6211 | -1.5885 | 373.975 | 6044.4202 | -0.0042477
229 |  | 2.3243 | 26.0182 | 4187 | 0.0026735 | 6.6211 | 6.6238 | -1.5885 | 374.0361 | 6070.4384 | -0.004247
230 |  | 2.3243 | 26.0139 | 4187 | 0.0026731 | 6.6238 | 6.6265 | -1.5885 | 374.0971 | 6096.4524 | -0.0042463
231 |  | 2.3243 | 26.0097 | 4187 | 0.0026727 | 6.6265 | 6.6291 | -1.5885 | 374.1582 | 6122.4621 | -0.0042456
232 |  | 2.3243 | 26.0055 | 4187 | 0.0026722 | 6.6291 | 6.6318 | -1.5885 | 374.2193 | 6148.4675 | -0.0042449
233 |  | 2.3243 | 26.0012 | 4187 | 0.0026718 | 6.6318 | 6.6345 | -1.5885 | 374.2804 | 6174.4687 | -0.0042442
234 |  | 2.3243 | 25.997 | 4187 | 0.0026714 | 6.6345 | 6.6371 | -1.5885 | 374.3415 | 6200.4657 | -0.0042435
235 |  | 2.3243 | 25.9927 | 4187 | 0.0026709 | 6.6371 | 6.6398 | -1.5885 | 374.4026 | 6226.4584 | -0.0042428
236 |  | 2.3243 | 25.9885 | 4187 | 0.0026705 | 6.6398 | 6.6425 | -1.5885 | 374.4637 | 6252.4469 | -0.0042421

## Fus90
|  |  | buis | verlies W/M | L /°C/sec
diam | wandikte |  | inhoud l/m |  | W/M
90 | 12.3 | 3.1416 | 3.3593 | 29.3393 | 4187
[8 empty] | J/sec/mtr | aantal mtr. | verlies
|  | buis | verlies W/M | L /°C/sec | verlies temp | begintemp | eindtemp | verlies | bij 1°C | totaal J/sec
|  | inhoud L |  | W/M | °C per M | °C | °C | per m°C | daling | aantal mtr
1 | 90 | 3.3593 | 29.3393 | 4187 | 0.0020859 | 6 | 6.0021 | -1.7258 | 479.4003 | 29.3393 | -0.0036
2 |  | 3.3593 | 29.3357 | 4187 | 0.0020857 | 6.0021 | 6.0042 | -1.7258 | 479.4591 | 58.675 | -0.0035996
3 |  | 3.3593 | 29.3321 | 4187 | 0.0020854 | 6.0042 | 6.0063 | -1.7258 | 479.5179 | 88.0072 | -0.0035991
4 |  | 3.3593 | 29.3285 | 4187 | 0.0020852 | 6.0063 | 6.0083 | -1.7258 | 479.5768 | 117.3357 | -0.0035987
5 |  | 3.3593 | 29.3249 | 4187 | 0.0020849 | 6.0083 | 6.0104 | -1.7258 | 479.6356 | 146.6606 | -0.0035982
6 |  | 3.3593 | 29.3213 | 4187 | 0.0020847 | 6.0104 | 6.0125 | -1.7258 | 479.6945 | 175.9819 | -0.0035978
7 |  | 3.3593 | 29.3177 | 4187 | 0.0020844 | 6.0125 | 6.0146 | -1.7258 | 479.7534 | 205.2997 | -0.0035974
8 |  | 3.3593 | 29.3141 | 4187 | 0.0020841 | 6.0146 | 6.0167 | -1.7258 | 479.8122 | 234.6138 | -0.0035969
9 |  | 3.3593 | 29.3105 | 4187 | 0.0020839 | 6.0167 | 6.0188 | -1.7258 | 479.8711 | 263.9243 | -0.0035965
10 |  | 3.3593 | 29.3069 | 4187 | 0.0020836 | 6.0188 | 6.0208 | -1.7258 | 479.93 | 293.2313 | -0.003596
11 |  | 3.3593 | 29.3033 | 4187 | 0.0020834 | 6.0208 | 6.0229 | -1.7258 | 479.9889 | 322.5346 | -0.0035956
12 |  | 3.3593 | 29.2997 | 4187 | 0.0020831 | 6.0229 | 6.025 | -1.7258 | 480.0478 | 351.8343 | -0.0035951
13 |  | 3.3593 | 29.2962 | 4187 | 0.0020829 | 6.025 | 6.0271 | -1.7258 | 480.1067 | 381.1305 | -0.0035947
14 |  | 3.3593 | 29.2926 | 4187 | 0.0020826 | 6.0271 | 6.0292 | -1.7258 | 480.1656 | 410.4231 | -0.0035943
15 |  | 3.3593 | 29.289 | 4187 | 0.0020824 | 6.0292 | 6.0313 | -1.7258 | 480.2246 | 439.712 | -0.0035938
16 |  | 3.3593 | 29.2854 | 4187 | 0.0020821 | 6.0313 | 6.0333 | -1.7258 | 480.2835 | 468.9974 | -0.0035934
17 |  | 3.3593 | 29.2818 | 4187 | 0.0020818 | 6.0333 | 6.0354 | -1.7258 | 480.3424 | 498.2792 | -0.0035929
18 |  | 3.3593 | 29.2782 | 4187 | 0.0020816 | 6.0354 | 6.0375 | -1.7258 | 480.4014 | 527.5573 | -0.0035925
19 |  | 3.3593 | 29.2746 | 4187 | 0.0020813 | 6.0375 | 6.0396 | -1.7258 | 480.4603 | 556.8319 | -0.0035921
20 |  | 3.3593 | 29.271 | 4187 | 0.0020811 | 6.0396 | 6.0417 | -1.7258 | 480.5193 | 586.1029 | -0.0035916
21 |  | 3.3593 | 29.2674 | 4187 | 0.0020808 | 6.0417 | 6.0438 | -1.7258 | 480.5783 | 615.3703 | -0.0035912
22 |  | 3.3593 | 29.2638 | 4187 | 0.0020806 | 6.0438 | 6.0458 | -1.7258 | 480.6372 | 644.6341 | -0.0035907
23 |  | 3.3593 | 29.2602 | 4187 | 0.0020803 | 6.0458 | 6.0479 | -1.7258 | 480.6962 | 673.8944 | -0.0035903
24 |  | 3.3593 | 29.2566 | 4187 | 0.0020801 | 6.0479 | 6.05 | -1.7258 | 480.7552 | 703.151 | -0.0035899
25 |  | 3.3593 | 29.253 | 4187 | 0.0020798 | 6.05 | 6.0521 | -1.7258 | 480.8142 | 732.404 | -0.0035894
26 |  | 3.3593 | 29.2495 | 4187 | 0.0020796 | 6.0521 | 6.0542 | -1.7258 | 480.8732 | 761.6535 | -0.003589
27 |  | 3.3593 | 29.2459 | 4187 | 0.0020793 | 6.0542 | 6.0562 | -1.7258 | 480.9322 | 790.8994 | -0.0035885
28 |  | 3.3593 | 29.2423 | 4187 | 0.002079 | 6.0562 | 6.0583 | -1.7258 | 480.9912 | 820.1416 | -0.0035881
29 |  | 3.3593 | 29.2387 | 4187 | 0.0020788 | 6.0583 | 6.0604 | -1.7258 | 481.0503 | 849.3803 | -0.0035877
30 |  | 3.3593 | 29.2351 | 4187 | 0.0020785 | 6.0604 | 6.0625 | -1.7258 | 481.1093 | 878.6154 | -0.0035872
31 |  | 3.3593 | 29.2315 | 4187 | 0.0020783 | 6.0625 | 6.0645 | -1.7258 | 481.1683 | 907.8469 | -0.0035868
32 |  | 3.3593 | 29.2279 | 4187 | 0.002078 | 6.0645 | 6.0666 | -1.7258 | 481.2274 | 937.0749 | -0.0035863
33 |  | 3.3593 | 29.2243 | 4187 | 0.0020778 | 6.0666 | 6.0687 | -1.7258 | 481.2864 | 966.2992 | -0.0035859
34 |  | 3.3593 | 29.2208 | 4187 | 0.0020775 | 6.0687 | 6.0708 | -1.7258 | 481.3455 | 995.52 | -0.0035855
35 |  | 3.3593 | 29.2172 | 4187 | 0.0020773 | 6.0708 | 6.0729 | -1.7258 | 481.4046 | 1024.7371 | -0.003585
36 |  | 3.3593 | 29.2136 | 4187 | 0.002077 | 6.0729 | 6.0749 | -1.7258 | 481.4637 | 1053.9507 | -0.0035846
37 |  | 3.3593 | 29.21 | 4187 | 0.0020767 | 6.0749 | 6.077 | -1.7258 | 481.5227 | 1083.1607 | -0.0035841
38 |  | 3.3593 | 29.2064 | 4187 | 0.0020765 | 6.077 | 6.0791 | -1.7258 | 481.5818 | 1112.3671 | -0.0035837
39 |  | 3.3593 | 29.2028 | 4187 | 0.0020762 | 6.0791 | 6.0812 | -1.7258 | 481.6409 | 1141.5699 | -0.0035833
40 |  | 3.3593 | 29.1992 | 4187 | 0.002076 | 6.0812 | 6.0832 | -1.7258 | 481.7 | 1170.7692 | -0.0035828
41 |  | 3.3593 | 29.1957 | 4187 | 0.0020757 | 6.0832 | 6.0853 | -1.7258 | 481.7591 | 1199.9649 | -0.0035824
42 |  | 3.3593 | 29.1921 | 4187 | 0.0020755 | 6.0853 | 6.0874 | -1.7258 | 481.8183 | 1229.1569 | -0.0035819
43 |  | 3.3593 | 29.1885 | 4187 | 0.0020752 | 6.0874 | 6.0895 | -1.7258 | 481.8774 | 1258.3454 | -0.0035815
44 |  | 3.3593 | 29.1849 | 4187 | 0.002075 | 6.0895 | 6.0915 | -1.7258 | 481.9365 | 1287.5304 | -0.0035811
45 |  | 3.3593 | 29.1813 | 4187 | 0.0020747 | 6.0915 | 6.0936 | -1.7258 | 481.9957 | 1316.7117 | -0.0035806
46 |  | 3.3593 | 29.1778 | 4187 | 0.0020745 | 6.0936 | 6.0957 | -1.7258 | 482.0548 | 1345.8895 | -0.0035802
47 |  | 3.3593 | 29.1742 | 4187 | 0.0020742 | 6.0957 | 6.0978 | -1.7258 | 482.114 | 1375.0636 | -0.0035797
48 |  | 3.3593 | 29.1706 | 4187 | 0.0020739 | 6.0978 | 6.0998 | -1.7258 | 482.1731 | 1404.2342 | -0.0035793
49 |  | 3.3593 | 29.167 | 4187 | 0.0020737 | 6.0998 | 6.1019 | -1.7258 | 482.2323 | 1433.4013 | -0.0035789
50 |  | 3.3593 | 29.1634 | 4187 | 0.0020734 | 6.1019 | 6.104 | -1.7258 | 482.2915 | 1462.5647 | -0.0035784
51 |  | 3.3593 | 29.1599 | 4187 | 0.0020732 | 6.104 | 6.1061 | -1.7258 | 482.3507 | 1491.7246 | -0.003578
52 |  | 3.3593 | 29.1563 | 4187 | 0.0020729 | 6.1061 | 6.1081 | -1.7258 | 482.4099 | 1520.8808 | -0.0035775
53 |  | 3.3593 | 29.1527 | 4187 | 0.0020727 | 6.1081 | 6.1102 | -1.7258 | 482.4691 | 1550.0335 | -0.0035771
54 |  | 3.3593 | 29.1491 | 4187 | 0.0020724 | 6.1102 | 6.1123 | -1.7258 | 482.5283 | 1579.1827 | -0.0035767
55 |  | 3.3593 | 29.1456 | 4187 | 0.0020722 | 6.1123 | 6.1143 | -1.7258 | 482.5875 | 1608.3282 | -0.0035762
56 |  | 3.3593 | 29.142 | 4187 | 0.0020719 | 6.1143 | 6.1164 | -1.7258 | 482.6467 | 1637.4702 | -0.0035758
57 |  | 3.3593 | 29.1384 | 4187 | 0.0020717 | 6.1164 | 6.1185 | -1.7258 | 482.7059 | 1666.6086 | -0.0035753
58 |  | 3.3593 | 29.1348 | 4187 | 0.0020714 | 6.1185 | 6.1206 | -1.7258 | 482.7652 | 1695.7434 | -0.0035749
59 |  | 3.3593 | 29.1312 | 4187 | 0.0020711 | 6.1206 | 6.1226 | -1.7258 | 482.8244 | 1724.8747 | -0.0035745
60 |  | 3.3593 | 29.1277 | 4187 | 0.0020709 | 6.1226 | 6.1247 | -1.7258 | 482.8837 | 1754.0023 | -0.003574
61 |  | 3.3593 | 29.1241 | 4187 | 0.0020706 | 6.1247 | 6.1268 | -1.7258 | 482.9429 | 1783.1264 | -0.0035736
62 |  | 3.3593 | 29.1205 | 4187 | 0.0020704 | 6.1268 | 6.1288 | -1.7258 | 483.0022 | 1812.247 | -0.0035732
63 |  | 3.3593 | 29.117 | 4187 | 0.0020701 | 6.1288 | 6.1309 | -1.7258 | 483.0615 | 1841.3639 | -0.0035727
64 |  | 3.3593 | 29.1134 | 4187 | 0.0020699 | 6.1309 | 6.133 | -1.7258 | 483.1207 | 1870.4773 | -0.0035723
65 |  | 3.3593 | 29.1098 | 4187 | 0.0020696 | 6.133 | 6.1351 | -1.7258 | 483.18 | 1899.5871 | -0.0035718
66 |  | 3.3593 | 29.1062 | 4187 | 0.0020694 | 6.1351 | 6.1371 | -1.7258 | 483.2393 | 1928.6934 | -0.0035714
67 |  | 3.3593 | 29.1027 | 4187 | 0.0020691 | 6.1371 | 6.1392 | -1.7258 | 483.2986 | 1957.796 | -0.003571
68 |  | 3.3593 | 29.0991 | 4187 | 0.0020689 | 6.1392 | 6.1413 | -1.7258 | 483.3579 | 1986.8951 | -0.0035705
69 |  | 3.3593 | 29.0955 | 4187 | 0.0020686 | 6.1413 | 6.1433 | -1.7258 | 483.4173 | 2015.9906 | -0.0035701
70 |  | 3.3593 | 29.092 | 4187 | 0.0020684 | 6.1433 | 6.1454 | -1.7258 | 483.4766 | 2045.0826 | -0.0035697
71 |  | 3.3593 | 29.0884 | 4187 | 0.0020681 | 6.1454 | 6.1475 | -1.7258 | 483.5359 | 2074.171 | -0.0035692
72 |  | 3.3593 | 29.0848 | 4187 | 0.0020678 | 6.1475 | 6.1495 | -1.7258 | 483.5953 | 2103.2558 | -0.0035688
73 |  | 3.3593 | 29.0812 | 4187 | 0.0020676 | 6.1495 | 6.1516 | -1.7258 | 483.6546 | 2132.337 | -0.0035683
74 |  | 3.3593 | 29.0777 | 4187 | 0.0020673 | 6.1516 | 6.1537 | -1.7258 | 483.7139 | 2161.4147 | -0.0035679
75 |  | 3.3593 | 29.0741 | 4187 | 0.0020671 | 6.1537 | 6.1557 | -1.7258 | 483.7733 | 2190.4888 | -0.0035675
76 |  | 3.3593 | 29.0705 | 4187 | 0.0020668 | 6.1557 | 6.1578 | -1.7258 | 483.8327 | 2219.5594 | -0.003567
77 |  | 3.3593 | 29.067 | 4187 | 0.0020666 | 6.1578 | 6.1599 | -1.7258 | 483.8921 | 2248.6263 | -0.0035666
78 |  | 3.3593 | 29.0634 | 4187 | 0.0020663 | 6.1599 | 6.1619 | -1.7258 | 483.9514 | 2277.6898 | -0.0035661
79 |  | 3.3593 | 29.0598 | 4187 | 0.0020661 | 6.1619 | 6.164 | -1.7258 | 484.0108 | 2306.7496 | -0.0035657
80 |  | 3.3593 | 29.0563 | 4187 | 0.0020658 | 6.164 | 6.1661 | -1.7258 | 484.0702 | 2335.8059 | -0.0035653
81 |  | 3.3593 | 29.0527 | 4187 | 0.0020656 | 6.1661 | 6.1681 | -1.7258 | 484.1296 | 2364.8586 | -0.0035648
82 |  | 3.3593 | 29.0491 | 4187 | 0.0020653 | 6.1681 | 6.1702 | -1.7258 | 484.189 | 2393.9077 | -0.0035644
83 |  | 3.3593 | 29.0456 | 4187 | 0.0020651 | 6.1702 | 6.1723 | -1.7258 | 484.2485 | 2422.9533 | -0.003564
84 |  | 3.3593 | 29.042 | 4187 | 0.0020648 | 6.1723 | 6.1743 | -1.7258 | 484.3079 | 2451.9953 | -0.0035635
85 |  | 3.3593 | 29.0385 | 4187 | 0.0020645 | 6.1743 | 6.1764 | -1.7258 | 484.3673 | 2481.0338 | -0.0035631
86 |  | 3.3593 | 29.0349 | 4187 | 0.0020643 | 6.1764 | 6.1785 | -1.7258 | 484.4268 | 2510.0687 | -0.0035626
87 |  | 3.3593 | 29.0313 | 4187 | 0.002064 | 6.1785 | 6.1805 | -1.7258 | 484.4862 | 2539.1 | -0.0035622
88 |  | 3.3593 | 29.0278 | 4187 | 0.0020638 | 6.1805 | 6.1826 | -1.7258 | 484.5457 | 2568.1278 | -0.0035618
89 |  | 3.3593 | 29.0242 | 4187 | 0.0020635 | 6.1826 | 6.1846 | -1.7258 | 484.6051 | 2597.152 | -0.0035613
90 |  | 3.3593 | 29.0206 | 4187 | 0.0020633 | 6.1846 | 6.1867 | -1.7258 | 484.6646 | 2626.1726 | -0.0035609
91 |  | 3.3593 | 29.0171 | 4187 | 0.002063 | 6.1867 | 6.1888 | -1.7258 | 484.7241 | 2655.1897 | -0.0035605
92 |  | 3.3593 | 29.0135 | 4187 | 0.0020628 | 6.1888 | 6.1908 | -1.7258 | 484.7835 | 2684.2032 | -0.00356
93 |  | 3.3593 | 29.01 | 4187 | 0.0020625 | 6.1908 | 6.1929 | -1.7258 | 484.843 | 2713.2132 | -0.0035596
94 |  | 3.3593 | 29.0064 | 4187 | 0.0020623 | 6.1929 | 6.195 | -1.7258 | 484.9025 | 2742.2196 | -0.0035592
95 |  | 3.3593 | 29.0028 | 4187 | 0.002062 | 6.195 | 6.197 | -1.7258 | 484.962 | 2771.2224 | -0.0035587
96 |  | 3.3593 | 28.9993 | 4187 | 0.0020618 | 6.197 | 6.1991 | -1.7258 | 485.0216 | 2800.2217 | -0.0035583
97 |  | 3.3593 | 28.9957 | 4187 | 0.0020615 | 6.1991 | 6.2011 | -1.7258 | 485.0811 | 2829.2175 | -0.0035578
98 |  | 3.3593 | 28.9922 | 4187 | 0.0020613 | 6.2011 | 6.2032 | -1.7258 | 485.1406 | 2858.2096 | -0.0035574
99 |  | 3.3593 | 28.9886 | 4187 | 0.002061 | 6.2032 | 6.2053 | -1.7258 | 485.2001 | 2887.1982 | -0.003557
100 |  | 3.3593 | 28.9851 | 4187 | 0.0020608 | 6.2053 | 6.2073 | -1.7258 | 485.2597 | 2916.1833 | -0.0035565
101 |  | 3.3593 | 28.9815 | 4187 | 0.0020605 | 6.2073 | 6.2094 | -1.7258 | 485.3192 | 2945.1648 | -0.0035561
102 |  | 3.3593 | 28.9779 | 4187 | 0.0020602 | 6.2094 | 6.2115 | -1.7258 | 485.3788 | 2974.1427 | -0.0035557
103 |  | 3.3593 | 28.9744 | 4187 | 0.00206 | 6.2115 | 6.2135 | -1.7258 | 485.4384 | 3003.1171 | -0.0035552
104 |  | 3.3593 | 28.9708 | 4187 | 0.0020597 | 6.2135 | 6.2156 | -1.7258 | 485.4979 | 3032.088 | -0.0035548
105 |  | 3.3593 | 28.9673 | 4187 | 0.0020595 | 6.2156 | 6.2176 | -1.7258 | 485.5575 | 3061.0552 | -0.0035544
106 |  | 3.3593 | 28.9637 | 4187 | 0.0020592 | 6.2176 | 6.2197 | -1.7258 | 485.6171 | 3090.019 | -0.0035539
107 |  | 3.3593 | 28.9602 | 4187 | 0.002059 | 6.2197 | 6.2218 | -1.7258 | 485.6767 | 3118.9791 | -0.0035535
108 |  | 3.3593 | 28.9566 | 4187 | 0.0020587 | 6.2218 | 6.2238 | -1.7258 | 485.7363 | 3147.9357 | -0.003553
109 |  | 3.3593 | 28.9531 | 4187 | 0.0020585 | 6.2238 | 6.2259 | -1.7258 | 485.7959 | 3176.8888 | -0.0035526
110 |  | 3.3593 | 28.9495 | 4187 | 0.0020582 | 6.2259 | 6.2279 | -1.7258 | 485.8555 | 3205.8383 | -0.0035522
111 |  | 3.3593 | 28.946 | 4187 | 0.002058 | 6.2279 | 6.23 | -1.7258 | 485.9151 | 3234.7843 | -0.0035517
112 |  | 3.3593 | 28.9424 | 4187 | 0.0020577 | 6.23 | 6.232 | -1.7258 | 485.9748 | 3263.7267 | -0.0035513
113 |  | 3.3593 | 28.9389 | 4187 | 0.0020575 | 6.232 | 6.2341 | -1.7258 | 486.0344 | 3292.6655 | -0.0035509
114 |  | 3.3593 | 28.9353 | 4187 | 0.0020572 | 6.2341 | 6.2362 | -1.7258 | 486.094 | 3321.6008 | -0.0035504
115 |  | 3.3593 | 28.9318 | 4187 | 0.002057 | 6.2362 | 6.2382 | -1.7258 | 486.1537 | 3350.5326 | -0.00355
116 |  | 3.3593 | 28.9282 | 4187 | 0.0020567 | 6.2382 | 6.2403 | -1.7258 | 486.2134 | 3379.4608 | -0.0035496
117 |  | 3.3593 | 28.9247 | 4187 | 0.0020565 | 6.2403 | 6.2423 | -1.7258 | 486.273 | 3408.3854 | -0.0035491
118 |  | 3.3593 | 28.9211 | 4187 | 0.0020562 | 6.2423 | 6.2444 | -1.7258 | 486.3327 | 3437.3065 | -0.0035487
119 |  | 3.3593 | 28.9176 | 4187 | 0.002056 | 6.2444 | 6.2464 | -1.7258 | 486.3924 | 3466.2241 | -0.0035483
120 |  | 3.3593 | 28.914 | 4187 | 0.0020557 | 6.2464 | 6.2485 | -1.7258 | 486.4521 | 3495.1381 | -0.0035478
121 |  | 3.3593 | 28.9105 | 4187 | 0.0020554 | 6.2485 | 6.2505 | -1.7258 | 486.5118 | 3524.0486 | -0.0035474
122 |  | 3.3593 | 28.9069 | 4187 | 0.0020552 | 6.2505 | 6.2526 | -1.7258 | 486.5715 | 3552.9555 | -0.0035469
123 |  | 3.3593 | 28.9034 | 4187 | 0.0020549 | 6.2526 | 6.2547 | -1.7258 | 486.6312 | 3581.8588 | -0.0035465
124 |  | 3.3593 | 28.8998 | 4187 | 0.0020547 | 6.2547 | 6.2567 | -1.7258 | 486.6909 | 3610.7587 | -0.0035461
125 |  | 3.3593 | 28.8963 | 4187 | 0.0020544 | 6.2567 | 6.2588 | -1.7258 | 486.7506 | 3639.6549 | -0.0035456
126 |  | 3.3593 | 28.8927 | 4187 | 0.0020542 | 6.2588 | 6.2608 | -1.7258 | 486.8104 | 3668.5477 | -0.0035452
127 |  | 3.3593 | 28.8892 | 4187 | 0.0020539 | 6.2608 | 6.2629 | -1.7258 | 486.8701 | 3697.4368 | -0.0035448
128 |  | 3.3593 | 28.8856 | 4187 | 0.0020537 | 6.2629 | 6.2649 | -1.7258 | 486.9298 | 3726.3225 | -0.0035443
129 |  | 3.3593 | 28.8821 | 4187 | 0.0020534 | 6.2649 | 6.267 | -1.7258 | 486.9896 | 3755.2046 | -0.0035439
130 |  | 3.3593 | 28.8785 | 4187 | 0.0020532 | 6.267 | 6.269 | -1.7258 | 487.0494 | 3784.0831 | -0.0035435
131 |  | 3.3593 | 28.875 | 4187 | 0.0020529 | 6.269 | 6.2711 | -1.7258 | 487.1091 | 3812.9581 | -0.003543
132 |  | 3.3593 | 28.8715 | 4187 | 0.0020527 | 6.2711 | 6.2731 | -1.7258 | 487.1689 | 3841.8296 | -0.0035426
133 |  | 3.3593 | 28.8679 | 4187 | 0.0020524 | 6.2731 | 6.2752 | -1.7258 | 487.2287 | 3870.6975 | -0.0035422
134 |  | 3.3593 | 28.8644 | 4187 | 0.0020522 | 6.2752 | 6.2772 | -1.7258 | 487.2885 | 3899.5619 | -0.0035417
135 |  | 3.3593 | 28.8608 | 4187 | 0.0020519 | 6.2772 | 6.2793 | -1.7258 | 487.3483 | 3928.4227 | -0.0035413
136 |  | 3.3593 | 28.8573 | 4187 | 0.0020517 | 6.2793 | 6.2814 | -1.7258 | 487.4081 | 3957.28 | -0.0035409
137 |  | 3.3593 | 28.8538 | 4187 | 0.0020514 | 6.2814 | 6.2834 | -1.7258 | 487.4679 | 3986.1338 | -0.0035404
138 |  | 3.3593 | 28.8502 | 4187 | 0.0020512 | 6.2834 | 6.2855 | -1.7258 | 487.5277 | 4014.984 | -0.00354
139 |  | 3.3593 | 28.8467 | 4187 | 0.0020509 | 6.2855 | 6.2875 | -1.7258 | 487.5875 | 4043.8307 | -0.0035396
140 |  | 3.3593 | 28.8431 | 4187 | 0.0020507 | 6.2875 | 6.2896 | -1.7258 | 487.6474 | 4072.6738 | -0.0035391
141 |  | 3.3593 | 28.8396 | 4187 | 0.0020504 | 6.2896 | 6.2916 | -1.7258 | 487.7072 | 4101.5134 | -0.0035387
142 |  | 3.3593 | 28.8361 | 4187 | 0.0020502 | 6.2916 | 6.2937 | -1.7258 | 487.7671 | 4130.3494 | -0.0035383
143 |  | 3.3593 | 28.8325 | 4187 | 0.0020499 | 6.2937 | 6.2957 | -1.7258 | 487.8269 | 4159.182 | -0.0035378
144 |  | 3.3593 | 28.829 | 4187 | 0.0020497 | 6.2957 | 6.2978 | -1.7258 | 487.8868 | 4188.0109 | -0.0035374
145 |  | 3.3593 | 28.8254 | 4187 | 0.0020494 | 6.2978 | 6.2998 | -1.7258 | 487.9467 | 4216.8364 | -0.0035369
146 |  | 3.3593 | 28.8219 | 4187 | 0.0020492 | 6.2998 | 6.3019 | -1.7258 | 488.0066 | 4245.6583 | -0.0035365
147 |  | 3.3593 | 28.8184 | 4187 | 0.0020489 | 6.3019 | 6.3039 | -1.7258 | 488.0664 | 4274.4767 | -0.0035361
148 |  | 3.3593 | 28.8148 | 4187 | 0.0020486 | 6.3039 | 6.306 | -1.7258 | 488.1263 | 4303.2915 | -0.0035356
149 |  | 3.3593 | 28.8113 | 4187 | 0.0020484 | 6.306 | 6.308 | -1.7258 | 488.1862 | 4332.1028 | -0.0035352
150 |  | 3.3593 | 28.8078 | 4187 | 0.0020481 | 6.308 | 6.31 | -1.7258 | 488.2461 | 4360.9105 | -0.0035348
151 |  | 3.3593 | 28.8042 | 4187 | 0.0020479 | 6.31 | 6.3121 | -1.7258 | 488.3061 | 4389.7148 | -0.0035343
152 |  | 3.3593 | 28.8007 | 4187 | 0.0020476 | 6.3121 | 6.3141 | -1.7258 | 488.366 | 4418.5155 | -0.0035339
153 |  | 3.3593 | 28.7972 | 4187 | 0.0020474 | 6.3141 | 6.3162 | -1.7258 | 488.4259 | 4447.3126 | -0.0035335
154 |  | 3.3593 | 28.7936 | 4187 | 0.0020471 | 6.3162 | 6.3182 | -1.7258 | 488.4859 | 4476.1062 | -0.003533
155 |  | 3.3593 | 28.7901 | 4187 | 0.0020469 | 6.3182 | 6.3203 | -1.7258 | 488.5458 | 4504.8963 | -0.0035326
156 |  | 3.3593 | 28.7866 | 4187 | 0.0020466 | 6.3203 | 6.3223 | -1.7258 | 488.6058 | 4533.6829 | -0.0035322
157 |  | 3.3593 | 28.783 | 4187 | 0.0020464 | 6.3223 | 6.3244 | -1.7258 | 488.6657 | 4562.4659 | -0.0035317
158 |  | 3.3593 | 28.7795 | 4187 | 0.0020461 | 6.3244 | 6.3264 | -1.7258 | 488.7257 | 4591.2454 | -0.0035313
159 |  | 3.3593 | 28.776 | 4187 | 0.0020459 | 6.3264 | 6.3285 | -1.7258 | 488.7857 | 4620.0214 | -0.0035309
160 |  | 3.3593 | 28.7724 | 4187 | 0.0020456 | 6.3285 | 6.3305 | -1.7258 | 488.8456 | 4648.7938 | -0.0035304
161 |  | 3.3593 | 28.7689 | 4187 | 0.0020454 | 6.3305 | 6.3326 | -1.7258 | 488.9056 | 4677.5627 | -0.00353
162 |  | 3.3593 | 28.7654 | 4187 | 0.0020451 | 6.3326 | 6.3346 | -1.7258 | 488.9656 | 4706.3281 | -0.0035296
163 |  | 3.3593 | 28.7618 | 4187 | 0.0020449 | 6.3346 | 6.3367 | -1.7258 | 489.0256 | 4735.0899 | -0.0035291
164 |  | 3.3593 | 28.7583 | 4187 | 0.0020446 | 6.3367 | 6.3387 | -1.7258 | 489.0856 | 4763.8483 | -0.0035287
165 |  | 3.3593 | 28.7548 | 4187 | 0.0020444 | 6.3387 | 6.3407 | -1.7258 | 489.1457 | 4792.603 | -0.0035283
166 |  | 3.3593 | 28.7513 | 4187 | 0.0020441 | 6.3407 | 6.3428 | -1.7258 | 489.2057 | 4821.3543 | -0.0035278
167 |  | 3.3593 | 28.7477 | 4187 | 0.0020439 | 6.3428 | 6.3448 | -1.7258 | 489.2657 | 4850.102 | -0.0035274
168 |  | 3.3593 | 28.7442 | 4187 | 0.0020436 | 6.3448 | 6.3469 | -1.7258 | 489.3258 | 4878.8462 | -0.003527
169 |  | 3.3593 | 28.7407 | 4187 | 0.0020434 | 6.3469 | 6.3489 | -1.7258 | 489.3858 | 4907.5869 | -0.0035265
170 |  | 3.3593 | 28.7371 | 4187 | 0.0020431 | 6.3489 | 6.351 | -1.7258 | 489.4459 | 4936.3241 | -0.0035261
171 |  | 3.3593 | 28.7336 | 4187 | 0.0020429 | 6.351 | 6.353 | -1.7258 | 489.5059 | 4965.0577 | -0.0035257
172 |  | 3.3593 | 28.7301 | 4187 | 0.0020426 | 6.353 | 6.355 | -1.7258 | 489.566 | 4993.7878 | -0.0035252
173 |  | 3.3593 | 28.7266 | 4187 | 0.0020424 | 6.355 | 6.3571 | -1.7258 | 489.6261 | 5022.5143 | -0.0035248
174 |  | 3.3593 | 28.723 | 4187 | 0.0020421 | 6.3571 | 6.3591 | -1.7258 | 489.6862 | 5051.2374 | -0.0035244
175 |  | 3.3593 | 28.7195 | 4187 | 0.0020419 | 6.3591 | 6.3612 | -1.7258 | 489.7463 | 5079.9569 | -0.003524
176 |  | 3.3593 | 28.716 | 4187 | 0.0020416 | 6.3612 | 6.3632 | -1.7258 | 489.8064 | 5108.6729 | -0.0035235
177 |  | 3.3593 | 28.7125 | 4187 | 0.0020414 | 6.3632 | 6.3653 | -1.7258 | 489.8665 | 5137.3854 | -0.0035231
178 |  | 3.3593 | 28.709 | 4187 | 0.0020411 | 6.3653 | 6.3673 | -1.7258 | 489.9266 | 5166.0943 | -0.0035227
179 |  | 3.3593 | 28.7054 | 4187 | 0.0020409 | 6.3673 | 6.3693 | -1.7258 | 489.9867 | 5194.7998 | -0.0035222
180 |  | 3.3593 | 28.7019 | 4187 | 0.0020406 | 6.3693 | 6.3714 | -1.7258 | 490.0468 | 5223.5017 | -0.0035218
181 |  | 3.3593 | 28.6984 | 4187 | 0.0020404 | 6.3714 | 6.3734 | -1.7258 | 490.107 | 5252.2001 | -0.0035214
182 |  | 3.3593 | 28.6949 | 4187 | 0.0020401 | 6.3734 | 6.3755 | -1.7258 | 490.1671 | 5280.8949 | -0.0035209
183 |  | 3.3593 | 28.6913 | 4187 | 0.0020399 | 6.3755 | 6.3775 | -1.7258 | 490.2273 | 5309.5863 | -0.0035205
184 |  | 3.3593 | 28.6878 | 4187 | 0.0020396 | 6.3775 | 6.3795 | -1.7258 | 490.2874 | 5338.2741 | -0.0035201
185 |  | 3.3593 | 28.6843 | 4187 | 0.0020394 | 6.3795 | 6.3816 | -1.7258 | 490.3476 | 5366.9584 | -0.0035196
186 |  | 3.3593 | 28.6808 | 4187 | 0.0020391 | 6.3816 | 6.3836 | -1.7258 | 490.4078 | 5395.6392 | -0.0035192
187 |  | 3.3593 | 28.6773 | 4187 | 0.0020389 | 6.3836 | 6.3857 | -1.7258 | 490.4679 | 5424.3164 | -0.0035188
188 |  | 3.3593 | 28.6737 | 4187 | 0.0020386 | 6.3857 | 6.3877 | -1.7258 | 490.5281 | 5452.9902 | -0.0035183
189 |  | 3.3593 | 28.6702 | 4187 | 0.0020384 | 6.3877 | 6.3897 | -1.7258 | 490.5883 | 5481.6604 | -0.0035179
190 |  | 3.3593 | 28.6667 | 4187 | 0.0020381 | 6.3897 | 6.3918 | -1.7258 | 490.6485 | 5510.3271 | -0.0035175
191 |  | 3.3593 | 28.6632 | 4187 | 0.0020379 | 6.3918 | 6.3938 | -1.7258 | 490.7087 | 5538.9903 | -0.003517
192 |  | 3.3593 | 28.6597 | 4187 | 0.0020376 | 6.3938 | 6.3958 | -1.7258 | 490.769 | 5567.65 | -0.0035166
193 |  | 3.3593 | 28.6562 | 4187 | 0.0020374 | 6.3958 | 6.3979 | -1.7258 | 490.8292 | 5596.3061 | -0.0035162
194 |  | 3.3593 | 28.6526 | 4187 | 0.0020371 | 6.3979 | 6.3999 | -1.7258 | 490.8894 | 5624.9588 | -0.0035157
195 |  | 3.3593 | 28.6491 | 4187 | 0.0020369 | 6.3999 | 6.402 | -1.7258 | 490.9497 | 5653.6079 | -0.0035153
196 |  | 3.3593 | 28.6456 | 4187 | 0.0020366 | 6.402 | 6.404 | -1.7258 | 491.0099 | 5682.2535 | -0.0035149
197 |  | 3.3593 | 28.6421 | 4187 | 0.0020364 | 6.404 | 6.406 | -1.7258 | 491.0702 | 5710.8956 | -0.0035145
198 |  | 3.3593 | 28.6386 | 4187 | 0.0020361 | 6.406 | 6.4081 | -1.7258 | 491.1304 | 5739.5342 | -0.003514
199 |  | 3.3593 | 28.6351 | 4187 | 0.0020359 | 6.4081 | 6.4101 | -1.7258 | 491.1907 | 5768.1693 | -0.0035136
200 |  | 3.3593 | 28.6316 | 4187 | 0.0020356 | 6.4101 | 6.4121 | -1.7258 | 491.251 | 5796.8008 | -0.0035132
201 |  | 3.3593 | 28.628 | 4187 | 0.0020354 | 6.4121 | 6.4142 | -1.7258 | 491.3113 | 5825.4289 | -0.0035127
202 |  | 3.3593 | 28.6245 | 4187 | 0.0020351 | 6.4142 | 6.4162 | -1.7258 | 491.3716 | 5854.0534 | -0.0035123
203 |  | 3.3593 | 28.621 | 4187 | 0.0020349 | 6.4162 | 6.4182 | -1.7258 | 491.4319 | 5882.6744 | -0.0035119
204 |  | 3.3593 | 28.6175 | 4187 | 0.0020346 | 6.4182 | 6.4203 | -1.7258 | 491.4922 | 5911.2919 | -0.0035114
205 |  | 3.3593 | 28.614 | 4187 | 0.0020344 | 6.4203 | 6.4223 | -1.7258 | 491.5525 | 5939.9059 | -0.003511
206 |  | 3.3593 | 28.6105 | 4187 | 0.0020341 | 6.4223 | 6.4243 | -1.7258 | 491.6128 | 5968.5164 | -0.0035106
207 |  | 3.3593 | 28.607 | 4187 | 0.0020339 | 6.4243 | 6.4264 | -1.7258 | 491.6731 | 5997.1233 | -0.0035101
208 |  | 3.3593 | 28.6035 | 4187 | 0.0020336 | 6.4264 | 6.4284 | -1.7258 | 491.7335 | 6025.7268 | -0.0035097
209 |  | 3.3593 | 28.6 | 4187 | 0.0020334 | 6.4284 | 6.4304 | -1.7258 | 491.7938 | 6054.3267 | -0.0035093
210 |  | 3.3593 | 28.5964 | 4187 | 0.0020331 | 6.4304 | 6.4325 | -1.7258 | 491.8542 | 6082.9232 | -0.0035088
211 |  | 3.3593 | 28.5929 | 4187 | 0.0020329 | 6.4325 | 6.4345 | -1.7258 | 491.9145 | 6111.5161 | -0.0035084
212 |  | 3.3593 | 28.5894 | 4187 | 0.0020326 | 6.4345 | 6.4365 | -1.7258 | 491.9749 | 6140.1055 | -0.003508
213 |  | 3.3593 | 28.5859 | 4187 | 0.0020324 | 6.4365 | 6.4386 | -1.7258 | 492.0353 | 6168.6915 | -0.0035076
214 |  | 3.3593 | 28.5824 | 4187 | 0.0020321 | 6.4386 | 6.4406 | -1.7258 | 492.0956 | 6197.2739 | -0.0035071
215 |  | 3.3593 | 28.5789 | 4187 | 0.0020319 | 6.4406 | 6.4426 | -1.7258 | 492.156 | 6225.8528 | -0.0035067
216 |  | 3.3593 | 28.5754 | 4187 | 0.0020316 | 6.4426 | 6.4447 | -1.7258 | 492.2164 | 6254.4282 | -0.0035063
217 |  | 3.3593 | 28.5719 | 4187 | 0.0020314 | 6.4447 | 6.4467 | -1.7258 | 492.2768 | 6283.0001 | -0.0035058
218 |  | 3.3593 | 28.5684 | 4187 | 0.0020311 | 6.4467 | 6.4487 | -1.7258 | 492.3372 | 6311.5684 | -0.0035054
219 |  | 3.3593 | 28.5649 | 4187 | 0.0020309 | 6.4487 | 6.4508 | -1.7258 | 492.3977 | 6340.1333 | -0.003505
220 |  | 3.3593 | 28.5614 | 4187 | 0.0020306 | 6.4508 | 6.4528 | -1.7258 | 492.4581 | 6368.6947 | -0.0035045
221 |  | 3.3593 | 28.5579 | 4187 | 0.0020304 | 6.4528 | 6.4548 | -1.7258 | 492.5185 | 6397.2526 | -0.0035041
222 |  | 3.3593 | 28.5544 | 4187 | 0.0020301 | 6.4548 | 6.4569 | -1.7258 | 492.579 | 6425.8069 | -0.0035037
223 |  | 3.3593 | 28.5509 | 4187 | 0.0020299 | 6.4569 | 6.4589 | -1.7258 | 492.6394 | 6454.3578 | -0.0035033
224 |  | 3.3593 | 28.5474 | 4187 | 0.0020296 | 6.4589 | 6.4609 | -1.7258 | 492.6999 | 6482.9051 | -0.0035028
225 |  | 3.3593 | 28.5439 | 4187 | 0.0020294 | 6.4609 | 6.4629 | -1.7258 | 492.7603 | 6511.449 | -0.0035024
226 |  | 3.3593 | 28.5404 | 4187 | 0.0020291 | 6.4629 | 6.465 | -1.7258 | 492.8208 | 6539.9893 | -0.003502
227 |  | 3.3593 | 28.5368 | 4187 | 0.0020289 | 6.465 | 6.467 | -1.7258 | 492.8813 | 6568.5262 | -0.0035015
228 |  | 3.3593 | 28.5333 | 4187 | 0.0020286 | 6.467 | 6.469 | -1.7258 | 492.9418 | 6597.0595 | -0.0035011
229 |  | 3.3593 | 28.5298 | 4187 | 0.0020284 | 6.469 | 6.4711 | -1.7258 | 493.0023 | 6625.5894 | -0.0035007
230 |  | 3.3593 | 28.5263 | 4187 | 0.0020281 | 6.4711 | 6.4731 | -1.7258 | 493.0628 | 6654.1157 | -0.0035002
231 |  | 3.3593 | 28.5228 | 4187 | 0.0020279 | 6.4731 | 6.4751 | -1.7258 | 493.1233 | 6682.6386 | -0.0034998
232 |  | 3.3593 | 28.5193 | 4187 | 0.0020276 | 6.4751 | 6.4771 | -1.7258 | 493.1838 | 6711.1579 | -0.0034994
233 |  | 3.3593 | 28.5158 | 4187 | 0.0020274 | 6.4771 | 6.4792 | -1.7258 | 493.2443 | 6739.6738 | -0.003499
234 |  | 3.3593 | 28.5123 | 4187 | 0.0020271 | 6.4792 | 6.4812 | -1.7258 | 493.3048 | 6768.1861 | -0.0034985
235 |  | 3.3593 | 28.5088 | 4187 | 0.0020269 | 6.4812 | 6.4832 | -1.7258 | 493.3654 | 6796.695 | -0.0034981
236 |  | 3.3593 | 28.5054 | 4187 | 0.0020266 | 6.4832 | 6.4853 | -1.7258 | 493.4259 | 6825.2003 | -0.0034977

## Fus110
|  |  | buis | verlies W/M | L /°C/sec
diam | wandikte |  | inhoud l/m |  | W/M
110 | 15.1 | 3.1416 | 5.0014 | 31.6308 | 4187
[8 empty] | J/sec/mtr | aantal mtr. | verlies
|  | buis | verlies W/M | L /°C/sec | verlies temp | begintemp | eindtemp | verlies | bij 1°C | totaal J/sec
|  | inhoud L |  | W/M | °C per M | °C | °C | per m°C | daling | aantal mtr
1 | 110 | 5.0014 | 31.6308 | 4187 | 0.0015105 | 6 | 6.0015 | -1.8606 | 662.0456 | 31.6308 | -0.0028104
2 |  | 5.0014 | 31.628 | 4187 | 0.0015103 | 6.0015 | 6.003 | -1.8606 | 662.1045 | 63.2589 | -0.0028102
3 |  | 5.0014 | 31.6252 | 4187 | 0.0015102 | 6.003 | 6.0045 | -1.8606 | 662.1633 | 94.8841 | -0.0028099
4 |  | 5.0014 | 31.6224 | 4187 | 0.0015101 | 6.0045 | 6.006 | -1.8606 | 662.2221 | 126.5065 | -0.0028097
5 |  | 5.0014 | 31.6196 | 4187 | 0.0015099 | 6.006 | 6.0076 | -1.8606 | 662.281 | 158.1261 | -0.0028094
6 |  | 5.0014 | 31.6168 | 4187 | 0.0015098 | 6.0076 | 6.0091 | -1.8606 | 662.3398 | 189.7429 | -0.0028092
7 |  | 5.0014 | 31.614 | 4187 | 0.0015097 | 6.0091 | 6.0106 | -1.8606 | 662.3987 | 221.3569 | -0.0028089
8 |  | 5.0014 | 31.6112 | 4187 | 0.0015095 | 6.0106 | 6.0121 | -1.8606 | 662.4575 | 252.968 | -0.0028087
9 |  | 5.0014 | 31.6084 | 4187 | 0.0015094 | 6.0121 | 6.0136 | -1.8606 | 662.5164 | 284.5764 | -0.0028084
10 |  | 5.0014 | 31.6056 | 4187 | 0.0015093 | 6.0136 | 6.0151 | -1.8606 | 662.5753 | 316.1819 | -0.0028082
11 |  | 5.0014 | 31.6027 | 4187 | 0.0015091 | 6.0151 | 6.0166 | -1.8606 | 662.6342 | 347.7847 | -0.0028079
12 |  | 5.0014 | 31.5999 | 4187 | 0.001509 | 6.0166 | 6.0181 | -1.8606 | 662.693 | 379.3846 | -0.0028077
13 |  | 5.0014 | 31.5971 | 4187 | 0.0015089 | 6.0181 | 6.0196 | -1.8606 | 662.7519 | 410.9818 | -0.0028074
14 |  | 5.0014 | 31.5943 | 4187 | 0.0015087 | 6.0196 | 6.0211 | -1.8606 | 662.8108 | 442.5761 | -0.0028072
15 |  | 5.0014 | 31.5915 | 4187 | 0.0015086 | 6.0211 | 6.0226 | -1.8606 | 662.8697 | 474.1676 | -0.0028069
16 |  | 5.0014 | 31.5887 | 4187 | 0.0015085 | 6.0226 | 6.0242 | -1.8606 | 662.9286 | 505.7563 | -0.0028067
17 |  | 5.0014 | 31.5859 | 4187 | 0.0015083 | 6.0242 | 6.0257 | -1.8606 | 662.9875 | 537.3422 | -0.0028064
18 |  | 5.0014 | 31.5831 | 4187 | 0.0015082 | 6.0257 | 6.0272 | -1.8606 | 663.0464 | 568.9253 | -0.0028062
19 |  | 5.0014 | 31.5803 | 4187 | 0.0015081 | 6.0272 | 6.0287 | -1.8606 | 663.1053 | 600.5056 | -0.0028059
20 |  | 5.0014 | 31.5775 | 4187 | 0.0015079 | 6.0287 | 6.0302 | -1.8606 | 663.1643 | 632.0831 | -0.0028057
21 |  | 5.0014 | 31.5747 | 4187 | 0.0015078 | 6.0302 | 6.0317 | -1.8606 | 663.2232 | 663.6577 | -0.0028054
22 |  | 5.0014 | 31.5719 | 4187 | 0.0015077 | 6.0317 | 6.0332 | -1.8606 | 663.2821 | 695.2296 | -0.0028052
23 |  | 5.0014 | 31.5691 | 4187 | 0.0015075 | 6.0332 | 6.0347 | -1.8606 | 663.3411 | 726.7987 | -0.0028049
24 |  | 5.0014 | 31.5663 | 4187 | 0.0015074 | 6.0347 | 6.0362 | -1.8606 | 663.4 | 758.3649 | -0.0028047
25 |  | 5.0014 | 31.5635 | 4187 | 0.0015073 | 6.0362 | 6.0377 | -1.8606 | 663.459 | 789.9284 | -0.0028045
26 |  | 5.0014 | 31.5607 | 4187 | 0.0015071 | 6.0377 | 6.0392 | -1.8606 | 663.5179 | 821.4891 | -0.0028042
27 |  | 5.0014 | 31.5578 | 4187 | 0.001507 | 6.0392 | 6.0407 | -1.8606 | 663.5769 | 853.0469 | -0.002804
28 |  | 5.0014 | 31.555 | 4187 | 0.0015069 | 6.0407 | 6.0422 | -1.8606 | 663.6358 | 884.6019 | -0.0028037
29 |  | 5.0014 | 31.5522 | 4187 | 0.0015067 | 6.0422 | 6.0437 | -1.8606 | 663.6948 | 916.1542 | -0.0028035
30 |  | 5.0014 | 31.5494 | 4187 | 0.0015066 | 6.0437 | 6.0453 | -1.8606 | 663.7538 | 947.7036 | -0.0028032
31 |  | 5.0014 | 31.5466 | 4187 | 0.0015064 | 6.0453 | 6.0468 | -1.8606 | 663.8128 | 979.2503 | -0.002803
32 |  | 5.0014 | 31.5438 | 4187 | 0.0015063 | 6.0468 | 6.0483 | -1.8606 | 663.8718 | 1010.7941 | -0.0028027
33 |  | 5.0014 | 31.541 | 4187 | 0.0015062 | 6.0483 | 6.0498 | -1.8606 | 663.9307 | 1042.3351 | -0.0028025
34 |  | 5.0014 | 31.5382 | 4187 | 0.001506 | 6.0498 | 6.0513 | -1.8606 | 663.9897 | 1073.8733 | -0.0028022
35 |  | 5.0014 | 31.5354 | 4187 | 0.0015059 | 6.0513 | 6.0528 | -1.8606 | 664.0487 | 1105.4088 | -0.002802
36 |  | 5.0014 | 31.5326 | 4187 | 0.0015058 | 6.0528 | 6.0543 | -1.8606 | 664.1078 | 1136.9414 | -0.0028017
37 |  | 5.0014 | 31.5298 | 4187 | 0.0015056 | 6.0543 | 6.0558 | -1.8606 | 664.1668 | 1168.4712 | -0.0028015
38 |  | 5.0014 | 31.527 | 4187 | 0.0015055 | 6.0558 | 6.0573 | -1.8606 | 664.2258 | 1199.9982 | -0.0028012
39 |  | 5.0014 | 31.5242 | 4187 | 0.0015054 | 6.0573 | 6.0588 | -1.8606 | 664.2848 | 1231.5224 | -0.002801
40 |  | 5.0014 | 31.5214 | 4187 | 0.0015052 | 6.0588 | 6.0603 | -1.8606 | 664.3438 | 1263.0439 | -0.0028007
41 |  | 5.0014 | 31.5186 | 4187 | 0.0015051 | 6.0603 | 6.0618 | -1.8606 | 664.4029 | 1294.5625 | -0.0028005
42 |  | 5.0014 | 31.5158 | 4187 | 0.001505 | 6.0618 | 6.0633 | -1.8606 | 664.4619 | 1326.0783 | -0.0028002
43 |  | 5.0014 | 31.513 | 4187 | 0.0015048 | 6.0633 | 6.0648 | -1.8606 | 664.5209 | 1357.5913 | -0.0028
44 |  | 5.0014 | 31.5102 | 4187 | 0.0015047 | 6.0648 | 6.0663 | -1.8606 | 664.58 | 1389.1015 | -0.0027997
45 |  | 5.0014 | 31.5074 | 4187 | 0.0015046 | 6.0663 | 6.0678 | -1.8606 | 664.639 | 1420.6089 | -0.0027995
46 |  | 5.0014 | 31.5046 | 4187 | 0.0015044 | 6.0678 | 6.0693 | -1.8606 | 664.6981 | 1452.1135 | -0.0027992
47 |  | 5.0014 | 31.5018 | 4187 | 0.0015043 | 6.0693 | 6.0708 | -1.8606 | 664.7572 | 1483.6154 | -0.002799
48 |  | 5.0014 | 31.499 | 4187 | 0.0015042 | 6.0708 | 6.0724 | -1.8606 | 664.8162 | 1515.1144 | -0.0027987
49 |  | 5.0014 | 31.4962 | 4187 | 0.001504 | 6.0724 | 6.0739 | -1.8606 | 664.8753 | 1546.6106 | -0.0027985
50 |  | 5.0014 | 31.4934 | 4187 | 0.0015039 | 6.0739 | 6.0754 | -1.8606 | 664.9344 | 1578.104 | -0.0027982
51 |  | 5.0014 | 31.4906 | 4187 | 0.0015038 | 6.0754 | 6.0769 | -1.8606 | 664.9935 | 1609.5946 | -0.002798
52 |  | 5.0014 | 31.4878 | 4187 | 0.0015036 | 6.0769 | 6.0784 | -1.8606 | 665.0526 | 1641.0825 | -0.0027977
53 |  | 5.0014 | 31.485 | 4187 | 0.0015035 | 6.0784 | 6.0799 | -1.8606 | 665.1117 | 1672.5675 | -0.0027975
54 |  | 5.0014 | 31.4822 | 4187 | 0.0015034 | 6.0799 | 6.0814 | -1.8606 | 665.1708 | 1704.0497 | -0.0027972
55 |  | 5.0014 | 31.4794 | 4187 | 0.0015032 | 6.0814 | 6.0829 | -1.8606 | 665.2299 | 1735.5291 | -0.002797
56 |  | 5.0014 | 31.4766 | 4187 | 0.0015031 | 6.0829 | 6.0844 | -1.8606 | 665.289 | 1767.0058 | -0.0027967
57 |  | 5.0014 | 31.4738 | 4187 | 0.001503 | 6.0844 | 6.0859 | -1.8606 | 665.3481 | 1798.4796 | -0.0027965
58 |  | 5.0014 | 31.471 | 4187 | 0.0015028 | 6.0859 | 6.0874 | -1.8606 | 665.4072 | 1829.9507 | -0.0027962
59 |  | 5.0014 | 31.4682 | 4187 | 0.0015027 | 6.0874 | 6.0889 | -1.8606 | 665.4664 | 1861.4189 | -0.002796
60 |  | 5.0014 | 31.4654 | 4187 | 0.0015026 | 6.0889 | 6.0904 | -1.8606 | 665.5255 | 1892.8844 | -0.0027957
61 |  | 5.0014 | 31.4627 | 4187 | 0.0015024 | 6.0904 | 6.0919 | -1.8606 | 665.5846 | 1924.347 | -0.0027955
62 |  | 5.0014 | 31.4599 | 4187 | 0.0015023 | 6.0919 | 6.0934 | -1.8606 | 665.6438 | 1955.8069 | -0.0027952
63 |  | 5.0014 | 31.4571 | 4187 | 0.0015022 | 6.0934 | 6.0949 | -1.8606 | 665.7029 | 1987.2639 | -0.002795
64 |  | 5.0014 | 31.4543 | 4187 | 0.001502 | 6.0949 | 6.0964 | -1.8606 | 665.7621 | 2018.7182 | -0.0027947
65 |  | 5.0014 | 31.4515 | 4187 | 0.0015019 | 6.0964 | 6.0979 | -1.8606 | 665.8212 | 2050.1697 | -0.0027945
66 |  | 5.0014 | 31.4487 | 4187 | 0.0015018 | 6.0979 | 6.0994 | -1.8606 | 665.8804 | 2081.6183 | -0.0027943
67 |  | 5.0014 | 31.4459 | 4187 | 0.0015016 | 6.0994 | 6.1009 | -1.8606 | 665.9396 | 2113.0642 | -0.002794
68 |  | 5.0014 | 31.4431 | 4187 | 0.0015015 | 6.1009 | 6.1024 | -1.8606 | 665.9987 | 2144.5073 | -0.0027938
69 |  | 5.0014 | 31.4403 | 4187 | 0.0015014 | 6.1024 | 6.1039 | -1.8606 | 666.0579 | 2175.9476 | -0.0027935
70 |  | 5.0014 | 31.4375 | 4187 | 0.0015012 | 6.1039 | 6.1054 | -1.8606 | 666.1171 | 2207.3851 | -0.0027933
71 |  | 5.0014 | 31.4347 | 4187 | 0.0015011 | 6.1054 | 6.1069 | -1.8606 | 666.1763 | 2238.8198 | -0.002793
72 |  | 5.0014 | 31.4319 | 4187 | 0.001501 | 6.1069 | 6.1084 | -1.8606 | 666.2355 | 2270.2517 | -0.0027928
73 |  | 5.0014 | 31.4291 | 4187 | 0.0015008 | 6.1084 | 6.1099 | -1.8606 | 666.2947 | 2301.6809 | -0.0027925
74 |  | 5.0014 | 31.4263 | 4187 | 0.0015007 | 6.1099 | 6.1114 | -1.8606 | 666.3539 | 2333.1072 | -0.0027923
75 |  | 5.0014 | 31.4235 | 4187 | 0.0015006 | 6.1114 | 6.1129 | -1.8606 | 666.4131 | 2364.5307 | -0.002792
76 |  | 5.0014 | 31.4207 | 4187 | 0.0015004 | 6.1129 | 6.1144 | -1.8606 | 666.4723 | 2395.9515 | -0.0027918
77 |  | 5.0014 | 31.418 | 4187 | 0.0015003 | 6.1144 | 6.1159 | -1.8606 | 666.5315 | 2427.3694 | -0.0027915
78 |  | 5.0014 | 31.4152 | 4187 | 0.0015002 | 6.1159 | 6.1174 | -1.8606 | 666.5908 | 2458.7846 | -0.0027913
79 |  | 5.0014 | 31.4124 | 4187 | 0.0015 | 6.1174 | 6.1189 | -1.8606 | 666.65 | 2490.197 | -0.002791
80 |  | 5.0014 | 31.4096 | 4187 | 0.0014999 | 6.1189 | 6.1204 | -1.8606 | 666.7092 | 2521.6066 | -0.0027908
81 |  | 5.0014 | 31.4068 | 4187 | 0.0014998 | 6.1204 | 6.1219 | -1.8606 | 666.7685 | 2553.0134 | -0.0027905
82 |  | 5.0014 | 31.404 | 4187 | 0.0014996 | 6.1219 | 6.1234 | -1.8606 | 666.8277 | 2584.4174 | -0.0027903
83 |  | 5.0014 | 31.4012 | 4187 | 0.0014995 | 6.1234 | 6.1249 | -1.8606 | 666.887 | 2615.8186 | -0.00279
84 |  | 5.0014 | 31.3984 | 4187 | 0.0014994 | 6.1249 | 6.1264 | -1.8606 | 666.9462 | 2647.217 | -0.0027898
85 |  | 5.0014 | 31.3956 | 4187 | 0.0014992 | 6.1264 | 6.1279 | -1.8606 | 667.0055 | 2678.6126 | -0.0027895
86 |  | 5.0014 | 31.3928 | 4187 | 0.0014991 | 6.1279 | 6.1294 | -1.8606 | 667.0648 | 2710.0055 | -0.0027893
87 |  | 5.0014 | 31.3901 | 4187 | 0.001499 | 6.1294 | 6.1309 | -1.8606 | 667.1241 | 2741.3955 | -0.002789
88 |  | 5.0014 | 31.3873 | 4187 | 0.0014988 | 6.1309 | 6.1324 | -1.8606 | 667.1833 | 2772.7828 | -0.0027888
89 |  | 5.0014 | 31.3845 | 4187 | 0.0014987 | 6.1324 | 6.1339 | -1.8606 | 667.2426 | 2804.1672 | -0.0027885
90 |  | 5.0014 | 31.3817 | 4187 | 0.0014986 | 6.1339 | 6.1354 | -1.8606 | 667.3019 | 2835.5489 | -0.0027883
91 |  | 5.0014 | 31.3789 | 4187 | 0.0014984 | 6.1354 | 6.1369 | -1.8606 | 667.3612 | 2866.9278 | -0.0027881
92 |  | 5.0014 | 31.3761 | 4187 | 0.0014983 | 6.1369 | 6.1384 | -1.8606 | 667.4205 | 2898.3039 | -0.0027878
93 |  | 5.0014 | 31.3733 | 4187 | 0.0014982 | 6.1384 | 6.1399 | -1.8606 | 667.4798 | 2929.6772 | -0.0027876
94 |  | 5.0014 | 31.3705 | 4187 | 0.001498 | 6.1399 | 6.1414 | -1.8606 | 667.5391 | 2961.0478 | -0.0027873
95 |  | 5.0014 | 31.3677 | 4187 | 0.0014979 | 6.1414 | 6.1429 | -1.8606 | 667.5984 | 2992.4155 | -0.0027871
96 |  | 5.0014 | 31.365 | 4187 | 0.0014978 | 6.1429 | 6.1444 | -1.8606 | 667.6578 | 3023.7805 | -0.0027868
97 |  | 5.0014 | 31.3622 | 4187 | 0.0014976 | 6.1444 | 6.1459 | -1.8606 | 667.7171 | 3055.1427 | -0.0027866
98 |  | 5.0014 | 31.3594 | 4187 | 0.0014975 | 6.1459 | 6.1474 | -1.8606 | 667.7764 | 3086.502 | -0.0027863
99 |  | 5.0014 | 31.3566 | 4187 | 0.0014974 | 6.1474 | 6.1489 | -1.8606 | 667.8358 | 3117.8586 | -0.0027861
100 |  | 5.0014 | 31.3538 | 4187 | 0.0014972 | 6.1489 | 6.1504 | -1.8606 | 667.8951 | 3149.2125 | -0.0027858
101 |  | 5.0014 | 31.351 | 4187 | 0.0014971 | 6.1504 | 6.1519 | -1.8606 | 667.9545 | 3180.5635 | -0.0027856
102 |  | 5.0014 | 31.3482 | 4187 | 0.001497 | 6.1519 | 6.1534 | -1.8606 | 668.0138 | 3211.9117 | -0.0027853
103 |  | 5.0014 | 31.3455 | 4187 | 0.0014968 | 6.1534 | 6.1549 | -1.8606 | 668.0732 | 3243.2572 | -0.0027851
104 |  | 5.0014 | 31.3427 | 4187 | 0.0014967 | 6.1549 | 6.1564 | -1.8606 | 668.1325 | 3274.5999 | -0.0027848
105 |  | 5.0014 | 31.3399 | 4187 | 0.0014966 | 6.1564 | 6.1579 | -1.8606 | 668.1919 | 3305.9397 | -0.0027846
106 |  | 5.0014 | 31.3371 | 4187 | 0.0014964 | 6.1579 | 6.1594 | -1.8606 | 668.2513 | 3337.2768 | -0.0027843
107 |  | 5.0014 | 31.3343 | 4187 | 0.0014963 | 6.1594 | 6.1609 | -1.8606 | 668.3107 | 3368.6112 | -0.0027841
108 |  | 5.0014 | 31.3315 | 4187 | 0.0014962 | 6.1609 | 6.1624 | -1.8606 | 668.37 | 3399.9427 | -0.0027838
109 |  | 5.0014 | 31.3287 | 4187 | 0.001496 | 6.1624 | 6.1639 | -1.8606 | 668.4294 | 3431.2714 | -0.0027836
110 |  | 5.0014 | 31.326 | 4187 | 0.0014959 | 6.1639 | 6.1653 | -1.8606 | 668.4888 | 3462.5974 | -0.0027833
111 |  | 5.0014 | 31.3232 | 4187 | 0.0014958 | 6.1653 | 6.1668 | -1.8606 | 668.5482 | 3493.9206 | -0.0027831
112 |  | 5.0014 | 31.3204 | 4187 | 0.0014956 | 6.1668 | 6.1683 | -1.8606 | 668.6076 | 3525.241 | -0.0027829
113 |  | 5.0014 | 31.3176 | 4187 | 0.0014955 | 6.1683 | 6.1698 | -1.8606 | 668.6671 | 3556.5586 | -0.0027826
114 |  | 5.0014 | 31.3148 | 4187 | 0.0014954 | 6.1698 | 6.1713 | -1.8606 | 668.7265 | 3587.8734 | -0.0027824
115 |  | 5.0014 | 31.3121 | 4187 | 0.0014952 | 6.1713 | 6.1728 | -1.8606 | 668.7859 | 3619.1855 | -0.0027821
116 |  | 5.0014 | 31.3093 | 4187 | 0.0014951 | 6.1728 | 6.1743 | -1.8606 | 668.8453 | 3650.4948 | -0.0027819
117 |  | 5.0014 | 31.3065 | 4187 | 0.001495 | 6.1743 | 6.1758 | -1.8606 | 668.9048 | 3681.8012 | -0.0027816
118 |  | 5.0014 | 31.3037 | 4187 | 0.0014948 | 6.1758 | 6.1773 | -1.8606 | 668.9642 | 3713.105 | -0.0027814
119 |  | 5.0014 | 31.3009 | 4187 | 0.0014947 | 6.1773 | 6.1788 | -1.8606 | 669.0236 | 3744.4059 | -0.0027811
120 |  | 5.0014 | 31.2981 | 4187 | 0.0014946 | 6.1788 | 6.1803 | -1.8606 | 669.0831 | 3775.704 | -0.0027809
121 |  | 5.0014 | 31.2954 | 4187 | 0.0014944 | 6.1803 | 6.1818 | -1.8606 | 669.1425 | 3806.9994 | -0.0027806
122 |  | 5.0014 | 31.2926 | 4187 | 0.0014943 | 6.1818 | 6.1833 | -1.8606 | 669.202 | 3838.292 | -0.0027804
123 |  | 5.0014 | 31.2898 | 4187 | 0.0014942 | 6.1833 | 6.1848 | -1.8606 | 669.2615 | 3869.5818 | -0.0027801
124 |  | 5.0014 | 31.287 | 4187 | 0.0014941 | 6.1848 | 6.1863 | -1.8606 | 669.3209 | 3900.8688 | -0.0027799
125 |  | 5.0014 | 31.2842 | 4187 | 0.0014939 | 6.1863 | 6.1878 | -1.8606 | 669.3804 | 3932.153 | -0.0027796
126 |  | 5.0014 | 31.2815 | 4187 | 0.0014938 | 6.1878 | 6.1893 | -1.8606 | 669.4399 | 3963.4345 | -0.0027794
127 |  | 5.0014 | 31.2787 | 4187 | 0.0014937 | 6.1893 | 6.1908 | -1.8606 | 669.4994 | 3994.7132 | -0.0027791
128 |  | 5.0014 | 31.2759 | 4187 | 0.0014935 | 6.1908 | 6.1923 | -1.8606 | 669.5589 | 4025.9891 | -0.0027789
129 |  | 5.0014 | 31.2731 | 4187 | 0.0014934 | 6.1923 | 6.1937 | -1.8606 | 669.6184 | 4057.2622 | -0.0027787
130 |  | 5.0014 | 31.2703 | 4187 | 0.0014933 | 6.1937 | 6.1952 | -1.8606 | 669.6779 | 4088.5325 | -0.0027784
131 |  | 5.0014 | 31.2676 | 4187 | 0.0014931 | 6.1952 | 6.1967 | -1.8606 | 669.7374 | 4119.8001 | -0.0027782
132 |  | 5.0014 | 31.2648 | 4187 | 0.001493 | 6.1967 | 6.1982 | -1.8606 | 669.7969 | 4151.0649 | -0.0027779
133 |  | 5.0014 | 31.262 | 4187 | 0.0014929 | 6.1982 | 6.1997 | -1.8606 | 669.8564 | 4182.3269 | -0.0027777
134 |  | 5.0014 | 31.2592 | 4187 | 0.0014927 | 6.1997 | 6.2012 | -1.8606 | 669.9159 | 4213.5861 | -0.0027774
135 |  | 5.0014 | 31.2565 | 4187 | 0.0014926 | 6.2012 | 6.2027 | -1.8606 | 669.9754 | 4244.8426 | -0.0027772
136 |  | 5.0014 | 31.2537 | 4187 | 0.0014925 | 6.2027 | 6.2042 | -1.8606 | 670.035 | 4276.0963 | -0.0027769
137 |  | 5.0014 | 31.2509 | 4187 | 0.0014923 | 6.2042 | 6.2057 | -1.8606 | 670.0945 | 4307.3472 | -0.0027767
138 |  | 5.0014 | 31.2481 | 4187 | 0.0014922 | 6.2057 | 6.2072 | -1.8606 | 670.1541 | 4338.5953 | -0.0027764
139 |  | 5.0014 | 31.2453 | 4187 | 0.0014921 | 6.2072 | 6.2087 | -1.8606 | 670.2136 | 4369.8407 | -0.0027762
140 |  | 5.0014 | 31.2426 | 4187 | 0.0014919 | 6.2087 | 6.2102 | -1.8606 | 670.2732 | 4401.0832 | -0.0027759
141 |  | 5.0014 | 31.2398 | 4187 | 0.0014918 | 6.2102 | 6.2117 | -1.8606 | 670.3327 | 4432.323 | -0.0027757
142 |  | 5.0014 | 31.237 | 4187 | 0.0014917 | 6.2117 | 6.2131 | -1.8606 | 670.3923 | 4463.56 | -0.0027754
143 |  | 5.0014 | 31.2342 | 4187 | 0.0014915 | 6.2131 | 6.2146 | -1.8606 | 670.4519 | 4494.7943 | -0.0027752
144 |  | 5.0014 | 31.2315 | 4187 | 0.0014914 | 6.2146 | 6.2161 | -1.8606 | 670.5114 | 4526.0258 | -0.002775
145 |  | 5.0014 | 31.2287 | 4187 | 0.0014913 | 6.2161 | 6.2176 | -1.8606 | 670.571 | 4557.2545 | -0.0027747
146 |  | 5.0014 | 31.2259 | 4187 | 0.0014911 | 6.2176 | 6.2191 | -1.8606 | 670.6306 | 4588.4804 | -0.0027745
147 |  | 5.0014 | 31.2231 | 4187 | 0.001491 | 6.2191 | 6.2206 | -1.8606 | 670.6902 | 4619.7035 | -0.0027742
148 |  | 5.0014 | 31.2204 | 4187 | 0.0014909 | 6.2206 | 6.2221 | -1.8606 | 670.7498 | 4650.9239 | -0.002774
149 |  | 5.0014 | 31.2176 | 4187 | 0.0014907 | 6.2221 | 6.2236 | -1.8606 | 670.8094 | 4682.1415 | -0.0027737
150 |  | 5.0014 | 31.2148 | 4187 | 0.0014906 | 6.2236 | 6.2251 | -1.8606 | 670.869 | 4713.3563 | -0.0027735
151 |  | 5.0014 | 31.2121 | 4187 | 0.0014905 | 6.2251 | 6.2266 | -1.8606 | 670.9286 | 4744.5684 | -0.0027732
152 |  | 5.0014 | 31.2093 | 4187 | 0.0014903 | 6.2266 | 6.2281 | -1.8606 | 670.9882 | 4775.7777 | -0.002773
153 |  | 5.0014 | 31.2065 | 4187 | 0.0014902 | 6.2281 | 6.2295 | -1.8606 | 671.0479 | 4806.9842 | -0.0027727
154 |  | 5.0014 | 31.2037 | 4187 | 0.0014901 | 6.2295 | 6.231 | -1.8606 | 671.1075 | 4838.1879 | -0.0027725
155 |  | 5.0014 | 31.201 | 4187 | 0.0014899 | 6.231 | 6.2325 | -1.8606 | 671.1671 | 4869.3888 | -0.0027722
156 |  | 5.0014 | 31.1982 | 4187 | 0.0014898 | 6.2325 | 6.234 | -1.8606 | 671.2268 | 4900.587 | -0.002772
157 |  | 5.0014 | 31.1954 | 4187 | 0.0014897 | 6.234 | 6.2355 | -1.8606 | 671.2864 | 4931.7825 | -0.0027717
158 |  | 5.0014 | 31.1926 | 4187 | 0.0014895 | 6.2355 | 6.237 | -1.8606 | 671.3461 | 4962.9751 | -0.0027715
159 |  | 5.0014 | 31.1899 | 4187 | 0.0014894 | 6.237 | 6.2385 | -1.8606 | 671.4057 | 4994.165 | -0.0027713
160 |  | 5.0014 | 31.1871 | 4187 | 0.0014893 | 6.2385 | 6.24 | -1.8606 | 671.4654 | 5025.3521 | -0.002771
161 |  | 5.0014 | 31.1843 | 4187 | 0.0014891 | 6.24 | 6.2415 | -1.8606 | 671.525 | 5056.5364 | -0.0027708
162 |  | 5.0014 | 31.1816 | 4187 | 0.001489 | 6.2415 | 6.243 | -1.8606 | 671.5847 | 5087.718 | -0.0027705
163 |  | 5.0014 | 31.1788 | 4187 | 0.0014889 | 6.243 | 6.2444 | -1.8606 | 671.6444 | 5118.8967 | -0.0027703
164 |  | 5.0014 | 31.176 | 4187 | 0.0014888 | 6.2444 | 6.2459 | -1.8606 | 671.7041 | 5150.0728 | -0.00277
165 |  | 5.0014 | 31.1732 | 4187 | 0.0014886 | 6.2459 | 6.2474 | -1.8606 | 671.7638 | 5181.246 | -0.0027698
166 |  | 5.0014 | 31.1705 | 4187 | 0.0014885 | 6.2474 | 6.2489 | -1.8606 | 671.8234 | 5212.4165 | -0.0027695
167 |  | 5.0014 | 31.1677 | 4187 | 0.0014884 | 6.2489 | 6.2504 | -1.8606 | 671.8831 | 5243.5842 | -0.0027693
168 |  | 5.0014 | 31.1649 | 4187 | 0.0014882 | 6.2504 | 6.2519 | -1.8606 | 671.9428 | 5274.7491 | -0.002769
169 |  | 5.0014 | 31.1622 | 4187 | 0.0014881 | 6.2519 | 6.2534 | -1.8606 | 672.0026 | 5305.9113 | -0.0027688
170 |  | 5.0014 | 31.1594 | 4187 | 0.001488 | 6.2534 | 6.2549 | -1.8606 | 672.0623 | 5337.0707 | -0.0027685
171 |  | 5.0014 | 31.1566 | 4187 | 0.0014878 | 6.2549 | 6.2563 | -1.8606 | 672.122 | 5368.2273 | -0.0027683
172 |  | 5.0014 | 31.1539 | 4187 | 0.0014877 | 6.2563 | 6.2578 | -1.8606 | 672.1817 | 5399.3812 | -0.0027681
173 |  | 5.0014 | 31.1511 | 4187 | 0.0014876 | 6.2578 | 6.2593 | -1.8606 | 672.2414 | 5430.5323 | -0.0027678
174 |  | 5.0014 | 31.1483 | 4187 | 0.0014874 | 6.2593 | 6.2608 | -1.8606 | 672.3012 | 5461.6806 | -0.0027676
175 |  | 5.0014 | 31.1456 | 4187 | 0.0014873 | 6.2608 | 6.2623 | -1.8606 | 672.3609 | 5492.8262 | -0.0027673
176 |  | 5.0014 | 31.1428 | 4187 | 0.0014872 | 6.2623 | 6.2638 | -1.8606 | 672.4207 | 5523.969 | -0.0027671
177 |  | 5.0014 | 31.14 | 4187 | 0.001487 | 6.2638 | 6.2653 | -1.8606 | 672.4804 | 5555.109 | -0.0027668
178 |  | 5.0014 | 31.1373 | 4187 | 0.0014869 | 6.2653 | 6.2668 | -1.8606 | 672.5402 | 5586.2463 | -0.0027666
179 |  | 5.0014 | 31.1345 | 4187 | 0.0014868 | 6.2668 | 6.2682 | -1.8606 | 672.5999 | 5617.3808 | -0.0027663
180 |  | 5.0014 | 31.1317 | 4187 | 0.0014866 | 6.2682 | 6.2697 | -1.8606 | 672.6597 | 5648.5125 | -0.0027661
181 |  | 5.0014 | 31.129 | 4187 | 0.0014865 | 6.2697 | 6.2712 | -1.8606 | 672.7195 | 5679.6415 | -0.0027658
182 |  | 5.0014 | 31.1262 | 4187 | 0.0014864 | 6.2712 | 6.2727 | -1.8606 | 672.7792 | 5710.7677 | -0.0027656
183 |  | 5.0014 | 31.1234 | 4187 | 0.0014862 | 6.2727 | 6.2742 | -1.8606 | 672.839 | 5741.8911 | -0.0027654
184 |  | 5.0014 | 31.1207 | 4187 | 0.0014861 | 6.2742 | 6.2757 | -1.8606 | 672.8988 | 5773.0118 | -0.0027651
185 |  | 5.0014 | 31.1179 | 4187 | 0.001486 | 6.2757 | 6.2772 | -1.8606 | 672.9586 | 5804.1297 | -0.0027649
186 |  | 5.0014 | 31.1151 | 4187 | 0.0014858 | 6.2772 | 6.2787 | -1.8606 | 673.0184 | 5835.2448 | -0.0027646
187 |  | 5.0014 | 31.1124 | 4187 | 0.0014857 | 6.2787 | 6.2801 | -1.8606 | 673.0782 | 5866.3572 | -0.0027644
188 |  | 5.0014 | 31.1096 | 4187 | 0.0014856 | 6.2801 | 6.2816 | -1.8606 | 673.138 | 5897.4668 | -0.0027641
189 |  | 5.0014 | 31.1068 | 4187 | 0.0014854 | 6.2816 | 6.2831 | -1.8606 | 673.1978 | 5928.5736 | -0.0027639
190 |  | 5.0014 | 31.1041 | 4187 | 0.0014853 | 6.2831 | 6.2846 | -1.8606 | 673.2577 | 5959.6777 | -0.0027636
191 |  | 5.0014 | 31.1013 | 4187 | 0.0014852 | 6.2846 | 6.2861 | -1.8606 | 673.3175 | 5990.779 | -0.0027634
192 |  | 5.0014 | 31.0986 | 4187 | 0.0014851 | 6.2861 | 6.2876 | -1.8606 | 673.3773 | 6021.8775 | -0.0027631
193 |  | 5.0014 | 31.0958 | 4187 | 0.0014849 | 6.2876 | 6.289 | -1.8606 | 673.4371 | 6052.9733 | -0.0027629
194 |  | 5.0014 | 31.093 | 4187 | 0.0014848 | 6.289 | 6.2905 | -1.8606 | 673.497 | 6084.0664 | -0.0027627
195 |  | 5.0014 | 31.0903 | 4187 | 0.0014847 | 6.2905 | 6.292 | -1.8606 | 673.5568 | 6115.1566 | -0.0027624
196 |  | 5.0014 | 31.0875 | 4187 | 0.0014845 | 6.292 | 6.2935 | -1.8606 | 673.6167 | 6146.2441 | -0.0027622
197 |  | 5.0014 | 31.0847 | 4187 | 0.0014844 | 6.2935 | 6.295 | -1.8606 | 673.6765 | 6177.3289 | -0.0027619
198 |  | 5.0014 | 31.082 | 4187 | 0.0014843 | 6.295 | 6.2965 | -1.8606 | 673.7364 | 6208.4108 | -0.0027617
199 |  | 5.0014 | 31.0792 | 4187 | 0.0014841 | 6.2965 | 6.298 | -1.8606 | 673.7963 | 6239.49 | -0.0027614
200 |  | 5.0014 | 31.0765 | 4187 | 0.001484 | 6.298 | 6.2994 | -1.8606 | 673.8561 | 6270.5665 | -0.0027612
201 |  | 5.0014 | 31.0737 | 4187 | 0.0014839 | 6.2994 | 6.3009 | -1.8606 | 673.916 | 6301.6402 | -0.0027609
202 |  | 5.0014 | 31.0709 | 4187 | 0.0014837 | 6.3009 | 6.3024 | -1.8606 | 673.9759 | 6332.7111 | -0.0027607
203 |  | 5.0014 | 31.0682 | 4187 | 0.0014836 | 6.3024 | 6.3039 | -1.8606 | 674.0358 | 6363.7793 | -0.0027604
204 |  | 5.0014 | 31.0654 | 4187 | 0.0014835 | 6.3039 | 6.3054 | -1.8606 | 674.0957 | 6394.8447 | -0.0027602
205 |  | 5.0014 | 31.0626 | 4187 | 0.0014833 | 6.3054 | 6.3069 | -1.8606 | 674.1556 | 6425.9073 | -0.00276
206 |  | 5.0014 | 31.0599 | 4187 | 0.0014832 | 6.3069 | 6.3083 | -1.8606 | 674.2155 | 6456.9672 | -0.0027597
207 |  | 5.0014 | 31.0571 | 4187 | 0.0014831 | 6.3083 | 6.3098 | -1.8606 | 674.2754 | 6488.0244 | -0.0027595
208 |  | 5.0014 | 31.0544 | 4187 | 0.0014829 | 6.3098 | 6.3113 | -1.8606 | 674.3353 | 6519.0787 | -0.0027592
209 |  | 5.0014 | 31.0516 | 4187 | 0.0014828 | 6.3113 | 6.3128 | -1.8606 | 674.3952 | 6550.1303 | -0.002759
210 |  | 5.0014 | 31.0489 | 4187 | 0.0014827 | 6.3128 | 6.3143 | -1.8606 | 674.4552 | 6581.1792 | -0.0027587
211 |  | 5.0014 | 31.0461 | 4187 | 0.0014825 | 6.3143 | 6.3158 | -1.8606 | 674.5151 | 6612.2253 | -0.0027585
212 |  | 5.0014 | 31.0433 | 4187 | 0.0014824 | 6.3158 | 6.3172 | -1.8606 | 674.575 | 6643.2686 | -0.0027582
213 |  | 5.0014 | 31.0406 | 4187 | 0.0014823 | 6.3172 | 6.3187 | -1.8606 | 674.635 | 6674.3092 | -0.002758
214 |  | 5.0014 | 31.0378 | 4187 | 0.0014822 | 6.3187 | 6.3202 | -1.8606 | 674.6949 | 6705.347 | -0.0027577
215 |  | 5.0014 | 31.0351 | 4187 | 0.001482 | 6.3202 | 6.3217 | -1.8606 | 674.7549 | 6736.3821 | -0.0027575
216 |  | 5.0014 | 31.0323 | 4187 | 0.0014819 | 6.3217 | 6.3232 | -1.8606 | 674.8148 | 6767.4144 | -0.0027573
217 |  | 5.0014 | 31.0295 | 4187 | 0.0014818 | 6.3232 | 6.3246 | -1.8606 | 674.8748 | 6798.4439 | -0.002757
218 |  | 5.0014 | 31.0268 | 4187 | 0.0014816 | 6.3246 | 6.3261 | -1.8606 | 674.9348 | 6829.4707 | -0.0027568
219 |  | 5.0014 | 31.024 | 4187 | 0.0014815 | 6.3261 | 6.3276 | -1.8606 | 674.9947 | 6860.4947 | -0.0027565
220 |  | 5.0014 | 31.0213 | 4187 | 0.0014814 | 6.3276 | 6.3291 | -1.8606 | 675.0547 | 6891.516 | -0.0027563
221 |  | 5.0014 | 31.0185 | 4187 | 0.0014812 | 6.3291 | 6.3306 | -1.8606 | 675.1147 | 6922.5345 | -0.002756
222 |  | 5.0014 | 31.0158 | 4187 | 0.0014811 | 6.3306 | 6.3321 | -1.8606 | 675.1747 | 6953.5503 | -0.0027558
223 |  | 5.0014 | 31.013 | 4187 | 0.001481 | 6.3321 | 6.3335 | -1.8606 | 675.2347 | 6984.5633 | -0.0027555
224 |  | 5.0014 | 31.0103 | 4187 | 0.0014808 | 6.3335 | 6.335 | -1.8606 | 675.2947 | 7015.5736 | -0.0027553
225 |  | 5.0014 | 31.0075 | 4187 | 0.0014807 | 6.335 | 6.3365 | -1.8606 | 675.3547 | 7046.5811 | -0.0027551
226 |  | 5.0014 | 31.0047 | 4187 | 0.0014806 | 6.3365 | 6.338 | -1.8606 | 675.4147 | 7077.5858 | -0.0027548
227 |  | 5.0014 | 31.002 | 4187 | 0.0014804 | 6.338 | 6.3395 | -1.8606 | 675.4747 | 7108.5878 | -0.0027546
228 |  | 5.0014 | 30.9992 | 4187 | 0.0014803 | 6.3395 | 6.3409 | -1.8606 | 675.5347 | 7139.587 | -0.0027543
229 |  | 5.0014 | 30.9965 | 4187 | 0.0014802 | 6.3409 | 6.3424 | -1.8606 | 675.5948 | 7170.5835 | -0.0027541
230 |  | 5.0014 | 30.9937 | 4187 | 0.00148 | 6.3424 | 6.3439 | -1.8606 | 675.6548 | 7201.5772 | -0.0027538
231 |  | 5.0014 | 30.991 | 4187 | 0.0014799 | 6.3439 | 6.3454 | -1.8606 | 675.7148 | 7232.5682 | -0.0027536
232 |  | 5.0014 | 30.9882 | 4187 | 0.0014798 | 6.3454 | 6.3469 | -1.8606 | 675.7749 | 7263.5564 | -0.0027533
233 |  | 5.0014 | 30.9855 | 4187 | 0.0014797 | 6.3469 | 6.3483 | -1.8606 | 675.8349 | 7294.5419 | -0.0027531
234 |  | 5.0014 | 30.9827 | 4187 | 0.0014795 | 6.3483 | 6.3498 | -1.8606 | 675.895 | 7325.5246 | -0.0027529
235 |  | 5.0014 | 30.98 | 4187 | 0.0014794 | 6.3498 | 6.3513 | -1.8606 | 675.955 | 7356.5045 | -0.0027526
236 |  | 5.0014 | 30.9772 | 4187 | 0.0014793 | 6.3513 | 6.3528 | -1.8606 | 676.0151 | 7387.4817 | -0.0027524

## Fus125
|  |  | buis | verlies W/M | L /°C/sec
diam | wandikte |  | inhoud l/m |  | W/M
125 | 17.1 | 3.1416 | 6.4753 | 33.1749 | 4187
[8 empty] | J/sec/mtr | aantal mtr. | verlies
|  | buis | verlies W/M | L /°C/sec | verlies temp | begintemp | eindtemp | verlies | bij 1°C | totaal J/sec
|  | inhoud L |  | W/M | °C per M | °C | °C | per m°C | daling | aantal mtr
1 | 125 | 6.4753 | 33.1749 | 4187 | 0.0012236 | 6 | 6.0012 | -1.9515 | 817.2494 | 33.1749 | -0.0023878
2 |  | 6.4753 | 33.1725 | 4187 | 0.0012235 | 6.0012 | 6.0024 | -1.9515 | 817.3082 | 66.3475 | -0.0023877
3 |  | 6.4753 | 33.1701 | 4187 | 0.0012234 | 6.0024 | 6.0037 | -1.9515 | 817.367 | 99.5176 | -0.0023875
4 |  | 6.4753 | 33.1678 | 4187 | 0.0012234 | 6.0037 | 6.0049 | -1.9515 | 817.4259 | 132.6854 | -0.0023873
5 |  | 6.4753 | 33.1654 | 4187 | 0.0012233 | 6.0049 | 6.0061 | -1.9515 | 817.4847 | 165.8507 | -0.0023872
6 |  | 6.4753 | 33.163 | 4187 | 0.0012232 | 6.0061 | 6.0073 | -1.9515 | 817.5436 | 199.0137 | -0.002387
7 |  | 6.4753 | 33.1606 | 4187 | 0.0012231 | 6.0073 | 6.0086 | -1.9515 | 817.6024 | 232.1743 | -0.0023868
8 |  | 6.4753 | 33.1582 | 4187 | 0.001223 | 6.0086 | 6.0098 | -1.9515 | 817.6613 | 265.3325 | -0.0023866
9 |  | 6.4753 | 33.1558 | 4187 | 0.0012229 | 6.0098 | 6.011 | -1.9515 | 817.7201 | 298.4884 | -0.0023865
10 |  | 6.4753 | 33.1534 | 4187 | 0.0012228 | 6.011 | 6.0122 | -1.9515 | 817.779 | 331.6418 | -0.0023863
11 |  | 6.4753 | 33.1511 | 4187 | 0.0012227 | 6.0122 | 6.0135 | -1.9515 | 817.8378 | 364.7929 | -0.0023861
12 |  | 6.4753 | 33.1487 | 4187 | 0.0012226 | 6.0135 | 6.0147 | -1.9515 | 817.8967 | 397.9415 | -0.002386
13 |  | 6.4753 | 33.1463 | 4187 | 0.0012226 | 6.0147 | 6.0159 | -1.9515 | 817.9556 | 431.0878 | -0.0023858
14 |  | 6.4753 | 33.1439 | 4187 | 0.0012225 | 6.0159 | 6.0171 | -1.9515 | 818.0145 | 464.2317 | -0.0023856
15 |  | 6.4753 | 33.1415 | 4187 | 0.0012224 | 6.0171 | 6.0183 | -1.9515 | 818.0733 | 497.3732 | -0.0023854
16 |  | 6.4753 | 33.1391 | 4187 | 0.0012223 | 6.0183 | 6.0196 | -1.9515 | 818.1322 | 530.5123 | -0.0023853
17 |  | 6.4753 | 33.1367 | 4187 | 0.0012222 | 6.0196 | 6.0208 | -1.9515 | 818.1911 | 563.6491 | -0.0023851
18 |  | 6.4753 | 33.1344 | 4187 | 0.0012221 | 6.0208 | 6.022 | -1.9515 | 818.25 | 596.7834 | -0.0023849
19 |  | 6.4753 | 33.132 | 4187 | 0.001222 | 6.022 | 6.0232 | -1.9515 | 818.3089 | 629.9154 | -0.0023848
20 |  | 6.4753 | 33.1296 | 4187 | 0.0012219 | 6.0232 | 6.0245 | -1.9515 | 818.3678 | 663.045 | -0.0023846
21 |  | 6.4753 | 33.1272 | 4187 | 0.0012219 | 6.0245 | 6.0257 | -1.9515 | 818.4267 | 696.1722 | -0.0023844
22 |  | 6.4753 | 33.1248 | 4187 | 0.0012218 | 6.0257 | 6.0269 | -1.9515 | 818.4856 | 729.297 | -0.0023842
23 |  | 6.4753 | 33.1224 | 4187 | 0.0012217 | 6.0269 | 6.0281 | -1.9515 | 818.5446 | 762.4194 | -0.0023841
24 |  | 6.4753 | 33.12 | 4187 | 0.0012216 | 6.0281 | 6.0293 | -1.9515 | 818.6035 | 795.5395 | -0.0023839
25 |  | 6.4753 | 33.1177 | 4187 | 0.0012215 | 6.0293 | 6.0306 | -1.9515 | 818.6624 | 828.6572 | -0.0023837
26 |  | 6.4753 | 33.1153 | 4187 | 0.0012214 | 6.0306 | 6.0318 | -1.9515 | 818.7213 | 861.7724 | -0.0023836
27 |  | 6.4753 | 33.1129 | 4187 | 0.0012213 | 6.0318 | 6.033 | -1.9515 | 818.7803 | 894.8853 | -0.0023834
28 |  | 6.4753 | 33.1105 | 4187 | 0.0012212 | 6.033 | 6.0342 | -1.9515 | 818.8392 | 927.9958 | -0.0023832
29 |  | 6.4753 | 33.1081 | 4187 | 0.0012212 | 6.0342 | 6.0354 | -1.9515 | 818.8982 | 961.104 | -0.002383
30 |  | 6.4753 | 33.1057 | 4187 | 0.0012211 | 6.0354 | 6.0367 | -1.9515 | 818.9571 | 994.2097 | -0.0023829
31 |  | 6.4753 | 33.1034 | 4187 | 0.001221 | 6.0367 | 6.0379 | -1.9515 | 819.016 | 1027.3131 | -0.0023827
32 |  | 6.4753 | 33.101 | 4187 | 0.0012209 | 6.0379 | 6.0391 | -1.9515 | 819.075 | 1060.4141 | -0.0023825
33 |  | 6.4753 | 33.0986 | 4187 | 0.0012208 | 6.0391 | 6.0403 | -1.9515 | 819.134 | 1093.5127 | -0.0023824
34 |  | 6.4753 | 33.0962 | 4187 | 0.0012207 | 6.0403 | 6.0416 | -1.9515 | 819.1929 | 1126.6089 | -0.0023822
35 |  | 6.4753 | 33.0938 | 4187 | 0.0012206 | 6.0416 | 6.0428 | -1.9515 | 819.2519 | 1159.7027 | -0.002382
36 |  | 6.4753 | 33.0915 | 4187 | 0.0012205 | 6.0428 | 6.044 | -1.9515 | 819.3109 | 1192.7942 | -0.0023818
37 |  | 6.4753 | 33.0891 | 4187 | 0.0012205 | 6.044 | 6.0452 | -1.9515 | 819.3698 | 1225.8832 | -0.0023817
38 |  | 6.4753 | 33.0867 | 4187 | 0.0012204 | 6.0452 | 6.0464 | -1.9515 | 819.4288 | 1258.9699 | -0.0023815
39 |  | 6.4753 | 33.0843 | 4187 | 0.0012203 | 6.0464 | 6.0477 | -1.9515 | 819.4878 | 1292.0542 | -0.0023813
40 |  | 6.4753 | 33.0819 | 4187 | 0.0012202 | 6.0477 | 6.0489 | -1.9515 | 819.5468 | 1325.1362 | -0.0023812
41 |  | 6.4753 | 33.0795 | 4187 | 0.0012201 | 6.0489 | 6.0501 | -1.9515 | 819.6058 | 1358.2157 | -0.002381
42 |  | 6.4753 | 33.0772 | 4187 | 0.00122 | 6.0501 | 6.0513 | -1.9515 | 819.6648 | 1391.2929 | -0.0023808
43 |  | 6.4753 | 33.0748 | 4187 | 0.0012199 | 6.0513 | 6.0525 | -1.9515 | 819.7238 | 1424.3676 | -0.0023806
44 |  | 6.4753 | 33.0724 | 4187 | 0.0012198 | 6.0525 | 6.0538 | -1.9515 | 819.7828 | 1457.44 | -0.0023805
45 |  | 6.4753 | 33.07 | 4187 | 0.0012197 | 6.0538 | 6.055 | -1.9515 | 819.8418 | 1490.5101 | -0.0023803
46 |  | 6.4753 | 33.0676 | 4187 | 0.0012197 | 6.055 | 6.0562 | -1.9515 | 819.9008 | 1523.5777 | -0.0023801
47 |  | 6.4753 | 33.0653 | 4187 | 0.0012196 | 6.0562 | 6.0574 | -1.9515 | 819.9598 | 1556.643 | -0.00238
48 |  | 6.4753 | 33.0629 | 4187 | 0.0012195 | 6.0574 | 6.0586 | -1.9515 | 820.0189 | 1589.7059 | -0.0023798
49 |  | 6.4753 | 33.0605 | 4187 | 0.0012194 | 6.0586 | 6.0599 | -1.9515 | 820.0779 | 1622.7664 | -0.0023796
50 |  | 6.4753 | 33.0581 | 4187 | 0.0012193 | 6.0599 | 6.0611 | -1.9515 | 820.1369 | 1655.8245 | -0.0023794
51 |  | 6.4753 | 33.0557 | 4187 | 0.0012192 | 6.0611 | 6.0623 | -1.9515 | 820.196 | 1688.8802 | -0.0023793
52 |  | 6.4753 | 33.0534 | 4187 | 0.0012191 | 6.0623 | 6.0635 | -1.9515 | 820.255 | 1721.9336 | -0.0023791
53 |  | 6.4753 | 33.051 | 4187 | 0.001219 | 6.0635 | 6.0647 | -1.9515 | 820.314 | 1754.9846 | -0.0023789
54 |  | 6.4753 | 33.0486 | 4187 | 0.001219 | 6.0647 | 6.0659 | -1.9515 | 820.3731 | 1788.0332 | -0.0023788
55 |  | 6.4753 | 33.0462 | 4187 | 0.0012189 | 6.0659 | 6.0672 | -1.9515 | 820.4321 | 1821.0794 | -0.0023786
56 |  | 6.4753 | 33.0438 | 4187 | 0.0012188 | 6.0672 | 6.0684 | -1.9515 | 820.4912 | 1854.1232 | -0.0023784
57 |  | 6.4753 | 33.0415 | 4187 | 0.0012187 | 6.0684 | 6.0696 | -1.9515 | 820.5503 | 1887.1647 | -0.0023782
58 |  | 6.4753 | 33.0391 | 4187 | 0.0012186 | 6.0696 | 6.0708 | -1.9515 | 820.6093 | 1920.2038 | -0.0023781
59 |  | 6.4753 | 33.0367 | 4187 | 0.0012185 | 6.0708 | 6.072 | -1.9515 | 820.6684 | 1953.2405 | -0.0023779
60 |  | 6.4753 | 33.0343 | 4187 | 0.0012184 | 6.072 | 6.0733 | -1.9515 | 820.7275 | 1986.2749 | -0.0023777
61 |  | 6.4753 | 33.032 | 4187 | 0.0012183 | 6.0733 | 6.0745 | -1.9515 | 820.7865 | 2019.3068 | -0.0023776
62 |  | 6.4753 | 33.0296 | 4187 | 0.0012183 | 6.0745 | 6.0757 | -1.9515 | 820.8456 | 2052.3364 | -0.0023774
63 |  | 6.4753 | 33.0272 | 4187 | 0.0012182 | 6.0757 | 6.0769 | -1.9515 | 820.9047 | 2085.3636 | -0.0023772
64 |  | 6.4753 | 33.0248 | 4187 | 0.0012181 | 6.0769 | 6.0781 | -1.9515 | 820.9638 | 2118.3884 | -0.002377
65 |  | 6.4753 | 33.0224 | 4187 | 0.001218 | 6.0781 | 6.0794 | -1.9515 | 821.0229 | 2151.4109 | -0.0023769
66 |  | 6.4753 | 33.0201 | 4187 | 0.0012179 | 6.0794 | 6.0806 | -1.9515 | 821.082 | 2184.4309 | -0.0023767
67 |  | 6.4753 | 33.0177 | 4187 | 0.0012178 | 6.0806 | 6.0818 | -1.9515 | 821.1411 | 2217.4486 | -0.0023765
68 |  | 6.4753 | 33.0153 | 4187 | 0.0012177 | 6.0818 | 6.083 | -1.9515 | 821.2002 | 2250.464 | -0.0023764
69 |  | 6.4753 | 33.0129 | 4187 | 0.0012176 | 6.083 | 6.0842 | -1.9515 | 821.2593 | 2283.4769 | -0.0023762
70 |  | 6.4753 | 33.0106 | 4187 | 0.0012176 | 6.0842 | 6.0854 | -1.9515 | 821.3184 | 2316.4875 | -0.002376
71 |  | 6.4753 | 33.0082 | 4187 | 0.0012175 | 6.0854 | 6.0867 | -1.9515 | 821.3776 | 2349.4957 | -0.0023758
72 |  | 6.4753 | 33.0058 | 4187 | 0.0012174 | 6.0867 | 6.0879 | -1.9515 | 821.4367 | 2382.5015 | -0.0023757
73 |  | 6.4753 | 33.0034 | 4187 | 0.0012173 | 6.0879 | 6.0891 | -1.9515 | 821.4958 | 2415.5049 | -0.0023755
74 |  | 6.4753 | 33.0011 | 4187 | 0.0012172 | 6.0891 | 6.0903 | -1.9515 | 821.5549 | 2448.506 | -0.0023753
75 |  | 6.4753 | 32.9987 | 4187 | 0.0012171 | 6.0903 | 6.0915 | -1.9515 | 821.6141 | 2481.5047 | -0.0023752
76 |  | 6.4753 | 32.9963 | 4187 | 0.001217 | 6.0915 | 6.0927 | -1.9515 | 821.6732 | 2514.501 | -0.002375
77 |  | 6.4753 | 32.9939 | 4187 | 0.0012169 | 6.0927 | 6.094 | -1.9515 | 821.7324 | 2547.4949 | -0.0023748
78 |  | 6.4753 | 32.9916 | 4187 | 0.0012169 | 6.094 | 6.0952 | -1.9515 | 821.7915 | 2580.4865 | -0.0023746
79 |  | 6.4753 | 32.9892 | 4187 | 0.0012168 | 6.0952 | 6.0964 | -1.9515 | 821.8507 | 2613.4757 | -0.0023745
80 |  | 6.4753 | 32.9868 | 4187 | 0.0012167 | 6.0964 | 6.0976 | -1.9515 | 821.9098 | 2646.4625 | -0.0023743
81 |  | 6.4753 | 32.9844 | 4187 | 0.0012166 | 6.0976 | 6.0988 | -1.9515 | 821.969 | 2679.4469 | -0.0023741
82 |  | 6.4753 | 32.9821 | 4187 | 0.0012165 | 6.0988 | 6.1 | -1.9515 | 822.0282 | 2712.429 | -0.002374
83 |  | 6.4753 | 32.9797 | 4187 | 0.0012164 | 6.1 | 6.1013 | -1.9515 | 822.0873 | 2745.4087 | -0.0023738
84 |  | 6.4753 | 32.9773 | 4187 | 0.0012163 | 6.1013 | 6.1025 | -1.9515 | 822.1465 | 2778.386 | -0.0023736
85 |  | 6.4753 | 32.9749 | 4187 | 0.0012162 | 6.1025 | 6.1037 | -1.9515 | 822.2057 | 2811.3609 | -0.0023735
86 |  | 6.4753 | 32.9726 | 4187 | 0.0012162 | 6.1037 | 6.1049 | -1.9515 | 822.2649 | 2844.3335 | -0.0023733
87 |  | 6.4753 | 32.9702 | 4187 | 0.0012161 | 6.1049 | 6.1061 | -1.9515 | 822.3241 | 2877.3037 | -0.0023731
88 |  | 6.4753 | 32.9678 | 4187 | 0.001216 | 6.1061 | 6.1073 | -1.9515 | 822.3833 | 2910.2715 | -0.0023729
89 |  | 6.4753 | 32.9655 | 4187 | 0.0012159 | 6.1073 | 6.1086 | -1.9515 | 822.4425 | 2943.237 | -0.0023728
90 |  | 6.4753 | 32.9631 | 4187 | 0.0012158 | 6.1086 | 6.1098 | -1.9515 | 822.5017 | 2976.2 | -0.0023726
91 |  | 6.4753 | 32.9607 | 4187 | 0.0012157 | 6.1098 | 6.111 | -1.9515 | 822.5609 | 3009.1607 | -0.0023724
92 |  | 6.4753 | 32.9583 | 4187 | 0.0012156 | 6.111 | 6.1122 | -1.9515 | 822.6201 | 3042.1191 | -0.0023723
93 |  | 6.4753 | 32.956 | 4187 | 0.0012155 | 6.1122 | 6.1134 | -1.9515 | 822.6793 | 3075.075 | -0.0023721
94 |  | 6.4753 | 32.9536 | 4187 | 0.0012155 | 6.1134 | 6.1146 | -1.9515 | 822.7385 | 3108.0286 | -0.0023719
95 |  | 6.4753 | 32.9512 | 4187 | 0.0012154 | 6.1146 | 6.1159 | -1.9515 | 822.7977 | 3140.9798 | -0.0023717
96 |  | 6.4753 | 32.9488 | 4187 | 0.0012153 | 6.1159 | 6.1171 | -1.9515 | 822.857 | 3173.9287 | -0.0023716
97 |  | 6.4753 | 32.9465 | 4187 | 0.0012152 | 6.1171 | 6.1183 | -1.9515 | 822.9162 | 3206.8752 | -0.0023714
98 |  | 6.4753 | 32.9441 | 4187 | 0.0012151 | 6.1183 | 6.1195 | -1.9515 | 822.9754 | 3239.8193 | -0.0023712
99 |  | 6.4753 | 32.9417 | 4187 | 0.001215 | 6.1195 | 6.1207 | -1.9515 | 823.0347 | 3272.761 | -0.0023711
100 |  | 6.4753 | 32.9394 | 4187 | 0.0012149 | 6.1207 | 6.1219 | -1.9515 | 823.0939 | 3305.7004 | -0.0023709
101 |  | 6.4753 | 32.937 | 4187 | 0.0012148 | 6.1219 | 6.1231 | -1.9515 | 823.1532 | 3338.6373 | -0.0023707
102 |  | 6.4753 | 32.9346 | 4187 | 0.0012148 | 6.1231 | 6.1244 | -1.9515 | 823.2124 | 3371.572 | -0.0023705
103 |  | 6.4753 | 32.9322 | 4187 | 0.0012147 | 6.1244 | 6.1256 | -1.9515 | 823.2717 | 3404.5042 | -0.0023704
104 |  | 6.4753 | 32.9299 | 4187 | 0.0012146 | 6.1256 | 6.1268 | -1.9515 | 823.3309 | 3437.4341 | -0.0023702
105 |  | 6.4753 | 32.9275 | 4187 | 0.0012145 | 6.1268 | 6.128 | -1.9515 | 823.3902 | 3470.3616 | -0.00237
106 |  | 6.4753 | 32.9251 | 4187 | 0.0012144 | 6.128 | 6.1292 | -1.9515 | 823.4495 | 3503.2867 | -0.0023699
107 |  | 6.4753 | 32.9228 | 4187 | 0.0012143 | 6.1292 | 6.1304 | -1.9515 | 823.5087 | 3536.2095 | -0.0023697
108 |  | 6.4753 | 32.9204 | 4187 | 0.0012142 | 6.1304 | 6.1316 | -1.9515 | 823.568 | 3569.1299 | -0.0023695
109 |  | 6.4753 | 32.918 | 4187 | 0.0012141 | 6.1316 | 6.1329 | -1.9515 | 823.6273 | 3602.0479 | -0.0023694
110 |  | 6.4753 | 32.9157 | 4187 | 0.0012141 | 6.1329 | 6.1341 | -1.9515 | 823.6866 | 3634.9636 | -0.0023692
111 |  | 6.4753 | 32.9133 | 4187 | 0.001214 | 6.1341 | 6.1353 | -1.9515 | 823.7459 | 3667.8769 | -0.002369
112 |  | 6.4753 | 32.9109 | 4187 | 0.0012139 | 6.1353 | 6.1365 | -1.9515 | 823.8052 | 3700.7878 | -0.0023688
113 |  | 6.4753 | 32.9086 | 4187 | 0.0012138 | 6.1365 | 6.1377 | -1.9515 | 823.8645 | 3733.6963 | -0.0023687
114 |  | 6.4753 | 32.9062 | 4187 | 0.0012137 | 6.1377 | 6.1389 | -1.9515 | 823.9238 | 3766.6025 | -0.0023685
115 |  | 6.4753 | 32.9038 | 4187 | 0.0012136 | 6.1389 | 6.1401 | -1.9515 | 823.9831 | 3799.5063 | -0.0023683
116 |  | 6.4753 | 32.9014 | 4187 | 0.0012135 | 6.1401 | 6.1414 | -1.9515 | 824.0424 | 3832.4078 | -0.0023682
117 |  | 6.4753 | 32.8991 | 4187 | 0.0012134 | 6.1414 | 6.1426 | -1.9515 | 824.1017 | 3865.3069 | -0.002368
118 |  | 6.4753 | 32.8967 | 4187 | 0.0012134 | 6.1426 | 6.1438 | -1.9515 | 824.161 | 3898.2036 | -0.0023678
119 |  | 6.4753 | 32.8943 | 4187 | 0.0012133 | 6.1438 | 6.145 | -1.9515 | 824.2204 | 3931.0979 | -0.0023677
120 |  | 6.4753 | 32.892 | 4187 | 0.0012132 | 6.145 | 6.1462 | -1.9515 | 824.2797 | 3963.9899 | -0.0023675
121 |  | 6.4753 | 32.8896 | 4187 | 0.0012131 | 6.1462 | 6.1474 | -1.9515 | 824.339 | 3996.8795 | -0.0023673
122 |  | 6.4753 | 32.8872 | 4187 | 0.001213 | 6.1474 | 6.1486 | -1.9515 | 824.3984 | 4029.7667 | -0.0023671
123 |  | 6.4753 | 32.8849 | 4187 | 0.0012129 | 6.1486 | 6.1498 | -1.9515 | 824.4577 | 4062.6516 | -0.002367
124 |  | 6.4753 | 32.8825 | 4187 | 0.0012128 | 6.1498 | 6.1511 | -1.9515 | 824.5171 | 4095.5341 | -0.0023668
125 |  | 6.4753 | 32.8801 | 4187 | 0.0012127 | 6.1511 | 6.1523 | -1.9515 | 824.5764 | 4128.4142 | -0.0023666
126 |  | 6.4753 | 32.8778 | 4187 | 0.0012127 | 6.1523 | 6.1535 | -1.9515 | 824.6358 | 4161.292 | -0.0023665
127 |  | 6.4753 | 32.8754 | 4187 | 0.0012126 | 6.1535 | 6.1547 | -1.9515 | 824.6951 | 4194.1674 | -0.0023663
128 |  | 6.4753 | 32.873 | 4187 | 0.0012125 | 6.1547 | 6.1559 | -1.9515 | 824.7545 | 4227.0405 | -0.0023661
129 |  | 6.4753 | 32.8707 | 4187 | 0.0012124 | 6.1559 | 6.1571 | -1.9515 | 824.8138 | 4259.9111 | -0.0023659
130 |  | 6.4753 | 32.8683 | 4187 | 0.0012123 | 6.1571 | 6.1583 | -1.9515 | 824.8732 | 4292.7794 | -0.0023658
131 |  | 6.4753 | 32.8659 | 4187 | 0.0012122 | 6.1583 | 6.1595 | -1.9515 | 824.9326 | 4325.6454 | -0.0023656
132 |  | 6.4753 | 32.8636 | 4187 | 0.0012121 | 6.1595 | 6.1608 | -1.9515 | 824.992 | 4358.509 | -0.0023654
133 |  | 6.4753 | 32.8612 | 4187 | 0.001212 | 6.1608 | 6.162 | -1.9515 | 825.0514 | 4391.3702 | -0.0023653
134 |  | 6.4753 | 32.8588 | 4187 | 0.001212 | 6.162 | 6.1632 | -1.9515 | 825.1108 | 4424.229 | -0.0023651
135 |  | 6.4753 | 32.8565 | 4187 | 0.0012119 | 6.1632 | 6.1644 | -1.9515 | 825.1701 | 4457.0855 | -0.0023649
136 |  | 6.4753 | 32.8541 | 4187 | 0.0012118 | 6.1644 | 6.1656 | -1.9515 | 825.2295 | 4489.9396 | -0.0023648
137 |  | 6.4753 | 32.8518 | 4187 | 0.0012117 | 6.1656 | 6.1668 | -1.9515 | 825.2889 | 4522.7914 | -0.0023646
138 |  | 6.4753 | 32.8494 | 4187 | 0.0012116 | 6.1668 | 6.168 | -1.9515 | 825.3484 | 4555.6407 | -0.0023644
139 |  | 6.4753 | 32.847 | 4187 | 0.0012115 | 6.168 | 6.1692 | -1.9515 | 825.4078 | 4588.4878 | -0.0023642
140 |  | 6.4753 | 32.8447 | 4187 | 0.0012114 | 6.1692 | 6.1705 | -1.9515 | 825.4672 | 4621.3324 | -0.0023641
141 |  | 6.4753 | 32.8423 | 4187 | 0.0012113 | 6.1705 | 6.1717 | -1.9515 | 825.5266 | 4654.1747 | -0.0023639
142 |  | 6.4753 | 32.8399 | 4187 | 0.0012113 | 6.1717 | 6.1729 | -1.9515 | 825.586 | 4687.0146 | -0.0023637
143 |  | 6.4753 | 32.8376 | 4187 | 0.0012112 | 6.1729 | 6.1741 | -1.9515 | 825.6455 | 4719.8522 | -0.0023636
144 |  | 6.4753 | 32.8352 | 4187 | 0.0012111 | 6.1741 | 6.1753 | -1.9515 | 825.7049 | 4752.6874 | -0.0023634
145 |  | 6.4753 | 32.8328 | 4187 | 0.001211 | 6.1753 | 6.1765 | -1.9515 | 825.7643 | 4785.5202 | -0.0023632
146 |  | 6.4753 | 32.8305 | 4187 | 0.0012109 | 6.1765 | 6.1777 | -1.9515 | 825.8238 | 4818.3507 | -0.0023631
147 |  | 6.4753 | 32.8281 | 4187 | 0.0012108 | 6.1777 | 6.1789 | -1.9515 | 825.8832 | 4851.1788 | -0.0023629
148 |  | 6.4753 | 32.8257 | 4187 | 0.0012107 | 6.1789 | 6.1801 | -1.9515 | 825.9427 | 4884.0046 | -0.0023627
149 |  | 6.4753 | 32.8234 | 4187 | 0.0012107 | 6.1801 | 6.1814 | -1.9515 | 826.0021 | 4916.828 | -0.0023625
150 |  | 6.4753 | 32.821 | 4187 | 0.0012106 | 6.1814 | 6.1826 | -1.9515 | 826.0616 | 4949.649 | -0.0023624
151 |  | 6.4753 | 32.8187 | 4187 | 0.0012105 | 6.1826 | 6.1838 | -1.9515 | 826.121 | 4982.4677 | -0.0023622
152 |  | 6.4753 | 32.8163 | 4187 | 0.0012104 | 6.1838 | 6.185 | -1.9515 | 826.1805 | 5015.284 | -0.002362
153 |  | 6.4753 | 32.8139 | 4187 | 0.0012103 | 6.185 | 6.1862 | -1.9515 | 826.24 | 5048.0979 | -0.0023619
154 |  | 6.4753 | 32.8116 | 4187 | 0.0012102 | 6.1862 | 6.1874 | -1.9515 | 826.2994 | 5080.9095 | -0.0023617
155 |  | 6.4753 | 32.8092 | 4187 | 0.0012101 | 6.1874 | 6.1886 | -1.9515 | 826.3589 | 5113.7187 | -0.0023615
156 |  | 6.4753 | 32.8069 | 4187 | 0.00121 | 6.1886 | 6.1898 | -1.9515 | 826.4184 | 5146.5255 | -0.0023614
157 |  | 6.4753 | 32.8045 | 4187 | 0.00121 | 6.1898 | 6.191 | -1.9515 | 826.4779 | 5179.33 | -0.0023612
158 |  | 6.4753 | 32.8021 | 4187 | 0.0012099 | 6.191 | 6.1922 | -1.9515 | 826.5374 | 5212.1321 | -0.002361
159 |  | 6.4753 | 32.7998 | 4187 | 0.0012098 | 6.1922 | 6.1935 | -1.9515 | 826.5969 | 5244.9319 | -0.0023608
160 |  | 6.4753 | 32.7974 | 4187 | 0.0012097 | 6.1935 | 6.1947 | -1.9515 | 826.6564 | 5277.7293 | -0.0023607
161 |  | 6.4753 | 32.795 | 4187 | 0.0012096 | 6.1947 | 6.1959 | -1.9515 | 826.7159 | 5310.5244 | -0.0023605
162 |  | 6.4753 | 32.7927 | 4187 | 0.0012095 | 6.1959 | 6.1971 | -1.9515 | 826.7754 | 5343.3171 | -0.0023603
163 |  | 6.4753 | 32.7903 | 4187 | 0.0012094 | 6.1971 | 6.1983 | -1.9515 | 826.8349 | 5376.1074 | -0.0023602
164 |  | 6.4753 | 32.788 | 4187 | 0.0012093 | 6.1983 | 6.1995 | -1.9515 | 826.8944 | 5408.8954 | -0.00236
165 |  | 6.4753 | 32.7856 | 4187 | 0.0012093 | 6.1995 | 6.2007 | -1.9515 | 826.9539 | 5441.681 | -0.0023598
166 |  | 6.4753 | 32.7832 | 4187 | 0.0012092 | 6.2007 | 6.2019 | -1.9515 | 827.0135 | 5474.4642 | -0.0023597
167 |  | 6.4753 | 32.7809 | 4187 | 0.0012091 | 6.2019 | 6.2031 | -1.9515 | 827.073 | 5507.2451 | -0.0023595
168 |  | 6.4753 | 32.7785 | 4187 | 0.001209 | 6.2031 | 6.2043 | -1.9515 | 827.1325 | 5540.0236 | -0.0023593
169 |  | 6.4753 | 32.7762 | 4187 | 0.0012089 | 6.2043 | 6.2055 | -1.9515 | 827.1921 | 5572.7998 | -0.0023591
170 |  | 6.4753 | 32.7738 | 4187 | 0.0012088 | 6.2055 | 6.2068 | -1.9515 | 827.2516 | 5605.5736 | -0.002359
171 |  | 6.4753 | 32.7714 | 4187 | 0.0012087 | 6.2068 | 6.208 | -1.9515 | 827.3112 | 5638.345 | -0.0023588
172 |  | 6.4753 | 32.7691 | 4187 | 0.0012086 | 6.208 | 6.2092 | -1.9515 | 827.3707 | 5671.1141 | -0.0023586
173 |  | 6.4753 | 32.7667 | 4187 | 0.0012086 | 6.2092 | 6.2104 | -1.9515 | 827.4303 | 5703.8809 | -0.0023585
174 |  | 6.4753 | 32.7644 | 4187 | 0.0012085 | 6.2104 | 6.2116 | -1.9515 | 827.4898 | 5736.6452 | -0.0023583
175 |  | 6.4753 | 32.762 | 4187 | 0.0012084 | 6.2116 | 6.2128 | -1.9515 | 827.5494 | 5769.4073 | -0.0023581
176 |  | 6.4753 | 32.7597 | 4187 | 0.0012083 | 6.2128 | 6.214 | -1.9515 | 827.609 | 5802.1669 | -0.002358
177 |  | 6.4753 | 32.7573 | 4187 | 0.0012082 | 6.214 | 6.2152 | -1.9515 | 827.6685 | 5834.9242 | -0.0023578
178 |  | 6.4753 | 32.7549 | 4187 | 0.0012081 | 6.2152 | 6.2164 | -1.9515 | 827.7281 | 5867.6792 | -0.0023576
179 |  | 6.4753 | 32.7526 | 4187 | 0.001208 | 6.2164 | 6.2176 | -1.9515 | 827.7877 | 5900.4317 | -0.0023574
180 |  | 6.4753 | 32.7502 | 4187 | 0.001208 | 6.2176 | 6.2188 | -1.9515 | 827.8473 | 5933.182 | -0.0023573
181 |  | 6.4753 | 32.7479 | 4187 | 0.0012079 | 6.2188 | 6.22 | -1.9515 | 827.9069 | 5965.9298 | -0.0023571
182 |  | 6.4753 | 32.7455 | 4187 | 0.0012078 | 6.22 | 6.2213 | -1.9515 | 827.9665 | 5998.6753 | -0.0023569
183 |  | 6.4753 | 32.7432 | 4187 | 0.0012077 | 6.2213 | 6.2225 | -1.9515 | 828.0261 | 6031.4185 | -0.0023568
184 |  | 6.4753 | 32.7408 | 4187 | 0.0012076 | 6.2225 | 6.2237 | -1.9515 | 828.0857 | 6064.1593 | -0.0023566
185 |  | 6.4753 | 32.7384 | 4187 | 0.0012075 | 6.2237 | 6.2249 | -1.9515 | 828.1453 | 6096.8977 | -0.0023564
186 |  | 6.4753 | 32.7361 | 4187 | 0.0012074 | 6.2249 | 6.2261 | -1.9515 | 828.2049 | 6129.6338 | -0.0023563
187 |  | 6.4753 | 32.7337 | 4187 | 0.0012073 | 6.2261 | 6.2273 | -1.9515 | 828.2645 | 6162.3676 | -0.0023561
188 |  | 6.4753 | 32.7314 | 4187 | 0.0012073 | 6.2273 | 6.2285 | -1.9515 | 828.3241 | 6195.0989 | -0.0023559
189 |  | 6.4753 | 32.729 | 4187 | 0.0012072 | 6.2285 | 6.2297 | -1.9515 | 828.3838 | 6227.8279 | -0.0023558
190 |  | 6.4753 | 32.7267 | 4187 | 0.0012071 | 6.2297 | 6.2309 | -1.9515 | 828.4434 | 6260.5546 | -0.0023556
191 |  | 6.4753 | 32.7243 | 4187 | 0.001207 | 6.2309 | 6.2321 | -1.9515 | 828.503 | 6293.2789 | -0.0023554
192 |  | 6.4753 | 32.722 | 4187 | 0.0012069 | 6.2321 | 6.2333 | -1.9515 | 828.5627 | 6326.0009 | -0.0023552
193 |  | 6.4753 | 32.7196 | 4187 | 0.0012068 | 6.2333 | 6.2345 | -1.9515 | 828.6223 | 6358.7205 | -0.0023551
194 |  | 6.4753 | 32.7172 | 4187 | 0.0012067 | 6.2345 | 6.2357 | -1.9515 | 828.682 | 6391.4377 | -0.0023549
195 |  | 6.4753 | 32.7149 | 4187 | 0.0012066 | 6.2357 | 6.2369 | -1.9515 | 828.7416 | 6424.1526 | -0.0023547
196 |  | 6.4753 | 32.7125 | 4187 | 0.0012066 | 6.2369 | 6.2382 | -1.9515 | 828.8013 | 6456.8651 | -0.0023546
197 |  | 6.4753 | 32.7102 | 4187 | 0.0012065 | 6.2382 | 6.2394 | -1.9515 | 828.8609 | 6489.5753 | -0.0023544
198 |  | 6.4753 | 32.7078 | 4187 | 0.0012064 | 6.2394 | 6.2406 | -1.9515 | 828.9206 | 6522.2831 | -0.0023542
199 |  | 6.4753 | 32.7055 | 4187 | 0.0012063 | 6.2406 | 6.2418 | -1.9515 | 828.9802 | 6554.9886 | -0.0023541
200 |  | 6.4753 | 32.7031 | 4187 | 0.0012062 | 6.2418 | 6.243 | -1.9515 | 829.0399 | 6587.6917 | -0.0023539
201 |  | 6.4753 | 32.7008 | 4187 | 0.0012061 | 6.243 | 6.2442 | -1.9515 | 829.0996 | 6620.3924 | -0.0023537
202 |  | 6.4753 | 32.6984 | 4187 | 0.001206 | 6.2442 | 6.2454 | -1.9515 | 829.1593 | 6653.0909 | -0.0023535
203 |  | 6.4753 | 32.6961 | 4187 | 0.001206 | 6.2454 | 6.2466 | -1.9515 | 829.219 | 6685.7869 | -0.0023534
204 |  | 6.4753 | 32.6937 | 4187 | 0.0012059 | 6.2466 | 6.2478 | -1.9515 | 829.2787 | 6718.4806 | -0.0023532
205 |  | 6.4753 | 32.6913 | 4187 | 0.0012058 | 6.2478 | 6.249 | -1.9515 | 829.3383 | 6751.1719 | -0.002353
206 |  | 6.4753 | 32.689 | 4187 | 0.0012057 | 6.249 | 6.2502 | -1.9515 | 829.398 | 6783.8609 | -0.0023529
207 |  | 6.4753 | 32.6866 | 4187 | 0.0012056 | 6.2502 | 6.2514 | -1.9515 | 829.4577 | 6816.5476 | -0.0023527
208 |  | 6.4753 | 32.6843 | 4187 | 0.0012055 | 6.2514 | 6.2526 | -1.9515 | 829.5175 | 6849.2319 | -0.0023525
209 |  | 6.4753 | 32.6819 | 4187 | 0.0012054 | 6.2526 | 6.2538 | -1.9515 | 829.5772 | 6881.9138 | -0.0023524
210 |  | 6.4753 | 32.6796 | 4187 | 0.0012053 | 6.2538 | 6.255 | -1.9515 | 829.6369 | 6914.5934 | -0.0023522
211 |  | 6.4753 | 32.6772 | 4187 | 0.0012053 | 6.255 | 6.2562 | -1.9515 | 829.6966 | 6947.2706 | -0.002352
212 |  | 6.4753 | 32.6749 | 4187 | 0.0012052 | 6.2562 | 6.2574 | -1.9515 | 829.7563 | 6979.9455 | -0.0023519
213 |  | 6.4753 | 32.6725 | 4187 | 0.0012051 | 6.2574 | 6.2587 | -1.9515 | 829.816 | 7012.618 | -0.0023517
214 |  | 6.4753 | 32.6702 | 4187 | 0.001205 | 6.2587 | 6.2599 | -1.9515 | 829.8758 | 7045.2882 | -0.0023515
215 |  | 6.4753 | 32.6678 | 4187 | 0.0012049 | 6.2599 | 6.2611 | -1.9515 | 829.9355 | 7077.956 | -0.0023513
216 |  | 6.4753 | 32.6655 | 4187 | 0.0012048 | 6.2611 | 6.2623 | -1.9515 | 829.9953 | 7110.6215 | -0.0023512
217 |  | 6.4753 | 32.6631 | 4187 | 0.0012047 | 6.2623 | 6.2635 | -1.9515 | 830.055 | 7143.2846 | -0.002351
218 |  | 6.4753 | 32.6608 | 4187 | 0.0012047 | 6.2635 | 6.2647 | -1.9515 | 830.1148 | 7175.9454 | -0.0023508
219 |  | 6.4753 | 32.6584 | 4187 | 0.0012046 | 6.2647 | 6.2659 | -1.9515 | 830.1745 | 7208.6038 | -0.0023507
220 |  | 6.4753 | 32.6561 | 4187 | 0.0012045 | 6.2659 | 6.2671 | -1.9515 | 830.2343 | 7241.2599 | -0.0023505
221 |  | 6.4753 | 32.6537 | 4187 | 0.0012044 | 6.2671 | 6.2683 | -1.9515 | 830.294 | 7273.9136 | -0.0023503
222 |  | 6.4753 | 32.6514 | 4187 | 0.0012043 | 6.2683 | 6.2695 | -1.9515 | 830.3538 | 7306.5649 | -0.0023502
223 |  | 6.4753 | 32.649 | 4187 | 0.0012042 | 6.2695 | 6.2707 | -1.9515 | 830.4136 | 7339.214 | -0.00235
224 |  | 6.4753 | 32.6467 | 4187 | 0.0012041 | 6.2707 | 6.2719 | -1.9515 | 830.4733 | 7371.8606 | -0.0023498
225 |  | 6.4753 | 32.6443 | 4187 | 0.001204 | 6.2719 | 6.2731 | -1.9515 | 830.5331 | 7404.5049 | -0.0023497
226 |  | 6.4753 | 32.642 | 4187 | 0.001204 | 6.2731 | 6.2743 | -1.9515 | 830.5929 | 7437.1469 | -0.0023495
227 |  | 6.4753 | 32.6396 | 4187 | 0.0012039 | 6.2743 | 6.2755 | -1.9515 | 830.6527 | 7469.7865 | -0.0023493
228 |  | 6.4753 | 32.6373 | 4187 | 0.0012038 | 6.2755 | 6.2767 | -1.9515 | 830.7125 | 7502.4238 | -0.0023491
229 |  | 6.4753 | 32.6349 | 4187 | 0.0012037 | 6.2767 | 6.2779 | -1.9515 | 830.7723 | 7535.0587 | -0.002349
230 |  | 6.4753 | 32.6326 | 4187 | 0.0012036 | 6.2779 | 6.2791 | -1.9515 | 830.8321 | 7567.6913 | -0.0023488
231 |  | 6.4753 | 32.6302 | 4187 | 0.0012035 | 6.2791 | 6.2803 | -1.9515 | 830.8919 | 7600.3215 | -0.0023486
232 |  | 6.4753 | 32.6279 | 4187 | 0.0012034 | 6.2803 | 6.2815 | -1.9515 | 830.9517 | 7632.9494 | -0.0023485
233 |  | 6.4753 | 32.6255 | 4187 | 0.0012034 | 6.2815 | 6.2827 | -1.9515 | 831.0115 | 7665.5749 | -0.0023483
234 |  | 6.4753 | 32.6232 | 4187 | 0.0012033 | 6.2827 | 6.2839 | -1.9515 | 831.0713 | 7698.1981 | -0.0023481
235 |  | 6.4753 | 32.6208 | 4187 | 0.0012032 | 6.2839 | 6.2851 | -1.9515 | 831.1312 | 7730.8189 | -0.002348
236 |  | 6.4753 | 32.6185 | 4187 | 0.0012031 | 6.2851 | 6.2863 | -1.9515 | 831.191 | 7763.4374 | -0.0023478

## Fus160
|  |  | buis | verlies W/M | L /°C/sec
diam | wandikte |  | inhoud l/m |  | W/M
160 | 21.9 | 3.1416 | 10.6048 | 35.8082 | 4187
[8 empty] | J/sec/mtr | aantal mtr. | verlies
|  | buis | verlies W/M | L /°C/sec | verlies temp | begintemp | eindtemp | verlies | bij 1°C | totaal J/sec
|  | inhoud L |  | W/M | °C per M | °C | °C | per m°C | daling | aantal mtr
1 | 160 | 10.6048 | 35.8082 | 4187 | 0.00080645 | 6 | 6.0008 | -2.1064 | 1240.0034 | 35.8082 | -0.0016987
2 |  | 10.6048 | 35.8065 | 4187 | 0.00080641 | 6.0008 | 6.0016 | -2.1064 | 1240.0622 | 71.6147 | -0.0016986
3 |  | 10.6048 | 35.8048 | 4187 | 0.00080637 | 6.0016 | 6.0024 | -2.1064 | 1240.121 | 107.4194 | -0.0016985
4 |  | 10.6048 | 35.8031 | 4187 | 0.00080633 | 6.0024 | 6.0032 | -2.1064 | 1240.1799 | 143.2225 | -0.0016984
5 |  | 10.6048 | 35.8014 | 4187 | 0.0008063 | 6.0032 | 6.004 | -2.1064 | 1240.2387 | 179.0239 | -0.0016984
6 |  | 10.6048 | 35.7997 | 4187 | 0.00080626 | 6.004 | 6.0048 | -2.1064 | 1240.2975 | 214.8236 | -0.0016983
7 |  | 10.6048 | 35.798 | 4187 | 0.00080622 | 6.0048 | 6.0056 | -2.1064 | 1240.3564 | 250.6216 | -0.0016982
8 |  | 10.6048 | 35.7963 | 4187 | 0.00080618 | 6.0056 | 6.0065 | -2.1064 | 1240.4152 | 286.4179 | -0.0016981
9 |  | 10.6048 | 35.7946 | 4187 | 0.00080614 | 6.0065 | 6.0073 | -2.1064 | 1240.4741 | 322.2125 | -0.001698
10 |  | 10.6048 | 35.7929 | 4187 | 0.00080611 | 6.0073 | 6.0081 | -2.1064 | 1240.5329 | 358.0054 | -0.001698
11 |  | 10.6048 | 35.7912 | 4187 | 0.00080607 | 6.0081 | 6.0089 | -2.1064 | 1240.5918 | 393.7965 | -0.0016979
12 |  | 10.6048 | 35.7895 | 4187 | 0.00080603 | 6.0089 | 6.0097 | -2.1064 | 1240.6506 | 429.586 | -0.0016978
13 |  | 10.6048 | 35.7878 | 4187 | 0.00080599 | 6.0097 | 6.0105 | -2.1064 | 1240.7095 | 465.3738 | -0.0016977
14 |  | 10.6048 | 35.7861 | 4187 | 0.00080595 | 6.0105 | 6.0113 | -2.1064 | 1240.7683 | 501.1599 | -0.0016976
15 |  | 10.6048 | 35.7844 | 4187 | 0.00080591 | 6.0113 | 6.0121 | -2.1064 | 1240.8272 | 536.9444 | -0.0016975
16 |  | 10.6048 | 35.7827 | 4187 | 0.00080588 | 6.0121 | 6.0129 | -2.1064 | 1240.8861 | 572.7271 | -0.0016975
17 |  | 10.6048 | 35.781 | 4187 | 0.00080584 | 6.0129 | 6.0137 | -2.1064 | 1240.9449 | 608.5081 | -0.0016974
18 |  | 10.6048 | 35.7793 | 4187 | 0.0008058 | 6.0137 | 6.0145 | -2.1064 | 1241.0038 | 644.2874 | -0.0016973
19 |  | 10.6048 | 35.7776 | 4187 | 0.00080576 | 6.0145 | 6.0153 | -2.1064 | 1241.0627 | 680.065 | -0.0016972
20 |  | 10.6048 | 35.7759 | 4187 | 0.00080572 | 6.0153 | 6.0161 | -2.1064 | 1241.1216 | 715.8409 | -0.0016971
21 |  | 10.6048 | 35.7742 | 4187 | 0.00080568 | 6.0161 | 6.0169 | -2.1064 | 1241.1804 | 751.6151 | -0.0016971
22 |  | 10.6048 | 35.7725 | 4187 | 0.00080565 | 6.0169 | 6.0177 | -2.1064 | 1241.2393 | 787.3877 | -0.001697
23 |  | 10.6048 | 35.7708 | 4187 | 0.00080561 | 6.0177 | 6.0185 | -2.1064 | 1241.2982 | 823.1585 | -0.0016969
24 |  | 10.6048 | 35.7691 | 4187 | 0.00080557 | 6.0185 | 6.0193 | -2.1064 | 1241.3571 | 858.9276 | -0.0016968
25 |  | 10.6048 | 35.7674 | 4187 | 0.00080553 | 6.0193 | 6.0201 | -2.1064 | 1241.416 | 894.695 | -0.0016967
26 |  | 10.6048 | 35.7657 | 4187 | 0.00080549 | 6.0201 | 6.021 | -2.1064 | 1241.4749 | 930.4608 | -0.0016967
27 |  | 10.6048 | 35.764 | 4187 | 0.00080546 | 6.021 | 6.0218 | -2.1064 | 1241.5338 | 966.2248 | -0.0016966
28 |  | 10.6048 | 35.7623 | 4187 | 0.00080542 | 6.0218 | 6.0226 | -2.1064 | 1241.5927 | 1001.9872 | -0.0016965
29 |  | 10.6048 | 35.7606 | 4187 | 0.00080538 | 6.0226 | 6.0234 | -2.1064 | 1241.6516 | 1037.7478 | -0.0016964
30 |  | 10.6048 | 35.7589 | 4187 | 0.00080534 | 6.0234 | 6.0242 | -2.1064 | 1241.7105 | 1073.5068 | -0.0016963
31 |  | 10.6048 | 35.7573 | 4187 | 0.0008053 | 6.0242 | 6.025 | -2.1064 | 1241.7694 | 1109.264 | -0.0016963
32 |  | 10.6048 | 35.7556 | 4187 | 0.00080526 | 6.025 | 6.0258 | -2.1064 | 1241.8283 | 1145.0196 | -0.0016962
33 |  | 10.6048 | 35.7539 | 4187 | 0.00080523 | 6.0258 | 6.0266 | -2.1064 | 1241.8872 | 1180.7734 | -0.0016961
34 |  | 10.6048 | 35.7522 | 4187 | 0.00080519 | 6.0266 | 6.0274 | -2.1064 | 1241.9461 | 1216.5256 | -0.001696
35 |  | 10.6048 | 35.7505 | 4187 | 0.00080515 | 6.0274 | 6.0282 | -2.1064 | 1242.005 | 1252.2761 | -0.0016959
36 |  | 10.6048 | 35.7488 | 4187 | 0.00080511 | 6.0282 | 6.029 | -2.1064 | 1242.064 | 1288.0248 | -0.0016959
37 |  | 10.6048 | 35.7471 | 4187 | 0.00080507 | 6.029 | 6.0298 | -2.1064 | 1242.1229 | 1323.7719 | -0.0016958
38 |  | 10.6048 | 35.7454 | 4187 | 0.00080504 | 6.0298 | 6.0306 | -2.1064 | 1242.1818 | 1359.5173 | -0.0016957
39 |  | 10.6048 | 35.7437 | 4187 | 0.000805 | 6.0306 | 6.0314 | -2.1064 | 1242.2407 | 1395.261 | -0.0016956
40 |  | 10.6048 | 35.742 | 4187 | 0.00080496 | 6.0314 | 6.0322 | -2.1064 | 1242.2997 | 1431.003 | -0.0016955
41 |  | 10.6048 | 35.7403 | 4187 | 0.00080492 | 6.0322 | 6.033 | -2.1064 | 1242.3586 | 1466.7433 | -0.0016955
42 |  | 10.6048 | 35.7386 | 4187 | 0.00080488 | 6.033 | 6.0338 | -2.1064 | 1242.4175 | 1502.4819 | -0.0016954
43 |  | 10.6048 | 35.7369 | 4187 | 0.00080484 | 6.0338 | 6.0346 | -2.1064 | 1242.4765 | 1538.2188 | -0.0016953
44 |  | 10.6048 | 35.7352 | 4187 | 0.00080481 | 6.0346 | 6.0354 | -2.1064 | 1242.5354 | 1573.954 | -0.0016952
45 |  | 10.6048 | 35.7335 | 4187 | 0.00080477 | 6.0354 | 6.0363 | -2.1064 | 1242.5944 | 1609.6875 | -0.0016951
46 |  | 10.6048 | 35.7318 | 4187 | 0.00080473 | 6.0363 | 6.0371 | -2.1064 | 1242.6533 | 1645.4193 | -0.0016951
47 |  | 10.6048 | 35.7301 | 4187 | 0.00080469 | 6.0371 | 6.0379 | -2.1064 | 1242.7123 | 1681.1494 | -0.001695
48 |  | 10.6048 | 35.7284 | 4187 | 0.00080465 | 6.0379 | 6.0387 | -2.1064 | 1242.7712 | 1716.8779 | -0.0016949
49 |  | 10.6048 | 35.7267 | 4187 | 0.00080462 | 6.0387 | 6.0395 | -2.1064 | 1242.8302 | 1752.6046 | -0.0016948
50 |  | 10.6048 | 35.725 | 4187 | 0.00080458 | 6.0395 | 6.0403 | -2.1064 | 1242.8892 | 1788.3296 | -0.0016947
51 |  | 10.6048 | 35.7233 | 4187 | 0.00080454 | 6.0403 | 6.0411 | -2.1064 | 1242.9481 | 1824.053 | -0.0016947
52 |  | 10.6048 | 35.7216 | 4187 | 0.0008045 | 6.0411 | 6.0419 | -2.1064 | 1243.0071 | 1859.7746 | -0.0016946
53 |  | 10.6048 | 35.72 | 4187 | 0.00080446 | 6.0419 | 6.0427 | -2.1064 | 1243.0661 | 1895.4946 | -0.0016945
54 |  | 10.6048 | 35.7183 | 4187 | 0.00080442 | 6.0427 | 6.0435 | -2.1064 | 1243.125 | 1931.2128 | -0.0016944
55 |  | 10.6048 | 35.7166 | 4187 | 0.00080439 | 6.0435 | 6.0443 | -2.1064 | 1243.184 | 1966.9294 | -0.0016943
56 |  | 10.6048 | 35.7149 | 4187 | 0.00080435 | 6.0443 | 6.0451 | -2.1064 | 1243.243 | 2002.6443 | -0.0016942
57 |  | 10.6048 | 35.7132 | 4187 | 0.00080431 | 6.0451 | 6.0459 | -2.1064 | 1243.302 | 2038.3574 | -0.0016942
58 |  | 10.6048 | 35.7115 | 4187 | 0.00080427 | 6.0459 | 6.0467 | -2.1064 | 1243.3609 | 2074.0689 | -0.0016941
59 |  | 10.6048 | 35.7098 | 4187 | 0.00080423 | 6.0467 | 6.0475 | -2.1064 | 1243.4199 | 2109.7787 | -0.001694
60 |  | 10.6048 | 35.7081 | 4187 | 0.0008042 | 6.0475 | 6.0483 | -2.1064 | 1243.4789 | 2145.4868 | -0.0016939
61 |  | 10.6048 | 35.7064 | 4187 | 0.00080416 | 6.0483 | 6.0491 | -2.1064 | 1243.5379 | 2181.1932 | -0.0016938
62 |  | 10.6048 | 35.7047 | 4187 | 0.00080412 | 6.0491 | 6.0499 | -2.1064 | 1243.5969 | 2216.8979 | -0.0016938
63 |  | 10.6048 | 35.703 | 4187 | 0.00080408 | 6.0499 | 6.0507 | -2.1064 | 1243.6559 | 2252.6009 | -0.0016937
64 |  | 10.6048 | 35.7013 | 4187 | 0.00080404 | 6.0507 | 6.0515 | -2.1064 | 1243.7149 | 2288.3022 | -0.0016936
65 |  | 10.6048 | 35.6996 | 4187 | 0.000804 | 6.0515 | 6.0523 | -2.1064 | 1243.7739 | 2324.0019 | -0.0016935
66 |  | 10.6048 | 35.6979 | 4187 | 0.00080397 | 6.0523 | 6.0531 | -2.1064 | 1243.8329 | 2359.6998 | -0.0016934
67 |  | 10.6048 | 35.6962 | 4187 | 0.00080393 | 6.0531 | 6.0539 | -2.1064 | 1243.8919 | 2395.396 | -0.0016934
68 |  | 10.6048 | 35.6945 | 4187 | 0.00080389 | 6.0539 | 6.0548 | -2.1064 | 1243.9509 | 2431.0906 | -0.0016933
69 |  | 10.6048 | 35.6929 | 4187 | 0.00080385 | 6.0548 | 6.0556 | -2.1064 | 1244.0099 | 2466.7834 | -0.0016932
70 |  | 10.6048 | 35.6912 | 4187 | 0.00080381 | 6.0556 | 6.0564 | -2.1064 | 1244.069 | 2502.4746 | -0.0016931
71 |  | 10.6048 | 35.6895 | 4187 | 0.00080378 | 6.0564 | 6.0572 | -2.1064 | 1244.128 | 2538.1641 | -0.001693
72 |  | 10.6048 | 35.6878 | 4187 | 0.00080374 | 6.0572 | 6.058 | -2.1064 | 1244.187 | 2573.8518 | -0.001693
73 |  | 10.6048 | 35.6861 | 4187 | 0.0008037 | 6.058 | 6.0588 | -2.1064 | 1244.246 | 2609.5379 | -0.0016929
74 |  | 10.6048 | 35.6844 | 4187 | 0.00080366 | 6.0588 | 6.0596 | -2.1064 | 1244.305 | 2645.2223 | -0.0016928
75 |  | 10.6048 | 35.6827 | 4187 | 0.00080362 | 6.0596 | 6.0604 | -2.1064 | 1244.3641 | 2680.905 | -0.0016927
76 |  | 10.6048 | 35.681 | 4187 | 0.00080359 | 6.0604 | 6.0612 | -2.1064 | 1244.4231 | 2716.586 | -0.0016926
77 |  | 10.6048 | 35.6793 | 4187 | 0.00080355 | 6.0612 | 6.062 | -2.1064 | 1244.4821 | 2752.2653 | -0.0016926
78 |  | 10.6048 | 35.6776 | 4187 | 0.00080351 | 6.062 | 6.0628 | -2.1064 | 1244.5412 | 2787.9429 | -0.0016925
79 |  | 10.6048 | 35.6759 | 4187 | 0.00080347 | 6.0628 | 6.0636 | -2.1064 | 1244.6002 | 2823.6188 | -0.0016924
80 |  | 10.6048 | 35.6742 | 4187 | 0.00080343 | 6.0636 | 6.0644 | -2.1064 | 1244.6593 | 2859.2931 | -0.0016923
81 |  | 10.6048 | 35.6725 | 4187 | 0.00080339 | 6.0644 | 6.0652 | -2.1064 | 1244.7183 | 2894.9656 | -0.0016922
82 |  | 10.6048 | 35.6708 | 4187 | 0.00080336 | 6.0652 | 6.066 | -2.1064 | 1244.7774 | 2930.6365 | -0.0016922
83 |  | 10.6048 | 35.6692 | 4187 | 0.00080332 | 6.066 | 6.0668 | -2.1064 | 1244.8364 | 2966.3056 | -0.0016921
84 |  | 10.6048 | 35.6675 | 4187 | 0.00080328 | 6.0668 | 6.0676 | -2.1064 | 1244.8955 | 3001.9731 | -0.001692
85 |  | 10.6048 | 35.6658 | 4187 | 0.00080324 | 6.0676 | 6.0684 | -2.1064 | 1244.9545 | 3037.6388 | -0.0016919
86 |  | 10.6048 | 35.6641 | 4187 | 0.0008032 | 6.0684 | 6.0692 | -2.1064 | 1245.0136 | 3073.3029 | -0.0016918
87 |  | 10.6048 | 35.6624 | 4187 | 0.00080317 | 6.0692 | 6.07 | -2.1064 | 1245.0727 | 3108.9653 | -0.0016918
88 |  | 10.6048 | 35.6607 | 4187 | 0.00080313 | 6.07 | 6.0708 | -2.1064 | 1245.1317 | 3144.626 | -0.0016917
89 |  | 10.6048 | 35.659 | 4187 | 0.00080309 | 6.0708 | 6.0716 | -2.1064 | 1245.1908 | 3180.285 | -0.0016916
90 |  | 10.6048 | 35.6573 | 4187 | 0.00080305 | 6.0716 | 6.0724 | -2.1064 | 1245.2499 | 3215.9423 | -0.0016915
91 |  | 10.6048 | 35.6556 | 4187 | 0.00080301 | 6.0724 | 6.0732 | -2.1064 | 1245.3089 | 3251.5979 | -0.0016914
92 |  | 10.6048 | 35.6539 | 4187 | 0.00080298 | 6.0732 | 6.074 | -2.1064 | 1245.368 | 3287.2519 | -0.0016914
93 |  | 10.6048 | 35.6522 | 4187 | 0.00080294 | 6.074 | 6.0748 | -2.1064 | 1245.4271 | 3322.9041 | -0.0016913
94 |  | 10.6048 | 35.6505 | 4187 | 0.0008029 | 6.0748 | 6.0756 | -2.1064 | 1245.4862 | 3358.5547 | -0.0016912
95 |  | 10.6048 | 35.6489 | 4187 | 0.00080286 | 6.0756 | 6.0764 | -2.1064 | 1245.5453 | 3394.2035 | -0.0016911
96 |  | 10.6048 | 35.6472 | 4187 | 0.00080282 | 6.0764 | 6.0772 | -2.1064 | 1245.6044 | 3429.8507 | -0.001691
97 |  | 10.6048 | 35.6455 | 4187 | 0.00080279 | 6.0772 | 6.078 | -2.1064 | 1245.6635 | 3465.4961 | -0.001691
98 |  | 10.6048 | 35.6438 | 4187 | 0.00080275 | 6.078 | 6.0789 | -2.1064 | 1245.7225 | 3501.1399 | -0.0016909
99 |  | 10.6048 | 35.6421 | 4187 | 0.00080271 | 6.0789 | 6.0797 | -2.1064 | 1245.7816 | 3536.782 | -0.0016908
100 |  | 10.6048 | 35.6404 | 4187 | 0.00080267 | 6.0797 | 6.0805 | -2.1064 | 1245.8407 | 3572.4224 | -0.0016907
101 |  | 10.6048 | 35.6387 | 4187 | 0.00080263 | 6.0805 | 6.0813 | -2.1064 | 1245.8998 | 3608.0611 | -0.0016906
102 |  | 10.6048 | 35.637 | 4187 | 0.00080259 | 6.0813 | 6.0821 | -2.1064 | 1245.959 | 3643.6981 | -0.0016906
103 |  | 10.6048 | 35.6353 | 4187 | 0.00080256 | 6.0821 | 6.0829 | -2.1064 | 1246.0181 | 3679.3335 | -0.0016905
104 |  | 10.6048 | 35.6336 | 4187 | 0.00080252 | 6.0829 | 6.0837 | -2.1064 | 1246.0772 | 3714.9671 | -0.0016904
105 |  | 10.6048 | 35.6319 | 4187 | 0.00080248 | 6.0837 | 6.0845 | -2.1064 | 1246.1363 | 3750.5991 | -0.0016903
106 |  | 10.6048 | 35.6303 | 4187 | 0.00080244 | 6.0845 | 6.0853 | -2.1064 | 1246.1954 | 3786.2293 | -0.0016902
107 |  | 10.6048 | 35.6286 | 4187 | 0.0008024 | 6.0853 | 6.0861 | -2.1064 | 1246.2545 | 3821.8579 | -0.0016902
108 |  | 10.6048 | 35.6269 | 4187 | 0.00080237 | 6.0861 | 6.0869 | -2.1064 | 1246.3136 | 3857.4848 | -0.0016901
109 |  | 10.6048 | 35.6252 | 4187 | 0.00080233 | 6.0869 | 6.0877 | -2.1064 | 1246.3728 | 3893.1099 | -0.00169
110 |  | 10.6048 | 35.6235 | 4187 | 0.00080229 | 6.0877 | 6.0885 | -2.1064 | 1246.4319 | 3928.7334 | -0.0016899
111 |  | 10.6048 | 35.6218 | 4187 | 0.00080225 | 6.0885 | 6.0893 | -2.1064 | 1246.491 | 3964.3552 | -0.0016898
112 |  | 10.6048 | 35.6201 | 4187 | 0.00080221 | 6.0893 | 6.0901 | -2.1064 | 1246.5502 | 3999.9754 | -0.0016898
113 |  | 10.6048 | 35.6184 | 4187 | 0.00080218 | 6.0901 | 6.0909 | -2.1064 | 1246.6093 | 4035.5938 | -0.0016897
114 |  | 10.6048 | 35.6167 | 4187 | 0.00080214 | 6.0909 | 6.0917 | -2.1064 | 1246.6684 | 4071.2105 | -0.0016896
115 |  | 10.6048 | 35.615 | 4187 | 0.0008021 | 6.0917 | 6.0925 | -2.1064 | 1246.7276 | 4106.8256 | -0.0016895
116 |  | 10.6048 | 35.6134 | 4187 | 0.00080206 | 6.0925 | 6.0933 | -2.1064 | 1246.7867 | 4142.4389 | -0.0016894
117 |  | 10.6048 | 35.6117 | 4187 | 0.00080202 | 6.0933 | 6.0941 | -2.1064 | 1246.8459 | 4178.0506 | -0.0016894
118 |  | 10.6048 | 35.61 | 4187 | 0.00080199 | 6.0941 | 6.0949 | -2.1064 | 1246.905 | 4213.6606 | -0.0016893
119 |  | 10.6048 | 35.6083 | 4187 | 0.00080195 | 6.0949 | 6.0957 | -2.1064 | 1246.9642 | 4249.2689 | -0.0016892
120 |  | 10.6048 | 35.6066 | 4187 | 0.00080191 | 6.0957 | 6.0965 | -2.1064 | 1247.0233 | 4284.8755 | -0.0016891
121 |  | 10.6048 | 35.6049 | 4187 | 0.00080187 | 6.0965 | 6.0973 | -2.1064 | 1247.0825 | 4320.4804 | -0.001689
122 |  | 10.6048 | 35.6032 | 4187 | 0.00080183 | 6.0973 | 6.0981 | -2.1064 | 1247.1417 | 4356.0836 | -0.001689
123 |  | 10.6048 | 35.6015 | 4187 | 0.0008018 | 6.0981 | 6.0989 | -2.1064 | 1247.2008 | 4391.6851 | -0.0016889
124 |  | 10.6048 | 35.5998 | 4187 | 0.00080176 | 6.0989 | 6.0997 | -2.1064 | 1247.26 | 4427.285 | -0.0016888
125 |  | 10.6048 | 35.5982 | 4187 | 0.00080172 | 6.0997 | 6.1005 | -2.1064 | 1247.3192 | 4462.8831 | -0.0016887
126 |  | 10.6048 | 35.5965 | 4187 | 0.00080168 | 6.1005 | 6.1013 | -2.1064 | 1247.3783 | 4498.4796 | -0.0016886
127 |  | 10.6048 | 35.5948 | 4187 | 0.00080164 | 6.1013 | 6.1021 | -2.1064 | 1247.4375 | 4534.0744 | -0.0016886
128 |  | 10.6048 | 35.5931 | 4187 | 0.00080161 | 6.1021 | 6.1029 | -2.1064 | 1247.4967 | 4569.6675 | -0.0016885
129 |  | 10.6048 | 35.5914 | 4187 | 0.00080157 | 6.1029 | 6.1037 | -2.1064 | 1247.5559 | 4605.2589 | -0.0016884
130 |  | 10.6048 | 35.5897 | 4187 | 0.00080153 | 6.1037 | 6.1045 | -2.1064 | 1247.6151 | 4640.8486 | -0.0016883
131 |  | 10.6048 | 35.588 | 4187 | 0.00080149 | 6.1045 | 6.1053 | -2.1064 | 1247.6742 | 4676.4366 | -0.0016882
132 |  | 10.6048 | 35.5863 | 4187 | 0.00080145 | 6.1053 | 6.1061 | -2.1064 | 1247.7334 | 4712.023 | -0.0016882
133 |  | 10.6048 | 35.5846 | 4187 | 0.00080142 | 6.1061 | 6.1069 | -2.1064 | 1247.7926 | 4747.6076 | -0.0016881
134 |  | 10.6048 | 35.583 | 4187 | 0.00080138 | 6.1069 | 6.1077 | -2.1064 | 1247.8518 | 4783.1906 | -0.001688
135 |  | 10.6048 | 35.5813 | 4187 | 0.00080134 | 6.1077 | 6.1085 | -2.1064 | 1247.911 | 4818.7718 | -0.0016879
136 |  | 10.6048 | 35.5796 | 4187 | 0.0008013 | 6.1085 | 6.1093 | -2.1064 | 1247.9702 | 4854.3514 | -0.0016878
137 |  | 10.6048 | 35.5779 | 4187 | 0.00080126 | 6.1093 | 6.1101 | -2.1064 | 1248.0294 | 4889.9293 | -0.0016878
138 |  | 10.6048 | 35.5762 | 4187 | 0.00080123 | 6.1101 | 6.1109 | -2.1064 | 1248.0886 | 4925.5055 | -0.0016877
139 |  | 10.6048 | 35.5745 | 4187 | 0.00080119 | 6.1109 | 6.1117 | -2.1064 | 1248.1479 | 4961.08 | -0.0016876
140 |  | 10.6048 | 35.5728 | 4187 | 0.00080115 | 6.1117 | 6.1125 | -2.1064 | 1248.2071 | 4996.6529 | -0.0016875
141 |  | 10.6048 | 35.5711 | 4187 | 0.00080111 | 6.1125 | 6.1133 | -2.1064 | 1248.2663 | 5032.224 | -0.0016874
142 |  | 10.6048 | 35.5695 | 4187 | 0.00080107 | 6.1133 | 6.1141 | -2.1064 | 1248.3255 | 5067.7935 | -0.0016874
143 |  | 10.6048 | 35.5678 | 4187 | 0.00080104 | 6.1141 | 6.1149 | -2.1064 | 1248.3847 | 5103.3613 | -0.0016873
144 |  | 10.6048 | 35.5661 | 4187 | 0.000801 | 6.1149 | 6.1157 | -2.1064 | 1248.4439 | 5138.9273 | -0.0016872
145 |  | 10.6048 | 35.5644 | 4187 | 0.00080096 | 6.1157 | 6.1165 | -2.1064 | 1248.5032 | 5174.4917 | -0.0016871
146 |  | 10.6048 | 35.5627 | 4187 | 0.00080092 | 6.1165 | 6.1173 | -2.1064 | 1248.5624 | 5210.0544 | -0.001687
147 |  | 10.6048 | 35.561 | 4187 | 0.00080088 | 6.1173 | 6.1181 | -2.1064 | 1248.6216 | 5245.6155 | -0.001687
148 |  | 10.6048 | 35.5593 | 4187 | 0.00080085 | 6.1181 | 6.1189 | -2.1064 | 1248.6809 | 5281.1748 | -0.0016869
149 |  | 10.6048 | 35.5576 | 4187 | 0.00080081 | 6.1189 | 6.1197 | -2.1064 | 1248.7401 | 5316.7325 | -0.0016868
150 |  | 10.6048 | 35.556 | 4187 | 0.00080077 | 6.1197 | 6.1205 | -2.1064 | 1248.7993 | 5352.2884 | -0.0016867
151 |  | 10.6048 | 35.5543 | 4187 | 0.00080073 | 6.1205 | 6.1213 | -2.1064 | 1248.8586 | 5387.8427 | -0.0016866
152 |  | 10.6048 | 35.5526 | 4187 | 0.00080069 | 6.1213 | 6.1221 | -2.1064 | 1248.9178 | 5423.3953 | -0.0016866
153 |  | 10.6048 | 35.5509 | 4187 | 0.00080066 | 6.1221 | 6.1229 | -2.1064 | 1248.9771 | 5458.9462 | -0.0016865
154 |  | 10.6048 | 35.5492 | 4187 | 0.00080062 | 6.1229 | 6.1237 | -2.1064 | 1249.0363 | 5494.4954 | -0.0016864
155 |  | 10.6048 | 35.5475 | 4187 | 0.00080058 | 6.1237 | 6.1245 | -2.1064 | 1249.0956 | 5530.0429 | -0.0016863
156 |  | 10.6048 | 35.5458 | 4187 | 0.00080054 | 6.1245 | 6.1253 | -2.1064 | 1249.1548 | 5565.5888 | -0.0016862
157 |  | 10.6048 | 35.5442 | 4187 | 0.0008005 | 6.1253 | 6.1261 | -2.1064 | 1249.2141 | 5601.1329 | -0.0016862
158 |  | 10.6048 | 35.5425 | 4187 | 0.00080047 | 6.1261 | 6.1269 | -2.1064 | 1249.2734 | 5636.6754 | -0.0016861
159 |  | 10.6048 | 35.5408 | 4187 | 0.00080043 | 6.1269 | 6.1277 | -2.1064 | 1249.3326 | 5672.2162 | -0.001686
160 |  | 10.6048 | 35.5391 | 4187 | 0.00080039 | 6.1277 | 6.1285 | -2.1064 | 1249.3919 | 5707.7553 | -0.0016859
161 |  | 10.6048 | 35.5374 | 4187 | 0.00080035 | 6.1285 | 6.1293 | -2.1064 | 1249.4512 | 5743.2927 | -0.0016858
162 |  | 10.6048 | 35.5357 | 4187 | 0.00080031 | 6.1293 | 6.1301 | -2.1064 | 1249.5105 | 5778.8284 | -0.0016858
163 |  | 10.6048 | 35.534 | 4187 | 0.00080028 | 6.1301 | 6.1309 | -2.1064 | 1249.5697 | 5814.3625 | -0.0016857
164 |  | 10.6048 | 35.5324 | 4187 | 0.00080024 | 6.1309 | 6.1317 | -2.1064 | 1249.629 | 5849.8948 | -0.0016856
165 |  | 10.6048 | 35.5307 | 4187 | 0.0008002 | 6.1317 | 6.1325 | -2.1064 | 1249.6883 | 5885.4255 | -0.0016855
166 |  | 10.6048 | 35.529 | 4187 | 0.00080016 | 6.1325 | 6.1333 | -2.1064 | 1249.7476 | 5920.9545 | -0.0016854
167 |  | 10.6048 | 35.5273 | 4187 | 0.00080012 | 6.1333 | 6.1341 | -2.1064 | 1249.8069 | 5956.4818 | -0.0016854
168 |  | 10.6048 | 35.5256 | 4187 | 0.00080009 | 6.1341 | 6.1349 | -2.1064 | 1249.8662 | 5992.0074 | -0.0016853
169 |  | 10.6048 | 35.5239 | 4187 | 0.00080005 | 6.1349 | 6.1357 | -2.1064 | 1249.9255 | 6027.5313 | -0.0016852
170 |  | 10.6048 | 35.5222 | 4187 | 0.00080001 | 6.1357 | 6.1365 | -2.1064 | 1249.9848 | 6063.0536 | -0.0016851
171 |  | 10.6048 | 35.5206 | 4187 | 0.00079997 | 6.1365 | 6.1373 | -2.1064 | 1250.0441 | 6098.5741 | -0.001685
172 |  | 10.6048 | 35.5189 | 4187 | 0.00079993 | 6.1373 | 6.1381 | -2.1064 | 1250.1034 | 6134.093 | -0.001685
173 |  | 10.6048 | 35.5172 | 4187 | 0.0007999 | 6.1381 | 6.1389 | -2.1064 | 1250.1627 | 6169.6102 | -0.0016849
174 |  | 10.6048 | 35.5155 | 4187 | 0.00079986 | 6.1389 | 6.1397 | -2.1064 | 1250.222 | 6205.1257 | -0.0016848
175 |  | 10.6048 | 35.5138 | 4187 | 0.00079982 | 6.1397 | 6.1405 | -2.1064 | 1250.2813 | 6240.6395 | -0.0016847
176 |  | 10.6048 | 35.5121 | 4187 | 0.00079978 | 6.1405 | 6.1413 | -2.1064 | 1250.3406 | 6276.1516 | -0.0016846
177 |  | 10.6048 | 35.5104 | 4187 | 0.00079974 | 6.1413 | 6.1421 | -2.1064 | 1250.3999 | 6311.6621 | -0.0016846
178 |  | 10.6048 | 35.5088 | 4187 | 0.00079971 | 6.1421 | 6.1429 | -2.1064 | 1250.4592 | 6347.1708 | -0.0016845
179 |  | 10.6048 | 35.5071 | 4187 | 0.00079967 | 6.1429 | 6.1437 | -2.1064 | 1250.5186 | 6382.6779 | -0.0016844
180 |  | 10.6048 | 35.5054 | 4187 | 0.00079963 | 6.1437 | 6.1445 | -2.1064 | 1250.5779 | 6418.1833 | -0.0016843
181 |  | 10.6048 | 35.5037 | 4187 | 0.00079959 | 6.1445 | 6.1453 | -2.1064 | 1250.6372 | 6453.687 | -0.0016842
182 |  | 10.6048 | 35.502 | 4187 | 0.00079955 | 6.1453 | 6.1461 | -2.1064 | 1250.6965 | 6489.1891 | -0.0016842
183 |  | 10.6048 | 35.5003 | 4187 | 0.00079952 | 6.1461 | 6.1469 | -2.1064 | 1250.7559 | 6524.6894 | -0.0016841
184 |  | 10.6048 | 35.4987 | 4187 | 0.00079948 | 6.1469 | 6.1477 | -2.1064 | 1250.8152 | 6560.1881 | -0.001684
185 |  | 10.6048 | 35.497 | 4187 | 0.00079944 | 6.1477 | 6.1485 | -2.1064 | 1250.8745 | 6595.685 | -0.0016839
186 |  | 10.6048 | 35.4953 | 4187 | 0.0007994 | 6.1485 | 6.1493 | -2.1064 | 1250.9339 | 6631.1803 | -0.0016838
187 |  | 10.6048 | 35.4936 | 4187 | 0.00079936 | 6.1493 | 6.1501 | -2.1064 | 1250.9932 | 6666.6739 | -0.0016838
188 |  | 10.6048 | 35.4919 | 4187 | 0.00079933 | 6.1501 | 6.1509 | -2.1064 | 1251.0526 | 6702.1659 | -0.0016837
189 |  | 10.6048 | 35.4902 | 4187 | 0.00079929 | 6.1509 | 6.1517 | -2.1064 | 1251.1119 | 6737.6561 | -0.0016836
190 |  | 10.6048 | 35.4886 | 4187 | 0.00079925 | 6.1517 | 6.1525 | -2.1064 | 1251.1713 | 6773.1447 | -0.0016835
191 |  | 10.6048 | 35.4869 | 4187 | 0.00079921 | 6.1525 | 6.1533 | -2.1064 | 1251.2306 | 6808.6315 | -0.0016834
192 |  | 10.6048 | 35.4852 | 4187 | 0.00079918 | 6.1533 | 6.1541 | -2.1064 | 1251.29 | 6844.1167 | -0.0016834
193 |  | 10.6048 | 35.4835 | 4187 | 0.00079914 | 6.1541 | 6.1549 | -2.1064 | 1251.3494 | 6879.6002 | -0.0016833
194 |  | 10.6048 | 35.4818 | 4187 | 0.0007991 | 6.1549 | 6.1557 | -2.1064 | 1251.4087 | 6915.082 | -0.0016832
195 |  | 10.6048 | 35.4801 | 4187 | 0.00079906 | 6.1557 | 6.1565 | -2.1064 | 1251.4681 | 6950.5622 | -0.0016831
196 |  | 10.6048 | 35.4785 | 4187 | 0.00079902 | 6.1565 | 6.1573 | -2.1064 | 1251.5275 | 6986.0406 | -0.001683
197 |  | 10.6048 | 35.4768 | 4187 | 0.00079899 | 6.1573 | 6.1581 | -2.1064 | 1251.5868 | 7021.5174 | -0.001683
198 |  | 10.6048 | 35.4751 | 4187 | 0.00079895 | 6.1581 | 6.1589 | -2.1064 | 1251.6462 | 7056.9925 | -0.0016829
199 |  | 10.6048 | 35.4734 | 4187 | 0.00079891 | 6.1589 | 6.1597 | -2.1064 | 1251.7056 | 7092.4659 | -0.0016828
200 |  | 10.6048 | 35.4717 | 4187 | 0.00079887 | 6.1597 | 6.1605 | -2.1064 | 1251.765 | 7127.9376 | -0.0016827
201 |  | 10.6048 | 35.47 | 4187 | 0.00079883 | 6.1605 | 6.1613 | -2.1064 | 1251.8244 | 7163.4077 | -0.0016826
202 |  | 10.6048 | 35.4684 | 4187 | 0.0007988 | 6.1613 | 6.1621 | -2.1064 | 1251.8837 | 7198.876 | -0.0016826
203 |  | 10.6048 | 35.4667 | 4187 | 0.00079876 | 6.1621 | 6.1629 | -2.1064 | 1251.9431 | 7234.3427 | -0.0016825
204 |  | 10.6048 | 35.465 | 4187 | 0.00079872 | 6.1629 | 6.1637 | -2.1064 | 1252.0025 | 7269.8077 | -0.0016824
205 |  | 10.6048 | 35.4633 | 4187 | 0.00079868 | 6.1637 | 6.1645 | -2.1064 | 1252.0619 | 7305.271 | -0.0016823
206 |  | 10.6048 | 35.4616 | 4187 | 0.00079864 | 6.1645 | 6.1653 | -2.1064 | 1252.1213 | 7340.7327 | -0.0016822
207 |  | 10.6048 | 35.4599 | 4187 | 0.00079861 | 6.1653 | 6.1661 | -2.1064 | 1252.1807 | 7376.1926 | -0.0016822
208 |  | 10.6048 | 35.4583 | 4187 | 0.00079857 | 6.1661 | 6.1669 | -2.1064 | 1252.2401 | 7411.6509 | -0.0016821
209 |  | 10.6048 | 35.4566 | 4187 | 0.00079853 | 6.1669 | 6.1677 | -2.1064 | 1252.2995 | 7447.1074 | -0.001682
210 |  | 10.6048 | 35.4549 | 4187 | 0.00079849 | 6.1677 | 6.1685 | -2.1064 | 1252.3589 | 7482.5623 | -0.0016819
211 |  | 10.6048 | 35.4532 | 4187 | 0.00079846 | 6.1685 | 6.1693 | -2.1064 | 1252.4184 | 7518.0156 | -0.0016818
212 |  | 10.6048 | 35.4515 | 4187 | 0.00079842 | 6.1693 | 6.1701 | -2.1064 | 1252.4778 | 7553.4671 | -0.0016818
213 |  | 10.6048 | 35.4499 | 4187 | 0.00079838 | 6.1701 | 6.1709 | -2.1064 | 1252.5372 | 7588.917 | -0.0016817
214 |  | 10.6048 | 35.4482 | 4187 | 0.00079834 | 6.1709 | 6.1717 | -2.1064 | 1252.5966 | 7624.3651 | -0.0016816
215 |  | 10.6048 | 35.4465 | 4187 | 0.0007983 | 6.1717 | 6.1725 | -2.1064 | 1252.656 | 7659.8116 | -0.0016815
216 |  | 10.6048 | 35.4448 | 4187 | 0.00079827 | 6.1725 | 6.1733 | -2.1064 | 1252.7155 | 7695.2564 | -0.0016814
217 |  | 10.6048 | 35.4431 | 4187 | 0.00079823 | 6.1733 | 6.1741 | -2.1064 | 1252.7749 | 7730.6996 | -0.0016814
218 |  | 10.6048 | 35.4414 | 4187 | 0.00079819 | 6.1741 | 6.1749 | -2.1064 | 1252.8343 | 7766.141 | -0.0016813
219 |  | 10.6048 | 35.4398 | 4187 | 0.00079815 | 6.1749 | 6.1757 | -2.1064 | 1252.8938 | 7801.5808 | -0.0016812
220 |  | 10.6048 | 35.4381 | 4187 | 0.00079811 | 6.1757 | 6.1765 | -2.1064 | 1252.9532 | 7837.0189 | -0.0016811
221 |  | 10.6048 | 35.4364 | 4187 | 0.00079808 | 6.1765 | 6.1773 | -2.1064 | 1253.0126 | 7872.4553 | -0.001681
222 |  | 10.6048 | 35.4347 | 4187 | 0.00079804 | 6.1773 | 6.1781 | -2.1064 | 1253.0721 | 7907.89 | -0.001681
223 |  | 10.6048 | 35.433 | 4187 | 0.000798 | 6.1781 | 6.1789 | -2.1064 | 1253.1315 | 7943.323 | -0.0016809
224 |  | 10.6048 | 35.4314 | 4187 | 0.00079796 | 6.1789 | 6.1797 | -2.1064 | 1253.191 | 7978.7544 | -0.0016808
225 |  | 10.6048 | 35.4297 | 4187 | 0.00079793 | 6.1797 | 6.1805 | -2.1064 | 1253.2504 | 8014.1841 | -0.0016807
226 |  | 10.6048 | 35.428 | 4187 | 0.00079789 | 6.1805 | 6.1813 | -2.1064 | 1253.3099 | 8049.6121 | -0.0016806
227 |  | 10.6048 | 35.4263 | 4187 | 0.00079785 | 6.1813 | 6.1821 | -2.1064 | 1253.3693 | 8085.0384 | -0.0016806
228 |  | 10.6048 | 35.4246 | 4187 | 0.00079781 | 6.1821 | 6.1829 | -2.1064 | 1253.4288 | 8120.463 | -0.0016805
229 |  | 10.6048 | 35.423 | 4187 | 0.00079777 | 6.1829 | 6.1837 | -2.1064 | 1253.4883 | 8155.886 | -0.0016804
230 |  | 10.6048 | 35.4213 | 4187 | 0.00079774 | 6.1837 | 6.1845 | -2.1064 | 1253.5477 | 8191.3073 | -0.0016803
231 |  | 10.6048 | 35.4196 | 4187 | 0.0007977 | 6.1845 | 6.1853 | -2.1064 | 1253.6072 | 8226.7269 | -0.0016802
232 |  | 10.6048 | 35.4179 | 4187 | 0.00079766 | 6.1853 | 6.1861 | -2.1064 | 1253.6667 | 8262.1448 | -0.0016802
233 |  | 10.6048 | 35.4162 | 4187 | 0.00079762 | 6.1861 | 6.1869 | -2.1064 | 1253.7261 | 8297.561 | -0.0016801
234 |  | 10.6048 | 35.4146 | 4187 | 0.00079758 | 6.1869 | 6.1877 | -2.1064 | 1253.7856 | 8332.9756 | -0.00168
235 |  | 10.6048 | 35.4129 | 4187 | 0.00079755 | 6.1877 | 6.1885 | -2.1064 | 1253.8451 | 8368.3885 | -0.0016799
236 |  | 10.6048 | 35.4112 | 4187 | 0.00079751 | 6.1885 | 6.1893 | -2.1064 | 1253.9046 | 8403.7997 | -0.0016798

## Fus200
|  |  | buis | verlies W/M | L /°C/sec
diam | wandikte |  | inhoud l/m |  | W/M
200 | 27.4 | 3.1416 | 16.5586 | 37.9427 | 4187
[8 empty] | J/sec/mtr | aantal mtr. | verlies
|  | buis | verlies W/M | L /°C/sec | verlies temp | begintemp | eindtemp | verlies | bij 1°C | totaal J/sec
|  | inhoud L |  | W/M | °C per M | °C | °C | per m°C | daling | aantal mtr
1 | 200 | 16.5586 | 37.9427 | 4187 | 0.00054727 | 6 | 6.0005 | -2.2319 | 1827.2503 | 37.9427 | -0.0012215
2 |  | 16.5586 | 37.9415 | 4187 | 0.00054725 | 6.0005 | 6.0011 | -2.2319 | 1827.3091 | 75.8841 | -0.0012214
3 |  | 16.5586 | 37.9402 | 4187 | 0.00054724 | 6.0011 | 6.0016 | -2.2319 | 1827.3679 | 113.8244 | -0.0012214
4 |  | 16.5586 | 37.939 | 4187 | 0.00054722 | 6.0016 | 6.0022 | -2.2319 | 1827.4268 | 151.7634 | -0.0012213
5 |  | 16.5586 | 37.9378 | 4187 | 0.0005472 | 6.0022 | 6.0027 | -2.2319 | 1827.4856 | 189.7012 | -0.0012213
6 |  | 16.5586 | 37.9366 | 4187 | 0.00054718 | 6.0027 | 6.0033 | -2.2319 | 1827.5444 | 227.6378 | -0.0012213
7 |  | 16.5586 | 37.9354 | 4187 | 0.00054716 | 6.0033 | 6.0038 | -2.2319 | 1827.6033 | 265.5731 | -0.0012212
8 |  | 16.5586 | 37.9341 | 4187 | 0.00054715 | 6.0038 | 6.0044 | -2.2319 | 1827.6621 | 303.5073 | -0.0012212
9 |  | 16.5586 | 37.9329 | 4187 | 0.00054713 | 6.0044 | 6.0049 | -2.2319 | 1827.721 | 341.4402 | -0.0012212
10 |  | 16.5586 | 37.9317 | 4187 | 0.00054711 | 6.0049 | 6.0055 | -2.2319 | 1827.7798 | 379.3719 | -0.0012211
11 |  | 16.5586 | 37.9305 | 4187 | 0.00054709 | 6.0055 | 6.006 | -2.2319 | 1827.8386 | 417.3023 | -0.0012211
12 |  | 16.5586 | 37.9292 | 4187 | 0.00054708 | 6.006 | 6.0066 | -2.2319 | 1827.8975 | 455.2316 | -0.001221
13 |  | 16.5586 | 37.928 | 4187 | 0.00054706 | 6.0066 | 6.0071 | -2.2319 | 1827.9563 | 493.1596 | -0.001221
14 |  | 16.5586 | 37.9268 | 4187 | 0.00054704 | 6.0071 | 6.0077 | -2.2319 | 1828.0152 | 531.0864 | -0.001221
15 |  | 16.5586 | 37.9256 | 4187 | 0.00054702 | 6.0077 | 6.0082 | -2.2319 | 1828.074 | 569.012 | -0.0012209
16 |  | 16.5586 | 37.9244 | 4187 | 0.00054701 | 6.0082 | 6.0088 | -2.2319 | 1828.1329 | 606.9364 | -0.0012209
17 |  | 16.5586 | 37.9231 | 4187 | 0.00054699 | 6.0088 | 6.0093 | -2.2319 | 1828.1917 | 644.8595 | -0.0012208
18 |  | 16.5586 | 37.9219 | 4187 | 0.00054697 | 6.0093 | 6.0098 | -2.2319 | 1828.2506 | 682.7814 | -0.0012208
19 |  | 16.5586 | 37.9207 | 4187 | 0.00054695 | 6.0098 | 6.0104 | -2.2319 | 1828.3094 | 720.7021 | -0.0012208
20 |  | 16.5586 | 37.9195 | 4187 | 0.00054694 | 6.0104 | 6.0109 | -2.2319 | 1828.3683 | 758.6216 | -0.0012207
21 |  | 16.5586 | 37.9183 | 4187 | 0.00054692 | 6.0109 | 6.0115 | -2.2319 | 1828.4272 | 796.5399 | -0.0012207
22 |  | 16.5586 | 37.917 | 4187 | 0.0005469 | 6.0115 | 6.012 | -2.2319 | 1828.486 | 834.4569 | -0.0012206
23 |  | 16.5586 | 37.9158 | 4187 | 0.00054688 | 6.012 | 6.0126 | -2.2319 | 1828.5449 | 872.3727 | -0.0012206
24 |  | 16.5586 | 37.9146 | 4187 | 0.00054687 | 6.0126 | 6.0131 | -2.2319 | 1828.6038 | 910.2873 | -0.0012206
25 |  | 16.5586 | 37.9134 | 4187 | 0.00054685 | 6.0131 | 6.0137 | -2.2319 | 1828.6626 | 948.2007 | -0.0012205
26 |  | 16.5586 | 37.9122 | 4187 | 0.00054683 | 6.0137 | 6.0142 | -2.2319 | 1828.7215 | 986.1129 | -0.0012205
27 |  | 16.5586 | 37.9109 | 4187 | 0.00054681 | 6.0142 | 6.0148 | -2.2319 | 1828.7804 | 1024.0238 | -0.0012204
28 |  | 16.5586 | 37.9097 | 4187 | 0.00054679 | 6.0148 | 6.0153 | -2.2319 | 1828.8392 | 1061.9335 | -0.0012204
29 |  | 16.5586 | 37.9085 | 4187 | 0.00054678 | 6.0153 | 6.0159 | -2.2319 | 1828.8981 | 1099.842 | -0.0012204
30 |  | 16.5586 | 37.9073 | 4187 | 0.00054676 | 6.0159 | 6.0164 | -2.2319 | 1828.957 | 1137.7493 | -0.0012203
31 |  | 16.5586 | 37.9061 | 4187 | 0.00054674 | 6.0164 | 6.017 | -2.2319 | 1829.0159 | 1175.6554 | -0.0012203
32 |  | 16.5586 | 37.9048 | 4187 | 0.00054672 | 6.017 | 6.0175 | -2.2319 | 1829.0748 | 1213.5602 | -0.0012202
33 |  | 16.5586 | 37.9036 | 4187 | 0.00054671 | 6.0175 | 6.0181 | -2.2319 | 1829.1336 | 1251.4638 | -0.0012202
34 |  | 16.5586 | 37.9024 | 4187 | 0.00054669 | 6.0181 | 6.0186 | -2.2319 | 1829.1925 | 1289.3662 | -0.0012202
35 |  | 16.5586 | 37.9012 | 4187 | 0.00054667 | 6.0186 | 6.0191 | -2.2319 | 1829.2514 | 1327.2674 | -0.0012201
36 |  | 16.5586 | 37.9 | 4187 | 0.00054665 | 6.0191 | 6.0197 | -2.2319 | 1829.3103 | 1365.1673 | -0.0012201
37 |  | 16.5586 | 37.8987 | 4187 | 0.00054664 | 6.0197 | 6.0202 | -2.2319 | 1829.3692 | 1403.0661 | -0.0012201
38 |  | 16.5586 | 37.8975 | 4187 | 0.00054662 | 6.0202 | 6.0208 | -2.2319 | 1829.4281 | 1440.9636 | -0.00122
39 |  | 16.5586 | 37.8963 | 4187 | 0.0005466 | 6.0208 | 6.0213 | -2.2319 | 1829.487 | 1478.8599 | -0.00122
40 |  | 16.5586 | 37.8951 | 4187 | 0.00054658 | 6.0213 | 6.0219 | -2.2319 | 1829.5459 | 1516.755 | -0.0012199
41 |  | 16.5586 | 37.8939 | 4187 | 0.00054657 | 6.0219 | 6.0224 | -2.2319 | 1829.6048 | 1554.6488 | -0.0012199
42 |  | 16.5586 | 37.8926 | 4187 | 0.00054655 | 6.0224 | 6.023 | -2.2319 | 1829.6637 | 1592.5414 | -0.0012199
43 |  | 16.5586 | 37.8914 | 4187 | 0.00054653 | 6.023 | 6.0235 | -2.2319 | 1829.7226 | 1630.4329 | -0.0012198
44 |  | 16.5586 | 37.8902 | 4187 | 0.00054651 | 6.0235 | 6.0241 | -2.2319 | 1829.7815 | 1668.3231 | -0.0012198
45 |  | 16.5586 | 37.889 | 4187 | 0.0005465 | 6.0241 | 6.0246 | -2.2319 | 1829.8404 | 1706.212 | -0.0012197
46 |  | 16.5586 | 37.8878 | 4187 | 0.00054648 | 6.0246 | 6.0252 | -2.2319 | 1829.8993 | 1744.0998 | -0.0012197
47 |  | 16.5586 | 37.8865 | 4187 | 0.00054646 | 6.0252 | 6.0257 | -2.2319 | 1829.9582 | 1781.9863 | -0.0012197
48 |  | 16.5586 | 37.8853 | 4187 | 0.00054644 | 6.0257 | 6.0262 | -2.2319 | 1830.0171 | 1819.8716 | -0.0012196
49 |  | 16.5586 | 37.8841 | 4187 | 0.00054643 | 6.0262 | 6.0268 | -2.2319 | 1830.0761 | 1857.7557 | -0.0012196
50 |  | 16.5586 | 37.8829 | 4187 | 0.00054641 | 6.0268 | 6.0273 | -2.2319 | 1830.135 | 1895.6386 | -0.0012195
51 |  | 16.5586 | 37.8817 | 4187 | 0.00054639 | 6.0273 | 6.0279 | -2.2319 | 1830.1939 | 1933.5203 | -0.0012195
52 |  | 16.5586 | 37.8804 | 4187 | 0.00054637 | 6.0279 | 6.0284 | -2.2319 | 1830.2528 | 1971.4007 | -0.0012195
53 |  | 16.5586 | 37.8792 | 4187 | 0.00054636 | 6.0284 | 6.029 | -2.2319 | 1830.3117 | 2009.2799 | -0.0012194
54 |  | 16.5586 | 37.878 | 4187 | 0.00054634 | 6.029 | 6.0295 | -2.2319 | 1830.3707 | 2047.1579 | -0.0012194
55 |  | 16.5586 | 37.8768 | 4187 | 0.00054632 | 6.0295 | 6.0301 | -2.2319 | 1830.4296 | 2085.0347 | -0.0012193
56 |  | 16.5586 | 37.8756 | 4187 | 0.0005463 | 6.0301 | 6.0306 | -2.2319 | 1830.4885 | 2122.9103 | -0.0012193
57 |  | 16.5586 | 37.8743 | 4187 | 0.00054628 | 6.0306 | 6.0312 | -2.2319 | 1830.5474 | 2160.7846 | -0.0012193
58 |  | 16.5586 | 37.8731 | 4187 | 0.00054627 | 6.0312 | 6.0317 | -2.2319 | 1830.6064 | 2198.6577 | -0.0012192
59 |  | 16.5586 | 37.8719 | 4187 | 0.00054625 | 6.0317 | 6.0323 | -2.2319 | 1830.6653 | 2236.5296 | -0.0012192
60 |  | 16.5586 | 37.8707 | 4187 | 0.00054623 | 6.0323 | 6.0328 | -2.2319 | 1830.7242 | 2274.4003 | -0.0012191
61 |  | 16.5586 | 37.8695 | 4187 | 0.00054621 | 6.0328 | 6.0334 | -2.2319 | 1830.7832 | 2312.2698 | -0.0012191
62 |  | 16.5586 | 37.8682 | 4187 | 0.0005462 | 6.0334 | 6.0339 | -2.2319 | 1830.8421 | 2350.138 | -0.0012191
63 |  | 16.5586 | 37.867 | 4187 | 0.00054618 | 6.0339 | 6.0344 | -2.2319 | 1830.9011 | 2388.0051 | -0.001219
64 |  | 16.5586 | 37.8658 | 4187 | 0.00054616 | 6.0344 | 6.035 | -2.2319 | 1830.96 | 2425.8709 | -0.001219
65 |  | 16.5586 | 37.8646 | 4187 | 0.00054614 | 6.035 | 6.0355 | -2.2319 | 1831.0189 | 2463.7354 | -0.001219
66 |  | 16.5586 | 37.8634 | 4187 | 0.00054613 | 6.0355 | 6.0361 | -2.2319 | 1831.0779 | 2501.5988 | -0.0012189
67 |  | 16.5586 | 37.8622 | 4187 | 0.00054611 | 6.0361 | 6.0366 | -2.2319 | 1831.1368 | 2539.461 | -0.0012189
68 |  | 16.5586 | 37.8609 | 4187 | 0.00054609 | 6.0366 | 6.0372 | -2.2319 | 1831.1958 | 2577.3219 | -0.0012188
69 |  | 16.5586 | 37.8597 | 4187 | 0.00054607 | 6.0372 | 6.0377 | -2.2319 | 1831.2547 | 2615.1816 | -0.0012188
70 |  | 16.5586 | 37.8585 | 4187 | 0.00054606 | 6.0377 | 6.0383 | -2.2319 | 1831.3137 | 2653.0401 | -0.0012188
71 |  | 16.5586 | 37.8573 | 4187 | 0.00054604 | 6.0383 | 6.0388 | -2.2319 | 1831.3727 | 2690.8974 | -0.0012187
72 |  | 16.5586 | 37.8561 | 4187 | 0.00054602 | 6.0388 | 6.0394 | -2.2319 | 1831.4316 | 2728.7534 | -0.0012187
73 |  | 16.5586 | 37.8548 | 4187 | 0.000546 | 6.0394 | 6.0399 | -2.2319 | 1831.4906 | 2766.6083 | -0.0012186
74 |  | 16.5586 | 37.8536 | 4187 | 0.00054599 | 6.0399 | 6.0405 | -2.2319 | 1831.5495 | 2804.4619 | -0.0012186
75 |  | 16.5586 | 37.8524 | 4187 | 0.00054597 | 6.0405 | 6.041 | -2.2319 | 1831.6085 | 2842.3143 | -0.0012186
76 |  | 16.5586 | 37.8512 | 4187 | 0.00054595 | 6.041 | 6.0415 | -2.2319 | 1831.6675 | 2880.1655 | -0.0012185
77 |  | 16.5586 | 37.85 | 4187 | 0.00054593 | 6.0415 | 6.0421 | -2.2319 | 1831.7264 | 2918.0154 | -0.0012185
78 |  | 16.5586 | 37.8487 | 4187 | 0.00054592 | 6.0421 | 6.0426 | -2.2319 | 1831.7854 | 2955.8642 | -0.0012184
79 |  | 16.5586 | 37.8475 | 4187 | 0.0005459 | 6.0426 | 6.0432 | -2.2319 | 1831.8444 | 2993.7117 | -0.0012184
80 |  | 16.5586 | 37.8463 | 4187 | 0.00054588 | 6.0432 | 6.0437 | -2.2319 | 1831.9033 | 3031.558 | -0.0012184
81 |  | 16.5586 | 37.8451 | 4187 | 0.00054586 | 6.0437 | 6.0443 | -2.2319 | 1831.9623 | 3069.4031 | -0.0012183
82 |  | 16.5586 | 37.8439 | 4187 | 0.00054585 | 6.0443 | 6.0448 | -2.2319 | 1832.0213 | 3107.247 | -0.0012183
83 |  | 16.5586 | 37.8427 | 4187 | 0.00054583 | 6.0448 | 6.0454 | -2.2319 | 1832.0803 | 3145.0896 | -0.0012182
84 |  | 16.5586 | 37.8414 | 4187 | 0.00054581 | 6.0454 | 6.0459 | -2.2319 | 1832.1393 | 3182.9311 | -0.0012182
85 |  | 16.5586 | 37.8402 | 4187 | 0.00054579 | 6.0459 | 6.0465 | -2.2319 | 1832.1982 | 3220.7713 | -0.0012182
86 |  | 16.5586 | 37.839 | 4187 | 0.00054577 | 6.0465 | 6.047 | -2.2319 | 1832.2572 | 3258.6103 | -0.0012181
87 |  | 16.5586 | 37.8378 | 4187 | 0.00054576 | 6.047 | 6.0475 | -2.2319 | 1832.3162 | 3296.4481 | -0.0012181
88 |  | 16.5586 | 37.8366 | 4187 | 0.00054574 | 6.0475 | 6.0481 | -2.2319 | 1832.3752 | 3334.2846 | -0.001218
89 |  | 16.5586 | 37.8353 | 4187 | 0.00054572 | 6.0481 | 6.0486 | -2.2319 | 1832.4342 | 3372.12 | -0.001218
90 |  | 16.5586 | 37.8341 | 4187 | 0.0005457 | 6.0486 | 6.0492 | -2.2319 | 1832.4932 | 3409.9541 | -0.001218
91 |  | 16.5586 | 37.8329 | 4187 | 0.00054569 | 6.0492 | 6.0497 | -2.2319 | 1832.5522 | 3447.787 | -0.0012179
92 |  | 16.5586 | 37.8317 | 4187 | 0.00054567 | 6.0497 | 6.0503 | -2.2319 | 1832.6112 | 3485.6187 | -0.0012179
93 |  | 16.5586 | 37.8305 | 4187 | 0.00054565 | 6.0503 | 6.0508 | -2.2319 | 1832.6702 | 3523.4492 | -0.0012179
94 |  | 16.5586 | 37.8293 | 4187 | 0.00054563 | 6.0508 | 6.0514 | -2.2319 | 1832.7292 | 3561.2784 | -0.0012178
95 |  | 16.5586 | 37.828 | 4187 | 0.00054562 | 6.0514 | 6.0519 | -2.2319 | 1832.7882 | 3599.1065 | -0.0012178
96 |  | 16.5586 | 37.8268 | 4187 | 0.0005456 | 6.0519 | 6.0525 | -2.2319 | 1832.8472 | 3636.9333 | -0.0012177
97 |  | 16.5586 | 37.8256 | 4187 | 0.00054558 | 6.0525 | 6.053 | -2.2319 | 1832.9062 | 3674.7589 | -0.0012177
98 |  | 16.5586 | 37.8244 | 4187 | 0.00054556 | 6.053 | 6.0535 | -2.2319 | 1832.9652 | 3712.5833 | -0.0012177
99 |  | 16.5586 | 37.8232 | 4187 | 0.00054555 | 6.0535 | 6.0541 | -2.2319 | 1833.0242 | 3750.4064 | -0.0012176
100 |  | 16.5586 | 37.8219 | 4187 | 0.00054553 | 6.0541 | 6.0546 | -2.2319 | 1833.0832 | 3788.2284 | -0.0012176
101 |  | 16.5586 | 37.8207 | 4187 | 0.00054551 | 6.0546 | 6.0552 | -2.2319 | 1833.1422 | 3826.0491 | -0.0012175
102 |  | 16.5586 | 37.8195 | 4187 | 0.00054549 | 6.0552 | 6.0557 | -2.2319 | 1833.2012 | 3863.8686 | -0.0012175
103 |  | 16.5586 | 37.8183 | 4187 | 0.00054548 | 6.0557 | 6.0563 | -2.2319 | 1833.2603 | 3901.6869 | -0.0012175
104 |  | 16.5586 | 37.8171 | 4187 | 0.00054546 | 6.0563 | 6.0568 | -2.2319 | 1833.3193 | 3939.504 | -0.0012174
105 |  | 16.5586 | 37.8159 | 4187 | 0.00054544 | 6.0568 | 6.0574 | -2.2319 | 1833.3783 | 3977.3199 | -0.0012174
106 |  | 16.5586 | 37.8146 | 4187 | 0.00054542 | 6.0574 | 6.0579 | -2.2319 | 1833.4373 | 4015.1345 | -0.0012173
107 |  | 16.5586 | 37.8134 | 4187 | 0.00054541 | 6.0579 | 6.0585 | -2.2319 | 1833.4963 | 4052.9479 | -0.0012173
108 |  | 16.5586 | 37.8122 | 4187 | 0.00054539 | 6.0585 | 6.059 | -2.2319 | 1833.5554 | 4090.7601 | -0.0012173
109 |  | 16.5586 | 37.811 | 4187 | 0.00054537 | 6.059 | 6.0595 | -2.2319 | 1833.6144 | 4128.5711 | -0.0012172
110 |  | 16.5586 | 37.8098 | 4187 | 0.00054535 | 6.0595 | 6.0601 | -2.2319 | 1833.6734 | 4166.3809 | -0.0012172
111 |  | 16.5586 | 37.8086 | 4187 | 0.00054534 | 6.0601 | 6.0606 | -2.2319 | 1833.7325 | 4204.1895 | -0.0012171
112 |  | 16.5586 | 37.8073 | 4187 | 0.00054532 | 6.0606 | 6.0612 | -2.2319 | 1833.7915 | 4241.9968 | -0.0012171
113 |  | 16.5586 | 37.8061 | 4187 | 0.0005453 | 6.0612 | 6.0617 | -2.2319 | 1833.8505 | 4279.8029 | -0.0012171
114 |  | 16.5586 | 37.8049 | 4187 | 0.00054528 | 6.0617 | 6.0623 | -2.2319 | 1833.9096 | 4317.6078 | -0.001217
115 |  | 16.5586 | 37.8037 | 4187 | 0.00054527 | 6.0623 | 6.0628 | -2.2319 | 1833.9686 | 4355.4115 | -0.001217
116 |  | 16.5586 | 37.8025 | 4187 | 0.00054525 | 6.0628 | 6.0634 | -2.2319 | 1834.0276 | 4393.214 | -0.001217
117 |  | 16.5586 | 37.8013 | 4187 | 0.00054523 | 6.0634 | 6.0639 | -2.2319 | 1834.0867 | 4431.0152 | -0.0012169
118 |  | 16.5586 | 37.8 | 4187 | 0.00054521 | 6.0639 | 6.0645 | -2.2319 | 1834.1457 | 4468.8153 | -0.0012169
119 |  | 16.5586 | 37.7988 | 4187 | 0.0005452 | 6.0645 | 6.065 | -2.2319 | 1834.2048 | 4506.6141 | -0.0012168
120 |  | 16.5586 | 37.7976 | 4187 | 0.00054518 | 6.065 | 6.0655 | -2.2319 | 1834.2638 | 4544.4117 | -0.0012168
121 |  | 16.5586 | 37.7964 | 4187 | 0.00054516 | 6.0655 | 6.0661 | -2.2319 | 1834.3229 | 4582.2081 | -0.0012168
122 |  | 16.5586 | 37.7952 | 4187 | 0.00054514 | 6.0661 | 6.0666 | -2.2319 | 1834.3819 | 4620.0033 | -0.0012167
123 |  | 16.5586 | 37.794 | 4187 | 0.00054513 | 6.0666 | 6.0672 | -2.2319 | 1834.441 | 4657.7972 | -0.0012167
124 |  | 16.5586 | 37.7927 | 4187 | 0.00054511 | 6.0672 | 6.0677 | -2.2319 | 1834.5 | 4695.59 | -0.0012166
125 |  | 16.5586 | 37.7915 | 4187 | 0.00054509 | 6.0677 | 6.0683 | -2.2319 | 1834.5591 | 4733.3815 | -0.0012166
126 |  | 16.5586 | 37.7903 | 4187 | 0.00054507 | 6.0683 | 6.0688 | -2.2319 | 1834.6182 | 4771.1718 | -0.0012166
127 |  | 16.5586 | 37.7891 | 4187 | 0.00054506 | 6.0688 | 6.0694 | -2.2319 | 1834.6772 | 4808.9609 | -0.0012165
128 |  | 16.5586 | 37.7879 | 4187 | 0.00054504 | 6.0694 | 6.0699 | -2.2319 | 1834.7363 | 4846.7487 | -0.0012165
129 |  | 16.5586 | 37.7867 | 4187 | 0.00054502 | 6.0699 | 6.0705 | -2.2319 | 1834.7954 | 4884.5354 | -0.0012164
130 |  | 16.5586 | 37.7854 | 4187 | 0.000545 | 6.0705 | 6.071 | -2.2319 | 1834.8544 | 4922.3208 | -0.0012164
131 |  | 16.5586 | 37.7842 | 4187 | 0.00054498 | 6.071 | 6.0715 | -2.2319 | 1834.9135 | 4960.105 | -0.0012164
132 |  | 16.5586 | 37.783 | 4187 | 0.00054497 | 6.0715 | 6.0721 | -2.2319 | 1834.9726 | 4997.8881 | -0.0012163
133 |  | 16.5586 | 37.7818 | 4187 | 0.00054495 | 6.0721 | 6.0726 | -2.2319 | 1835.0316 | 5035.6698 | -0.0012163
134 |  | 16.5586 | 37.7806 | 4187 | 0.00054493 | 6.0726 | 6.0732 | -2.2319 | 1835.0907 | 5073.4504 | -0.0012162
135 |  | 16.5586 | 37.7794 | 4187 | 0.00054491 | 6.0732 | 6.0737 | -2.2319 | 1835.1498 | 5111.2298 | -0.0012162
136 |  | 16.5586 | 37.7781 | 4187 | 0.0005449 | 6.0737 | 6.0743 | -2.2319 | 1835.2089 | 5149.0079 | -0.0012162
137 |  | 16.5586 | 37.7769 | 4187 | 0.00054488 | 6.0743 | 6.0748 | -2.2319 | 1835.268 | 5186.7848 | -0.0012161
138 |  | 16.5586 | 37.7757 | 4187 | 0.00054486 | 6.0748 | 6.0754 | -2.2319 | 1835.327 | 5224.5605 | -0.0012161
139 |  | 16.5586 | 37.7745 | 4187 | 0.00054484 | 6.0754 | 6.0759 | -2.2319 | 1835.3861 | 5262.335 | -0.0012161
140 |  | 16.5586 | 37.7733 | 4187 | 0.00054483 | 6.0759 | 6.0764 | -2.2319 | 1835.4452 | 5300.1083 | -0.001216
141 |  | 16.5586 | 37.7721 | 4187 | 0.00054481 | 6.0764 | 6.077 | -2.2319 | 1835.5043 | 5337.8804 | -0.001216
142 |  | 16.5586 | 37.7708 | 4187 | 0.00054479 | 6.077 | 6.0775 | -2.2319 | 1835.5634 | 5375.6512 | -0.0012159
143 |  | 16.5586 | 37.7696 | 4187 | 0.00054477 | 6.0775 | 6.0781 | -2.2319 | 1835.6225 | 5413.4208 | -0.0012159
144 |  | 16.5586 | 37.7684 | 4187 | 0.00054476 | 6.0781 | 6.0786 | -2.2319 | 1835.6816 | 5451.1893 | -0.0012159
145 |  | 16.5586 | 37.7672 | 4187 | 0.00054474 | 6.0786 | 6.0792 | -2.2319 | 1835.7407 | 5488.9564 | -0.0012158
146 |  | 16.5586 | 37.766 | 4187 | 0.00054472 | 6.0792 | 6.0797 | -2.2319 | 1835.7998 | 5526.7224 | -0.0012158
147 |  | 16.5586 | 37.7648 | 4187 | 0.0005447 | 6.0797 | 6.0803 | -2.2319 | 1835.8589 | 5564.4872 | -0.0012157
148 |  | 16.5586 | 37.7635 | 4187 | 0.00054469 | 6.0803 | 6.0808 | -2.2319 | 1835.918 | 5602.2507 | -0.0012157
149 |  | 16.5586 | 37.7623 | 4187 | 0.00054467 | 6.0808 | 6.0813 | -2.2319 | 1835.9771 | 5640.0131 | -0.0012157
150 |  | 16.5586 | 37.7611 | 4187 | 0.00054465 | 6.0813 | 6.0819 | -2.2319 | 1836.0362 | 5677.7742 | -0.0012156
151 |  | 16.5586 | 37.7599 | 4187 | 0.00054463 | 6.0819 | 6.0824 | -2.2319 | 1836.0953 | 5715.5341 | -0.0012156
152 |  | 16.5586 | 37.7587 | 4187 | 0.00054462 | 6.0824 | 6.083 | -2.2319 | 1836.1544 | 5753.2928 | -0.0012155
153 |  | 16.5586 | 37.7575 | 4187 | 0.0005446 | 6.083 | 6.0835 | -2.2319 | 1836.2135 | 5791.0503 | -0.0012155
154 |  | 16.5586 | 37.7563 | 4187 | 0.00054458 | 6.0835 | 6.0841 | -2.2319 | 1836.2726 | 5828.8065 | -0.0012155
155 |  | 16.5586 | 37.755 | 4187 | 0.00054456 | 6.0841 | 6.0846 | -2.2319 | 1836.3318 | 5866.5615 | -0.0012154
156 |  | 16.5586 | 37.7538 | 4187 | 0.00054455 | 6.0846 | 6.0852 | -2.2319 | 1836.3909 | 5904.3154 | -0.0012154
157 |  | 16.5586 | 37.7526 | 4187 | 0.00054453 | 6.0852 | 6.0857 | -2.2319 | 1836.45 | 5942.068 | -0.0012153
158 |  | 16.5586 | 37.7514 | 4187 | 0.00054451 | 6.0857 | 6.0863 | -2.2319 | 1836.5091 | 5979.8194 | -0.0012153
159 |  | 16.5586 | 37.7502 | 4187 | 0.00054449 | 6.0863 | 6.0868 | -2.2319 | 1836.5682 | 6017.5695 | -0.0012153
160 |  | 16.5586 | 37.749 | 4187 | 0.00054448 | 6.0868 | 6.0873 | -2.2319 | 1836.6274 | 6055.3185 | -0.0012152
161 |  | 16.5586 | 37.7477 | 4187 | 0.00054446 | 6.0873 | 6.0879 | -2.2319 | 1836.6865 | 6093.0663 | -0.0012152
162 |  | 16.5586 | 37.7465 | 4187 | 0.00054444 | 6.0879 | 6.0884 | -2.2319 | 1836.7456 | 6130.8128 | -0.0012152
163 |  | 16.5586 | 37.7453 | 4187 | 0.00054442 | 6.0884 | 6.089 | -2.2319 | 1836.8048 | 6168.5581 | -0.0012151
164 |  | 16.5586 | 37.7441 | 4187 | 0.00054441 | 6.089 | 6.0895 | -2.2319 | 1836.8639 | 6206.3022 | -0.0012151
165 |  | 16.5586 | 37.7429 | 4187 | 0.00054439 | 6.0895 | 6.0901 | -2.2319 | 1836.923 | 6244.0451 | -0.001215
166 |  | 16.5586 | 37.7417 | 4187 | 0.00054437 | 6.0901 | 6.0906 | -2.2319 | 1836.9822 | 6281.7868 | -0.001215
167 |  | 16.5586 | 37.7405 | 4187 | 0.00054435 | 6.0906 | 6.0912 | -2.2319 | 1837.0413 | 6319.5272 | -0.001215
168 |  | 16.5586 | 37.7392 | 4187 | 0.00054434 | 6.0912 | 6.0917 | -2.2319 | 1837.1004 | 6357.2665 | -0.0012149
169 |  | 16.5586 | 37.738 | 4187 | 0.00054432 | 6.0917 | 6.0922 | -2.2319 | 1837.1596 | 6395.0045 | -0.0012149
170 |  | 16.5586 | 37.7368 | 4187 | 0.0005443 | 6.0922 | 6.0928 | -2.2319 | 1837.2187 | 6432.7413 | -0.0012148
171 |  | 16.5586 | 37.7356 | 4187 | 0.00054428 | 6.0928 | 6.0933 | -2.2319 | 1837.2779 | 6470.4769 | -0.0012148
172 |  | 16.5586 | 37.7344 | 4187 | 0.00054427 | 6.0933 | 6.0939 | -2.2319 | 1837.337 | 6508.2113 | -0.0012148
173 |  | 16.5586 | 37.7332 | 4187 | 0.00054425 | 6.0939 | 6.0944 | -2.2319 | 1837.3962 | 6545.9445 | -0.0012147
174 |  | 16.5586 | 37.732 | 4187 | 0.00054423 | 6.0944 | 6.095 | -2.2319 | 1837.4553 | 6583.6764 | -0.0012147
175 |  | 16.5586 | 37.7307 | 4187 | 0.00054421 | 6.095 | 6.0955 | -2.2319 | 1837.5145 | 6621.4072 | -0.0012146
176 |  | 16.5586 | 37.7295 | 4187 | 0.0005442 | 6.0955 | 6.096 | -2.2319 | 1837.5736 | 6659.1367 | -0.0012146
177 |  | 16.5586 | 37.7283 | 4187 | 0.00054418 | 6.096 | 6.0966 | -2.2319 | 1837.6328 | 6696.865 | -0.0012146
178 |  | 16.5586 | 37.7271 | 4187 | 0.00054416 | 6.0966 | 6.0971 | -2.2319 | 1837.6919 | 6734.5921 | -0.0012145
179 |  | 16.5586 | 37.7259 | 4187 | 0.00054414 | 6.0971 | 6.0977 | -2.2319 | 1837.7511 | 6772.318 | -0.0012145
180 |  | 16.5586 | 37.7247 | 4187 | 0.00054413 | 6.0977 | 6.0982 | -2.2319 | 1837.8103 | 6810.0426 | -0.0012144
181 |  | 16.5586 | 37.7235 | 4187 | 0.00054411 | 6.0982 | 6.0988 | -2.2319 | 1837.8694 | 6847.7661 | -0.0012144
182 |  | 16.5586 | 37.7222 | 4187 | 0.00054409 | 6.0988 | 6.0993 | -2.2319 | 1837.9286 | 6885.4883 | -0.0012144
183 |  | 16.5586 | 37.721 | 4187 | 0.00054407 | 6.0993 | 6.0999 | -2.2319 | 1837.9878 | 6923.2093 | -0.0012143
184 |  | 16.5586 | 37.7198 | 4187 | 0.00054406 | 6.0999 | 6.1004 | -2.2319 | 1838.0469 | 6960.9291 | -0.0012143
185 |  | 16.5586 | 37.7186 | 4187 | 0.00054404 | 6.1004 | 6.1009 | -2.2319 | 1838.1061 | 6998.6477 | -0.0012143
186 |  | 16.5586 | 37.7174 | 4187 | 0.00054402 | 6.1009 | 6.1015 | -2.2319 | 1838.1653 | 7036.3651 | -0.0012142
187 |  | 16.5586 | 37.7162 | 4187 | 0.000544 | 6.1015 | 6.102 | -2.2319 | 1838.2245 | 7074.0813 | -0.0012142
188 |  | 16.5586 | 37.715 | 4187 | 0.00054399 | 6.102 | 6.1026 | -2.2319 | 1838.2836 | 7111.7962 | -0.0012141
189 |  | 16.5586 | 37.7137 | 4187 | 0.00054397 | 6.1026 | 6.1031 | -2.2319 | 1838.3428 | 7149.51 | -0.0012141
190 |  | 16.5586 | 37.7125 | 4187 | 0.00054395 | 6.1031 | 6.1037 | -2.2319 | 1838.402 | 7187.2225 | -0.0012141
191 |  | 16.5586 | 37.7113 | 4187 | 0.00054393 | 6.1037 | 6.1042 | -2.2319 | 1838.4612 | 7224.9338 | -0.001214
192 |  | 16.5586 | 37.7101 | 4187 | 0.00054392 | 6.1042 | 6.1048 | -2.2319 | 1838.5204 | 7262.6439 | -0.001214
193 |  | 16.5586 | 37.7089 | 4187 | 0.0005439 | 6.1048 | 6.1053 | -2.2319 | 1838.5796 | 7300.3528 | -0.0012139
194 |  | 16.5586 | 37.7077 | 4187 | 0.00054388 | 6.1053 | 6.1058 | -2.2319 | 1838.6388 | 7338.0604 | -0.0012139
195 |  | 16.5586 | 37.7065 | 4187 | 0.00054386 | 6.1058 | 6.1064 | -2.2319 | 1838.698 | 7375.7669 | -0.0012139
196 |  | 16.5586 | 37.7052 | 4187 | 0.00054385 | 6.1064 | 6.1069 | -2.2319 | 1838.7571 | 7413.4721 | -0.0012138
197 |  | 16.5586 | 37.704 | 4187 | 0.00054383 | 6.1069 | 6.1075 | -2.2319 | 1838.8163 | 7451.1762 | -0.0012138
198 |  | 16.5586 | 37.7028 | 4187 | 0.00054381 | 6.1075 | 6.108 | -2.2319 | 1838.8755 | 7488.879 | -0.0012137
199 |  | 16.5586 | 37.7016 | 4187 | 0.00054379 | 6.108 | 6.1086 | -2.2319 | 1838.9347 | 7526.5806 | -0.0012137
200 |  | 16.5586 | 37.7004 | 4187 | 0.00054378 | 6.1086 | 6.1091 | -2.2319 | 1838.9939 | 7564.281 | -0.0012137
201 |  | 16.5586 | 37.6992 | 4187 | 0.00054376 | 6.1091 | 6.1096 | -2.2319 | 1839.0531 | 7601.9801 | -0.0012136
202 |  | 16.5586 | 37.698 | 4187 | 0.00054374 | 6.1096 | 6.1102 | -2.2319 | 1839.1124 | 7639.6781 | -0.0012136
203 |  | 16.5586 | 37.6967 | 4187 | 0.00054372 | 6.1102 | 6.1107 | -2.2319 | 1839.1716 | 7677.3748 | -0.0012135
204 |  | 16.5586 | 37.6955 | 4187 | 0.00054371 | 6.1107 | 6.1113 | -2.2319 | 1839.2308 | 7715.0704 | -0.0012135
205 |  | 16.5586 | 37.6943 | 4187 | 0.00054369 | 6.1113 | 6.1118 | -2.2319 | 1839.29 | 7752.7647 | -0.0012135
206 |  | 16.5586 | 37.6931 | 4187 | 0.00054367 | 6.1118 | 6.1124 | -2.2319 | 1839.3492 | 7790.4578 | -0.0012134
207 |  | 16.5586 | 37.6919 | 4187 | 0.00054365 | 6.1124 | 6.1129 | -2.2319 | 1839.4084 | 7828.1497 | -0.0012134
208 |  | 16.5586 | 37.6907 | 4187 | 0.00054364 | 6.1129 | 6.1135 | -2.2319 | 1839.4676 | 7865.8403 | -0.0012134
209 |  | 16.5586 | 37.6895 | 4187 | 0.00054362 | 6.1135 | 6.114 | -2.2319 | 1839.5268 | 7903.5298 | -0.0012133
210 |  | 16.5586 | 37.6882 | 4187 | 0.0005436 | 6.114 | 6.1145 | -2.2319 | 1839.5861 | 7941.2181 | -0.0012133
211 |  | 16.5586 | 37.687 | 4187 | 0.00054358 | 6.1145 | 6.1151 | -2.2319 | 1839.6453 | 7978.9051 | -0.0012132
212 |  | 16.5586 | 37.6858 | 4187 | 0.00054357 | 6.1151 | 6.1156 | -2.2319 | 1839.7045 | 8016.5909 | -0.0012132
213 |  | 16.5586 | 37.6846 | 4187 | 0.00054355 | 6.1156 | 6.1162 | -2.2319 | 1839.7637 | 8054.2755 | -0.0012132
214 |  | 16.5586 | 37.6834 | 4187 | 0.00054353 | 6.1162 | 6.1167 | -2.2319 | 1839.823 | 8091.9589 | -0.0012131
215 |  | 16.5586 | 37.6822 | 4187 | 0.00054351 | 6.1167 | 6.1173 | -2.2319 | 1839.8822 | 8129.6411 | -0.0012131
216 |  | 16.5586 | 37.681 | 4187 | 0.0005435 | 6.1173 | 6.1178 | -2.2319 | 1839.9414 | 8167.3221 | -0.001213
217 |  | 16.5586 | 37.6798 | 4187 | 0.00054348 | 6.1178 | 6.1183 | -2.2319 | 1840.0007 | 8205.0018 | -0.001213
218 |  | 16.5586 | 37.6785 | 4187 | 0.00054346 | 6.1183 | 6.1189 | -2.2319 | 1840.0599 | 8242.6804 | -0.001213
219 |  | 16.5586 | 37.6773 | 4187 | 0.00054344 | 6.1189 | 6.1194 | -2.2319 | 1840.1191 | 8280.3577 | -0.0012129
220 |  | 16.5586 | 37.6761 | 4187 | 0.00054343 | 6.1194 | 6.12 | -2.2319 | 1840.1784 | 8318.0338 | -0.0012129
221 |  | 16.5586 | 37.6749 | 4187 | 0.00054341 | 6.12 | 6.1205 | -2.2319 | 1840.2376 | 8355.7087 | -0.0012128
222 |  | 16.5586 | 37.6737 | 4187 | 0.00054339 | 6.1205 | 6.1211 | -2.2319 | 1840.2969 | 8393.3824 | -0.0012128
223 |  | 16.5586 | 37.6725 | 4187 | 0.00054337 | 6.1211 | 6.1216 | -2.2319 | 1840.3561 | 8431.0549 | -0.0012128
224 |  | 16.5586 | 37.6713 | 4187 | 0.00054336 | 6.1216 | 6.1221 | -2.2319 | 1840.4154 | 8468.7262 | -0.0012127
225 |  | 16.5586 | 37.6701 | 4187 | 0.00054334 | 6.1221 | 6.1227 | -2.2319 | 1840.4746 | 8506.3962 | -0.0012127
226 |  | 16.5586 | 37.6688 | 4187 | 0.00054332 | 6.1227 | 6.1232 | -2.2319 | 1840.5339 | 8544.0651 | -0.0012126
227 |  | 16.5586 | 37.6676 | 4187 | 0.0005433 | 6.1232 | 6.1238 | -2.2319 | 1840.5931 | 8581.7327 | -0.0012126
228 |  | 16.5586 | 37.6664 | 4187 | 0.00054329 | 6.1238 | 6.1243 | -2.2319 | 1840.6524 | 8619.3991 | -0.0012126
229 |  | 16.5586 | 37.6652 | 4187 | 0.00054327 | 6.1243 | 6.1249 | -2.2319 | 1840.7116 | 8657.0643 | -0.0012125
230 |  | 16.5586 | 37.664 | 4187 | 0.00054325 | 6.1249 | 6.1254 | -2.2319 | 1840.7709 | 8694.7283 | -0.0012125
231 |  | 16.5586 | 37.6628 | 4187 | 0.00054323 | 6.1254 | 6.126 | -2.2319 | 1840.8301 | 8732.3911 | -0.0012125
232 |  | 16.5586 | 37.6616 | 4187 | 0.00054322 | 6.126 | 6.1265 | -2.2319 | 1840.8894 | 8770.0527 | -0.0012124
233 |  | 16.5586 | 37.6604 | 4187 | 0.0005432 | 6.1265 | 6.127 | -2.2319 | 1840.9487 | 8807.713 | -0.0012124
234 |  | 16.5586 | 37.6591 | 4187 | 0.00054318 | 6.127 | 6.1276 | -2.2319 | 1841.0079 | 8845.3721 | -0.0012123
235 |  | 16.5586 | 37.6579 | 4187 | 0.00054316 | 6.1276 | 6.1281 | -2.2319 | 1841.0672 | 8883.0301 | -0.0012123
236 |  | 16.5586 | 37.6567 | 4187 | 0.00054315 | 6.1281 | 6.1287 | -2.2319 | 1841.1265 | 8920.6868 | -0.0012123

## Fus250
|  |  | buis | verlies W/M | L /°C/sec
diam | wandikte |  | inhoud l/m |  | W/M
250 | 34.2 | 3.1416 | 25.9013 | 39.9249 | 4187
[8 empty] | J/sec/mtr | aantal mtr. | verlies
|  | buis | verlies W/M | L /°C/sec | verlies temp | begintemp | eindtemp | verlies | bij 1°C | totaal J/sec
|  | inhoud L |  | W/M | °C per M | °C | °C | per m°C | daling | aantal mtr
1 | 250 | 25.9013 | 39.9249 | 4187 | 0.00036815 | 6 | 6.0004 | -2.3485 | 2716.3203 | 39.9249 | -0.0008646
2 |  | 25.9013 | 39.924 | 4187 | 0.00036814 | 6.0004 | 6.0007 | -2.3485 | 2716.3791 | 79.8489 | -0.00086458
3 |  | 25.9013 | 39.9231 | 4187 | 0.00036813 | 6.0007 | 6.0011 | -2.3485 | 2716.4379 | 119.772 | -0.00086456
4 |  | 25.9013 | 39.9223 | 4187 | 0.00036812 | 6.0011 | 6.0015 | -2.3485 | 2716.4967 | 159.6943 | -0.00086454
5 |  | 25.9013 | 39.9214 | 4187 | 0.00036811 | 6.0015 | 6.0018 | -2.3485 | 2716.5556 | 199.6157 | -0.00086452
6 |  | 25.9013 | 39.9206 | 4187 | 0.00036811 | 6.0018 | 6.0022 | -2.3485 | 2716.6144 | 239.5363 | -0.0008645
7 |  | 25.9013 | 39.9197 | 4187 | 0.0003681 | 6.0022 | 6.0026 | -2.3485 | 2716.6732 | 279.456 | -0.00086448
8 |  | 25.9013 | 39.9188 | 4187 | 0.00036809 | 6.0026 | 6.0029 | -2.3485 | 2716.7321 | 319.3748 | -0.00086447
9 |  | 25.9013 | 39.918 | 4187 | 0.00036808 | 6.0029 | 6.0033 | -2.3485 | 2716.7909 | 359.2927 | -0.00086445
10 |  | 25.9013 | 39.9171 | 4187 | 0.00036807 | 6.0033 | 6.0037 | -2.3485 | 2716.8497 | 399.2098 | -0.00086443
11 |  | 25.9013 | 39.9162 | 4187 | 0.00036807 | 6.0037 | 6.004 | -2.3485 | 2716.9086 | 439.1261 | -0.00086441
12 |  | 25.9013 | 39.9154 | 4187 | 0.00036806 | 6.004 | 6.0044 | -2.3485 | 2716.9674 | 479.0414 | -0.00086439
13 |  | 25.9013 | 39.9145 | 4187 | 0.00036805 | 6.0044 | 6.0048 | -2.3485 | 2717.0262 | 518.9559 | -0.00086437
14 |  | 25.9013 | 39.9136 | 4187 | 0.00036804 | 6.0048 | 6.0052 | -2.3485 | 2717.0851 | 558.8696 | -0.00086435
15 |  | 25.9013 | 39.9128 | 4187 | 0.00036803 | 6.0052 | 6.0055 | -2.3485 | 2717.1439 | 598.7823 | -0.00086433
16 |  | 25.9013 | 39.9119 | 4187 | 0.00036803 | 6.0055 | 6.0059 | -2.3485 | 2717.2028 | 638.6943 | -0.00086432
17 |  | 25.9013 | 39.911 | 4187 | 0.00036802 | 6.0059 | 6.0063 | -2.3485 | 2717.2616 | 678.6053 | -0.0008643
18 |  | 25.9013 | 39.9102 | 4187 | 0.00036801 | 6.0063 | 6.0066 | -2.3485 | 2717.3204 | 718.5155 | -0.00086428
19 |  | 25.9013 | 39.9093 | 4187 | 0.000368 | 6.0066 | 6.007 | -2.3485 | 2717.3793 | 758.4248 | -0.00086426
20 |  | 25.9013 | 39.9085 | 4187 | 0.00036799 | 6.007 | 6.0074 | -2.3485 | 2717.4381 | 798.3332 | -0.00086424
21 |  | 25.9013 | 39.9076 | 4187 | 0.00036799 | 6.0074 | 6.0077 | -2.3485 | 2717.497 | 838.2408 | -0.00086422
22 |  | 25.9013 | 39.9067 | 4187 | 0.00036798 | 6.0077 | 6.0081 | -2.3485 | 2717.5558 | 878.1475 | -0.0008642
23 |  | 25.9013 | 39.9059 | 4187 | 0.00036797 | 6.0081 | 6.0085 | -2.3485 | 2717.6147 | 918.0534 | -0.00086419
24 |  | 25.9013 | 39.905 | 4187 | 0.00036796 | 6.0085 | 6.0088 | -2.3485 | 2717.6735 | 957.9584 | -0.00086417
25 |  | 25.9013 | 39.9041 | 4187 | 0.00036795 | 6.0088 | 6.0092 | -2.3485 | 2717.7324 | 997.8625 | -0.00086415
26 |  | 25.9013 | 39.9033 | 4187 | 0.00036795 | 6.0092 | 6.0096 | -2.3485 | 2717.7913 | 1037.7658 | -0.00086413
27 |  | 25.9013 | 39.9024 | 4187 | 0.00036794 | 6.0096 | 6.0099 | -2.3485 | 2717.8501 | 1077.6682 | -0.00086411
28 |  | 25.9013 | 39.9015 | 4187 | 0.00036793 | 6.0099 | 6.0103 | -2.3485 | 2717.909 | 1117.5697 | -0.00086409
29 |  | 25.9013 | 39.9007 | 4187 | 0.00036792 | 6.0103 | 6.0107 | -2.3485 | 2717.9678 | 1157.4704 | -0.00086407
30 |  | 25.9013 | 39.8998 | 4187 | 0.00036791 | 6.0107 | 6.011 | -2.3485 | 2718.0267 | 1197.3702 | -0.00086405
31 |  | 25.9013 | 39.8989 | 4187 | 0.00036791 | 6.011 | 6.0114 | -2.3485 | 2718.0855 | 1237.2692 | -0.00086404
32 |  | 25.9013 | 39.8981 | 4187 | 0.0003679 | 6.0114 | 6.0118 | -2.3485 | 2718.1444 | 1277.1672 | -0.00086402
33 |  | 25.9013 | 39.8972 | 4187 | 0.00036789 | 6.0118 | 6.0121 | -2.3485 | 2718.2033 | 1317.0645 | -0.000864
34 |  | 25.9013 | 39.8964 | 4187 | 0.00036788 | 6.0121 | 6.0125 | -2.3485 | 2718.2621 | 1356.9608 | -0.00086398
35 |  | 25.9013 | 39.8955 | 4187 | 0.00036787 | 6.0125 | 6.0129 | -2.3485 | 2718.321 | 1396.8563 | -0.00086396
36 |  | 25.9013 | 39.8946 | 4187 | 0.00036787 | 6.0129 | 6.0132 | -2.3485 | 2718.3799 | 1436.7509 | -0.00086394
37 |  | 25.9013 | 39.8938 | 4187 | 0.00036786 | 6.0132 | 6.0136 | -2.3485 | 2718.4387 | 1476.6447 | -0.00086392
38 |  | 25.9013 | 39.8929 | 4187 | 0.00036785 | 6.0136 | 6.014 | -2.3485 | 2718.4976 | 1516.5376 | -0.0008639
39 |  | 25.9013 | 39.892 | 4187 | 0.00036784 | 6.014 | 6.0144 | -2.3485 | 2718.5565 | 1556.4296 | -0.00086389
40 |  | 25.9013 | 39.8912 | 4187 | 0.00036783 | 6.0144 | 6.0147 | -2.3485 | 2718.6154 | 1596.3208 | -0.00086387
41 |  | 25.9013 | 39.8903 | 4187 | 0.00036783 | 6.0147 | 6.0151 | -2.3485 | 2718.6742 | 1636.2111 | -0.00086385
42 |  | 25.9013 | 39.8894 | 4187 | 0.00036782 | 6.0151 | 6.0155 | -2.3485 | 2718.7331 | 1676.1005 | -0.00086383
43 |  | 25.9013 | 39.8886 | 4187 | 0.00036781 | 6.0155 | 6.0158 | -2.3485 | 2718.792 | 1715.9891 | -0.00086381
44 |  | 25.9013 | 39.8877 | 4187 | 0.0003678 | 6.0158 | 6.0162 | -2.3485 | 2718.8509 | 1755.8768 | -0.00086379
45 |  | 25.9013 | 39.8868 | 4187 | 0.00036779 | 6.0162 | 6.0166 | -2.3485 | 2718.9097 | 1795.7637 | -0.00086377
46 |  | 25.9013 | 39.886 | 4187 | 0.00036779 | 6.0166 | 6.0169 | -2.3485 | 2718.9686 | 1835.6497 | -0.00086375
47 |  | 25.9013 | 39.8851 | 4187 | 0.00036778 | 6.0169 | 6.0173 | -2.3485 | 2719.0275 | 1875.5348 | -0.00086374
48 |  | 25.9013 | 39.8843 | 4187 | 0.00036777 | 6.0173 | 6.0177 | -2.3485 | 2719.0864 | 1915.419 | -0.00086372
49 |  | 25.9013 | 39.8834 | 4187 | 0.00036776 | 6.0177 | 6.018 | -2.3485 | 2719.1453 | 1955.3024 | -0.0008637
50 |  | 25.9013 | 39.8825 | 4187 | 0.00036775 | 6.018 | 6.0184 | -2.3485 | 2719.2042 | 1995.185 | -0.00086368
51 |  | 25.9013 | 39.8817 | 4187 | 0.00036775 | 6.0184 | 6.0188 | -2.3485 | 2719.2631 | 2035.0666 | -0.00086366
52 |  | 25.9013 | 39.8808 | 4187 | 0.00036774 | 6.0188 | 6.0191 | -2.3485 | 2719.3219 | 2074.9474 | -0.00086364
53 |  | 25.9013 | 39.8799 | 4187 | 0.00036773 | 6.0191 | 6.0195 | -2.3485 | 2719.3808 | 2114.8274 | -0.00086362
54 |  | 25.9013 | 39.8791 | 4187 | 0.00036772 | 6.0195 | 6.0199 | -2.3485 | 2719.4397 | 2154.7064 | -0.00086361
55 |  | 25.9013 | 39.8782 | 4187 | 0.00036771 | 6.0199 | 6.0202 | -2.3485 | 2719.4986 | 2194.5847 | -0.00086359
56 |  | 25.9013 | 39.8773 | 4187 | 0.00036771 | 6.0202 | 6.0206 | -2.3485 | 2719.5575 | 2234.462 | -0.00086357
57 |  | 25.9013 | 39.8765 | 4187 | 0.0003677 | 6.0206 | 6.021 | -2.3485 | 2719.6164 | 2274.3385 | -0.00086355
58 |  | 25.9013 | 39.8756 | 4187 | 0.00036769 | 6.021 | 6.0213 | -2.3485 | 2719.6753 | 2314.2141 | -0.00086353
59 |  | 25.9013 | 39.8748 | 4187 | 0.00036768 | 6.0213 | 6.0217 | -2.3485 | 2719.7342 | 2354.0889 | -0.00086351
60 |  | 25.9013 | 39.8739 | 4187 | 0.00036768 | 6.0217 | 6.0221 | -2.3485 | 2719.7931 | 2393.9628 | -0.00086349
61 |  | 25.9013 | 39.873 | 4187 | 0.00036767 | 6.0221 | 6.0224 | -2.3485 | 2719.852 | 2433.8358 | -0.00086347
62 |  | 25.9013 | 39.8722 | 4187 | 0.00036766 | 6.0224 | 6.0228 | -2.3485 | 2719.9109 | 2473.708 | -0.00086346
63 |  | 25.9013 | 39.8713 | 4187 | 0.00036765 | 6.0228 | 6.0232 | -2.3485 | 2719.9698 | 2513.5793 | -0.00086344
64 |  | 25.9013 | 39.8704 | 4187 | 0.00036764 | 6.0232 | 6.0235 | -2.3485 | 2720.0287 | 2553.4497 | -0.00086342
65 |  | 25.9013 | 39.8696 | 4187 | 0.00036764 | 6.0235 | 6.0239 | -2.3485 | 2720.0876 | 2593.3193 | -0.0008634
66 |  | 25.9013 | 39.8687 | 4187 | 0.00036763 | 6.0239 | 6.0243 | -2.3485 | 2720.1465 | 2633.188 | -0.00086338
67 |  | 25.9013 | 39.8679 | 4187 | 0.00036762 | 6.0243 | 6.0246 | -2.3485 | 2720.2054 | 2673.0559 | -0.00086336
68 |  | 25.9013 | 39.867 | 4187 | 0.00036761 | 6.0246 | 6.025 | -2.3485 | 2720.2643 | 2712.9228 | -0.00086334
69 |  | 25.9013 | 39.8661 | 4187 | 0.0003676 | 6.025 | 6.0254 | -2.3485 | 2720.3232 | 2752.789 | -0.00086332
70 |  | 25.9013 | 39.8653 | 4187 | 0.0003676 | 6.0254 | 6.0258 | -2.3485 | 2720.3822 | 2792.6542 | -0.00086331
71 |  | 25.9013 | 39.8644 | 4187 | 0.00036759 | 6.0258 | 6.0261 | -2.3485 | 2720.4411 | 2832.5186 | -0.00086329
72 |  | 25.9013 | 39.8635 | 4187 | 0.00036758 | 6.0261 | 6.0265 | -2.3485 | 2720.5 | 2872.3822 | -0.00086327
73 |  | 25.9013 | 39.8627 | 4187 | 0.00036757 | 6.0265 | 6.0269 | -2.3485 | 2720.5589 | 2912.2448 | -0.00086325
74 |  | 25.9013 | 39.8618 | 4187 | 0.00036756 | 6.0269 | 6.0272 | -2.3485 | 2720.6178 | 2952.1066 | -0.00086323
75 |  | 25.9013 | 39.8609 | 4187 | 0.00036756 | 6.0272 | 6.0276 | -2.3485 | 2720.6767 | 2991.9676 | -0.00086321
76 |  | 25.9013 | 39.8601 | 4187 | 0.00036755 | 6.0276 | 6.028 | -2.3485 | 2720.7356 | 3031.8277 | -0.00086319
77 |  | 25.9013 | 39.8592 | 4187 | 0.00036754 | 6.028 | 6.0283 | -2.3485 | 2720.7946 | 3071.6869 | -0.00086318
78 |  | 25.9013 | 39.8584 | 4187 | 0.00036753 | 6.0283 | 6.0287 | -2.3485 | 2720.8535 | 3111.5452 | -0.00086316
79 |  | 25.9013 | 39.8575 | 4187 | 0.00036752 | 6.0287 | 6.0291 | -2.3485 | 2720.9124 | 3151.4027 | -0.00086314
80 |  | 25.9013 | 39.8566 | 4187 | 0.00036752 | 6.0291 | 6.0294 | -2.3485 | 2720.9713 | 3191.2594 | -0.00086312
81 |  | 25.9013 | 39.8558 | 4187 | 0.00036751 | 6.0294 | 6.0298 | -2.3485 | 2721.0303 | 3231.1151 | -0.0008631
82 |  | 25.9013 | 39.8549 | 4187 | 0.0003675 | 6.0298 | 6.0302 | -2.3485 | 2721.0892 | 3270.97 | -0.00086308
83 |  | 25.9013 | 39.854 | 4187 | 0.00036749 | 6.0302 | 6.0305 | -2.3485 | 2721.1481 | 3310.8241 | -0.00086306
84 |  | 25.9013 | 39.8532 | 4187 | 0.00036748 | 6.0305 | 6.0309 | -2.3485 | 2721.207 | 3350.6773 | -0.00086304
85 |  | 25.9013 | 39.8523 | 4187 | 0.00036748 | 6.0309 | 6.0313 | -2.3485 | 2721.266 | 3390.5296 | -0.00086303
86 |  | 25.9013 | 39.8515 | 4187 | 0.00036747 | 6.0313 | 6.0316 | -2.3485 | 2721.3249 | 3430.381 | -0.00086301
87 |  | 25.9013 | 39.8506 | 4187 | 0.00036746 | 6.0316 | 6.032 | -2.3485 | 2721.3838 | 3470.2316 | -0.00086299
88 |  | 25.9013 | 39.8497 | 4187 | 0.00036745 | 6.032 | 6.0324 | -2.3485 | 2721.4428 | 3510.0813 | -0.00086297
89 |  | 25.9013 | 39.8489 | 4187 | 0.00036744 | 6.0324 | 6.0327 | -2.3485 | 2721.5017 | 3549.9302 | -0.00086295
90 |  | 25.9013 | 39.848 | 4187 | 0.00036744 | 6.0327 | 6.0331 | -2.3485 | 2721.5607 | 3589.7782 | -0.00086293
91 |  | 25.9013 | 39.8471 | 4187 | 0.00036743 | 6.0331 | 6.0335 | -2.3485 | 2721.6196 | 3629.6253 | -0.00086291
92 |  | 25.9013 | 39.8463 | 4187 | 0.00036742 | 6.0335 | 6.0338 | -2.3485 | 2721.6785 | 3669.4716 | -0.00086289
93 |  | 25.9013 | 39.8454 | 4187 | 0.00036741 | 6.0338 | 6.0342 | -2.3485 | 2721.7375 | 3709.317 | -0.00086288
94 |  | 25.9013 | 39.8445 | 4187 | 0.0003674 | 6.0342 | 6.0346 | -2.3485 | 2721.7964 | 3749.1616 | -0.00086286
95 |  | 25.9013 | 39.8437 | 4187 | 0.0003674 | 6.0346 | 6.0349 | -2.3485 | 2721.8554 | 3789.0052 | -0.00086284
96 |  | 25.9013 | 39.8428 | 4187 | 0.00036739 | 6.0349 | 6.0353 | -2.3485 | 2721.9143 | 3828.8481 | -0.00086282
97 |  | 25.9013 | 39.842 | 4187 | 0.00036738 | 6.0353 | 6.0357 | -2.3485 | 2721.9732 | 3868.69 | -0.0008628
98 |  | 25.9013 | 39.8411 | 4187 | 0.00036737 | 6.0357 | 6.036 | -2.3485 | 2722.0322 | 3908.5311 | -0.00086278
99 |  | 25.9013 | 39.8402 | 4187 | 0.00036736 | 6.036 | 6.0364 | -2.3485 | 2722.0911 | 3948.3713 | -0.00086276
100 |  | 25.9013 | 39.8394 | 4187 | 0.00036736 | 6.0364 | 6.0368 | -2.3485 | 2722.1501 | 3988.2107 | -0.00086275
101 |  | 25.9013 | 39.8385 | 4187 | 0.00036735 | 6.0368 | 6.0371 | -2.3485 | 2722.209 | 4028.0492 | -0.00086273
102 |  | 25.9013 | 39.8376 | 4187 | 0.00036734 | 6.0371 | 6.0375 | -2.3485 | 2722.268 | 4067.8869 | -0.00086271
103 |  | 25.9013 | 39.8368 | 4187 | 0.00036733 | 6.0375 | 6.0379 | -2.3485 | 2722.3269 | 4107.7237 | -0.00086269
104 |  | 25.9013 | 39.8359 | 4187 | 0.00036732 | 6.0379 | 6.0382 | -2.3485 | 2722.3859 | 4147.5596 | -0.00086267
105 |  | 25.9013 | 39.8351 | 4187 | 0.00036732 | 6.0382 | 6.0386 | -2.3485 | 2722.4449 | 4187.3946 | -0.00086265
106 |  | 25.9013 | 39.8342 | 4187 | 0.00036731 | 6.0386 | 6.039 | -2.3485 | 2722.5038 | 4227.2288 | -0.00086263
107 |  | 25.9013 | 39.8333 | 4187 | 0.0003673 | 6.039 | 6.0393 | -2.3485 | 2722.5628 | 4267.0622 | -0.00086261
108 |  | 25.9013 | 39.8325 | 4187 | 0.00036729 | 6.0393 | 6.0397 | -2.3485 | 2722.6217 | 4306.8946 | -0.0008626
109 |  | 25.9013 | 39.8316 | 4187 | 0.00036729 | 6.0397 | 6.0401 | -2.3485 | 2722.6807 | 4346.7262 | -0.00086258
110 |  | 25.9013 | 39.8307 | 4187 | 0.00036728 | 6.0401 | 6.0404 | -2.3485 | 2722.7397 | 4386.557 | -0.00086256
111 |  | 25.9013 | 39.8299 | 4187 | 0.00036727 | 6.0404 | 6.0408 | -2.3485 | 2722.7986 | 4426.3869 | -0.00086254
112 |  | 25.9013 | 39.829 | 4187 | 0.00036726 | 6.0408 | 6.0412 | -2.3485 | 2722.8576 | 4466.2159 | -0.00086252
113 |  | 25.9013 | 39.8282 | 4187 | 0.00036725 | 6.0412 | 6.0415 | -2.3485 | 2722.9166 | 4506.044 | -0.0008625
114 |  | 25.9013 | 39.8273 | 4187 | 0.00036725 | 6.0415 | 6.0419 | -2.3485 | 2722.9755 | 4545.8713 | -0.00086248
115 |  | 25.9013 | 39.8264 | 4187 | 0.00036724 | 6.0419 | 6.0423 | -2.3485 | 2723.0345 | 4585.6978 | -0.00086247
116 |  | 25.9013 | 39.8256 | 4187 | 0.00036723 | 6.0423 | 6.0427 | -2.3485 | 2723.0935 | 4625.5233 | -0.00086245
117 |  | 25.9013 | 39.8247 | 4187 | 0.00036722 | 6.0427 | 6.043 | -2.3485 | 2723.1524 | 4665.348 | -0.00086243
118 |  | 25.9013 | 39.8238 | 4187 | 0.00036721 | 6.043 | 6.0434 | -2.3485 | 2723.2114 | 4705.1719 | -0.00086241
119 |  | 25.9013 | 39.823 | 4187 | 0.00036721 | 6.0434 | 6.0438 | -2.3485 | 2723.2704 | 4744.9948 | -0.00086239
120 |  | 25.9013 | 39.8221 | 4187 | 0.0003672 | 6.0438 | 6.0441 | -2.3485 | 2723.3294 | 4784.817 | -0.00086237
121 |  | 25.9013 | 39.8213 | 4187 | 0.00036719 | 6.0441 | 6.0445 | -2.3485 | 2723.3883 | 4824.6382 | -0.00086235
122 |  | 25.9013 | 39.8204 | 4187 | 0.00036718 | 6.0445 | 6.0449 | -2.3485 | 2723.4473 | 4864.4586 | -0.00086233
123 |  | 25.9013 | 39.8195 | 4187 | 0.00036717 | 6.0449 | 6.0452 | -2.3485 | 2723.5063 | 4904.2782 | -0.00086232
124 |  | 25.9013 | 39.8187 | 4187 | 0.00036717 | 6.0452 | 6.0456 | -2.3485 | 2723.5653 | 4944.0968 | -0.0008623
125 |  | 25.9013 | 39.8178 | 4187 | 0.00036716 | 6.0456 | 6.046 | -2.3485 | 2723.6242 | 4983.9146 | -0.00086228
126 |  | 25.9013 | 39.8169 | 4187 | 0.00036715 | 6.046 | 6.0463 | -2.3485 | 2723.6832 | 5023.7316 | -0.00086226
127 |  | 25.9013 | 39.8161 | 4187 | 0.00036714 | 6.0463 | 6.0467 | -2.3485 | 2723.7422 | 5063.5477 | -0.00086224
128 |  | 25.9013 | 39.8152 | 4187 | 0.00036713 | 6.0467 | 6.0471 | -2.3485 | 2723.8012 | 5103.3629 | -0.00086222
129 |  | 25.9013 | 39.8144 | 4187 | 0.00036713 | 6.0471 | 6.0474 | -2.3485 | 2723.8602 | 5143.1772 | -0.0008622
130 |  | 25.9013 | 39.8135 | 4187 | 0.00036712 | 6.0474 | 6.0478 | -2.3485 | 2723.9192 | 5182.9907 | -0.00086218
131 |  | 25.9013 | 39.8126 | 4187 | 0.00036711 | 6.0478 | 6.0482 | -2.3485 | 2723.9782 | 5222.8034 | -0.00086217
132 |  | 25.9013 | 39.8118 | 4187 | 0.0003671 | 6.0482 | 6.0485 | -2.3485 | 2724.0372 | 5262.6151 | -0.00086215
133 |  | 25.9013 | 39.8109 | 4187 | 0.00036709 | 6.0485 | 6.0489 | -2.3485 | 2724.0961 | 5302.426 | -0.00086213
134 |  | 25.9013 | 39.81 | 4187 | 0.00036709 | 6.0489 | 6.0493 | -2.3485 | 2724.1551 | 5342.2361 | -0.00086211
135 |  | 25.9013 | 39.8092 | 4187 | 0.00036708 | 6.0493 | 6.0496 | -2.3485 | 2724.2141 | 5382.0453 | -0.00086209
136 |  | 25.9013 | 39.8083 | 4187 | 0.00036707 | 6.0496 | 6.05 | -2.3485 | 2724.2731 | 5421.8536 | -0.00086207
137 |  | 25.9013 | 39.8075 | 4187 | 0.00036706 | 6.05 | 6.0504 | -2.3485 | 2724.3321 | 5461.6611 | -0.00086205
138 |  | 25.9013 | 39.8066 | 4187 | 0.00036705 | 6.0504 | 6.0507 | -2.3485 | 2724.3911 | 5501.4677 | -0.00086204
139 |  | 25.9013 | 39.8057 | 4187 | 0.00036705 | 6.0507 | 6.0511 | -2.3485 | 2724.4501 | 5541.2734 | -0.00086202
140 |  | 25.9013 | 39.8049 | 4187 | 0.00036704 | 6.0511 | 6.0515 | -2.3485 | 2724.5091 | 5581.0783 | -0.000862
141 |  | 25.9013 | 39.804 | 4187 | 0.00036703 | 6.0515 | 6.0518 | -2.3485 | 2724.5681 | 5620.8823 | -0.00086198
142 |  | 25.9013 | 39.8032 | 4187 | 0.00036702 | 6.0518 | 6.0522 | -2.3485 | 2724.6271 | 5660.6854 | -0.00086196
143 |  | 25.9013 | 39.8023 | 4187 | 0.00036701 | 6.0522 | 6.0526 | -2.3485 | 2724.6861 | 5700.4877 | -0.00086194
144 |  | 25.9013 | 39.8014 | 4187 | 0.00036701 | 6.0526 | 6.0529 | -2.3485 | 2724.7451 | 5740.2892 | -0.00086192
145 |  | 25.9013 | 39.8006 | 4187 | 0.000367 | 6.0529 | 6.0533 | -2.3485 | 2724.8042 | 5780.0897 | -0.0008619
146 |  | 25.9013 | 39.7997 | 4187 | 0.00036699 | 6.0533 | 6.0537 | -2.3485 | 2724.8632 | 5819.8894 | -0.00086189
147 |  | 25.9013 | 39.7988 | 4187 | 0.00036698 | 6.0537 | 6.054 | -2.3485 | 2724.9222 | 5859.6883 | -0.00086187
148 |  | 25.9013 | 39.798 | 4187 | 0.00036698 | 6.054 | 6.0544 | -2.3485 | 2724.9812 | 5899.4862 | -0.00086185
149 |  | 25.9013 | 39.7971 | 4187 | 0.00036697 | 6.0544 | 6.0548 | -2.3485 | 2725.0402 | 5939.2834 | -0.00086183
150 |  | 25.9013 | 39.7963 | 4187 | 0.00036696 | 6.0548 | 6.0551 | -2.3485 | 2725.0992 | 5979.0796 | -0.00086181
151 |  | 25.9013 | 39.7954 | 4187 | 0.00036695 | 6.0551 | 6.0555 | -2.3485 | 2725.1582 | 6018.875 | -0.00086179
152 |  | 25.9013 | 39.7945 | 4187 | 0.00036694 | 6.0555 | 6.0559 | -2.3485 | 2725.2172 | 6058.6695 | -0.00086177
153 |  | 25.9013 | 39.7937 | 4187 | 0.00036694 | 6.0559 | 6.0562 | -2.3485 | 2725.2763 | 6098.4632 | -0.00086176
154 |  | 25.9013 | 39.7928 | 4187 | 0.00036693 | 6.0562 | 6.0566 | -2.3485 | 2725.3353 | 6138.256 | -0.00086174
155 |  | 25.9013 | 39.7919 | 4187 | 0.00036692 | 6.0566 | 6.057 | -2.3485 | 2725.3943 | 6178.048 | -0.00086172
156 |  | 25.9013 | 39.7911 | 4187 | 0.00036691 | 6.057 | 6.0573 | -2.3485 | 2725.4533 | 6217.839 | -0.0008617
157 |  | 25.9013 | 39.7902 | 4187 | 0.0003669 | 6.0573 | 6.0577 | -2.3485 | 2725.5123 | 6257.6293 | -0.00086168
158 |  | 25.9013 | 39.7894 | 4187 | 0.0003669 | 6.0577 | 6.0581 | -2.3485 | 2725.5714 | 6297.4186 | -0.00086166
159 |  | 25.9013 | 39.7885 | 4187 | 0.00036689 | 6.0581 | 6.0584 | -2.3485 | 2725.6304 | 6337.2071 | -0.00086164
160 |  | 25.9013 | 39.7876 | 4187 | 0.00036688 | 6.0584 | 6.0588 | -2.3485 | 2725.6894 | 6376.9948 | -0.00086162
161 |  | 25.9013 | 39.7868 | 4187 | 0.00036687 | 6.0588 | 6.0592 | -2.3485 | 2725.7484 | 6416.7816 | -0.00086161
162 |  | 25.9013 | 39.7859 | 4187 | 0.00036686 | 6.0592 | 6.0595 | -2.3485 | 2725.8075 | 6456.5675 | -0.00086159
163 |  | 25.9013 | 39.7851 | 4187 | 0.00036686 | 6.0595 | 6.0599 | -2.3485 | 2725.8665 | 6496.3525 | -0.00086157
164 |  | 25.9013 | 39.7842 | 4187 | 0.00036685 | 6.0599 | 6.0603 | -2.3485 | 2725.9255 | 6536.1367 | -0.00086155
165 |  | 25.9013 | 39.7833 | 4187 | 0.00036684 | 6.0603 | 6.0606 | -2.3485 | 2725.9846 | 6575.92 | -0.00086153
166 |  | 25.9013 | 39.7825 | 4187 | 0.00036683 | 6.0606 | 6.061 | -2.3485 | 2726.0436 | 6615.7025 | -0.00086151
167 |  | 25.9013 | 39.7816 | 4187 | 0.00036682 | 6.061 | 6.0614 | -2.3485 | 2726.1026 | 6655.4841 | -0.00086149
168 |  | 25.9013 | 39.7807 | 4187 | 0.00036682 | 6.0614 | 6.0617 | -2.3485 | 2726.1617 | 6695.2649 | -0.00086148
169 |  | 25.9013 | 39.7799 | 4187 | 0.00036681 | 6.0617 | 6.0621 | -2.3485 | 2726.2207 | 6735.0447 | -0.00086146
170 |  | 25.9013 | 39.779 | 4187 | 0.0003668 | 6.0621 | 6.0625 | -2.3485 | 2726.2797 | 6774.8238 | -0.00086144
171 |  | 25.9013 | 39.7782 | 4187 | 0.00036679 | 6.0625 | 6.0628 | -2.3485 | 2726.3388 | 6814.6019 | -0.00086142
172 |  | 25.9013 | 39.7773 | 4187 | 0.00036678 | 6.0628 | 6.0632 | -2.3485 | 2726.3978 | 6854.3792 | -0.0008614
173 |  | 25.9013 | 39.7764 | 4187 | 0.00036678 | 6.0632 | 6.0636 | -2.3485 | 2726.4569 | 6894.1557 | -0.00086138
174 |  | 25.9013 | 39.7756 | 4187 | 0.00036677 | 6.0636 | 6.0639 | -2.3485 | 2726.5159 | 6933.9313 | -0.00086136
175 |  | 25.9013 | 39.7747 | 4187 | 0.00036676 | 6.0639 | 6.0643 | -2.3485 | 2726.575 | 6973.706 | -0.00086135
176 |  | 25.9013 | 39.7739 | 4187 | 0.00036675 | 6.0643 | 6.0647 | -2.3485 | 2726.634 | 7013.4798 | -0.00086133
177 |  | 25.9013 | 39.773 | 4187 | 0.00036674 | 6.0647 | 6.065 | -2.3485 | 2726.6931 | 7053.2528 | -0.00086131
178 |  | 25.9013 | 39.7721 | 4187 | 0.00036674 | 6.065 | 6.0654 | -2.3485 | 2726.7521 | 7093.0249 | -0.00086129
179 |  | 25.9013 | 39.7713 | 4187 | 0.00036673 | 6.0654 | 6.0658 | -2.3485 | 2726.8112 | 7132.7962 | -0.00086127
180 |  | 25.9013 | 39.7704 | 4187 | 0.00036672 | 6.0658 | 6.0661 | -2.3485 | 2726.8702 | 7172.5666 | -0.00086125
181 |  | 25.9013 | 39.7695 | 4187 | 0.00036671 | 6.0661 | 6.0665 | -2.3485 | 2726.9293 | 7212.3362 | -0.00086123
182 |  | 25.9013 | 39.7687 | 4187 | 0.0003667 | 6.0665 | 6.0669 | -2.3485 | 2726.9883 | 7252.1049 | -0.00086121
183 |  | 25.9013 | 39.7678 | 4187 | 0.0003667 | 6.0669 | 6.0672 | -2.3485 | 2727.0474 | 7291.8727 | -0.0008612
184 |  | 25.9013 | 39.767 | 4187 | 0.00036669 | 6.0672 | 6.0676 | -2.3485 | 2727.1064 | 7331.6397 | -0.00086118
185 |  | 25.9013 | 39.7661 | 4187 | 0.00036668 | 6.0676 | 6.068 | -2.3485 | 2727.1655 | 7371.4058 | -0.00086116
186 |  | 25.9013 | 39.7652 | 4187 | 0.00036667 | 6.068 | 6.0683 | -2.3485 | 2727.2246 | 7411.171 | -0.00086114
187 |  | 25.9013 | 39.7644 | 4187 | 0.00036667 | 6.0683 | 6.0687 | -2.3485 | 2727.2836 | 7450.9354 | -0.00086112
188 |  | 25.9013 | 39.7635 | 4187 | 0.00036666 | 6.0687 | 6.0691 | -2.3485 | 2727.3427 | 7490.6989 | -0.0008611
189 |  | 25.9013 | 39.7627 | 4187 | 0.00036665 | 6.0691 | 6.0694 | -2.3485 | 2727.4017 | 7530.4616 | -0.00086108
190 |  | 25.9013 | 39.7618 | 4187 | 0.00036664 | 6.0694 | 6.0698 | -2.3485 | 2727.4608 | 7570.2234 | -0.00086107
191 |  | 25.9013 | 39.7609 | 4187 | 0.00036663 | 6.0698 | 6.0702 | -2.3485 | 2727.5199 | 7609.9843 | -0.00086105
192 |  | 25.9013 | 39.7601 | 4187 | 0.00036663 | 6.0702 | 6.0705 | -2.3485 | 2727.5789 | 7649.7444 | -0.00086103
193 |  | 25.9013 | 39.7592 | 4187 | 0.00036662 | 6.0705 | 6.0709 | -2.3485 | 2727.638 | 7689.5036 | -0.00086101
194 |  | 25.9013 | 39.7584 | 4187 | 0.00036661 | 6.0709 | 6.0713 | -2.3485 | 2727.6971 | 7729.2619 | -0.00086099
195 |  | 25.9013 | 39.7575 | 4187 | 0.0003666 | 6.0713 | 6.0716 | -2.3485 | 2727.7561 | 7769.0194 | -0.00086097
196 |  | 25.9013 | 39.7566 | 4187 | 0.00036659 | 6.0716 | 6.072 | -2.3485 | 2727.8152 | 7808.7761 | -0.00086095
197 |  | 25.9013 | 39.7558 | 4187 | 0.00036659 | 6.072 | 6.0724 | -2.3485 | 2727.8743 | 7848.5318 | -0.00086093
198 |  | 25.9013 | 39.7549 | 4187 | 0.00036658 | 6.0724 | 6.0727 | -2.3485 | 2727.9334 | 7888.2867 | -0.00086092
199 |  | 25.9013 | 39.754 | 4187 | 0.00036657 | 6.0727 | 6.0731 | -2.3485 | 2727.9924 | 7928.0408 | -0.0008609
200 |  | 25.9013 | 39.7532 | 4187 | 0.00036656 | 6.0731 | 6.0735 | -2.3485 | 2728.0515 | 7967.794 | -0.00086088
201 |  | 25.9013 | 39.7523 | 4187 | 0.00036655 | 6.0735 | 6.0738 | -2.3485 | 2728.1106 | 8007.5463 | -0.00086086
202 |  | 25.9013 | 39.7515 | 4187 | 0.00036655 | 6.0738 | 6.0742 | -2.3485 | 2728.1697 | 8047.2978 | -0.00086084
203 |  | 25.9013 | 39.7506 | 4187 | 0.00036654 | 6.0742 | 6.0746 | -2.3485 | 2728.2288 | 8087.0484 | -0.00086082
204 |  | 25.9013 | 39.7497 | 4187 | 0.00036653 | 6.0746 | 6.0749 | -2.3485 | 2728.2878 | 8126.7981 | -0.0008608
205 |  | 25.9013 | 39.7489 | 4187 | 0.00036652 | 6.0749 | 6.0753 | -2.3485 | 2728.3469 | 8166.547 | -0.00086079
206 |  | 25.9013 | 39.748 | 4187 | 0.00036651 | 6.0753 | 6.0757 | -2.3485 | 2728.406 | 8206.295 | -0.00086077
207 |  | 25.9013 | 39.7472 | 4187 | 0.00036651 | 6.0757 | 6.076 | -2.3485 | 2728.4651 | 8246.0422 | -0.00086075
208 |  | 25.9013 | 39.7463 | 4187 | 0.0003665 | 6.076 | 6.0764 | -2.3485 | 2728.5242 | 8285.7885 | -0.00086073
209 |  | 25.9013 | 39.7454 | 4187 | 0.00036649 | 6.0764 | 6.0768 | -2.3485 | 2728.5833 | 8325.5339 | -0.00086071
210 |  | 25.9013 | 39.7446 | 4187 | 0.00036648 | 6.0768 | 6.0771 | -2.3485 | 2728.6424 | 8365.2785 | -0.00086069
211 |  | 25.9013 | 39.7437 | 4187 | 0.00036647 | 6.0771 | 6.0775 | -2.3485 | 2728.7015 | 8405.0222 | -0.00086067
212 |  | 25.9013 | 39.7429 | 4187 | 0.00036647 | 6.0775 | 6.0779 | -2.3485 | 2728.7606 | 8444.7651 | -0.00086066
213 |  | 25.9013 | 39.742 | 4187 | 0.00036646 | 6.0779 | 6.0782 | -2.3485 | 2728.8196 | 8484.5071 | -0.00086064
214 |  | 25.9013 | 39.7411 | 4187 | 0.00036645 | 6.0782 | 6.0786 | -2.3485 | 2728.8787 | 8524.2482 | -0.00086062
215 |  | 25.9013 | 39.7403 | 4187 | 0.00036644 | 6.0786 | 6.079 | -2.3485 | 2728.9378 | 8563.9885 | -0.0008606
216 |  | 25.9013 | 39.7394 | 4187 | 0.00036644 | 6.079 | 6.0793 | -2.3485 | 2728.9969 | 8603.7279 | -0.00086058
217 |  | 25.9013 | 39.7386 | 4187 | 0.00036643 | 6.0793 | 6.0797 | -2.3485 | 2729.056 | 8643.4665 | -0.00086056
218 |  | 25.9013 | 39.7377 | 4187 | 0.00036642 | 6.0797 | 6.0801 | -2.3485 | 2729.1151 | 8683.2042 | -0.00086054
219 |  | 25.9013 | 39.7368 | 4187 | 0.00036641 | 6.0801 | 6.0804 | -2.3485 | 2729.1742 | 8722.941 | -0.00086052
220 |  | 25.9013 | 39.736 | 4187 | 0.0003664 | 6.0804 | 6.0808 | -2.3485 | 2729.2333 | 8762.677 | -0.00086051
221 |  | 25.9013 | 39.7351 | 4187 | 0.0003664 | 6.0808 | 6.0812 | -2.3485 | 2729.2924 | 8802.4121 | -0.00086049
222 |  | 25.9013 | 39.7343 | 4187 | 0.00036639 | 6.0812 | 6.0815 | -2.3485 | 2729.3516 | 8842.1463 | -0.00086047
223 |  | 25.9013 | 39.7334 | 4187 | 0.00036638 | 6.0815 | 6.0819 | -2.3485 | 2729.4107 | 8881.8797 | -0.00086045
224 |  | 25.9013 | 39.7325 | 4187 | 0.00036637 | 6.0819 | 6.0823 | -2.3485 | 2729.4698 | 8921.6123 | -0.00086043
225 |  | 25.9013 | 39.7317 | 4187 | 0.00036636 | 6.0823 | 6.0826 | -2.3485 | 2729.5289 | 8961.3439 | -0.00086041
226 |  | 25.9013 | 39.7308 | 4187 | 0.00036636 | 6.0826 | 6.083 | -2.3485 | 2729.588 | 9001.0748 | -0.00086039
227 |  | 25.9013 | 39.73 | 4187 | 0.00036635 | 6.083 | 6.0834 | -2.3485 | 2729.6471 | 9040.8047 | -0.00086038
228 |  | 25.9013 | 39.7291 | 4187 | 0.00036634 | 6.0834 | 6.0837 | -2.3485 | 2729.7062 | 9080.5338 | -0.00086036
229 |  | 25.9013 | 39.7282 | 4187 | 0.00036633 | 6.0837 | 6.0841 | -2.3485 | 2729.7653 | 9120.262 | -0.00086034
230 |  | 25.9013 | 39.7274 | 4187 | 0.00036632 | 6.0841 | 6.0845 | -2.3485 | 2729.8244 | 9159.9894 | -0.00086032
231 |  | 25.9013 | 39.7265 | 4187 | 0.00036632 | 6.0845 | 6.0848 | -2.3485 | 2729.8836 | 9199.7159 | -0.0008603
232 |  | 25.9013 | 39.7256 | 4187 | 0.00036631 | 6.0848 | 6.0852 | -2.3485 | 2729.9427 | 9239.4416 | -0.00086028
233 |  | 25.9013 | 39.7248 | 4187 | 0.0003663 | 6.0852 | 6.0856 | -2.3485 | 2730.0018 | 9279.1663 | -0.00086026
234 |  | 25.9013 | 39.7239 | 4187 | 0.00036629 | 6.0856 | 6.0859 | -2.3485 | 2730.0609 | 9318.8903 | -0.00086025
235 |  | 25.9013 | 39.7231 | 4187 | 0.00036628 | 6.0859 | 6.0863 | -2.3485 | 2730.12 | 9358.6133 | -0.00086023
236 |  | 25.9013 | 39.7222 | 4187 | 0.00036628 | 6.0863 | 6.0867 | -2.3485 | 2730.1792 | 9398.3355 | -0.00086021

## Fus315
|  |  | buis | verlies W/M | L /°C/sec
diam | wandikte |  | inhoud l/m |  | W/M
315 | 42.6 | 3.1416 | 41.4753 | 42.1458 | 4187
[8 empty] | J/sec/mtr | aantal mtr. | verlies
|  | buis | verlies W/M | L /°C/sec | verlies temp | begintemp | eindtemp | verlies | bij 1°C | totaal J/sec
|  | inhoud L |  | W/M | °C per M | °C | °C | per m°C | daling | aantal mtr
1 | 315 | 41.4753 | 42.1458 | 4187 | 0.0002427 | 6 | 6.0002 | -2.4792 | 4120.3971 | 42.1458 | -0.00060168
2 |  | 41.4753 | 42.1452 | 4187 | 0.00024269 | 6.0002 | 6.0005 | -2.4792 | 4120.4559 | 84.2909 | -0.00060167
3 |  | 41.4753 | 42.1445 | 4187 | 0.00024269 | 6.0005 | 6.0007 | -2.4792 | 4120.5148 | 126.4355 | -0.00060166
4 |  | 41.4753 | 42.1439 | 4187 | 0.00024268 | 6.0007 | 6.001 | -2.4792 | 4120.5736 | 168.5794 | -0.00060165
5 |  | 41.4753 | 42.1433 | 4187 | 0.00024268 | 6.001 | 6.0012 | -2.4792 | 4120.6324 | 210.7227 | -0.00060165
6 |  | 41.4753 | 42.1427 | 4187 | 0.00024268 | 6.0012 | 6.0015 | -2.4792 | 4120.6912 | 252.8655 | -0.00060164
7 |  | 41.4753 | 42.1421 | 4187 | 0.00024267 | 6.0015 | 6.0017 | -2.4792 | 4120.7501 | 295.0076 | -0.00060163
8 |  | 41.4753 | 42.1415 | 4187 | 0.00024267 | 6.0017 | 6.0019 | -2.4792 | 4120.8089 | 337.1492 | -0.00060162
9 |  | 41.4753 | 42.1409 | 4187 | 0.00024267 | 6.0019 | 6.0022 | -2.4792 | 4120.8677 | 379.2901 | -0.00060161
10 |  | 41.4753 | 42.1403 | 4187 | 0.00024266 | 6.0022 | 6.0024 | -2.4792 | 4120.9266 | 421.4305 | -0.0006016
11 |  | 41.4753 | 42.1397 | 4187 | 0.00024266 | 6.0024 | 6.0027 | -2.4792 | 4120.9854 | 463.5702 | -0.00060159
12 |  | 41.4753 | 42.1391 | 4187 | 0.00024266 | 6.0027 | 6.0029 | -2.4792 | 4121.0442 | 505.7093 | -0.00060159
13 |  | 41.4753 | 42.1385 | 4187 | 0.00024265 | 6.0029 | 6.0032 | -2.4792 | 4121.1031 | 547.8479 | -0.00060158
14 |  | 41.4753 | 42.1379 | 4187 | 0.00024265 | 6.0032 | 6.0034 | -2.4792 | 4121.1619 | 589.9858 | -0.00060157
15 |  | 41.4753 | 42.1373 | 4187 | 0.00024265 | 6.0034 | 6.0036 | -2.4792 | 4121.2207 | 632.1231 | -0.00060156
16 |  | 41.4753 | 42.1367 | 4187 | 0.00024264 | 6.0036 | 6.0039 | -2.4792 | 4121.2796 | 674.2598 | -0.00060155
17 |  | 41.4753 | 42.1361 | 4187 | 0.00024264 | 6.0039 | 6.0041 | -2.4792 | 4121.3384 | 716.396 | -0.00060154
18 |  | 41.4753 | 42.1355 | 4187 | 0.00024264 | 6.0041 | 6.0044 | -2.4792 | 4121.3972 | 758.5315 | -0.00060153
19 |  | 41.4753 | 42.1349 | 4187 | 0.00024263 | 6.0044 | 6.0046 | -2.4792 | 4121.4561 | 800.6664 | -0.00060153
20 |  | 41.4753 | 42.1343 | 4187 | 0.00024263 | 6.0046 | 6.0049 | -2.4792 | 4121.5149 | 842.8007 | -0.00060152
21 |  | 41.4753 | 42.1337 | 4187 | 0.00024263 | 6.0049 | 6.0051 | -2.4792 | 4121.5738 | 884.9345 | -0.00060151
22 |  | 41.4753 | 42.1331 | 4187 | 0.00024262 | 6.0051 | 6.0053 | -2.4792 | 4121.6326 | 927.0676 | -0.0006015
23 |  | 41.4753 | 42.1325 | 4187 | 0.00024262 | 6.0053 | 6.0056 | -2.4792 | 4121.6914 | 969.2001 | -0.00060149
24 |  | 41.4753 | 42.1319 | 4187 | 0.00024262 | 6.0056 | 6.0058 | -2.4792 | 4121.7503 | 1011.332 | -0.00060148
25 |  | 41.4753 | 42.1313 | 4187 | 0.00024261 | 6.0058 | 6.0061 | -2.4792 | 4121.8091 | 1053.4633 | -0.00060147
26 |  | 41.4753 | 42.1307 | 4187 | 0.00024261 | 6.0061 | 6.0063 | -2.4792 | 4121.868 | 1095.5941 | -0.00060147
27 |  | 41.4753 | 42.1301 | 4187 | 0.0002426 | 6.0063 | 6.0066 | -2.4792 | 4121.9268 | 1137.7242 | -0.00060146
28 |  | 41.4753 | 42.1295 | 4187 | 0.0002426 | 6.0066 | 6.0068 | -2.4792 | 4121.9857 | 1179.8537 | -0.00060145
29 |  | 41.4753 | 42.1289 | 4187 | 0.0002426 | 6.0068 | 6.007 | -2.4792 | 4122.0445 | 1221.9826 | -0.00060144
30 |  | 41.4753 | 42.1283 | 4187 | 0.00024259 | 6.007 | 6.0073 | -2.4792 | 4122.1034 | 1264.1109 | -0.00060143
31 |  | 41.4753 | 42.1277 | 4187 | 0.00024259 | 6.0073 | 6.0075 | -2.4792 | 4122.1622 | 1306.2386 | -0.00060142
32 |  | 41.4753 | 42.1271 | 4187 | 0.00024259 | 6.0075 | 6.0078 | -2.4792 | 4122.2211 | 1348.3657 | -0.00060141
33 |  | 41.4753 | 42.1265 | 4187 | 0.00024258 | 6.0078 | 6.008 | -2.4792 | 4122.2799 | 1390.4922 | -0.00060141
34 |  | 41.4753 | 42.1259 | 4187 | 0.00024258 | 6.008 | 6.0082 | -2.4792 | 4122.3388 | 1432.6181 | -0.0006014
35 |  | 41.4753 | 42.1253 | 4187 | 0.00024258 | 6.0082 | 6.0085 | -2.4792 | 4122.3976 | 1474.7434 | -0.00060139
36 |  | 41.4753 | 42.1247 | 4187 | 0.00024257 | 6.0085 | 6.0087 | -2.4792 | 4122.4565 | 1516.8681 | -0.00060138
37 |  | 41.4753 | 42.1241 | 4187 | 0.00024257 | 6.0087 | 6.009 | -2.4792 | 4122.5153 | 1558.9922 | -0.00060137
38 |  | 41.4753 | 42.1235 | 4187 | 0.00024257 | 6.009 | 6.0092 | -2.4792 | 4122.5742 | 1601.1157 | -0.00060136
39 |  | 41.4753 | 42.1229 | 4187 | 0.00024256 | 6.0092 | 6.0095 | -2.4792 | 4122.633 | 1643.2386 | -0.00060135
40 |  | 41.4753 | 42.1223 | 4187 | 0.00024256 | 6.0095 | 6.0097 | -2.4792 | 4122.6919 | 1685.3609 | -0.00060135
41 |  | 41.4753 | 42.1217 | 4187 | 0.00024256 | 6.0097 | 6.0099 | -2.4792 | 4122.7507 | 1727.4826 | -0.00060134
42 |  | 41.4753 | 42.1211 | 4187 | 0.00024255 | 6.0099 | 6.0102 | -2.4792 | 4122.8096 | 1769.6037 | -0.00060133
43 |  | 41.4753 | 42.1205 | 4187 | 0.00024255 | 6.0102 | 6.0104 | -2.4792 | 4122.8685 | 1811.7242 | -0.00060132
44 |  | 41.4753 | 42.1199 | 4187 | 0.00024255 | 6.0104 | 6.0107 | -2.4792 | 4122.9273 | 1853.8441 | -0.00060131
45 |  | 41.4753 | 42.1193 | 4187 | 0.00024254 | 6.0107 | 6.0109 | -2.4792 | 4122.9862 | 1895.9633 | -0.0006013
46 |  | 41.4753 | 42.1187 | 4187 | 0.00024254 | 6.0109 | 6.0112 | -2.4792 | 4123.045 | 1938.082 | -0.00060129
47 |  | 41.4753 | 42.1181 | 4187 | 0.00024254 | 6.0112 | 6.0114 | -2.4792 | 4123.1039 | 1980.2001 | -0.00060129
48 |  | 41.4753 | 42.1175 | 4187 | 0.00024253 | 6.0114 | 6.0116 | -2.4792 | 4123.1628 | 2022.3176 | -0.00060128
49 |  | 41.4753 | 42.1169 | 4187 | 0.00024253 | 6.0116 | 6.0119 | -2.4792 | 4123.2216 | 2064.4345 | -0.00060127
50 |  | 41.4753 | 42.1163 | 4187 | 0.00024253 | 6.0119 | 6.0121 | -2.4792 | 4123.2805 | 2106.5508 | -0.00060126
51 |  | 41.4753 | 42.1157 | 4187 | 0.00024252 | 6.0121 | 6.0124 | -2.4792 | 4123.3394 | 2148.6664 | -0.00060125
52 |  | 41.4753 | 42.1151 | 4187 | 0.00024252 | 6.0124 | 6.0126 | -2.4792 | 4123.3982 | 2190.7815 | -0.00060124
53 |  | 41.4753 | 42.1145 | 4187 | 0.00024251 | 6.0126 | 6.0129 | -2.4792 | 4123.4571 | 2232.896 | -0.00060123
54 |  | 41.4753 | 42.1139 | 4187 | 0.00024251 | 6.0129 | 6.0131 | -2.4792 | 4123.516 | 2275.0099 | -0.00060123
55 |  | 41.4753 | 42.1133 | 4187 | 0.00024251 | 6.0131 | 6.0133 | -2.4792 | 4123.5748 | 2317.1231 | -0.00060122
56 |  | 41.4753 | 42.1127 | 4187 | 0.0002425 | 6.0133 | 6.0136 | -2.4792 | 4123.6337 | 2359.2358 | -0.00060121
57 |  | 41.4753 | 42.1121 | 4187 | 0.0002425 | 6.0136 | 6.0138 | -2.4792 | 4123.6926 | 2401.3479 | -0.0006012
58 |  | 41.4753 | 42.1115 | 4187 | 0.0002425 | 6.0138 | 6.0141 | -2.4792 | 4123.7514 | 2443.4594 | -0.00060119
59 |  | 41.4753 | 42.1109 | 4187 | 0.00024249 | 6.0141 | 6.0143 | -2.4792 | 4123.8103 | 2485.5702 | -0.00060118
60 |  | 41.4753 | 42.1103 | 4187 | 0.00024249 | 6.0143 | 6.0146 | -2.4792 | 4123.8692 | 2527.6805 | -0.00060117
61 |  | 41.4753 | 42.1097 | 4187 | 0.00024249 | 6.0146 | 6.0148 | -2.4792 | 4123.9281 | 2569.7902 | -0.00060117
62 |  | 41.4753 | 42.1091 | 4187 | 0.00024248 | 6.0148 | 6.015 | -2.4792 | 4123.9869 | 2611.8992 | -0.00060116
63 |  | 41.4753 | 42.1085 | 4187 | 0.00024248 | 6.015 | 6.0153 | -2.4792 | 4124.0458 | 2654.0077 | -0.00060115
64 |  | 41.4753 | 42.1079 | 4187 | 0.00024248 | 6.0153 | 6.0155 | -2.4792 | 4124.1047 | 2696.1156 | -0.00060114
65 |  | 41.4753 | 42.1073 | 4187 | 0.00024247 | 6.0155 | 6.0158 | -2.4792 | 4124.1636 | 2738.2228 | -0.00060113
66 |  | 41.4753 | 42.1067 | 4187 | 0.00024247 | 6.0158 | 6.016 | -2.4792 | 4124.2224 | 2780.3295 | -0.00060112
67 |  | 41.4753 | 42.1061 | 4187 | 0.00024247 | 6.016 | 6.0163 | -2.4792 | 4124.2813 | 2822.4355 | -0.00060111
68 |  | 41.4753 | 42.1055 | 4187 | 0.00024246 | 6.0163 | 6.0165 | -2.4792 | 4124.3402 | 2864.541 | -0.00060111
69 |  | 41.4753 | 42.1049 | 4187 | 0.00024246 | 6.0165 | 6.0167 | -2.4792 | 4124.3991 | 2906.6459 | -0.0006011
70 |  | 41.4753 | 42.1043 | 4187 | 0.00024246 | 6.0167 | 6.017 | -2.4792 | 4124.458 | 2948.7501 | -0.00060109
71 |  | 41.4753 | 42.1037 | 4187 | 0.00024245 | 6.017 | 6.0172 | -2.4792 | 4124.5169 | 2990.8538 | -0.00060108
72 |  | 41.4753 | 42.1031 | 4187 | 0.00024245 | 6.0172 | 6.0175 | -2.4792 | 4124.5757 | 3032.9568 | -0.00060107
73 |  | 41.4753 | 42.1025 | 4187 | 0.00024245 | 6.0175 | 6.0177 | -2.4792 | 4124.6346 | 3075.0593 | -0.00060106
74 |  | 41.4753 | 42.1019 | 4187 | 0.00024244 | 6.0177 | 6.018 | -2.4792 | 4124.6935 | 3117.1611 | -0.00060105
75 |  | 41.4753 | 42.1013 | 4187 | 0.00024244 | 6.018 | 6.0182 | -2.4792 | 4124.7524 | 3159.2624 | -0.00060105
76 |  | 41.4753 | 42.1007 | 4187 | 0.00024244 | 6.0182 | 6.0184 | -2.4792 | 4124.8113 | 3201.363 | -0.00060104
77 |  | 41.4753 | 42.1 | 4187 | 0.00024243 | 6.0184 | 6.0187 | -2.4792 | 4124.8702 | 3243.4631 | -0.00060103
78 |  | 41.4753 | 42.0994 | 4187 | 0.00024243 | 6.0187 | 6.0189 | -2.4792 | 4124.9291 | 3285.5625 | -0.00060102
79 |  | 41.4753 | 42.0988 | 4187 | 0.00024242 | 6.0189 | 6.0192 | -2.4792 | 4124.9879 | 3327.6614 | -0.00060101
80 |  | 41.4753 | 42.0982 | 4187 | 0.00024242 | 6.0192 | 6.0194 | -2.4792 | 4125.0468 | 3369.7596 | -0.000601
81 |  | 41.4753 | 42.0976 | 4187 | 0.00024242 | 6.0194 | 6.0196 | -2.4792 | 4125.1057 | 3411.8573 | -0.00060099
82 |  | 41.4753 | 42.097 | 4187 | 0.00024241 | 6.0196 | 6.0199 | -2.4792 | 4125.1646 | 3453.9543 | -0.00060098
83 |  | 41.4753 | 42.0964 | 4187 | 0.00024241 | 6.0199 | 6.0201 | -2.4792 | 4125.2235 | 3496.0508 | -0.00060098
84 |  | 41.4753 | 42.0958 | 4187 | 0.00024241 | 6.0201 | 6.0204 | -2.4792 | 4125.2824 | 3538.1466 | -0.00060097
85 |  | 41.4753 | 42.0952 | 4187 | 0.0002424 | 6.0204 | 6.0206 | -2.4792 | 4125.3413 | 3580.2418 | -0.00060096
86 |  | 41.4753 | 42.0946 | 4187 | 0.0002424 | 6.0206 | 6.0209 | -2.4792 | 4125.4002 | 3622.3365 | -0.00060095
87 |  | 41.4753 | 42.094 | 4187 | 0.0002424 | 6.0209 | 6.0211 | -2.4792 | 4125.4591 | 3664.4305 | -0.00060094
88 |  | 41.4753 | 42.0934 | 4187 | 0.00024239 | 6.0211 | 6.0213 | -2.4792 | 4125.518 | 3706.524 | -0.00060093
89 |  | 41.4753 | 42.0928 | 4187 | 0.00024239 | 6.0213 | 6.0216 | -2.4792 | 4125.5769 | 3748.6168 | -0.00060092
90 |  | 41.4753 | 42.0922 | 4187 | 0.00024239 | 6.0216 | 6.0218 | -2.4792 | 4125.6358 | 3790.709 | -0.00060092
91 |  | 41.4753 | 42.0916 | 4187 | 0.00024238 | 6.0218 | 6.0221 | -2.4792 | 4125.6947 | 3832.8007 | -0.00060091
92 |  | 41.4753 | 42.091 | 4187 | 0.00024238 | 6.0221 | 6.0223 | -2.4792 | 4125.7536 | 3874.8917 | -0.0006009
93 |  | 41.4753 | 42.0904 | 4187 | 0.00024238 | 6.0223 | 6.0226 | -2.4792 | 4125.8125 | 3916.9821 | -0.00060089
94 |  | 41.4753 | 42.0898 | 4187 | 0.00024237 | 6.0226 | 6.0228 | -2.4792 | 4125.8714 | 3959.072 | -0.00060088
95 |  | 41.4753 | 42.0892 | 4187 | 0.00024237 | 6.0228 | 6.023 | -2.4792 | 4125.9303 | 4001.1612 | -0.00060087
96 |  | 41.4753 | 42.0886 | 4187 | 0.00024237 | 6.023 | 6.0233 | -2.4792 | 4125.9892 | 4043.2498 | -0.00060086
97 |  | 41.4753 | 42.088 | 4187 | 0.00024236 | 6.0233 | 6.0235 | -2.4792 | 4126.0481 | 4085.3379 | -0.00060086
98 |  | 41.4753 | 42.0874 | 4187 | 0.00024236 | 6.0235 | 6.0238 | -2.4792 | 4126.107 | 4127.4253 | -0.00060085
99 |  | 41.4753 | 42.0868 | 4187 | 0.00024236 | 6.0238 | 6.024 | -2.4792 | 4126.1659 | 4169.5121 | -0.00060084
100 |  | 41.4753 | 42.0862 | 4187 | 0.00024235 | 6.024 | 6.0243 | -2.4792 | 4126.2248 | 4211.5984 | -0.00060083
101 |  | 41.4753 | 42.0856 | 4187 | 0.00024235 | 6.0243 | 6.0245 | -2.4792 | 4126.2837 | 4253.684 | -0.00060082
102 |  | 41.4753 | 42.085 | 4187 | 0.00024235 | 6.0245 | 6.0247 | -2.4792 | 4126.3426 | 4295.769 | -0.00060081
103 |  | 41.4753 | 42.0844 | 4187 | 0.00024234 | 6.0247 | 6.025 | -2.4792 | 4126.4015 | 4337.8534 | -0.0006008
104 |  | 41.4753 | 42.0838 | 4187 | 0.00024234 | 6.025 | 6.0252 | -2.4792 | 4126.4604 | 4379.9373 | -0.0006008
105 |  | 41.4753 | 42.0832 | 4187 | 0.00024233 | 6.0252 | 6.0255 | -2.4792 | 4126.5194 | 4422.0205 | -0.00060079
106 |  | 41.4753 | 42.0826 | 4187 | 0.00024233 | 6.0255 | 6.0257 | -2.4792 | 4126.5783 | 4464.1031 | -0.00060078
107 |  | 41.4753 | 42.082 | 4187 | 0.00024233 | 6.0257 | 6.0259 | -2.4792 | 4126.6372 | 4506.1851 | -0.00060077
108 |  | 41.4753 | 42.0814 | 4187 | 0.00024232 | 6.0259 | 6.0262 | -2.4792 | 4126.6961 | 4548.2666 | -0.00060076
109 |  | 41.4753 | 42.0808 | 4187 | 0.00024232 | 6.0262 | 6.0264 | -2.4792 | 4126.755 | 4590.3474 | -0.00060075
110 |  | 41.4753 | 42.0802 | 4187 | 0.00024232 | 6.0264 | 6.0267 | -2.4792 | 4126.8139 | 4632.4276 | -0.00060074
111 |  | 41.4753 | 42.0796 | 4187 | 0.00024231 | 6.0267 | 6.0269 | -2.4792 | 4126.8728 | 4674.5072 | -0.00060074
112 |  | 41.4753 | 42.079 | 4187 | 0.00024231 | 6.0269 | 6.0272 | -2.4792 | 4126.9318 | 4716.5862 | -0.00060073
113 |  | 41.4753 | 42.0784 | 4187 | 0.00024231 | 6.0272 | 6.0274 | -2.4792 | 4126.9907 | 4758.6647 | -0.00060072
114 |  | 41.4753 | 42.0778 | 4187 | 0.0002423 | 6.0274 | 6.0276 | -2.4792 | 4127.0496 | 4800.7425 | -0.00060071
115 |  | 41.4753 | 42.0772 | 4187 | 0.0002423 | 6.0276 | 6.0279 | -2.4792 | 4127.1085 | 4842.8197 | -0.0006007
116 |  | 41.4753 | 42.0766 | 4187 | 0.0002423 | 6.0279 | 6.0281 | -2.4792 | 4127.1674 | 4884.8963 | -0.00060069
117 |  | 41.4753 | 42.076 | 4187 | 0.00024229 | 6.0281 | 6.0284 | -2.4792 | 4127.2263 | 4926.9723 | -0.00060068
118 |  | 41.4753 | 42.0754 | 4187 | 0.00024229 | 6.0284 | 6.0286 | -2.4792 | 4127.2853 | 4969.0477 | -0.00060068
119 |  | 41.4753 | 42.0748 | 4187 | 0.00024229 | 6.0286 | 6.0289 | -2.4792 | 4127.3442 | 5011.1225 | -0.00060067
120 |  | 41.4753 | 42.0742 | 4187 | 0.00024228 | 6.0289 | 6.0291 | -2.4792 | 4127.4031 | 5053.1968 | -0.00060066
121 |  | 41.4753 | 42.0736 | 4187 | 0.00024228 | 6.0291 | 6.0293 | -2.4792 | 4127.462 | 5095.2704 | -0.00060065
122 |  | 41.4753 | 42.073 | 4187 | 0.00024228 | 6.0293 | 6.0296 | -2.4792 | 4127.521 | 5137.3434 | -0.00060064
123 |  | 41.4753 | 42.0724 | 4187 | 0.00024227 | 6.0296 | 6.0298 | -2.4792 | 4127.5799 | 5179.4158 | -0.00060063
124 |  | 41.4753 | 42.0718 | 4187 | 0.00024227 | 6.0298 | 6.0301 | -2.4792 | 4127.6388 | 5221.4876 | -0.00060062
125 |  | 41.4753 | 42.0712 | 4187 | 0.00024227 | 6.0301 | 6.0303 | -2.4792 | 4127.6977 | 5263.5588 | -0.00060062
126 |  | 41.4753 | 42.0706 | 4187 | 0.00024226 | 6.0303 | 6.0306 | -2.4792 | 4127.7567 | 5305.6294 | -0.00060061
127 |  | 41.4753 | 42.07 | 4187 | 0.00024226 | 6.0306 | 6.0308 | -2.4792 | 4127.8156 | 5347.6994 | -0.0006006
128 |  | 41.4753 | 42.0694 | 4187 | 0.00024226 | 6.0308 | 6.031 | -2.4792 | 4127.8745 | 5389.7688 | -0.00060059
129 |  | 41.4753 | 42.0688 | 4187 | 0.00024225 | 6.031 | 6.0313 | -2.4792 | 4127.9335 | 5431.8376 | -0.00060058
130 |  | 41.4753 | 42.0682 | 4187 | 0.00024225 | 6.0313 | 6.0315 | -2.4792 | 4127.9924 | 5473.9059 | -0.00060057
131 |  | 41.4753 | 42.0676 | 4187 | 0.00024225 | 6.0315 | 6.0318 | -2.4792 | 4128.0513 | 5515.9735 | -0.00060056
132 |  | 41.4753 | 42.067 | 4187 | 0.00024224 | 6.0318 | 6.032 | -2.4792 | 4128.1103 | 5558.0405 | -0.00060056
133 |  | 41.4753 | 42.0664 | 4187 | 0.00024224 | 6.032 | 6.0322 | -2.4792 | 4128.1692 | 5600.1069 | -0.00060055
134 |  | 41.4753 | 42.0658 | 4187 | 0.00024223 | 6.0322 | 6.0325 | -2.4792 | 4128.2281 | 5642.1727 | -0.00060054
135 |  | 41.4753 | 42.0652 | 4187 | 0.00024223 | 6.0325 | 6.0327 | -2.4792 | 4128.2871 | 5684.2379 | -0.00060053
136 |  | 41.4753 | 42.0646 | 4187 | 0.00024223 | 6.0327 | 6.033 | -2.4792 | 4128.346 | 5726.3025 | -0.00060052
137 |  | 41.4753 | 42.064 | 4187 | 0.00024222 | 6.033 | 6.0332 | -2.4792 | 4128.4049 | 5768.3665 | -0.00060051
138 |  | 41.4753 | 42.0634 | 4187 | 0.00024222 | 6.0332 | 6.0335 | -2.4792 | 4128.4639 | 5810.4299 | -0.0006005
139 |  | 41.4753 | 42.0628 | 4187 | 0.00024222 | 6.0335 | 6.0337 | -2.4792 | 4128.5228 | 5852.4927 | -0.0006005
140 |  | 41.4753 | 42.0622 | 4187 | 0.00024221 | 6.0337 | 6.0339 | -2.4792 | 4128.5818 | 5894.5549 | -0.00060049
141 |  | 41.4753 | 42.0616 | 4187 | 0.00024221 | 6.0339 | 6.0342 | -2.4792 | 4128.6407 | 5936.6165 | -0.00060048
142 |  | 41.4753 | 42.061 | 4187 | 0.00024221 | 6.0342 | 6.0344 | -2.4792 | 4128.6996 | 5978.6775 | -0.00060047
143 |  | 41.4753 | 42.0604 | 4187 | 0.0002422 | 6.0344 | 6.0347 | -2.4792 | 4128.7586 | 6020.7379 | -0.00060046
144 |  | 41.4753 | 42.0598 | 4187 | 0.0002422 | 6.0347 | 6.0349 | -2.4792 | 4128.8175 | 6062.7977 | -0.00060045
145 |  | 41.4753 | 42.0592 | 4187 | 0.0002422 | 6.0349 | 6.0352 | -2.4792 | 4128.8765 | 6104.8569 | -0.00060044
146 |  | 41.4753 | 42.0586 | 4187 | 0.00024219 | 6.0352 | 6.0354 | -2.4792 | 4128.9354 | 6146.9155 | -0.00060044
147 |  | 41.4753 | 42.058 | 4187 | 0.00024219 | 6.0354 | 6.0356 | -2.4792 | 4128.9944 | 6188.9735 | -0.00060043
148 |  | 41.4753 | 42.0574 | 4187 | 0.00024219 | 6.0356 | 6.0359 | -2.4792 | 4129.0533 | 6231.0309 | -0.00060042
149 |  | 41.4753 | 42.0568 | 4187 | 0.00024218 | 6.0359 | 6.0361 | -2.4792 | 4129.1123 | 6273.0877 | -0.00060041
150 |  | 41.4753 | 42.0562 | 4187 | 0.00024218 | 6.0361 | 6.0364 | -2.4792 | 4129.1712 | 6315.1439 | -0.0006004
151 |  | 41.4753 | 42.0556 | 4187 | 0.00024218 | 6.0364 | 6.0366 | -2.4792 | 4129.2302 | 6357.1995 | -0.00060039
152 |  | 41.4753 | 42.055 | 4187 | 0.00024217 | 6.0366 | 6.0368 | -2.4792 | 4129.2891 | 6399.2545 | -0.00060038
153 |  | 41.4753 | 42.0544 | 4187 | 0.00024217 | 6.0368 | 6.0371 | -2.4792 | 4129.3481 | 6441.3089 | -0.00060038
154 |  | 41.4753 | 42.0538 | 4187 | 0.00024217 | 6.0371 | 6.0373 | -2.4792 | 4129.407 | 6483.3627 | -0.00060037
155 |  | 41.4753 | 42.0532 | 4187 | 0.00024216 | 6.0373 | 6.0376 | -2.4792 | 4129.466 | 6525.4159 | -0.00060036
156 |  | 41.4753 | 42.0526 | 4187 | 0.00024216 | 6.0376 | 6.0378 | -2.4792 | 4129.5249 | 6567.4685 | -0.00060035
157 |  | 41.4753 | 42.052 | 4187 | 0.00024216 | 6.0378 | 6.0381 | -2.4792 | 4129.5839 | 6609.5205 | -0.00060034
158 |  | 41.4753 | 42.0514 | 4187 | 0.00024215 | 6.0381 | 6.0383 | -2.4792 | 4129.6428 | 6651.5718 | -0.00060033
159 |  | 41.4753 | 42.0508 | 4187 | 0.00024215 | 6.0383 | 6.0385 | -2.4792 | 4129.7018 | 6693.6226 | -0.00060032
160 |  | 41.4753 | 42.0502 | 4187 | 0.00024214 | 6.0385 | 6.0388 | -2.4792 | 4129.7607 | 6735.6728 | -0.00060032
161 |  | 41.4753 | 42.0496 | 4187 | 0.00024214 | 6.0388 | 6.039 | -2.4792 | 4129.8197 | 6777.7224 | -0.00060031
162 |  | 41.4753 | 42.049 | 4187 | 0.00024214 | 6.039 | 6.0393 | -2.4792 | 4129.8787 | 6819.7714 | -0.0006003
163 |  | 41.4753 | 42.0484 | 4187 | 0.00024213 | 6.0393 | 6.0395 | -2.4792 | 4129.9376 | 6861.8198 | -0.00060029
164 |  | 41.4753 | 42.0478 | 4187 | 0.00024213 | 6.0395 | 6.0398 | -2.4792 | 4129.9966 | 6903.8676 | -0.00060028
165 |  | 41.4753 | 42.0472 | 4187 | 0.00024213 | 6.0398 | 6.04 | -2.4792 | 4130.0555 | 6945.9148 | -0.00060027
166 |  | 41.4753 | 42.0466 | 4187 | 0.00024212 | 6.04 | 6.0402 | -2.4792 | 4130.1145 | 6987.9614 | -0.00060026
167 |  | 41.4753 | 42.046 | 4187 | 0.00024212 | 6.0402 | 6.0405 | -2.4792 | 4130.1735 | 7030.0074 | -0.00060026
168 |  | 41.4753 | 42.0454 | 4187 | 0.00024212 | 6.0405 | 6.0407 | -2.4792 | 4130.2324 | 7072.0528 | -0.00060025
169 |  | 41.4753 | 42.0448 | 4187 | 0.00024211 | 6.0407 | 6.041 | -2.4792 | 4130.2914 | 7114.0976 | -0.00060024
170 |  | 41.4753 | 42.0442 | 4187 | 0.00024211 | 6.041 | 6.0412 | -2.4792 | 4130.3504 | 7156.1418 | -0.00060023
171 |  | 41.4753 | 42.0436 | 4187 | 0.00024211 | 6.0412 | 6.0415 | -2.4792 | 4130.4093 | 7198.1853 | -0.00060022
172 |  | 41.4753 | 42.043 | 4187 | 0.0002421 | 6.0415 | 6.0417 | -2.4792 | 4130.4683 | 7240.2283 | -0.00060021
173 |  | 41.4753 | 42.0424 | 4187 | 0.0002421 | 6.0417 | 6.0419 | -2.4792 | 4130.5273 | 7282.2707 | -0.0006002
174 |  | 41.4753 | 42.0418 | 4187 | 0.0002421 | 6.0419 | 6.0422 | -2.4792 | 4130.5862 | 7324.3125 | -0.0006002
175 |  | 41.4753 | 42.0412 | 4187 | 0.00024209 | 6.0422 | 6.0424 | -2.4792 | 4130.6452 | 7366.3537 | -0.00060019
176 |  | 41.4753 | 42.0406 | 4187 | 0.00024209 | 6.0424 | 6.0427 | -2.4792 | 4130.7042 | 7408.3943 | -0.00060018
177 |  | 41.4753 | 42.04 | 4187 | 0.00024209 | 6.0427 | 6.0429 | -2.4792 | 4130.7632 | 7450.4343 | -0.00060017
178 |  | 41.4753 | 42.0394 | 4187 | 0.00024208 | 6.0429 | 6.0431 | -2.4792 | 4130.8221 | 7492.4737 | -0.00060016
179 |  | 41.4753 | 42.0388 | 4187 | 0.00024208 | 6.0431 | 6.0434 | -2.4792 | 4130.8811 | 7534.5125 | -0.00060015
180 |  | 41.4753 | 42.0382 | 4187 | 0.00024208 | 6.0434 | 6.0436 | -2.4792 | 4130.9401 | 7576.5507 | -0.00060014
181 |  | 41.4753 | 42.0376 | 4187 | 0.00024207 | 6.0436 | 6.0439 | -2.4792 | 4130.999 | 7618.5882 | -0.00060014
182 |  | 41.4753 | 42.037 | 4187 | 0.00024207 | 6.0439 | 6.0441 | -2.4792 | 4131.058 | 7660.6252 | -0.00060013
183 |  | 41.4753 | 42.0364 | 4187 | 0.00024207 | 6.0441 | 6.0444 | -2.4792 | 4131.117 | 7702.6616 | -0.00060012
184 |  | 41.4753 | 42.0358 | 4187 | 0.00024206 | 6.0444 | 6.0446 | -2.4792 | 4131.176 | 7744.6974 | -0.00060011
185 |  | 41.4753 | 42.0352 | 4187 | 0.00024206 | 6.0446 | 6.0448 | -2.4792 | 4131.235 | 7786.7326 | -0.0006001
186 |  | 41.4753 | 42.0346 | 4187 | 0.00024205 | 6.0448 | 6.0451 | -2.4792 | 4131.2939 | 7828.7672 | -0.00060009
187 |  | 41.4753 | 42.034 | 4187 | 0.00024205 | 6.0451 | 6.0453 | -2.4792 | 4131.3529 | 7870.8012 | -0.00060008
188 |  | 41.4753 | 42.0334 | 4187 | 0.00024205 | 6.0453 | 6.0456 | -2.4792 | 4131.4119 | 7912.8346 | -0.00060008
189 |  | 41.4753 | 42.0328 | 4187 | 0.00024204 | 6.0456 | 6.0458 | -2.4792 | 4131.4709 | 7954.8673 | -0.00060007
190 |  | 41.4753 | 42.0322 | 4187 | 0.00024204 | 6.0458 | 6.046 | -2.4792 | 4131.5299 | 7996.8995 | -0.00060006
191 |  | 41.4753 | 42.0316 | 4187 | 0.00024204 | 6.046 | 6.0463 | -2.4792 | 4131.5888 | 8038.9311 | -0.00060005
192 |  | 41.4753 | 42.031 | 4187 | 0.00024203 | 6.0463 | 6.0465 | -2.4792 | 4131.6478 | 8080.9621 | -0.00060004
193 |  | 41.4753 | 42.0304 | 4187 | 0.00024203 | 6.0465 | 6.0468 | -2.4792 | 4131.7068 | 8122.9925 | -0.00060003
194 |  | 41.4753 | 42.0298 | 4187 | 0.00024203 | 6.0468 | 6.047 | -2.4792 | 4131.7658 | 8165.0223 | -0.00060002
195 |  | 41.4753 | 42.0292 | 4187 | 0.00024202 | 6.047 | 6.0473 | -2.4792 | 4131.8248 | 8207.0515 | -0.00060002
196 |  | 41.4753 | 42.0286 | 4187 | 0.00024202 | 6.0473 | 6.0475 | -2.4792 | 4131.8838 | 8249.0801 | -0.00060001
197 |  | 41.4753 | 42.028 | 4187 | 0.00024202 | 6.0475 | 6.0477 | -2.4792 | 4131.9428 | 8291.108 | -0.0006
198 |  | 41.4753 | 42.0274 | 4187 | 0.00024201 | 6.0477 | 6.048 | -2.4792 | 4132.0017 | 8333.1354 | -0.00059999
199 |  | 41.4753 | 42.0268 | 4187 | 0.00024201 | 6.048 | 6.0482 | -2.4792 | 4132.0607 | 8375.1622 | -0.00059998
200 |  | 41.4753 | 42.0262 | 4187 | 0.00024201 | 6.0482 | 6.0485 | -2.4792 | 4132.1197 | 8417.1884 | -0.00059997
201 |  | 41.4753 | 42.0256 | 4187 | 0.000242 | 6.0485 | 6.0487 | -2.4792 | 4132.1787 | 8459.214 | -0.00059996
202 |  | 41.4753 | 42.025 | 4187 | 0.000242 | 6.0487 | 6.049 | -2.4792 | 4132.2377 | 8501.239 | -0.00059996
203 |  | 41.4753 | 42.0244 | 4187 | 0.000242 | 6.049 | 6.0492 | -2.4792 | 4132.2967 | 8543.2634 | -0.00059995
204 |  | 41.4753 | 42.0238 | 4187 | 0.00024199 | 6.0492 | 6.0494 | -2.4792 | 4132.3557 | 8585.2872 | -0.00059994
205 |  | 41.4753 | 42.0232 | 4187 | 0.00024199 | 6.0494 | 6.0497 | -2.4792 | 4132.4147 | 8627.3103 | -0.00059993
206 |  | 41.4753 | 42.0226 | 4187 | 0.00024199 | 6.0497 | 6.0499 | -2.4792 | 4132.4737 | 8669.3329 | -0.00059992
207 |  | 41.4753 | 42.022 | 4187 | 0.00024198 | 6.0499 | 6.0502 | -2.4792 | 4132.5327 | 8711.3549 | -0.00059991
208 |  | 41.4753 | 42.0214 | 4187 | 0.00024198 | 6.0502 | 6.0504 | -2.4792 | 4132.5917 | 8753.3763 | -0.0005999
209 |  | 41.4753 | 42.0208 | 4187 | 0.00024198 | 6.0504 | 6.0506 | -2.4792 | 4132.6507 | 8795.3971 | -0.0005999
210 |  | 41.4753 | 42.0202 | 4187 | 0.00024197 | 6.0506 | 6.0509 | -2.4792 | 4132.7097 | 8837.4173 | -0.00059989
211 |  | 41.4753 | 42.0196 | 4187 | 0.00024197 | 6.0509 | 6.0511 | -2.4792 | 4132.7687 | 8879.4369 | -0.00059988
212 |  | 41.4753 | 42.019 | 4187 | 0.00024197 | 6.0511 | 6.0514 | -2.4792 | 4132.8277 | 8921.4559 | -0.00059987
213 |  | 41.4753 | 42.0184 | 4187 | 0.00024196 | 6.0514 | 6.0516 | -2.4792 | 4132.8867 | 8963.4743 | -0.00059986
214 |  | 41.4753 | 42.0178 | 4187 | 0.00024196 | 6.0516 | 6.0519 | -2.4792 | 4132.9457 | 9005.492 | -0.00059985
215 |  | 41.4753 | 42.0172 | 4187 | 0.00024195 | 6.0519 | 6.0521 | -2.4792 | 4133.0047 | 9047.5092 | -0.00059984
216 |  | 41.4753 | 42.0166 | 4187 | 0.00024195 | 6.0521 | 6.0523 | -2.4792 | 4133.0637 | 9089.5258 | -0.00059984
217 |  | 41.4753 | 42.016 | 4187 | 0.00024195 | 6.0523 | 6.0526 | -2.4792 | 4133.1227 | 9131.5418 | -0.00059983
218 |  | 41.4753 | 42.0154 | 4187 | 0.00024194 | 6.0526 | 6.0528 | -2.4792 | 4133.1817 | 9173.5572 | -0.00059982
219 |  | 41.4753 | 42.0148 | 4187 | 0.00024194 | 6.0528 | 6.0531 | -2.4792 | 4133.2407 | 9215.572 | -0.00059981
220 |  | 41.4753 | 42.0142 | 4187 | 0.00024194 | 6.0531 | 6.0533 | -2.4792 | 4133.2997 | 9257.5862 | -0.0005998
221 |  | 41.4753 | 42.0136 | 4187 | 0.00024193 | 6.0533 | 6.0536 | -2.4792 | 4133.3587 | 9299.5998 | -0.00059979
222 |  | 41.4753 | 42.013 | 4187 | 0.00024193 | 6.0536 | 6.0538 | -2.4792 | 4133.4177 | 9341.6128 | -0.00059978
223 |  | 41.4753 | 42.0124 | 4187 | 0.00024193 | 6.0538 | 6.054 | -2.4792 | 4133.4768 | 9383.6251 | -0.00059978
224 |  | 41.4753 | 42.0118 | 4187 | 0.00024192 | 6.054 | 6.0543 | -2.4792 | 4133.5358 | 9425.6369 | -0.00059977
225 |  | 41.4753 | 42.0112 | 4187 | 0.00024192 | 6.0543 | 6.0545 | -2.4792 | 4133.5948 | 9467.6481 | -0.00059976
226 |  | 41.4753 | 42.0106 | 4187 | 0.00024192 | 6.0545 | 6.0548 | -2.4792 | 4133.6538 | 9509.6587 | -0.00059975
227 |  | 41.4753 | 42.01 | 4187 | 0.00024191 | 6.0548 | 6.055 | -2.4792 | 4133.7128 | 9551.6687 | -0.00059974
228 |  | 41.4753 | 42.0094 | 4187 | 0.00024191 | 6.055 | 6.0552 | -2.4792 | 4133.7718 | 9593.6781 | -0.00059973
229 |  | 41.4753 | 42.0088 | 4187 | 0.00024191 | 6.0552 | 6.0555 | -2.4792 | 4133.8308 | 9635.6869 | -0.00059973
230 |  | 41.4753 | 42.0082 | 4187 | 0.0002419 | 6.0555 | 6.0557 | -2.4792 | 4133.8898 | 9677.6951 | -0.00059972
231 |  | 41.4753 | 42.0076 | 4187 | 0.0002419 | 6.0557 | 6.056 | -2.4792 | 4133.9489 | 9719.7027 | -0.00059971
232 |  | 41.4753 | 42.007 | 4187 | 0.0002419 | 6.056 | 6.0562 | -2.4792 | 4134.0079 | 9761.7097 | -0.0005997
233 |  | 41.4753 | 42.0064 | 4187 | 0.00024189 | 6.0562 | 6.0565 | -2.4792 | 4134.0669 | 9803.7161 | -0.00059969
234 |  | 41.4753 | 42.0058 | 4187 | 0.00024189 | 6.0565 | 6.0567 | -2.4792 | 4134.1259 | 9845.7219 | -0.00059968
235 |  | 41.4753 | 42.0052 | 4187 | 0.00024189 | 6.0567 | 6.0569 | -2.4792 | 4134.1849 | 9887.727 | -0.00059967
236 |  | 41.4753 | 42.0046 | 4187 | 0.00024188 | 6.0569 | 6.0572 | -2.4792 | 4134.244 | 9929.7316 | -0.00059967

## Fus355
|  |  | buis | verlies W/M | L /°C/sec
diam | wandikte |  | inhoud l/m |  | W/M
355 | 48 | 3.1416 | 52.6853 | 42.9796 | 4187
[8 empty] | J/sec/mtr | aantal mtr. | verlies
|  | buis | verlies W/M | L /°C/sec | verlies temp | begintemp | eindtemp | verlies | bij 1°C | totaal J/sec
|  | inhoud L |  | W/M | °C per M | °C | °C | per m°C | daling | aantal mtr
1 | 355 | 52.6853 | 42.9796 | 4187 | 0.00019484 | 6 | 6.0002 | -2.5282 | 5132.5082 | 42.9796 | -0.00049259
2 |  | 52.6853 | 42.9791 | 4187 | 0.00019483 | 6.0002 | 6.0004 | -2.5282 | 5132.5671 | 85.9588 | -0.00049258
3 |  | 52.6853 | 42.9786 | 4187 | 0.00019483 | 6.0004 | 6.0006 | -2.5282 | 5132.6259 | 128.9374 | -0.00049258
4 |  | 52.6853 | 42.9782 | 4187 | 0.00019483 | 6.0006 | 6.0008 | -2.5282 | 5132.6847 | 171.9156 | -0.00049257
5 |  | 52.6853 | 42.9777 | 4187 | 0.00019483 | 6.0008 | 6.001 | -2.5282 | 5132.7435 | 214.8932 | -0.00049257
6 |  | 52.6853 | 42.9772 | 4187 | 0.00019483 | 6.001 | 6.0012 | -2.5282 | 5132.8024 | 257.8704 | -0.00049256
7 |  | 52.6853 | 42.9767 | 4187 | 0.00019482 | 6.0012 | 6.0014 | -2.5282 | 5132.8612 | 300.8471 | -0.00049255
8 |  | 52.6853 | 42.9762 | 4187 | 0.00019482 | 6.0014 | 6.0016 | -2.5282 | 5132.92 | 343.8233 | -0.00049255
9 |  | 52.6853 | 42.9757 | 4187 | 0.00019482 | 6.0016 | 6.0018 | -2.5282 | 5132.9789 | 386.799 | -0.00049254
10 |  | 52.6853 | 42.9752 | 4187 | 0.00019482 | 6.0018 | 6.0019 | -2.5282 | 5133.0377 | 429.7742 | -0.00049254
11 |  | 52.6853 | 42.9747 | 4187 | 0.00019481 | 6.0019 | 6.0021 | -2.5282 | 5133.0965 | 472.7489 | -0.00049253
12 |  | 52.6853 | 42.9742 | 4187 | 0.00019481 | 6.0021 | 6.0023 | -2.5282 | 5133.1553 | 515.7231 | -0.00049253
13 |  | 52.6853 | 42.9737 | 4187 | 0.00019481 | 6.0023 | 6.0025 | -2.5282 | 5133.2142 | 558.6968 | -0.00049252
14 |  | 52.6853 | 42.9732 | 4187 | 0.00019481 | 6.0025 | 6.0027 | -2.5282 | 5133.273 | 601.6701 | -0.00049251
15 |  | 52.6853 | 42.9727 | 4187 | 0.00019481 | 6.0027 | 6.0029 | -2.5282 | 5133.3318 | 644.6428 | -0.00049251
16 |  | 52.6853 | 42.9722 | 4187 | 0.0001948 | 6.0029 | 6.0031 | -2.5282 | 5133.3907 | 687.615 | -0.0004925
17 |  | 52.6853 | 42.9718 | 4187 | 0.0001948 | 6.0031 | 6.0033 | -2.5282 | 5133.4495 | 730.5868 | -0.0004925
18 |  | 52.6853 | 42.9713 | 4187 | 0.0001948 | 6.0033 | 6.0035 | -2.5282 | 5133.5083 | 773.5581 | -0.00049249
19 |  | 52.6853 | 42.9708 | 4187 | 0.0001948 | 6.0035 | 6.0037 | -2.5282 | 5133.5672 | 816.5288 | -0.00049249
20 |  | 52.6853 | 42.9703 | 4187 | 0.00019479 | 6.0037 | 6.0039 | -2.5282 | 5133.626 | 859.4991 | -0.00049248
21 |  | 52.6853 | 42.9698 | 4187 | 0.00019479 | 6.0039 | 6.0041 | -2.5282 | 5133.6849 | 902.4689 | -0.00049248
22 |  | 52.6853 | 42.9693 | 4187 | 0.00019479 | 6.0041 | 6.0043 | -2.5282 | 5133.7437 | 945.4382 | -0.00049247
23 |  | 52.6853 | 42.9688 | 4187 | 0.00019479 | 6.0043 | 6.0045 | -2.5282 | 5133.8025 | 988.407 | -0.00049246
24 |  | 52.6853 | 42.9683 | 4187 | 0.00019479 | 6.0045 | 6.0047 | -2.5282 | 5133.8614 | 1031.3753 | -0.00049246
25 |  | 52.6853 | 42.9678 | 4187 | 0.00019478 | 6.0047 | 6.0049 | -2.5282 | 5133.9202 | 1074.3431 | -0.00049245
26 |  | 52.6853 | 42.9673 | 4187 | 0.00019478 | 6.0049 | 6.0051 | -2.5282 | 5133.9791 | 1117.3104 | -0.00049245
27 |  | 52.6853 | 42.9668 | 4187 | 0.00019478 | 6.0051 | 6.0053 | -2.5282 | 5134.0379 | 1160.2772 | -0.00049244
28 |  | 52.6853 | 42.9663 | 4187 | 0.00019478 | 6.0053 | 6.0055 | -2.5282 | 5134.0967 | 1203.2436 | -0.00049244
29 |  | 52.6853 | 42.9658 | 4187 | 0.00019477 | 6.0055 | 6.0056 | -2.5282 | 5134.1556 | 1246.2094 | -0.00049243
30 |  | 52.6853 | 42.9654 | 4187 | 0.00019477 | 6.0056 | 6.0058 | -2.5282 | 5134.2144 | 1289.1748 | -0.00049242
31 |  | 52.6853 | 42.9649 | 4187 | 0.00019477 | 6.0058 | 6.006 | -2.5282 | 5134.2733 | 1332.1396 | -0.00049242
32 |  | 52.6853 | 42.9644 | 4187 | 0.00019477 | 6.006 | 6.0062 | -2.5282 | 5134.3321 | 1375.104 | -0.00049241
33 |  | 52.6853 | 42.9639 | 4187 | 0.00019477 | 6.0062 | 6.0064 | -2.5282 | 5134.391 | 1418.0679 | -0.00049241
34 |  | 52.6853 | 42.9634 | 4187 | 0.00019476 | 6.0064 | 6.0066 | -2.5282 | 5134.4498 | 1461.0313 | -0.0004924
35 |  | 52.6853 | 42.9629 | 4187 | 0.00019476 | 6.0066 | 6.0068 | -2.5282 | 5134.5086 | 1503.9941 | -0.0004924
36 |  | 52.6853 | 42.9624 | 4187 | 0.00019476 | 6.0068 | 6.007 | -2.5282 | 5134.5675 | 1546.9565 | -0.00049239
37 |  | 52.6853 | 42.9619 | 4187 | 0.00019476 | 6.007 | 6.0072 | -2.5282 | 5134.6263 | 1589.9184 | -0.00049239
38 |  | 52.6853 | 42.9614 | 4187 | 0.00019475 | 6.0072 | 6.0074 | -2.5282 | 5134.6852 | 1632.8799 | -0.00049238
39 |  | 52.6853 | 42.9609 | 4187 | 0.00019475 | 6.0074 | 6.0076 | -2.5282 | 5134.744 | 1675.8408 | -0.00049237
40 |  | 52.6853 | 42.9604 | 4187 | 0.00019475 | 6.0076 | 6.0078 | -2.5282 | 5134.8029 | 1718.8012 | -0.00049237
41 |  | 52.6853 | 42.9599 | 4187 | 0.00019475 | 6.0078 | 6.008 | -2.5282 | 5134.8617 | 1761.7611 | -0.00049236
42 |  | 52.6853 | 42.9594 | 4187 | 0.00019474 | 6.008 | 6.0082 | -2.5282 | 5134.9206 | 1804.7206 | -0.00049236
43 |  | 52.6853 | 42.959 | 4187 | 0.00019474 | 6.0082 | 6.0084 | -2.5282 | 5134.9794 | 1847.6795 | -0.00049235
44 |  | 52.6853 | 42.9585 | 4187 | 0.00019474 | 6.0084 | 6.0086 | -2.5282 | 5135.0383 | 1890.638 | -0.00049235
45 |  | 52.6853 | 42.958 | 4187 | 0.00019474 | 6.0086 | 6.0088 | -2.5282 | 5135.0971 | 1933.596 | -0.00049234
46 |  | 52.6853 | 42.9575 | 4187 | 0.00019474 | 6.0088 | 6.009 | -2.5282 | 5135.156 | 1976.5534 | -0.00049233
47 |  | 52.6853 | 42.957 | 4187 | 0.00019473 | 6.009 | 6.0092 | -2.5282 | 5135.2149 | 2019.5104 | -0.00049233
48 |  | 52.6853 | 42.9565 | 4187 | 0.00019473 | 6.0092 | 6.0093 | -2.5282 | 5135.2737 | 2062.4669 | -0.00049232
49 |  | 52.6853 | 42.956 | 4187 | 0.00019473 | 6.0093 | 6.0095 | -2.5282 | 5135.3326 | 2105.4229 | -0.00049232
50 |  | 52.6853 | 42.9555 | 4187 | 0.00019473 | 6.0095 | 6.0097 | -2.5282 | 5135.3914 | 2148.3784 | -0.00049231
51 |  | 52.6853 | 42.955 | 4187 | 0.00019472 | 6.0097 | 6.0099 | -2.5282 | 5135.4503 | 2191.3334 | -0.00049231
52 |  | 52.6853 | 42.9545 | 4187 | 0.00019472 | 6.0099 | 6.0101 | -2.5282 | 5135.5091 | 2234.2879 | -0.0004923
53 |  | 52.6853 | 42.954 | 4187 | 0.00019472 | 6.0101 | 6.0103 | -2.5282 | 5135.568 | 2277.242 | -0.00049229
54 |  | 52.6853 | 42.9535 | 4187 | 0.00019472 | 6.0103 | 6.0105 | -2.5282 | 5135.6269 | 2320.1955 | -0.00049229
55 |  | 52.6853 | 42.953 | 4187 | 0.00019472 | 6.0105 | 6.0107 | -2.5282 | 5135.6857 | 2363.1485 | -0.00049228
56 |  | 52.6853 | 42.9526 | 4187 | 0.00019471 | 6.0107 | 6.0109 | -2.5282 | 5135.7446 | 2406.1011 | -0.00049228
57 |  | 52.6853 | 42.9521 | 4187 | 0.00019471 | 6.0109 | 6.0111 | -2.5282 | 5135.8034 | 2449.0531 | -0.00049227
58 |  | 52.6853 | 42.9516 | 4187 | 0.00019471 | 6.0111 | 6.0113 | -2.5282 | 5135.8623 | 2492.0047 | -0.00049227
59 |  | 52.6853 | 42.9511 | 4187 | 0.00019471 | 6.0113 | 6.0115 | -2.5282 | 5135.9212 | 2534.9558 | -0.00049226
60 |  | 52.6853 | 42.9506 | 4187 | 0.0001947 | 6.0115 | 6.0117 | -2.5282 | 5135.98 | 2577.9064 | -0.00049226
61 |  | 52.6853 | 42.9501 | 4187 | 0.0001947 | 6.0117 | 6.0119 | -2.5282 | 5136.0389 | 2620.8565 | -0.00049225
62 |  | 52.6853 | 42.9496 | 4187 | 0.0001947 | 6.0119 | 6.0121 | -2.5282 | 5136.0978 | 2663.806 | -0.00049224
63 |  | 52.6853 | 42.9491 | 4187 | 0.0001947 | 6.0121 | 6.0123 | -2.5282 | 5136.1566 | 2706.7552 | -0.00049224
64 |  | 52.6853 | 42.9486 | 4187 | 0.0001947 | 6.0123 | 6.0125 | -2.5282 | 5136.2155 | 2749.7038 | -0.00049223
65 |  | 52.6853 | 42.9481 | 4187 | 0.00019469 | 6.0125 | 6.0127 | -2.5282 | 5136.2744 | 2792.6519 | -0.00049223
66 |  | 52.6853 | 42.9476 | 4187 | 0.00019469 | 6.0127 | 6.0129 | -2.5282 | 5136.3332 | 2835.5995 | -0.00049222
67 |  | 52.6853 | 42.9471 | 4187 | 0.00019469 | 6.0129 | 6.013 | -2.5282 | 5136.3921 | 2878.5466 | -0.00049222
68 |  | 52.6853 | 42.9466 | 4187 | 0.00019469 | 6.013 | 6.0132 | -2.5282 | 5136.451 | 2921.4933 | -0.00049221
69 |  | 52.6853 | 42.9462 | 4187 | 0.00019468 | 6.0132 | 6.0134 | -2.5282 | 5136.5098 | 2964.4394 | -0.0004922
70 |  | 52.6853 | 42.9457 | 4187 | 0.00019468 | 6.0134 | 6.0136 | -2.5282 | 5136.5687 | 3007.3851 | -0.0004922
71 |  | 52.6853 | 42.9452 | 4187 | 0.00019468 | 6.0136 | 6.0138 | -2.5282 | 5136.6276 | 3050.3303 | -0.00049219
72 |  | 52.6853 | 42.9447 | 4187 | 0.00019468 | 6.0138 | 6.014 | -2.5282 | 5136.6864 | 3093.2749 | -0.00049219
73 |  | 52.6853 | 42.9442 | 4187 | 0.00019468 | 6.014 | 6.0142 | -2.5282 | 5136.7453 | 3136.2191 | -0.00049218
74 |  | 52.6853 | 42.9437 | 4187 | 0.00019467 | 6.0142 | 6.0144 | -2.5282 | 5136.8042 | 3179.1628 | -0.00049218
75 |  | 52.6853 | 42.9432 | 4187 | 0.00019467 | 6.0144 | 6.0146 | -2.5282 | 5136.8631 | 3222.106 | -0.00049217
76 |  | 52.6853 | 42.9427 | 4187 | 0.00019467 | 6.0146 | 6.0148 | -2.5282 | 5136.9219 | 3265.0487 | -0.00049217
77 |  | 52.6853 | 42.9422 | 4187 | 0.00019467 | 6.0148 | 6.015 | -2.5282 | 5136.9808 | 3307.9909 | -0.00049216
78 |  | 52.6853 | 42.9417 | 4187 | 0.00019466 | 6.015 | 6.0152 | -2.5282 | 5137.0397 | 3350.9327 | -0.00049215
79 |  | 52.6853 | 42.9412 | 4187 | 0.00019466 | 6.0152 | 6.0154 | -2.5282 | 5137.0986 | 3393.8739 | -0.00049215
80 |  | 52.6853 | 42.9407 | 4187 | 0.00019466 | 6.0154 | 6.0156 | -2.5282 | 5137.1574 | 3436.8146 | -0.00049214
81 |  | 52.6853 | 42.9402 | 4187 | 0.00019466 | 6.0156 | 6.0158 | -2.5282 | 5137.2163 | 3479.7549 | -0.00049214
82 |  | 52.6853 | 42.9398 | 4187 | 0.00019466 | 6.0158 | 6.016 | -2.5282 | 5137.2752 | 3522.6946 | -0.00049213
83 |  | 52.6853 | 42.9393 | 4187 | 0.00019465 | 6.016 | 6.0162 | -2.5282 | 5137.3341 | 3565.6339 | -0.00049213
84 |  | 52.6853 | 42.9388 | 4187 | 0.00019465 | 6.0162 | 6.0164 | -2.5282 | 5137.3929 | 3608.5726 | -0.00049212
85 |  | 52.6853 | 42.9383 | 4187 | 0.00019465 | 6.0164 | 6.0166 | -2.5282 | 5137.4518 | 3651.5109 | -0.00049211
86 |  | 52.6853 | 42.9378 | 4187 | 0.00019465 | 6.0166 | 6.0167 | -2.5282 | 5137.5107 | 3694.4487 | -0.00049211
87 |  | 52.6853 | 42.9373 | 4187 | 0.00019464 | 6.0167 | 6.0169 | -2.5282 | 5137.5696 | 3737.386 | -0.0004921
88 |  | 52.6853 | 42.9368 | 4187 | 0.00019464 | 6.0169 | 6.0171 | -2.5282 | 5137.6285 | 3780.3228 | -0.0004921
89 |  | 52.6853 | 42.9363 | 4187 | 0.00019464 | 6.0171 | 6.0173 | -2.5282 | 5137.6874 | 3823.2591 | -0.00049209
90 |  | 52.6853 | 42.9358 | 4187 | 0.00019464 | 6.0173 | 6.0175 | -2.5282 | 5137.7462 | 3866.1949 | -0.00049209
91 |  | 52.6853 | 42.9353 | 4187 | 0.00019464 | 6.0175 | 6.0177 | -2.5282 | 5137.8051 | 3909.1302 | -0.00049208
92 |  | 52.6853 | 42.9348 | 4187 | 0.00019463 | 6.0177 | 6.0179 | -2.5282 | 5137.864 | 3952.0651 | -0.00049207
93 |  | 52.6853 | 42.9343 | 4187 | 0.00019463 | 6.0179 | 6.0181 | -2.5282 | 5137.9229 | 3994.9994 | -0.00049207
94 |  | 52.6853 | 42.9338 | 4187 | 0.00019463 | 6.0181 | 6.0183 | -2.5282 | 5137.9818 | 4037.9333 | -0.00049206
95 |  | 52.6853 | 42.9334 | 4187 | 0.00019463 | 6.0183 | 6.0185 | -2.5282 | 5138.0407 | 4080.8666 | -0.00049206
96 |  | 52.6853 | 42.9329 | 4187 | 0.00019462 | 6.0185 | 6.0187 | -2.5282 | 5138.0996 | 4123.7995 | -0.00049205
97 |  | 52.6853 | 42.9324 | 4187 | 0.00019462 | 6.0187 | 6.0189 | -2.5282 | 5138.1584 | 4166.7319 | -0.00049205
98 |  | 52.6853 | 42.9319 | 4187 | 0.00019462 | 6.0189 | 6.0191 | -2.5282 | 5138.2173 | 4209.6637 | -0.00049204
99 |  | 52.6853 | 42.9314 | 4187 | 0.00019462 | 6.0191 | 6.0193 | -2.5282 | 5138.2762 | 4252.5951 | -0.00049204
100 |  | 52.6853 | 42.9309 | 4187 | 0.00019462 | 6.0193 | 6.0195 | -2.5282 | 5138.3351 | 4295.526 | -0.00049203
101 |  | 52.6853 | 42.9304 | 4187 | 0.00019461 | 6.0195 | 6.0197 | -2.5282 | 5138.394 | 4338.4564 | -0.00049202
102 |  | 52.6853 | 42.9299 | 4187 | 0.00019461 | 6.0197 | 6.0199 | -2.5282 | 5138.4529 | 4381.3863 | -0.00049202
103 |  | 52.6853 | 42.9294 | 4187 | 0.00019461 | 6.0199 | 6.0201 | -2.5282 | 5138.5118 | 4424.3158 | -0.00049201
104 |  | 52.6853 | 42.9289 | 4187 | 0.00019461 | 6.0201 | 6.0203 | -2.5282 | 5138.5707 | 4467.2447 | -0.00049201
105 |  | 52.6853 | 42.9284 | 4187 | 0.0001946 | 6.0203 | 6.0204 | -2.5282 | 5138.6296 | 4510.1731 | -0.000492
106 |  | 52.6853 | 42.9279 | 4187 | 0.0001946 | 6.0204 | 6.0206 | -2.5282 | 5138.6885 | 4553.1011 | -0.000492
107 |  | 52.6853 | 42.9275 | 4187 | 0.0001946 | 6.0206 | 6.0208 | -2.5282 | 5138.7474 | 4596.0285 | -0.00049199
108 |  | 52.6853 | 42.927 | 4187 | 0.0001946 | 6.0208 | 6.021 | -2.5282 | 5138.8063 | 4638.9555 | -0.00049198
109 |  | 52.6853 | 42.9265 | 4187 | 0.0001946 | 6.021 | 6.0212 | -2.5282 | 5138.8652 | 4681.8819 | -0.00049198
110 |  | 52.6853 | 42.926 | 4187 | 0.00019459 | 6.0212 | 6.0214 | -2.5282 | 5138.9241 | 4724.8079 | -0.00049197
111 |  | 52.6853 | 42.9255 | 4187 | 0.00019459 | 6.0214 | 6.0216 | -2.5282 | 5138.9829 | 4767.7334 | -0.00049197
112 |  | 52.6853 | 42.925 | 4187 | 0.00019459 | 6.0216 | 6.0218 | -2.5282 | 5139.0418 | 4810.6584 | -0.00049196
113 |  | 52.6853 | 42.9245 | 4187 | 0.00019459 | 6.0218 | 6.022 | -2.5282 | 5139.1007 | 4853.5829 | -0.00049196
114 |  | 52.6853 | 42.924 | 4187 | 0.00019458 | 6.022 | 6.0222 | -2.5282 | 5139.1596 | 4896.5069 | -0.00049195
115 |  | 52.6853 | 42.9235 | 4187 | 0.00019458 | 6.0222 | 6.0224 | -2.5282 | 5139.2185 | 4939.4304 | -0.00049195
116 |  | 52.6853 | 42.923 | 4187 | 0.00019458 | 6.0224 | 6.0226 | -2.5282 | 5139.2774 | 4982.3534 | -0.00049194
117 |  | 52.6853 | 42.9225 | 4187 | 0.00019458 | 6.0226 | 6.0228 | -2.5282 | 5139.3363 | 5025.276 | -0.00049193
118 |  | 52.6853 | 42.922 | 4187 | 0.00019458 | 6.0228 | 6.023 | -2.5282 | 5139.3953 | 5068.198 | -0.00049193
119 |  | 52.6853 | 42.9215 | 4187 | 0.00019457 | 6.023 | 6.0232 | -2.5282 | 5139.4542 | 5111.1196 | -0.00049192
120 |  | 52.6853 | 42.9211 | 4187 | 0.00019457 | 6.0232 | 6.0234 | -2.5282 | 5139.5131 | 5154.0406 | -0.00049192
121 |  | 52.6853 | 42.9206 | 4187 | 0.00019457 | 6.0234 | 6.0236 | -2.5282 | 5139.572 | 5196.9612 | -0.00049191
122 |  | 52.6853 | 42.9201 | 4187 | 0.00019457 | 6.0236 | 6.0238 | -2.5282 | 5139.6309 | 5239.8812 | -0.00049191
123 |  | 52.6853 | 42.9196 | 4187 | 0.00019456 | 6.0238 | 6.0239 | -2.5282 | 5139.6898 | 5282.8008 | -0.0004919
124 |  | 52.6853 | 42.9191 | 4187 | 0.00019456 | 6.0239 | 6.0241 | -2.5282 | 5139.7487 | 5325.7199 | -0.00049189
125 |  | 52.6853 | 42.9186 | 4187 | 0.00019456 | 6.0241 | 6.0243 | -2.5282 | 5139.8076 | 5368.6385 | -0.00049189
126 |  | 52.6853 | 42.9181 | 4187 | 0.00019456 | 6.0243 | 6.0245 | -2.5282 | 5139.8665 | 5411.5566 | -0.00049188
127 |  | 52.6853 | 42.9176 | 4187 | 0.00019456 | 6.0245 | 6.0247 | -2.5282 | 5139.9254 | 5454.4742 | -0.00049188
128 |  | 52.6853 | 42.9171 | 4187 | 0.00019455 | 6.0247 | 6.0249 | -2.5282 | 5139.9843 | 5497.3913 | -0.00049187
129 |  | 52.6853 | 42.9166 | 4187 | 0.00019455 | 6.0249 | 6.0251 | -2.5282 | 5140.0432 | 5540.308 | -0.00049187
130 |  | 52.6853 | 42.9161 | 4187 | 0.00019455 | 6.0251 | 6.0253 | -2.5282 | 5140.1021 | 5583.2241 | -0.00049186
131 |  | 52.6853 | 42.9156 | 4187 | 0.00019455 | 6.0253 | 6.0255 | -2.5282 | 5140.161 | 5626.1398 | -0.00049185
132 |  | 52.6853 | 42.9152 | 4187 | 0.00019454 | 6.0255 | 6.0257 | -2.5282 | 5140.22 | 5669.0549 | -0.00049185
133 |  | 52.6853 | 42.9147 | 4187 | 0.00019454 | 6.0257 | 6.0259 | -2.5282 | 5140.2789 | 5711.9696 | -0.00049184
134 |  | 52.6853 | 42.9142 | 4187 | 0.00019454 | 6.0259 | 6.0261 | -2.5282 | 5140.3378 | 5754.8837 | -0.00049184
135 |  | 52.6853 | 42.9137 | 4187 | 0.00019454 | 6.0261 | 6.0263 | -2.5282 | 5140.3967 | 5797.7974 | -0.00049183
136 |  | 52.6853 | 42.9132 | 4187 | 0.00019454 | 6.0263 | 6.0265 | -2.5282 | 5140.4556 | 5840.7106 | -0.00049183
137 |  | 52.6853 | 42.9127 | 4187 | 0.00019453 | 6.0265 | 6.0267 | -2.5282 | 5140.5145 | 5883.6233 | -0.00049182
138 |  | 52.6853 | 42.9122 | 4187 | 0.00019453 | 6.0267 | 6.0269 | -2.5282 | 5140.5734 | 5926.5355 | -0.00049182
139 |  | 52.6853 | 42.9117 | 4187 | 0.00019453 | 6.0269 | 6.0271 | -2.5282 | 5140.6324 | 5969.4472 | -0.00049181
140 |  | 52.6853 | 42.9112 | 4187 | 0.00019453 | 6.0271 | 6.0273 | -2.5282 | 5140.6913 | 6012.3584 | -0.0004918
141 |  | 52.6853 | 42.9107 | 4187 | 0.00019452 | 6.0273 | 6.0274 | -2.5282 | 5140.7502 | 6055.2692 | -0.0004918
142 |  | 52.6853 | 42.9102 | 4187 | 0.00019452 | 6.0274 | 6.0276 | -2.5282 | 5140.8091 | 6098.1794 | -0.00049179
143 |  | 52.6853 | 42.9097 | 4187 | 0.00019452 | 6.0276 | 6.0278 | -2.5282 | 5140.868 | 6141.0891 | -0.00049179
144 |  | 52.6853 | 42.9093 | 4187 | 0.00019452 | 6.0278 | 6.028 | -2.5282 | 5140.927 | 6183.9984 | -0.00049178
145 |  | 52.6853 | 42.9088 | 4187 | 0.00019452 | 6.028 | 6.0282 | -2.5282 | 5140.9859 | 6226.9071 | -0.00049178
146 |  | 52.6853 | 42.9083 | 4187 | 0.00019451 | 6.0282 | 6.0284 | -2.5282 | 5141.0448 | 6269.8154 | -0.00049177
147 |  | 52.6853 | 42.9078 | 4187 | 0.00019451 | 6.0284 | 6.0286 | -2.5282 | 5141.1037 | 6312.7232 | -0.00049176
148 |  | 52.6853 | 42.9073 | 4187 | 0.00019451 | 6.0286 | 6.0288 | -2.5282 | 5141.1626 | 6355.6305 | -0.00049176
149 |  | 52.6853 | 42.9068 | 4187 | 0.00019451 | 6.0288 | 6.029 | -2.5282 | 5141.2216 | 6398.5373 | -0.00049175
150 |  | 52.6853 | 42.9063 | 4187 | 0.0001945 | 6.029 | 6.0292 | -2.5282 | 5141.2805 | 6441.4436 | -0.00049175
151 |  | 52.6853 | 42.9058 | 4187 | 0.0001945 | 6.0292 | 6.0294 | -2.5282 | 5141.3394 | 6484.3494 | -0.00049174
152 |  | 52.6853 | 42.9053 | 4187 | 0.0001945 | 6.0294 | 6.0296 | -2.5282 | 5141.3983 | 6527.2547 | -0.00049174
153 |  | 52.6853 | 42.9048 | 4187 | 0.0001945 | 6.0296 | 6.0298 | -2.5282 | 5141.4573 | 6570.1595 | -0.00049173
154 |  | 52.6853 | 42.9043 | 4187 | 0.0001945 | 6.0298 | 6.03 | -2.5282 | 5141.5162 | 6613.0639 | -0.00049173
155 |  | 52.6853 | 42.9038 | 4187 | 0.00019449 | 6.03 | 6.0302 | -2.5282 | 5141.5751 | 6655.9677 | -0.00049172
156 |  | 52.6853 | 42.9034 | 4187 | 0.00019449 | 6.0302 | 6.0304 | -2.5282 | 5141.634 | 6698.871 | -0.00049171
157 |  | 52.6853 | 42.9029 | 4187 | 0.00019449 | 6.0304 | 6.0306 | -2.5282 | 5141.693 | 6741.7739 | -0.00049171
158 |  | 52.6853 | 42.9024 | 4187 | 0.00019449 | 6.0306 | 6.0308 | -2.5282 | 5141.7519 | 6784.6763 | -0.0004917
159 |  | 52.6853 | 42.9019 | 4187 | 0.00019448 | 6.0308 | 6.031 | -2.5282 | 5141.8108 | 6827.5781 | -0.0004917
160 |  | 52.6853 | 42.9014 | 4187 | 0.00019448 | 6.031 | 6.0311 | -2.5282 | 5141.8698 | 6870.4795 | -0.00049169
161 |  | 52.6853 | 42.9009 | 4187 | 0.00019448 | 6.0311 | 6.0313 | -2.5282 | 5141.9287 | 6913.3804 | -0.00049169
162 |  | 52.6853 | 42.9004 | 4187 | 0.00019448 | 6.0313 | 6.0315 | -2.5282 | 5141.9876 | 6956.2808 | -0.00049168
163 |  | 52.6853 | 42.8999 | 4187 | 0.00019448 | 6.0315 | 6.0317 | -2.5282 | 5142.0466 | 6999.1807 | -0.00049167
164 |  | 52.6853 | 42.8994 | 4187 | 0.00019447 | 6.0317 | 6.0319 | -2.5282 | 5142.1055 | 7042.0801 | -0.00049167
165 |  | 52.6853 | 42.8989 | 4187 | 0.00019447 | 6.0319 | 6.0321 | -2.5282 | 5142.1644 | 7084.9791 | -0.00049166
166 |  | 52.6853 | 42.8984 | 4187 | 0.00019447 | 6.0321 | 6.0323 | -2.5282 | 5142.2234 | 7127.8775 | -0.00049166
167 |  | 52.6853 | 42.8979 | 4187 | 0.00019447 | 6.0323 | 6.0325 | -2.5282 | 5142.2823 | 7170.7754 | -0.00049165
168 |  | 52.6853 | 42.8975 | 4187 | 0.00019446 | 6.0325 | 6.0327 | -2.5282 | 5142.3412 | 7213.6729 | -0.00049165
169 |  | 52.6853 | 42.897 | 4187 | 0.00019446 | 6.0327 | 6.0329 | -2.5282 | 5142.4002 | 7256.5699 | -0.00049164
170 |  | 52.6853 | 42.8965 | 4187 | 0.00019446 | 6.0329 | 6.0331 | -2.5282 | 5142.4591 | 7299.4663 | -0.00049164
171 |  | 52.6853 | 42.896 | 4187 | 0.00019446 | 6.0331 | 6.0333 | -2.5282 | 5142.518 | 7342.3623 | -0.00049163
172 |  | 52.6853 | 42.8955 | 4187 | 0.00019446 | 6.0333 | 6.0335 | -2.5282 | 5142.577 | 7385.2578 | -0.00049162
173 |  | 52.6853 | 42.895 | 4187 | 0.00019445 | 6.0335 | 6.0337 | -2.5282 | 5142.6359 | 7428.1528 | -0.00049162
174 |  | 52.6853 | 42.8945 | 4187 | 0.00019445 | 6.0337 | 6.0339 | -2.5282 | 5142.6949 | 7471.0473 | -0.00049161
175 |  | 52.6853 | 42.894 | 4187 | 0.00019445 | 6.0339 | 6.0341 | -2.5282 | 5142.7538 | 7513.9413 | -0.00049161
176 |  | 52.6853 | 42.8935 | 4187 | 0.00019445 | 6.0341 | 6.0343 | -2.5282 | 5142.8128 | 7556.8348 | -0.0004916
177 |  | 52.6853 | 42.893 | 4187 | 0.00019444 | 6.0343 | 6.0345 | -2.5282 | 5142.8717 | 7599.7278 | -0.0004916
178 |  | 52.6853 | 42.8925 | 4187 | 0.00019444 | 6.0345 | 6.0346 | -2.5282 | 5142.9306 | 7642.6204 | -0.00049159
179 |  | 52.6853 | 42.892 | 4187 | 0.00019444 | 6.0346 | 6.0348 | -2.5282 | 5142.9896 | 7685.5124 | -0.00049158
180 |  | 52.6853 | 42.8916 | 4187 | 0.00019444 | 6.0348 | 6.035 | -2.5282 | 5143.0485 | 7728.404 | -0.00049158
181 |  | 52.6853 | 42.8911 | 4187 | 0.00019443 | 6.035 | 6.0352 | -2.5282 | 5143.1075 | 7771.295 | -0.00049157
182 |  | 52.6853 | 42.8906 | 4187 | 0.00019443 | 6.0352 | 6.0354 | -2.5282 | 5143.1664 | 7814.1856 | -0.00049157
183 |  | 52.6853 | 42.8901 | 4187 | 0.00019443 | 6.0354 | 6.0356 | -2.5282 | 5143.2254 | 7857.0757 | -0.00049156
184 |  | 52.6853 | 42.8896 | 4187 | 0.00019443 | 6.0356 | 6.0358 | -2.5282 | 5143.2843 | 7899.9652 | -0.00049156
185 |  | 52.6853 | 42.8891 | 4187 | 0.00019443 | 6.0358 | 6.036 | -2.5282 | 5143.3433 | 7942.8543 | -0.00049155
186 |  | 52.6853 | 42.8886 | 4187 | 0.00019442 | 6.036 | 6.0362 | -2.5282 | 5143.4022 | 7985.7429 | -0.00049155
187 |  | 52.6853 | 42.8881 | 4187 | 0.00019442 | 6.0362 | 6.0364 | -2.5282 | 5143.4612 | 8028.631 | -0.00049154
188 |  | 52.6853 | 42.8876 | 4187 | 0.00019442 | 6.0364 | 6.0366 | -2.5282 | 5143.5201 | 8071.5187 | -0.00049153
189 |  | 52.6853 | 42.8871 | 4187 | 0.00019442 | 6.0366 | 6.0368 | -2.5282 | 5143.5791 | 8114.4058 | -0.00049153
190 |  | 52.6853 | 42.8866 | 4187 | 0.00019441 | 6.0368 | 6.037 | -2.5282 | 5143.638 | 8157.2924 | -0.00049152
191 |  | 52.6853 | 42.8861 | 4187 | 0.00019441 | 6.037 | 6.0372 | -2.5282 | 5143.697 | 8200.1786 | -0.00049152
192 |  | 52.6853 | 42.8857 | 4187 | 0.00019441 | 6.0372 | 6.0374 | -2.5282 | 5143.7559 | 8243.0642 | -0.00049151
193 |  | 52.6853 | 42.8852 | 4187 | 0.00019441 | 6.0374 | 6.0376 | -2.5282 | 5143.8149 | 8285.9494 | -0.00049151
194 |  | 52.6853 | 42.8847 | 4187 | 0.00019441 | 6.0376 | 6.0378 | -2.5282 | 5143.8738 | 8328.834 | -0.0004915
195 |  | 52.6853 | 42.8842 | 4187 | 0.0001944 | 6.0378 | 6.038 | -2.5282 | 5143.9328 | 8371.7182 | -0.00049149
196 |  | 52.6853 | 42.8837 | 4187 | 0.0001944 | 6.038 | 6.0381 | -2.5282 | 5143.9917 | 8414.6019 | -0.00049149
197 |  | 52.6853 | 42.8832 | 4187 | 0.0001944 | 6.0381 | 6.0383 | -2.5282 | 5144.0507 | 8457.4851 | -0.00049148
198 |  | 52.6853 | 42.8827 | 4187 | 0.0001944 | 6.0383 | 6.0385 | -2.5282 | 5144.1096 | 8500.3678 | -0.00049148
199 |  | 52.6853 | 42.8822 | 4187 | 0.00019439 | 6.0385 | 6.0387 | -2.5282 | 5144.1686 | 8543.25 | -0.00049147
200 |  | 52.6853 | 42.8817 | 4187 | 0.00019439 | 6.0387 | 6.0389 | -2.5282 | 5144.2276 | 8586.1317 | -0.00049147
201 |  | 52.6853 | 42.8812 | 4187 | 0.00019439 | 6.0389 | 6.0391 | -2.5282 | 5144.2865 | 8629.013 | -0.00049146
202 |  | 52.6853 | 42.8807 | 4187 | 0.00019439 | 6.0391 | 6.0393 | -2.5282 | 5144.3455 | 8671.8937 | -0.00049145
203 |  | 52.6853 | 42.8802 | 4187 | 0.00019439 | 6.0393 | 6.0395 | -2.5282 | 5144.4044 | 8714.774 | -0.00049145
204 |  | 52.6853 | 42.8798 | 4187 | 0.00019438 | 6.0395 | 6.0397 | -2.5282 | 5144.4634 | 8757.6537 | -0.00049144
205 |  | 52.6853 | 42.8793 | 4187 | 0.00019438 | 6.0397 | 6.0399 | -2.5282 | 5144.5224 | 8800.533 | -0.00049144
206 |  | 52.6853 | 42.8788 | 4187 | 0.00019438 | 6.0399 | 6.0401 | -2.5282 | 5144.5813 | 8843.4117 | -0.00049143
207 |  | 52.6853 | 42.8783 | 4187 | 0.00019438 | 6.0401 | 6.0403 | -2.5282 | 5144.6403 | 8886.29 | -0.00049143
208 |  | 52.6853 | 42.8778 | 4187 | 0.00019437 | 6.0403 | 6.0405 | -2.5282 | 5144.6992 | 8929.1678 | -0.00049142
209 |  | 52.6853 | 42.8773 | 4187 | 0.00019437 | 6.0405 | 6.0407 | -2.5282 | 5144.7582 | 8972.0451 | -0.00049142
210 |  | 52.6853 | 42.8768 | 4187 | 0.00019437 | 6.0407 | 6.0409 | -2.5282 | 5144.8172 | 9014.9219 | -0.00049141
211 |  | 52.6853 | 42.8763 | 4187 | 0.00019437 | 6.0409 | 6.0411 | -2.5282 | 5144.8761 | 9057.7982 | -0.0004914
212 |  | 52.6853 | 42.8758 | 4187 | 0.00019437 | 6.0411 | 6.0413 | -2.5282 | 5144.9351 | 9100.6741 | -0.0004914
213 |  | 52.6853 | 42.8753 | 4187 | 0.00019436 | 6.0413 | 6.0414 | -2.5282 | 5144.9941 | 9143.5494 | -0.00049139
214 |  | 52.6853 | 42.8748 | 4187 | 0.00019436 | 6.0414 | 6.0416 | -2.5282 | 5145.053 | 9186.4242 | -0.00049139
215 |  | 52.6853 | 42.8743 | 4187 | 0.00019436 | 6.0416 | 6.0418 | -2.5282 | 5145.112 | 9229.2986 | -0.00049138
216 |  | 52.6853 | 42.8739 | 4187 | 0.00019436 | 6.0418 | 6.042 | -2.5282 | 5145.171 | 9272.1724 | -0.00049138
217 |  | 52.6853 | 42.8734 | 4187 | 0.00019435 | 6.042 | 6.0422 | -2.5282 | 5145.2299 | 9315.0458 | -0.00049137
218 |  | 52.6853 | 42.8729 | 4187 | 0.00019435 | 6.0422 | 6.0424 | -2.5282 | 5145.2889 | 9357.9187 | -0.00049136
219 |  | 52.6853 | 42.8724 | 4187 | 0.00019435 | 6.0424 | 6.0426 | -2.5282 | 5145.3479 | 9400.7911 | -0.00049136
220 |  | 52.6853 | 42.8719 | 4187 | 0.00019435 | 6.0426 | 6.0428 | -2.5282 | 5145.4069 | 9443.6629 | -0.00049135
221 |  | 52.6853 | 42.8714 | 4187 | 0.00019435 | 6.0428 | 6.043 | -2.5282 | 5145.4658 | 9486.5343 | -0.00049135
222 |  | 52.6853 | 42.8709 | 4187 | 0.00019434 | 6.043 | 6.0432 | -2.5282 | 5145.5248 | 9529.4053 | -0.00049134
223 |  | 52.6853 | 42.8704 | 4187 | 0.00019434 | 6.0432 | 6.0434 | -2.5282 | 5145.5838 | 9572.2757 | -0.00049134
224 |  | 52.6853 | 42.8699 | 4187 | 0.00019434 | 6.0434 | 6.0436 | -2.5282 | 5145.6427 | 9615.1456 | -0.00049133
225 |  | 52.6853 | 42.8694 | 4187 | 0.00019434 | 6.0436 | 6.0438 | -2.5282 | 5145.7017 | 9658.015 | -0.00049133
226 |  | 52.6853 | 42.8689 | 4187 | 0.00019433 | 6.0438 | 6.044 | -2.5282 | 5145.7607 | 9700.884 | -0.00049132
227 |  | 52.6853 | 42.8685 | 4187 | 0.00019433 | 6.044 | 6.0442 | -2.5282 | 5145.8197 | 9743.7524 | -0.00049131
228 |  | 52.6853 | 42.868 | 4187 | 0.00019433 | 6.0442 | 6.0444 | -2.5282 | 5145.8786 | 9786.6204 | -0.00049131
229 |  | 52.6853 | 42.8675 | 4187 | 0.00019433 | 6.0444 | 6.0446 | -2.5282 | 5145.9376 | 9829.4879 | -0.0004913
230 |  | 52.6853 | 42.867 | 4187 | 0.00019433 | 6.0446 | 6.0448 | -2.5282 | 5145.9966 | 9872.3548 | -0.0004913
231 |  | 52.6853 | 42.8665 | 4187 | 0.00019432 | 6.0448 | 6.0449 | -2.5282 | 5146.0556 | 9915.2213 | -0.00049129
232 |  | 52.6853 | 42.866 | 4187 | 0.00019432 | 6.0449 | 6.0451 | -2.5282 | 5146.1146 | 9958.0873 | -0.00049129
233 |  | 52.6853 | 42.8655 | 4187 | 0.00019432 | 6.0451 | 6.0453 | -2.5282 | 5146.1735 | 10000.9528 | -0.00049128
234 |  | 52.6853 | 42.865 | 4187 | 0.00019432 | 6.0453 | 6.0455 | -2.5282 | 5146.2325 | 10043.8178 | -0.00049127
235 |  | 52.6853 | 42.8645 | 4187 | 0.00019431 | 6.0455 | 6.0457 | -2.5282 | 5146.2915 | 10086.6824 | -0.00049127
236 |  | 52.6853 | 42.864 | 4187 | 0.00019431 | 6.0457 | 6.0459 | -2.5282 | 5146.3505 | 10129.5464 | -0.00049126

## 20
|  |  | buis | verlies W/M | L /°C/sec
diam | wandikte |  | inhoud l/m |  | W/M
20 | 2.8 | 3.1416 | 0.16286 | 11.8741 | 4187
[8 empty] | J/sec/mtr | aantal mtr. | verlies
|  | buis | verlies W/M | L /°C/sec | verlies temp | begintemp | eindtemp | verlies | bij 1°C | totaal J/sec
|  | inhoud L |  | W/M | °C per M | °C | °C | per m°C | daling | aantal mtr
1 | 20 | 0.16286 | 11.8741 | 4187 | 0.017413 | 6 | 6.0174 | -0.69847 | 57.4273 | 11.8741 | -0.012163
2 |  | 0.16286 | 11.8619 | 4187 | 0.017395 | 6.0174 | 6.0348 | -0.69847 | 57.4862 | 23.736 | -0.01215
3 |  | 0.16286 | 11.8497 | 4187 | 0.017378 | 6.0348 | 6.0522 | -0.69847 | 57.5452 | 35.5857 | -0.012138
4 |  | 0.16286 | 11.8376 | 4187 | 0.01736 | 6.0522 | 6.0695 | -0.69847 | 57.6042 | 47.4233 | -0.012125
5 |  | 0.16286 | 11.8255 | 4187 | 0.017342 | 6.0695 | 6.0869 | -0.69847 | 57.6632 | 59.2488 | -0.012113
6 |  | 0.16286 | 11.8134 | 4187 | 0.017324 | 6.0869 | 6.1042 | -0.69847 | 57.7224 | 71.0621 | -0.012101
7 |  | 0.16286 | 11.8013 | 4187 | 0.017307 | 6.1042 | 6.1215 | -0.69847 | 57.7816 | 82.8634 | -0.012088
8 |  | 0.16286 | 11.7892 | 4187 | 0.017289 | 6.1215 | 6.1388 | -0.69847 | 57.8408 | 94.6526 | -0.012076
9 |  | 0.16286 | 11.7771 | 4187 | 0.017271 | 6.1388 | 6.1561 | -0.69847 | 57.9001 | 106.4297 | -0.012063
10 |  | 0.16286 | 11.765 | 4187 | 0.017253 | 6.1561 | 6.1733 | -0.69847 | 57.9595 | 118.1947 | -0.012051
11 |  | 0.16286 | 11.753 | 4187 | 0.017236 | 6.1733 | 6.1906 | -0.69847 | 58.0189 | 129.9477 | -0.012039
12 |  | 0.16286 | 11.7409 | 4187 | 0.017218 | 6.1906 | 6.2078 | -0.69847 | 58.0784 | 141.6887 | -0.012026
13 |  | 0.16286 | 11.7289 | 4187 | 0.0172 | 6.2078 | 6.225 | -0.69847 | 58.1379 | 153.4176 | -0.012014
14 |  | 0.16286 | 11.7169 | 4187 | 0.017183 | 6.225 | 6.2422 | -0.69847 | 58.1976 | 165.1345 | -0.012002
15 |  | 0.16286 | 11.7049 | 4187 | 0.017165 | 6.2422 | 6.2593 | -0.69847 | 58.2572 | 176.8394 | -0.011989
16 |  | 0.16286 | 11.6929 | 4187 | 0.017148 | 6.2593 | 6.2765 | -0.69847 | 58.317 | 188.5323 | -0.011977
17 |  | 0.16286 | 11.6809 | 4187 | 0.01713 | 6.2765 | 6.2936 | -0.69847 | 58.3768 | 200.2133 | -0.011965
18 |  | 0.16286 | 11.669 | 4187 | 0.017113 | 6.2936 | 6.3107 | -0.69847 | 58.4366 | 211.8823 | -0.011953
19 |  | 0.16286 | 11.657 | 4187 | 0.017095 | 6.3107 | 6.3278 | -0.69847 | 58.4965 | 223.5393 | -0.01194
20 |  | 0.16286 | 11.6451 | 4187 | 0.017078 | 6.3278 | 6.3449 | -0.69847 | 58.5565 | 235.1844 | -0.011928
21 |  | 0.16286 | 11.6332 | 4187 | 0.01706 | 6.3449 | 6.362 | -0.69847 | 58.6166 | 246.8175 | -0.011916
22 |  | 0.16286 | 11.6212 | 4187 | 0.017043 | 6.362 | 6.379 | -0.69847 | 58.6767 | 258.4388 | -0.011904
23 |  | 0.16286 | 11.6093 | 4187 | 0.017025 | 6.379 | 6.396 | -0.69847 | 58.7368 | 270.0481 | -0.011892
24 |  | 0.16286 | 11.5974 | 4187 | 0.017008 | 6.396 | 6.413 | -0.69847 | 58.7971 | 281.6455 | -0.011879
25 |  | 0.16286 | 11.5856 | 4187 | 0.01699 | 6.413 | 6.43 | -0.69847 | 58.8573 | 293.2311 | -0.011867
26 |  | 0.16286 | 11.5737 | 4187 | 0.016973 | 6.43 | 6.447 | -0.69847 | 58.9177 | 304.8048 | -0.011855
27 |  | 0.16286 | 11.5618 | 4187 | 0.016955 | 6.447 | 6.464 | -0.69847 | 58.9781 | 316.3666 | -0.011843
28 |  | 0.16286 | 11.55 | 4187 | 0.016938 | 6.464 | 6.4809 | -0.69847 | 59.0386 | 327.9166 | -0.011831
29 |  | 0.16286 | 11.5382 | 4187 | 0.016921 | 6.4809 | 6.4978 | -0.69847 | 59.0991 | 339.4548 | -0.011819
30 |  | 0.16286 | 11.5263 | 4187 | 0.016903 | 6.4978 | 6.5147 | -0.69847 | 59.1597 | 350.9811 | -0.011807
31 |  | 0.16286 | 11.5145 | 4187 | 0.016886 | 6.5147 | 6.5316 | -0.69847 | 59.2204 | 362.4957 | -0.011794
32 |  | 0.16286 | 11.5027 | 4187 | 0.016869 | 6.5316 | 6.5485 | -0.69847 | 59.2811 | 373.9984 | -0.011782
33 |  | 0.16286 | 11.491 | 4187 | 0.016852 | 6.5485 | 6.5653 | -0.69847 | 59.3419 | 385.4894 | -0.01177
34 |  | 0.16286 | 11.4792 | 4187 | 0.016834 | 6.5653 | 6.5822 | -0.69847 | 59.4027 | 396.9686 | -0.011758
35 |  | 0.16286 | 11.4674 | 4187 | 0.016817 | 6.5822 | 6.599 | -0.69847 | 59.4636 | 408.436 | -0.011746
36 |  | 0.16286 | 11.4557 | 4187 | 0.0168 | 6.599 | 6.6158 | -0.69847 | 59.5246 | 419.8917 | -0.011734
37 |  | 0.16286 | 11.444 | 4187 | 0.016783 | 6.6158 | 6.6326 | -0.69847 | 59.5856 | 431.3357 | -0.011722
38 |  | 0.16286 | 11.4322 | 4187 | 0.016765 | 6.6326 | 6.6493 | -0.69847 | 59.6467 | 442.7679 | -0.01171
39 |  | 0.16286 | 11.4205 | 4187 | 0.016748 | 6.6493 | 6.6661 | -0.69847 | 59.7079 | 454.1884 | -0.011698
40 |  | 0.16286 | 11.4088 | 4187 | 0.016731 | 6.6661 | 6.6828 | -0.69847 | 59.7691 | 465.5973 | -0.011686
41 |  | 0.16286 | 11.3971 | 4187 | 0.016714 | 6.6828 | 6.6995 | -0.69847 | 59.8304 | 476.9944 | -0.011674
42 |  | 0.16286 | 11.3855 | 4187 | 0.016697 | 6.6995 | 6.7162 | -0.69847 | 59.8918 | 488.3799 | -0.011662
43 |  | 0.16286 | 11.3738 | 4187 | 0.01668 | 6.7162 | 6.7329 | -0.69847 | 59.9532 | 499.7537 | -0.01165
44 |  | 0.16286 | 11.3622 | 4187 | 0.016663 | 6.7329 | 6.7496 | -0.69847 | 60.0146 | 511.1158 | -0.011638
45 |  | 0.16286 | 11.3505 | 4187 | 0.016646 | 6.7496 | 6.7662 | -0.69847 | 60.0762 | 522.4663 | -0.011626
46 |  | 0.16286 | 11.3389 | 4187 | 0.016628 | 6.7662 | 6.7828 | -0.69847 | 60.1378 | 533.8052 | -0.011615
47 |  | 0.16286 | 11.3273 | 4187 | 0.016611 | 6.7828 | 6.7994 | -0.69847 | 60.1994 | 545.1325 | -0.011603
48 |  | 0.16286 | 11.3157 | 4187 | 0.016594 | 6.7994 | 6.816 | -0.69847 | 60.2612 | 556.4482 | -0.011591
49 |  | 0.16286 | 11.3041 | 4187 | 0.016577 | 6.816 | 6.8326 | -0.69847 | 60.323 | 567.7523 | -0.011579
50 |  | 0.16286 | 11.2925 | 4187 | 0.01656 | 6.8326 | 6.8492 | -0.69847 | 60.3848 | 579.0448 | -0.011567
51 |  | 0.16286 | 11.2809 | 4187 | 0.016543 | 6.8492 | 6.8657 | -0.69847 | 60.4467 | 590.3257 | -0.011555
52 |  | 0.16286 | 11.2694 | 4187 | 0.016527 | 6.8657 | 6.8822 | -0.69847 | 60.5087 | 601.5951 | -0.011543
53 |  | 0.16286 | 11.2578 | 4187 | 0.01651 | 6.8822 | 6.8987 | -0.69847 | 60.5707 | 612.8529 | -0.011532
54 |  | 0.16286 | 11.2463 | 4187 | 0.016493 | 6.8987 | 6.9152 | -0.69847 | 60.6329 | 624.0992 | -0.01152
55 |  | 0.16286 | 11.2348 | 4187 | 0.016476 | 6.9152 | 6.9317 | -0.69847 | 60.695 | 635.334 | -0.011508
56 |  | 0.16286 | 11.2233 | 4187 | 0.016459 | 6.9317 | 6.9482 | -0.69847 | 60.7573 | 646.5573 | -0.011496
57 |  | 0.16286 | 11.2118 | 4187 | 0.016442 | 6.9482 | 6.9646 | -0.69847 | 60.8196 | 657.7691 | -0.011484
58 |  | 0.16286 | 11.2003 | 4187 | 0.016425 | 6.9646 | 6.981 | -0.69847 | 60.8819 | 668.9693 | -0.011473
59 |  | 0.16286 | 11.1888 | 4187 | 0.016408 | 6.981 | 6.9975 | -0.69847 | 60.9443 | 680.1582 | -0.011461
60 |  | 0.16286 | 11.1774 | 4187 | 0.016392 | 6.9975 | 7.0138 | -0.69847 | 61.0068 | 691.3355 | -0.011449
61 |  | 0.16286 | 11.1659 | 4187 | 0.016375 | 7.0138 | 7.0302 | -0.69847 | 61.0694 | 702.5014 | -0.011437
62 |  | 0.16286 | 11.1545 | 4187 | 0.016358 | 7.0302 | 7.0466 | -0.69847 | 61.132 | 713.6559 | -0.011426
63 |  | 0.16286 | 11.1431 | 4187 | 0.016341 | 7.0466 | 7.0629 | -0.69847 | 61.1947 | 724.799 | -0.011414
64 |  | 0.16286 | 11.1316 | 4187 | 0.016325 | 7.0629 | 7.0792 | -0.69847 | 61.2574 | 735.9306 | -0.011402
65 |  | 0.16286 | 11.1202 | 4187 | 0.016308 | 7.0792 | 7.0956 | -0.69847 | 61.3202 | 747.0508 | -0.011391
66 |  | 0.16286 | 11.1088 | 4187 | 0.016291 | 7.0956 | 7.1118 | -0.69847 | 61.3831 | 758.1597 | -0.011379
67 |  | 0.16286 | 11.0975 | 4187 | 0.016274 | 7.1118 | 7.1281 | -0.69847 | 61.4461 | 769.2572 | -0.011367
68 |  | 0.16286 | 11.0861 | 4187 | 0.016258 | 7.1281 | 7.1444 | -0.69847 | 61.5091 | 780.3432 | -0.011356
69 |  | 0.16286 | 11.0747 | 4187 | 0.016241 | 7.1444 | 7.1606 | -0.69847 | 61.5721 | 791.418 | -0.011344
70 |  | 0.16286 | 11.0634 | 4187 | 0.016224 | 7.1606 | 7.1768 | -0.69847 | 61.6353 | 802.4814 | -0.011332
71 |  | 0.16286 | 11.0521 | 4187 | 0.016208 | 7.1768 | 7.193 | -0.69847 | 61.6985 | 813.5335 | -0.011321
72 |  | 0.16286 | 11.0407 | 4187 | 0.016191 | 7.193 | 7.2092 | -0.69847 | 61.7617 | 824.5742 | -0.011309
73 |  | 0.16286 | 11.0294 | 4187 | 0.016175 | 7.2092 | 7.2254 | -0.69847 | 61.8251 | 835.6036 | -0.011298
74 |  | 0.16286 | 11.0181 | 4187 | 0.016158 | 7.2254 | 7.2416 | -0.69847 | 61.8885 | 846.6218 | -0.011286
75 |  | 0.16286 | 11.0069 | 4187 | 0.016142 | 7.2416 | 7.2577 | -0.69847 | 61.9519 | 857.6286 | -0.011274
76 |  | 0.16286 | 10.9956 | 4187 | 0.016125 | 7.2577 | 7.2738 | -0.69847 | 62.0154 | 868.6242 | -0.011263
77 |  | 0.16286 | 10.9843 | 4187 | 0.016109 | 7.2738 | 7.2899 | -0.69847 | 62.079 | 879.6085 | -0.011251
78 |  | 0.16286 | 10.9731 | 4187 | 0.016092 | 7.2899 | 7.306 | -0.69847 | 62.1427 | 890.5816 | -0.01124
79 |  | 0.16286 | 10.9618 | 4187 | 0.016076 | 7.306 | 7.3221 | -0.69847 | 62.2064 | 901.5434 | -0.011228
80 |  | 0.16286 | 10.9506 | 4187 | 0.016059 | 7.3221 | 7.3382 | -0.69847 | 62.2702 | 912.494 | -0.011217
81 |  | 0.16286 | 10.9394 | 4187 | 0.016043 | 7.3382 | 7.3542 | -0.69847 | 62.334 | 923.4334 | -0.011205
82 |  | 0.16286 | 10.9282 | 4187 | 0.016026 | 7.3542 | 7.3702 | -0.69847 | 62.3979 | 934.3615 | -0.011194
83 |  | 0.16286 | 10.917 | 4187 | 0.01601 | 7.3702 | 7.3863 | -0.69847 | 62.4619 | 945.2785 | -0.011182
84 |  | 0.16286 | 10.9058 | 4187 | 0.015993 | 7.3863 | 7.4022 | -0.69847 | 62.526 | 956.1843 | -0.011171
85 |  | 0.16286 | 10.8946 | 4187 | 0.015977 | 7.4022 | 7.4182 | -0.69847 | 62.5901 | 967.0789 | -0.011159
86 |  | 0.16286 | 10.8835 | 4187 | 0.015961 | 7.4182 | 7.4342 | -0.69847 | 62.6543 | 977.9624 | -0.011148
87 |  | 0.16286 | 10.8723 | 4187 | 0.015944 | 7.4342 | 7.4501 | -0.69847 | 62.7185 | 988.8347 | -0.011137
88 |  | 0.16286 | 10.8612 | 4187 | 0.015928 | 7.4501 | 7.4661 | -0.69847 | 62.7828 | 999.6959 | -0.011125
89 |  | 0.16286 | 10.8501 | 4187 | 0.015912 | 7.4661 | 7.482 | -0.69847 | 62.8472 | 1010.546 | -0.011114
90 |  | 0.16286 | 10.8389 | 4187 | 0.015895 | 7.482 | 7.4979 | -0.69847 | 62.9116 | 1021.3849 | -0.011102
91 |  | 0.16286 | 10.8278 | 4187 | 0.015879 | 7.4979 | 7.5137 | -0.69847 | 62.9761 | 1032.2128 | -0.011091
92 |  | 0.16286 | 10.8167 | 4187 | 0.015863 | 7.5137 | 7.5296 | -0.69847 | 63.0407 | 1043.0295 | -0.01108
93 |  | 0.16286 | 10.8057 | 4187 | 0.015847 | 7.5296 | 7.5454 | -0.69847 | 63.1053 | 1053.8352 | -0.011068
94 |  | 0.16286 | 10.7946 | 4187 | 0.01583 | 7.5454 | 7.5613 | -0.69847 | 63.1701 | 1064.6298 | -0.011057
95 |  | 0.16286 | 10.7835 | 4187 | 0.015814 | 7.5613 | 7.5771 | -0.69847 | 63.2348 | 1075.4133 | -0.011046
96 |  | 0.16286 | 10.7725 | 4187 | 0.015798 | 7.5771 | 7.5929 | -0.69847 | 63.2997 | 1086.1858 | -0.011034
97 |  | 0.16286 | 10.7615 | 4187 | 0.015782 | 7.5929 | 7.6087 | -0.69847 | 63.3646 | 1096.9473 | -0.011023
98 |  | 0.16286 | 10.7504 | 4187 | 0.015766 | 7.6087 | 7.6244 | -0.69847 | 63.4295 | 1107.6977 | -0.011012
99 |  | 0.16286 | 10.7394 | 4187 | 0.015749 | 7.6244 | 7.6402 | -0.69847 | 63.4946 | 1118.4371 | -0.011001
100 |  | 0.16286 | 10.7284 | 4187 | 0.015733 | 7.6402 | 7.6559 | -0.69847 | 63.5597 | 1129.1656 | -0.010989
101 |  | 0.16286 | 10.7174 | 4187 | 0.015717 | 7.6559 | 7.6716 | -0.69847 | 63.6249 | 1139.883 | -0.010978
102 |  | 0.16286 | 10.7065 | 4187 | 0.015701 | 7.6716 | 7.6873 | -0.69847 | 63.6901 | 1150.5895 | -0.010967
103 |  | 0.16286 | 10.6955 | 4187 | 0.015685 | 7.6873 | 7.703 | -0.69847 | 63.7554 | 1161.285 | -0.010956
104 |  | 0.16286 | 10.6845 | 4187 | 0.015669 | 7.703 | 7.7187 | -0.69847 | 63.8208 | 1171.9695 | -0.010944
105 |  | 0.16286 | 10.6736 | 4187 | 0.015653 | 7.7187 | 7.7343 | -0.69847 | 63.8862 | 1182.6431 | -0.010933
106 |  | 0.16286 | 10.6627 | 4187 | 0.015637 | 7.7343 | 7.75 | -0.69847 | 63.9517 | 1193.3058 | -0.010922
107 |  | 0.16286 | 10.6517 | 4187 | 0.015621 | 7.75 | 7.7656 | -0.69847 | 64.0173 | 1203.9575 | -0.010911
108 |  | 0.16286 | 10.6408 | 4187 | 0.015605 | 7.7656 | 7.7812 | -0.69847 | 64.0829 | 1214.5983 | -0.0109
109 |  | 0.16286 | 10.6299 | 4187 | 0.015589 | 7.7812 | 7.7968 | -0.69847 | 64.1486 | 1225.2283 | -0.010888
110 |  | 0.16286 | 10.619 | 4187 | 0.015573 | 7.7968 | 7.8124 | -0.69847 | 64.2144 | 1235.8473 | -0.010877
111 |  | 0.16286 | 10.6082 | 4187 | 0.015557 | 7.8124 | 7.8279 | -0.69847 | 64.2803 | 1246.4555 | -0.010866
112 |  | 0.16286 | 10.5973 | 4187 | 0.015541 | 7.8279 | 7.8435 | -0.69847 | 64.3462 | 1257.0528 | -0.010855
113 |  | 0.16286 | 10.5864 | 4187 | 0.015525 | 7.8435 | 7.859 | -0.69847 | 64.4121 | 1267.6392 | -0.010844
114 |  | 0.16286 | 10.5756 | 4187 | 0.015509 | 7.859 | 7.8745 | -0.69847 | 64.4782 | 1278.2148 | -0.010833
115 |  | 0.16286 | 10.5648 | 4187 | 0.015493 | 7.8745 | 7.89 | -0.69847 | 64.5443 | 1288.7796 | -0.010822
116 |  | 0.16286 | 10.5539 | 4187 | 0.015477 | 7.89 | 7.9055 | -0.69847 | 64.6105 | 1299.3335 | -0.010811
117 |  | 0.16286 | 10.5431 | 4187 | 0.015462 | 7.9055 | 7.9209 | -0.69847 | 64.6767 | 1309.8766 | -0.010799
118 |  | 0.16286 | 10.5323 | 4187 | 0.015446 | 7.9209 | 7.9364 | -0.69847 | 64.7431 | 1320.409 | -0.010788
119 |  | 0.16286 | 10.5215 | 4187 | 0.01543 | 7.9364 | 7.9518 | -0.69847 | 64.8094 | 1330.9305 | -0.010777
120 |  | 0.16286 | 10.5108 | 4187 | 0.015414 | 7.9518 | 7.9672 | -0.69847 | 64.8759 | 1341.4413 | -0.010766
121 |  | 0.16286 | 10.5 | 4187 | 0.015398 | 7.9672 | 7.9826 | -0.69847 | 64.9424 | 1351.9413 | -0.010755
122 |  | 0.16286 | 10.4892 | 4187 | 0.015382 | 7.9826 | 7.998 | -0.69847 | 65.009 | 1362.4305 | -0.010744
123 |  | 0.16286 | 10.4785 | 4187 | 0.015367 | 7.998 | 8.0134 | -0.69847 | 65.0757 | 1372.909 | -0.010733
124 |  | 0.16286 | 10.4678 | 4187 | 0.015351 | 8.0134 | 8.0287 | -0.69847 | 65.1424 | 1383.3768 | -0.010722
125 |  | 0.16286 | 10.457 | 4187 | 0.015335 | 8.0287 | 8.0441 | -0.69847 | 65.2092 | 1393.8339 | -0.010711
126 |  | 0.16286 | 10.4463 | 4187 | 0.01532 | 8.0441 | 8.0594 | -0.69847 | 65.276 | 1404.2802 | -0.0107
127 |  | 0.16286 | 10.4356 | 4187 | 0.015304 | 8.0594 | 8.0747 | -0.69847 | 65.343 | 1414.7158 | -0.010689
128 |  | 0.16286 | 10.4249 | 4187 | 0.015288 | 8.0747 | 8.09 | -0.69847 | 65.41 | 1425.1408 | -0.010678
129 |  | 0.16286 | 10.4143 | 4187 | 0.015273 | 8.09 | 8.1052 | -0.69847 | 65.477 | 1435.555 | -0.010667
130 |  | 0.16286 | 10.4036 | 4187 | 0.015257 | 8.1052 | 8.1205 | -0.69847 | 65.5442 | 1445.9586 | -0.010657
131 |  | 0.16286 | 10.3929 | 4187 | 0.015241 | 8.1205 | 8.1357 | -0.69847 | 65.6114 | 1456.3516 | -0.010646
132 |  | 0.16286 | 10.3823 | 4187 | 0.015226 | 8.1357 | 8.151 | -0.69847 | 65.6787 | 1466.7339 | -0.010635
133 |  | 0.16286 | 10.3717 | 4187 | 0.01521 | 8.151 | 8.1662 | -0.69847 | 65.746 | 1477.1055 | -0.010624
134 |  | 0.16286 | 10.361 | 4187 | 0.015194 | 8.1662 | 8.1814 | -0.69847 | 65.8134 | 1487.4666 | -0.010613
135 |  | 0.16286 | 10.3504 | 4187 | 0.015179 | 8.1814 | 8.1965 | -0.69847 | 65.8809 | 1497.817 | -0.010602
136 |  | 0.16286 | 10.3398 | 4187 | 0.015163 | 8.1965 | 8.2117 | -0.69847 | 65.9485 | 1508.1568 | -0.010591
137 |  | 0.16286 | 10.3292 | 4187 | 0.015148 | 8.2117 | 8.2269 | -0.69847 | 66.0161 | 1518.4861 | -0.01058
138 |  | 0.16286 | 10.3187 | 4187 | 0.015132 | 8.2269 | 8.242 | -0.69847 | 66.0838 | 1528.8047 | -0.01057
139 |  | 0.16286 | 10.3081 | 4187 | 0.015117 | 8.242 | 8.2571 | -0.69847 | 66.1515 | 1539.1128 | -0.010559
140 |  | 0.16286 | 10.2975 | 4187 | 0.015101 | 8.2571 | 8.2722 | -0.69847 | 66.2194 | 1549.4103 | -0.010548
141 |  | 0.16286 | 10.287 | 4187 | 0.015086 | 8.2722 | 8.2873 | -0.69847 | 66.2873 | 1559.6973 | -0.010537
142 |  | 0.16286 | 10.2764 | 4187 | 0.01507 | 8.2873 | 8.3024 | -0.69847 | 66.3552 | 1569.9737 | -0.010526
143 |  | 0.16286 | 10.2659 | 4187 | 0.015055 | 8.3024 | 8.3174 | -0.69847 | 66.4233 | 1580.2397 | -0.010516
144 |  | 0.16286 | 10.2554 | 4187 | 0.01504 | 8.3174 | 8.3325 | -0.69847 | 66.4914 | 1590.4951 | -0.010505
145 |  | 0.16286 | 10.2449 | 4187 | 0.015024 | 8.3325 | 8.3475 | -0.69847 | 66.5596 | 1600.74 | -0.010494
146 |  | 0.16286 | 10.2344 | 4187 | 0.015009 | 8.3475 | 8.3625 | -0.69847 | 66.6278 | 1610.9744 | -0.010483
147 |  | 0.16286 | 10.2239 | 4187 | 0.014993 | 8.3625 | 8.3775 | -0.69847 | 66.6961 | 1621.1983 | -0.010472
148 |  | 0.16286 | 10.2134 | 4187 | 0.014978 | 8.3775 | 8.3925 | -0.69847 | 66.7645 | 1631.4117 | -0.010462
149 |  | 0.16286 | 10.203 | 4187 | 0.014963 | 8.3925 | 8.4074 | -0.69847 | 66.833 | 1641.6147 | -0.010451
150 |  | 0.16286 | 10.1925 | 4187 | 0.014947 | 8.4074 | 8.4224 | -0.69847 | 66.9015 | 1651.8072 | -0.01044
151 |  | 0.16286 | 10.1821 | 4187 | 0.014932 | 8.4224 | 8.4373 | -0.69847 | 66.9701 | 1661.9893 | -0.01043
152 |  | 0.16286 | 10.1717 | 4187 | 0.014917 | 8.4373 | 8.4522 | -0.69847 | 67.0388 | 1672.161 | -0.010419
153 |  | 0.16286 | 10.1612 | 4187 | 0.014901 | 8.4522 | 8.4671 | -0.69847 | 67.1075 | 1682.3222 | -0.010408
154 |  | 0.16286 | 10.1508 | 4187 | 0.014886 | 8.4671 | 8.482 | -0.69847 | 67.1763 | 1692.473 | -0.010398
155 |  | 0.16286 | 10.1404 | 4187 | 0.014871 | 8.482 | 8.4969 | -0.69847 | 67.2452 | 1702.6135 | -0.010387
156 |  | 0.16286 | 10.13 | 4187 | 0.014856 | 8.4969 | 8.5117 | -0.69847 | 67.3141 | 1712.7435 | -0.010376
157 |  | 0.16286 | 10.1197 | 4187 | 0.014841 | 8.5117 | 8.5266 | -0.69847 | 67.3832 | 1722.8632 | -0.010366
158 |  | 0.16286 | 10.1093 | 4187 | 0.014825 | 8.5266 | 8.5414 | -0.69847 | 67.4523 | 1732.9725 | -0.010355
159 |  | 0.16286 | 10.099 | 4187 | 0.01481 | 8.5414 | 8.5562 | -0.69847 | 67.5214 | 1743.0715 | -0.010344
160 |  | 0.16286 | 10.0886 | 4187 | 0.014795 | 8.5562 | 8.571 | -0.69847 | 67.5906 | 1753.1601 | -0.010334
161 |  | 0.16286 | 10.0783 | 4187 | 0.01478 | 8.571 | 8.5858 | -0.69847 | 67.66 | 1763.2383 | -0.010323
162 |  | 0.16286 | 10.068 | 4187 | 0.014765 | 8.5858 | 8.6006 | -0.69847 | 67.7293 | 1773.3063 | -0.010313
163 |  | 0.16286 | 10.0576 | 4187 | 0.01475 | 8.6006 | 8.6153 | -0.69847 | 67.7988 | 1783.3639 | -0.010302
164 |  | 0.16286 | 10.0473 | 4187 | 0.014734 | 8.6153 | 8.63 | -0.69847 | 67.8683 | 1793.4113 | -0.010292
165 |  | 0.16286 | 10.037 | 4187 | 0.014719 | 8.63 | 8.6448 | -0.69847 | 67.9379 | 1803.4483 | -0.010281
166 |  | 0.16286 | 10.0268 | 4187 | 0.014704 | 8.6448 | 8.6595 | -0.69847 | 68.0075 | 1813.4751 | -0.010271
167 |  | 0.16286 | 10.0165 | 4187 | 0.014689 | 8.6595 | 8.6742 | -0.69847 | 68.0773 | 1823.4916 | -0.01026
168 |  | 0.16286 | 10.0062 | 4187 | 0.014674 | 8.6742 | 8.6888 | -0.69847 | 68.1471 | 1833.4978 | -0.01025
169 |  | 0.16286 | 9.996 | 4187 | 0.014659 | 8.6888 | 8.7035 | -0.69847 | 68.217 | 1843.4938 | -0.010239
170 |  | 0.16286 | 9.9857 | 4187 | 0.014644 | 8.7035 | 8.7181 | -0.69847 | 68.2869 | 1853.4795 | -0.010229
171 |  | 0.16286 | 9.9755 | 4187 | 0.014629 | 8.7181 | 8.7328 | -0.69847 | 68.3569 | 1863.455 | -0.010218
172 |  | 0.16286 | 9.9653 | 4187 | 0.014614 | 8.7328 | 8.7474 | -0.69847 | 68.427 | 1873.4203 | -0.010208
173 |  | 0.16286 | 9.9551 | 4187 | 0.014599 | 8.7474 | 8.762 | -0.69847 | 68.4972 | 1883.3754 | -0.010197
174 |  | 0.16286 | 9.9449 | 4187 | 0.014584 | 8.762 | 8.7766 | -0.69847 | 68.5674 | 1893.3203 | -0.010187
175 |  | 0.16286 | 9.9347 | 4187 | 0.014569 | 8.7766 | 8.7911 | -0.69847 | 68.6377 | 1903.255 | -0.010176
176 |  | 0.16286 | 9.9245 | 4187 | 0.014554 | 8.7911 | 8.8057 | -0.69847 | 68.7081 | 1913.1796 | -0.010166
177 |  | 0.16286 | 9.9144 | 4187 | 0.014539 | 8.8057 | 8.8202 | -0.69847 | 68.7785 | 1923.0939 | -0.010155
178 |  | 0.16286 | 9.9042 | 4187 | 0.014525 | 8.8202 | 8.8347 | -0.69847 | 68.8491 | 1932.9981 | -0.010145
179 |  | 0.16286 | 9.8941 | 4187 | 0.01451 | 8.8347 | 8.8493 | -0.69847 | 68.9197 | 1942.8922 | -0.010135
180 |  | 0.16286 | 9.8839 | 4187 | 0.014495 | 8.8493 | 8.8637 | -0.69847 | 68.9903 | 1952.7761 | -0.010124
181 |  | 0.16286 | 9.8738 | 4187 | 0.01448 | 8.8637 | 8.8782 | -0.69847 | 69.0611 | 1962.6499 | -0.010114
182 |  | 0.16286 | 9.8637 | 4187 | 0.014465 | 8.8782 | 8.8927 | -0.69847 | 69.1319 | 1972.5136 | -0.010103
183 |  | 0.16286 | 9.8536 | 4187 | 0.01445 | 8.8927 | 8.9071 | -0.69847 | 69.2028 | 1982.3672 | -0.010093
184 |  | 0.16286 | 9.8435 | 4187 | 0.014435 | 8.9071 | 8.9216 | -0.69847 | 69.2737 | 1992.2107 | -0.010083
185 |  | 0.16286 | 9.8334 | 4187 | 0.014421 | 8.9216 | 8.936 | -0.69847 | 69.3448 | 2002.0441 | -0.010072
186 |  | 0.16286 | 9.8233 | 4187 | 0.014406 | 8.936 | 8.9504 | -0.69847 | 69.4159 | 2011.8674 | -0.010062
187 |  | 0.16286 | 9.8133 | 4187 | 0.014391 | 8.9504 | 8.9648 | -0.69847 | 69.487 | 2021.6807 | -0.010052
188 |  | 0.16286 | 9.8032 | 4187 | 0.014376 | 8.9648 | 8.9792 | -0.69847 | 69.5583 | 2031.4839 | -0.010042
189 |  | 0.16286 | 9.7932 | 4187 | 0.014362 | 8.9792 | 8.9935 | -0.69847 | 69.6296 | 2041.2771 | -0.010031
190 |  | 0.16286 | 9.7832 | 4187 | 0.014347 | 8.9935 | 9.0079 | -0.69847 | 69.701 | 2051.0603 | -0.010021
191 |  | 0.16286 | 9.7731 | 4187 | 0.014332 | 9.0079 | 9.0222 | -0.69847 | 69.7725 | 2060.8334 | -0.010011
192 |  | 0.16286 | 9.7631 | 4187 | 0.014318 | 9.0222 | 9.0365 | -0.69847 | 69.844 | 2070.5965 | -0.01
193 |  | 0.16286 | 9.7531 | 4187 | 0.014303 | 9.0365 | 9.0508 | -0.69847 | 69.9156 | 2080.3496 | -0.0099902
194 |  | 0.16286 | 9.7431 | 4187 | 0.014288 | 9.0508 | 9.0651 | -0.69847 | 69.9873 | 2090.0928 | -0.00998
195 |  | 0.16286 | 9.7331 | 4187 | 0.014274 | 9.0651 | 9.0794 | -0.69847 | 70.0591 | 2099.8259 | -0.0099698
196 |  | 0.16286 | 9.7232 | 4187 | 0.014259 | 9.0794 | 9.0937 | -0.69847 | 70.1309 | 2109.5491 | -0.0099596
197 |  | 0.16286 | 9.7132 | 4187 | 0.014244 | 9.0937 | 9.1079 | -0.69847 | 70.2028 | 2119.2623 | -0.0099494
198 |  | 0.16286 | 9.7033 | 4187 | 0.01423 | 9.1079 | 9.1221 | -0.69847 | 70.2748 | 2128.9656 | -0.0099392
199 |  | 0.16286 | 9.6933 | 4187 | 0.014215 | 9.1221 | 9.1363 | -0.69847 | 70.3469 | 2138.6589 | -0.009929
200 |  | 0.16286 | 9.6834 | 4187 | 0.014201 | 9.1363 | 9.1505 | -0.69847 | 70.419 | 2148.3423 | -0.0099188
201 |  | 0.16286 | 9.6735 | 4187 | 0.014186 | 9.1505 | 9.1647 | -0.69847 | 70.4912 | 2158.0158 | -0.0099087
202 |  | 0.16286 | 9.6636 | 4187 | 0.014172 | 9.1647 | 9.1789 | -0.69847 | 70.5635 | 2167.6794 | -0.0098985
203 |  | 0.16286 | 9.6537 | 4187 | 0.014157 | 9.1789 | 9.1931 | -0.69847 | 70.6358 | 2177.3331 | -0.0098884
204 |  | 0.16286 | 9.6438 | 4187 | 0.014143 | 9.1931 | 9.2072 | -0.69847 | 70.7083 | 2186.9769 | -0.0098783
205 |  | 0.16286 | 9.6339 | 4187 | 0.014128 | 9.2072 | 9.2213 | -0.69847 | 70.7808 | 2196.6108 | -0.0098681
206 |  | 0.16286 | 9.624 | 4187 | 0.014114 | 9.2213 | 9.2354 | -0.69847 | 70.8533 | 2206.2348 | -0.009858
207 |  | 0.16286 | 9.6142 | 4187 | 0.014099 | 9.2354 | 9.2495 | -0.69847 | 70.926 | 2215.849 | -0.0098479
208 |  | 0.16286 | 9.6043 | 4187 | 0.014085 | 9.2495 | 9.2636 | -0.69847 | 70.9987 | 2225.4533 | -0.0098378
209 |  | 0.16286 | 9.5945 | 4187 | 0.01407 | 9.2636 | 9.2777 | -0.69847 | 71.0715 | 2235.0478 | -0.0098278
210 |  | 0.16286 | 9.5847 | 4187 | 0.014056 | 9.2777 | 9.2918 | -0.69847 | 71.1444 | 2244.6325 | -0.0098177
211 |  | 0.16286 | 9.5749 | 4187 | 0.014042 | 9.2918 | 9.3058 | -0.69847 | 71.2173 | 2254.2073 | -0.0098076
212 |  | 0.16286 | 9.565 | 4187 | 0.014027 | 9.3058 | 9.3198 | -0.69847 | 71.2904 | 2263.7724 | -0.0097976
213 |  | 0.16286 | 9.5552 | 4187 | 0.014013 | 9.3198 | 9.3338 | -0.69847 | 71.3635 | 2273.3276 | -0.0097876
214 |  | 0.16286 | 9.5455 | 4187 | 0.013998 | 9.3338 | 9.3478 | -0.69847 | 71.4366 | 2282.8731 | -0.0097775
215 |  | 0.16286 | 9.5357 | 4187 | 0.013984 | 9.3478 | 9.3618 | -0.69847 | 71.5099 | 2292.4088 | -0.0097675
216 |  | 0.16286 | 9.5259 | 4187 | 0.01397 | 9.3618 | 9.3758 | -0.69847 | 71.5832 | 2301.9347 | -0.0097575
217 |  | 0.16286 | 9.5162 | 4187 | 0.013955 | 9.3758 | 9.3897 | -0.69847 | 71.6566 | 2311.4508 | -0.0097475
218 |  | 0.16286 | 9.5064 | 4187 | 0.013941 | 9.3897 | 9.4037 | -0.69847 | 71.7301 | 2320.9573 | -0.0097375
219 |  | 0.16286 | 9.4967 | 4187 | 0.013927 | 9.4037 | 9.4176 | -0.69847 | 71.8036 | 2330.4539 | -0.0097276
220 |  | 0.16286 | 9.4869 | 4187 | 0.013913 | 9.4176 | 9.4315 | -0.69847 | 71.8773 | 2339.9409 | -0.0097176
221 |  | 0.16286 | 9.4772 | 4187 | 0.013898 | 9.4315 | 9.4454 | -0.69847 | 71.951 | 2349.4181 | -0.0097076
222 |  | 0.16286 | 9.4675 | 4187 | 0.013884 | 9.4454 | 9.4593 | -0.69847 | 72.0247 | 2358.8856 | -0.0096977
223 |  | 0.16286 | 9.4578 | 4187 | 0.01387 | 9.4593 | 9.4732 | -0.69847 | 72.0986 | 2368.3434 | -0.0096878
224 |  | 0.16286 | 9.4481 | 4187 | 0.013856 | 9.4732 | 9.487 | -0.69847 | 72.1725 | 2377.7916 | -0.0096778
225 |  | 0.16286 | 9.4385 | 4187 | 0.013841 | 9.487 | 9.5009 | -0.69847 | 72.2465 | 2387.23 | -0.0096679
226 |  | 0.16286 | 9.4288 | 4187 | 0.013827 | 9.5009 | 9.5147 | -0.69847 | 72.3206 | 2396.6588 | -0.009658
227 |  | 0.16286 | 9.4191 | 4187 | 0.013813 | 9.5147 | 9.5285 | -0.69847 | 72.3947 | 2406.0779 | -0.0096481
228 |  | 0.16286 | 9.4095 | 4187 | 0.013799 | 9.5285 | 9.5423 | -0.69847 | 72.469 | 2415.4874 | -0.0096382
229 |  | 0.16286 | 9.3998 | 4187 | 0.013785 | 9.5423 | 9.5561 | -0.69847 | 72.5433 | 2424.8873 | -0.0096284
230 |  | 0.16286 | 9.3902 | 4187 | 0.013771 | 9.5561 | 9.5699 | -0.69847 | 72.6177 | 2434.2775 | -0.0096185
231 |  | 0.16286 | 9.3806 | 4187 | 0.013757 | 9.5699 | 9.5836 | -0.69847 | 72.6921 | 2443.6581 | -0.0096087
232 |  | 0.16286 | 9.371 | 4187 | 0.013743 | 9.5836 | 9.5974 | -0.69847 | 72.7667 | 2453.0291 | -0.0095988
233 |  | 0.16286 | 9.3614 | 4187 | 0.013728 | 9.5974 | 9.6111 | -0.69847 | 72.8413 | 2462.3905 | -0.009589
234 |  | 0.16286 | 9.3518 | 4187 | 0.013714 | 9.6111 | 9.6248 | -0.69847 | 72.916 | 2471.7423 | -0.0095792
235 |  | 0.16286 | 9.3422 | 4187 | 0.0137 | 9.6248 | 9.6385 | -0.69847 | 72.9907 | 2481.0845 | -0.0095694
236 |  | 0.16286 | 9.3327 | 4187 | 0.013686 | 9.6385 | 9.6522 | -0.69847 | 73.0656 | 2490.4171 | -0.0095595

## 25
|  |  | buis | verlies W/M | L /°C/sec
diam | wandikte |  | inhoud l/m |  | W/M
25 | 3.5 | 3.1416 | 0.25447 | 13.991 | 4187
[8 empty] | J/sec/mtr | aantal mtr. | verlies
|  | buis | verlies W/M | L /°C/sec | verlies temp | begintemp | eindtemp | verlies | bij 1°C | totaal J/sec
|  | inhoud L |  | W/M | °C per M | °C | °C | per m°C | daling | aantal mtr
1 | 25 | 0.25447 | 13.991 | 4187 | 0.013131 | 6 | 6.0131 | -0.823 | 76.1532 | 13.991 | -0.010807
2 |  | 0.25447 | 13.9802 | 4187 | 0.013121 | 6.0131 | 6.0263 | -0.823 | 76.2121 | 27.9712 | -0.010799
3 |  | 0.25447 | 13.9694 | 4187 | 0.013111 | 6.0263 | 6.0394 | -0.823 | 76.271 | 41.9407 | -0.01079
4 |  | 0.25447 | 13.9586 | 4187 | 0.013101 | 6.0394 | 6.0525 | -0.823 | 76.33 | 55.8993 | -0.010782
5 |  | 0.25447 | 13.9478 | 4187 | 0.013091 | 6.0525 | 6.0656 | -0.823 | 76.389 | 69.8471 | -0.010774
6 |  | 0.25447 | 13.9371 | 4187 | 0.013081 | 6.0656 | 6.0786 | -0.823 | 76.448 | 83.7842 | -0.010765
7 |  | 0.25447 | 13.9263 | 4187 | 0.013071 | 6.0786 | 6.0917 | -0.823 | 76.5071 | 97.7105 | -0.010757
8 |  | 0.25447 | 13.9155 | 4187 | 0.013061 | 6.0917 | 6.1048 | -0.823 | 76.5663 | 111.626 | -0.010749
9 |  | 0.25447 | 13.9048 | 4187 | 0.01305 | 6.1048 | 6.1178 | -0.823 | 76.6255 | 125.5308 | -0.010741
10 |  | 0.25447 | 13.8941 | 4187 | 0.01304 | 6.1178 | 6.1309 | -0.823 | 76.6847 | 139.4249 | -0.010732
11 |  | 0.25447 | 13.8833 | 4187 | 0.01303 | 6.1309 | 6.1439 | -0.823 | 76.744 | 153.3082 | -0.010724
12 |  | 0.25447 | 13.8726 | 4187 | 0.01302 | 6.1439 | 6.1569 | -0.823 | 76.8033 | 167.1808 | -0.010716
13 |  | 0.25447 | 13.8619 | 4187 | 0.01301 | 6.1569 | 6.1699 | -0.823 | 76.8627 | 181.0427 | -0.010707
14 |  | 0.25447 | 13.8512 | 4187 | 0.013 | 6.1699 | 6.1829 | -0.823 | 76.9221 | 194.8939 | -0.010699
15 |  | 0.25447 | 13.8405 | 4187 | 0.01299 | 6.1829 | 6.1959 | -0.823 | 76.9816 | 208.7344 | -0.010691
16 |  | 0.25447 | 13.8298 | 4187 | 0.01298 | 6.1959 | 6.2089 | -0.823 | 77.0411 | 222.5642 | -0.010683
17 |  | 0.25447 | 13.8191 | 4187 | 0.01297 | 6.2089 | 6.2219 | -0.823 | 77.1006 | 236.3833 | -0.010674
18 |  | 0.25447 | 13.8084 | 4187 | 0.01296 | 6.2219 | 6.2348 | -0.823 | 77.1602 | 250.1917 | -0.010666
19 |  | 0.25447 | 13.7978 | 4187 | 0.01295 | 6.2348 | 6.2478 | -0.823 | 77.2199 | 263.9895 | -0.010658
20 |  | 0.25447 | 13.7871 | 4187 | 0.01294 | 6.2478 | 6.2607 | -0.823 | 77.2796 | 277.7766 | -0.01065
21 |  | 0.25447 | 13.7765 | 4187 | 0.01293 | 6.2607 | 6.2736 | -0.823 | 77.3393 | 291.553 | -0.010641
22 |  | 0.25447 | 13.7658 | 4187 | 0.01292 | 6.2736 | 6.2866 | -0.823 | 77.3991 | 305.3188 | -0.010633
23 |  | 0.25447 | 13.7552 | 4187 | 0.01291 | 6.2866 | 6.2995 | -0.823 | 77.4589 | 319.074 | -0.010625
24 |  | 0.25447 | 13.7446 | 4187 | 0.0129 | 6.2995 | 6.3124 | -0.823 | 77.5188 | 332.8186 | -0.010617
25 |  | 0.25447 | 13.7339 | 4187 | 0.01289 | 6.3124 | 6.3253 | -0.823 | 77.5787 | 346.5525 | -0.010609
26 |  | 0.25447 | 13.7233 | 4187 | 0.01288 | 6.3253 | 6.3381 | -0.823 | 77.6387 | 360.2759 | -0.0106
27 |  | 0.25447 | 13.7127 | 4187 | 0.01287 | 6.3381 | 6.351 | -0.823 | 77.6987 | 373.9886 | -0.010592
28 |  | 0.25447 | 13.7021 | 4187 | 0.01286 | 6.351 | 6.3639 | -0.823 | 77.7588 | 387.6907 | -0.010584
29 |  | 0.25447 | 13.6916 | 4187 | 0.01285 | 6.3639 | 6.3767 | -0.823 | 77.8189 | 401.3823 | -0.010576
30 |  | 0.25447 | 13.681 | 4187 | 0.01284 | 6.3767 | 6.3896 | -0.823 | 77.8791 | 415.0633 | -0.010568
31 |  | 0.25447 | 13.6704 | 4187 | 0.012831 | 6.3896 | 6.4024 | -0.823 | 77.9393 | 428.7337 | -0.01056
32 |  | 0.25447 | 13.6599 | 4187 | 0.012821 | 6.4024 | 6.4152 | -0.823 | 77.9995 | 442.3935 | -0.010551
33 |  | 0.25447 | 13.6493 | 4187 | 0.012811 | 6.4152 | 6.428 | -0.823 | 78.0598 | 456.0428 | -0.010543
34 |  | 0.25447 | 13.6388 | 4187 | 0.012801 | 6.428 | 6.4408 | -0.823 | 78.1201 | 469.6816 | -0.010535
35 |  | 0.25447 | 13.6282 | 4187 | 0.012791 | 6.4408 | 6.4536 | -0.823 | 78.1805 | 483.3098 | -0.010527
36 |  | 0.25447 | 13.6177 | 4187 | 0.012781 | 6.4536 | 6.4664 | -0.823 | 78.241 | 496.9275 | -0.010519
37 |  | 0.25447 | 13.6072 | 4187 | 0.012771 | 6.4664 | 6.4792 | -0.823 | 78.3015 | 510.5347 | -0.010511
38 |  | 0.25447 | 13.5967 | 4187 | 0.012761 | 6.4792 | 6.4919 | -0.823 | 78.362 | 524.1313 | -0.010503
39 |  | 0.25447 | 13.5862 | 4187 | 0.012751 | 6.4919 | 6.5047 | -0.823 | 78.4226 | 537.7175 | -0.010494
40 |  | 0.25447 | 13.5757 | 4187 | 0.012742 | 6.5047 | 6.5174 | -0.823 | 78.4832 | 551.2932 | -0.010486
41 |  | 0.25447 | 13.5652 | 4187 | 0.012732 | 6.5174 | 6.5302 | -0.823 | 78.5439 | 564.8584 | -0.010478
42 |  | 0.25447 | 13.5547 | 4187 | 0.012722 | 6.5302 | 6.5429 | -0.823 | 78.6046 | 578.4131 | -0.01047
43 |  | 0.25447 | 13.5442 | 4187 | 0.012712 | 6.5429 | 6.5556 | -0.823 | 78.6653 | 591.9573 | -0.010462
44 |  | 0.25447 | 13.5338 | 4187 | 0.012702 | 6.5556 | 6.5683 | -0.823 | 78.7261 | 605.4911 | -0.010454
45 |  | 0.25447 | 13.5233 | 4187 | 0.012692 | 6.5683 | 6.581 | -0.823 | 78.787 | 619.0144 | -0.010446
46 |  | 0.25447 | 13.5129 | 4187 | 0.012683 | 6.581 | 6.5937 | -0.823 | 78.8479 | 632.5273 | -0.010438
47 |  | 0.25447 | 13.5024 | 4187 | 0.012673 | 6.5937 | 6.6063 | -0.823 | 78.9089 | 646.0297 | -0.01043
48 |  | 0.25447 | 13.492 | 4187 | 0.012663 | 6.6063 | 6.619 | -0.823 | 78.9699 | 659.5217 | -0.010422
49 |  | 0.25447 | 13.4816 | 4187 | 0.012653 | 6.619 | 6.6317 | -0.823 | 79.0309 | 673.0033 | -0.010414
50 |  | 0.25447 | 13.4712 | 4187 | 0.012644 | 6.6317 | 6.6443 | -0.823 | 79.092 | 686.4745 | -0.010406
51 |  | 0.25447 | 13.4608 | 4187 | 0.012634 | 6.6443 | 6.6569 | -0.823 | 79.1531 | 699.9352 | -0.010398
52 |  | 0.25447 | 13.4504 | 4187 | 0.012624 | 6.6569 | 6.6696 | -0.823 | 79.2143 | 713.3856 | -0.01039
53 |  | 0.25447 | 13.44 | 4187 | 0.012614 | 6.6696 | 6.6822 | -0.823 | 79.2756 | 726.8256 | -0.010382
54 |  | 0.25447 | 13.4296 | 4187 | 0.012604 | 6.6822 | 6.6948 | -0.823 | 79.3368 | 740.2552 | -0.010374
55 |  | 0.25447 | 13.4192 | 4187 | 0.012595 | 6.6948 | 6.7074 | -0.823 | 79.3982 | 753.6744 | -0.010365
56 |  | 0.25447 | 13.4089 | 4187 | 0.012585 | 6.7074 | 6.72 | -0.823 | 79.4596 | 767.0832 | -0.010357
57 |  | 0.25447 | 13.3985 | 4187 | 0.012575 | 6.72 | 6.7325 | -0.823 | 79.521 | 780.4817 | -0.010349
58 |  | 0.25447 | 13.3881 | 4187 | 0.012566 | 6.7325 | 6.7451 | -0.823 | 79.5824 | 793.8699 | -0.010341
59 |  | 0.25447 | 13.3778 | 4187 | 0.012556 | 6.7451 | 6.7577 | -0.823 | 79.644 | 807.2477 | -0.010334
60 |  | 0.25447 | 13.3675 | 4187 | 0.012546 | 6.7577 | 6.7702 | -0.823 | 79.7055 | 820.6152 | -0.010326
61 |  | 0.25447 | 13.3571 | 4187 | 0.012536 | 6.7702 | 6.7827 | -0.823 | 79.7672 | 833.9723 | -0.010318
62 |  | 0.25447 | 13.3468 | 4187 | 0.012527 | 6.7827 | 6.7953 | -0.823 | 79.8288 | 847.3192 | -0.01031
63 |  | 0.25447 | 13.3365 | 4187 | 0.012517 | 6.7953 | 6.8078 | -0.823 | 79.8905 | 860.6557 | -0.010302
64 |  | 0.25447 | 13.3262 | 4187 | 0.012507 | 6.8078 | 6.8203 | -0.823 | 79.9523 | 873.9819 | -0.010294
65 |  | 0.25447 | 13.3159 | 4187 | 0.012498 | 6.8203 | 6.8328 | -0.823 | 80.0141 | 887.2978 | -0.010286
66 |  | 0.25447 | 13.3056 | 4187 | 0.012488 | 6.8328 | 6.8453 | -0.823 | 80.0759 | 900.6035 | -0.010278
67 |  | 0.25447 | 13.2954 | 4187 | 0.012478 | 6.8453 | 6.8577 | -0.823 | 80.1378 | 913.8988 | -0.01027
68 |  | 0.25447 | 13.2851 | 4187 | 0.012469 | 6.8577 | 6.8702 | -0.823 | 80.1998 | 927.1839 | -0.010262
69 |  | 0.25447 | 13.2748 | 4187 | 0.012459 | 6.8702 | 6.8827 | -0.823 | 80.2618 | 940.4588 | -0.010254
70 |  | 0.25447 | 13.2646 | 4187 | 0.01245 | 6.8827 | 6.8951 | -0.823 | 80.3238 | 953.7233 | -0.010246
71 |  | 0.25447 | 13.2543 | 4187 | 0.01244 | 6.8951 | 6.9076 | -0.823 | 80.3859 | 966.9777 | -0.010238
72 |  | 0.25447 | 13.2441 | 4187 | 0.01243 | 6.9076 | 6.92 | -0.823 | 80.4481 | 980.2218 | -0.01023
73 |  | 0.25447 | 13.2339 | 4187 | 0.012421 | 6.92 | 6.9324 | -0.823 | 80.5103 | 993.4556 | -0.010222
74 |  | 0.25447 | 13.2236 | 4187 | 0.012411 | 6.9324 | 6.9448 | -0.823 | 80.5725 | 1006.6793 | -0.010214
75 |  | 0.25447 | 13.2134 | 4187 | 0.012402 | 6.9448 | 6.9572 | -0.823 | 80.6348 | 1019.8927 | -0.010207
76 |  | 0.25447 | 13.2032 | 4187 | 0.012392 | 6.9572 | 6.9696 | -0.823 | 80.6971 | 1033.0959 | -0.010199
77 |  | 0.25447 | 13.193 | 4187 | 0.012382 | 6.9696 | 6.982 | -0.823 | 80.7595 | 1046.2889 | -0.010191
78 |  | 0.25447 | 13.1828 | 4187 | 0.012373 | 6.982 | 6.9944 | -0.823 | 80.8219 | 1059.4718 | -0.010183
79 |  | 0.25447 | 13.1726 | 4187 | 0.012363 | 6.9944 | 7.0067 | -0.823 | 80.8844 | 1072.6444 | -0.010175
80 |  | 0.25447 | 13.1625 | 4187 | 0.012354 | 7.0067 | 7.0191 | -0.823 | 80.9469 | 1085.8069 | -0.010167
81 |  | 0.25447 | 13.1523 | 4187 | 0.012344 | 7.0191 | 7.0314 | -0.823 | 81.0095 | 1098.9592 | -0.010159
82 |  | 0.25447 | 13.1421 | 4187 | 0.012335 | 7.0314 | 7.0438 | -0.823 | 81.0721 | 1112.1013 | -0.010151
83 |  | 0.25447 | 13.132 | 4187 | 0.012325 | 7.0438 | 7.0561 | -0.823 | 81.1348 | 1125.2333 | -0.010144
84 |  | 0.25447 | 13.1219 | 4187 | 0.012316 | 7.0561 | 7.0684 | -0.823 | 81.1975 | 1138.3552 | -0.010136
85 |  | 0.25447 | 13.1117 | 4187 | 0.012306 | 7.0684 | 7.0807 | -0.823 | 81.2603 | 1151.4669 | -0.010128
86 |  | 0.25447 | 13.1016 | 4187 | 0.012297 | 7.0807 | 7.093 | -0.823 | 81.3231 | 1164.5685 | -0.01012
87 |  | 0.25447 | 13.0915 | 4187 | 0.012287 | 7.093 | 7.1053 | -0.823 | 81.386 | 1177.6599 | -0.010112
88 |  | 0.25447 | 13.0814 | 4187 | 0.012278 | 7.1053 | 7.1176 | -0.823 | 81.4489 | 1190.7413 | -0.010105
89 |  | 0.25447 | 13.0713 | 4187 | 0.012268 | 7.1176 | 7.1299 | -0.823 | 81.5118 | 1203.8125 | -0.010097
90 |  | 0.25447 | 13.0612 | 4187 | 0.012259 | 7.1299 | 7.1421 | -0.823 | 81.5749 | 1216.8737 | -0.010089
91 |  | 0.25447 | 13.0511 | 4187 | 0.012249 | 7.1421 | 7.1544 | -0.823 | 81.6379 | 1229.9248 | -0.010081
92 |  | 0.25447 | 13.041 | 4187 | 0.01224 | 7.1544 | 7.1666 | -0.823 | 81.701 | 1242.9658 | -0.010073
93 |  | 0.25447 | 13.0309 | 4187 | 0.01223 | 7.1666 | 7.1788 | -0.823 | 81.7642 | 1255.9967 | -0.010066
94 |  | 0.25447 | 13.0208 | 4187 | 0.012221 | 7.1788 | 7.191 | -0.823 | 81.8274 | 1269.0175 | -0.010058
95 |  | 0.25447 | 13.0108 | 4187 | 0.012211 | 7.191 | 7.2033 | -0.823 | 81.8906 | 1282.0283 | -0.01005
96 |  | 0.25447 | 13.0007 | 4187 | 0.012202 | 7.2033 | 7.2155 | -0.823 | 81.9539 | 1295.029 | -0.010042
97 |  | 0.25447 | 12.9907 | 4187 | 0.012193 | 7.2155 | 7.2277 | -0.823 | 82.0173 | 1308.0197 | -0.010034
98 |  | 0.25447 | 12.9807 | 4187 | 0.012183 | 7.2277 | 7.2398 | -0.823 | 82.0807 | 1321.0004 | -0.010027
99 |  | 0.25447 | 12.9706 | 4187 | 0.012174 | 7.2398 | 7.252 | -0.823 | 82.1442 | 1333.971 | -0.010019
100 |  | 0.25447 | 12.9606 | 4187 | 0.012164 | 7.252 | 7.2642 | -0.823 | 82.2077 | 1346.9316 | -0.010011
101 |  | 0.25447 | 12.9506 | 4187 | 0.012155 | 7.2642 | 7.2763 | -0.823 | 82.2712 | 1359.8822 | -0.010004
102 |  | 0.25447 | 12.9406 | 4187 | 0.012146 | 7.2763 | 7.2885 | -0.823 | 82.3348 | 1372.8228 | -0.0099958
103 |  | 0.25447 | 12.9306 | 4187 | 0.012136 | 7.2885 | 7.3006 | -0.823 | 82.3985 | 1385.7534 | -0.0099881
104 |  | 0.25447 | 12.9206 | 4187 | 0.012127 | 7.3006 | 7.3127 | -0.823 | 82.4621 | 1398.6741 | -0.0099804
105 |  | 0.25447 | 12.9106 | 4187 | 0.012117 | 7.3127 | 7.3249 | -0.823 | 82.5259 | 1411.5847 | -0.0099726
106 |  | 0.25447 | 12.9007 | 4187 | 0.012108 | 7.3249 | 7.337 | -0.823 | 82.5897 | 1424.4854 | -0.0099649
107 |  | 0.25447 | 12.8907 | 4187 | 0.012099 | 7.337 | 7.3491 | -0.823 | 82.6535 | 1437.3761 | -0.0099572
108 |  | 0.25447 | 12.8807 | 4187 | 0.012089 | 7.3491 | 7.3612 | -0.823 | 82.7174 | 1450.2568 | -0.0099496
109 |  | 0.25447 | 12.8708 | 4187 | 0.01208 | 7.3612 | 7.3732 | -0.823 | 82.7814 | 1463.1276 | -0.0099419
110 |  | 0.25447 | 12.8608 | 4187 | 0.012071 | 7.3732 | 7.3853 | -0.823 | 82.8454 | 1475.9884 | -0.0099342
111 |  | 0.25447 | 12.8509 | 4187 | 0.012061 | 7.3853 | 7.3974 | -0.823 | 82.9094 | 1488.8393 | -0.0099265
112 |  | 0.25447 | 12.841 | 4187 | 0.012052 | 7.3974 | 7.4094 | -0.823 | 82.9735 | 1501.6803 | -0.0099188
113 |  | 0.25447 | 12.8311 | 4187 | 0.012043 | 7.4094 | 7.4215 | -0.823 | 83.0376 | 1514.5114 | -0.0099112
114 |  | 0.25447 | 12.8212 | 4187 | 0.012033 | 7.4215 | 7.4335 | -0.823 | 83.1018 | 1527.3326 | -0.0099035
115 |  | 0.25447 | 12.8113 | 4187 | 0.012024 | 7.4335 | 7.4455 | -0.823 | 83.1661 | 1540.1438 | -0.0098959
116 |  | 0.25447 | 12.8014 | 4187 | 0.012015 | 7.4455 | 7.4575 | -0.823 | 83.2304 | 1552.9452 | -0.0098882
117 |  | 0.25447 | 12.7915 | 4187 | 0.012006 | 7.4575 | 7.4695 | -0.823 | 83.2947 | 1565.7366 | -0.0098806
118 |  | 0.25447 | 12.7816 | 4187 | 0.011996 | 7.4695 | 7.4815 | -0.823 | 83.3591 | 1578.5182 | -0.009873
119 |  | 0.25447 | 12.7717 | 4187 | 0.011987 | 7.4815 | 7.4935 | -0.823 | 83.4235 | 1591.29 | -0.0098653
120 |  | 0.25447 | 12.7619 | 4187 | 0.011978 | 7.4935 | 7.5055 | -0.823 | 83.488 | 1604.0518 | -0.0098577
121 |  | 0.25447 | 12.752 | 4187 | 0.011969 | 7.5055 | 7.5175 | -0.823 | 83.5526 | 1616.8038 | -0.0098501
122 |  | 0.25447 | 12.7421 | 4187 | 0.011959 | 7.5175 | 7.5294 | -0.823 | 83.6171 | 1629.5459 | -0.0098425
123 |  | 0.25447 | 12.7323 | 4187 | 0.01195 | 7.5294 | 7.5414 | -0.823 | 83.6818 | 1642.2782 | -0.0098349
124 |  | 0.25447 | 12.7225 | 4187 | 0.011941 | 7.5414 | 7.5533 | -0.823 | 83.7465 | 1655.0007 | -0.0098273
125 |  | 0.25447 | 12.7126 | 4187 | 0.011932 | 7.5533 | 7.5652 | -0.823 | 83.8112 | 1667.7134 | -0.0098197
126 |  | 0.25447 | 12.7028 | 4187 | 0.011922 | 7.5652 | 7.5772 | -0.823 | 83.876 | 1680.4162 | -0.0098121
127 |  | 0.25447 | 12.693 | 4187 | 0.011913 | 7.5772 | 7.5891 | -0.823 | 83.9408 | 1693.1092 | -0.0098045
128 |  | 0.25447 | 12.6832 | 4187 | 0.011904 | 7.5891 | 7.601 | -0.823 | 84.0057 | 1705.7924 | -0.009797
129 |  | 0.25447 | 12.6734 | 4187 | 0.011895 | 7.601 | 7.6129 | -0.823 | 84.0707 | 1718.4658 | -0.0097894
130 |  | 0.25447 | 12.6636 | 4187 | 0.011886 | 7.6129 | 7.6248 | -0.823 | 84.1357 | 1731.1294 | -0.0097818
131 |  | 0.25447 | 12.6538 | 4187 | 0.011876 | 7.6248 | 7.6366 | -0.823 | 84.2007 | 1743.7832 | -0.0097743
132 |  | 0.25447 | 12.6441 | 4187 | 0.011867 | 7.6366 | 7.6485 | -0.823 | 84.2658 | 1756.4273 | -0.0097667
133 |  | 0.25447 | 12.6343 | 4187 | 0.011858 | 7.6485 | 7.6604 | -0.823 | 84.3309 | 1769.0616 | -0.0097592
134 |  | 0.25447 | 12.6245 | 4187 | 0.011849 | 7.6604 | 7.6722 | -0.823 | 84.3961 | 1781.6861 | -0.0097516
135 |  | 0.25447 | 12.6148 | 4187 | 0.01184 | 7.6722 | 7.6841 | -0.823 | 84.4614 | 1794.3009 | -0.0097441
136 |  | 0.25447 | 12.605 | 4187 | 0.011831 | 7.6841 | 7.6959 | -0.823 | 84.5267 | 1806.906 | -0.0097366
137 |  | 0.25447 | 12.5953 | 4187 | 0.011821 | 7.6959 | 7.7077 | -0.823 | 84.592 | 1819.5013 | -0.0097291
138 |  | 0.25447 | 12.5856 | 4187 | 0.011812 | 7.7077 | 7.7195 | -0.823 | 84.6574 | 1832.0868 | -0.0097216
139 |  | 0.25447 | 12.5759 | 4187 | 0.011803 | 7.7195 | 7.7313 | -0.823 | 84.7228 | 1844.6627 | -0.009714
140 |  | 0.25447 | 12.5661 | 4187 | 0.011794 | 7.7313 | 7.7431 | -0.823 | 84.7883 | 1857.2288 | -0.0097065
141 |  | 0.25447 | 12.5564 | 4187 | 0.011785 | 7.7431 | 7.7549 | -0.823 | 84.8539 | 1869.7853 | -0.009699
142 |  | 0.25447 | 12.5467 | 4187 | 0.011776 | 7.7549 | 7.7667 | -0.823 | 84.9195 | 1882.332 | -0.0096916
143 |  | 0.25447 | 12.537 | 4187 | 0.011767 | 7.7667 | 7.7784 | -0.823 | 84.9851 | 1894.869 | -0.0096841
144 |  | 0.25447 | 12.5274 | 4187 | 0.011758 | 7.7784 | 7.7902 | -0.823 | 85.0508 | 1907.3964 | -0.0096766
145 |  | 0.25447 | 12.5177 | 4187 | 0.011749 | 7.7902 | 7.802 | -0.823 | 85.1165 | 1919.9141 | -0.0096691
146 |  | 0.25447 | 12.508 | 4187 | 0.01174 | 7.802 | 7.8137 | -0.823 | 85.1823 | 1932.4221 | -0.0096616
147 |  | 0.25447 | 12.4983 | 4187 | 0.01173 | 7.8137 | 7.8254 | -0.823 | 85.2482 | 1944.9204 | -0.0096542
148 |  | 0.25447 | 12.4887 | 4187 | 0.011721 | 7.8254 | 7.8371 | -0.823 | 85.3141 | 1957.4091 | -0.0096467
149 |  | 0.25447 | 12.479 | 4187 | 0.011712 | 7.8371 | 7.8489 | -0.823 | 85.38 | 1969.8882 | -0.0096393
150 |  | 0.25447 | 12.4694 | 4187 | 0.011703 | 7.8489 | 7.8606 | -0.823 | 85.446 | 1982.3576 | -0.0096318
151 |  | 0.25447 | 12.4598 | 4187 | 0.011694 | 7.8606 | 7.8723 | -0.823 | 85.5121 | 1994.8173 | -0.0096244
152 |  | 0.25447 | 12.4502 | 4187 | 0.011685 | 7.8723 | 7.8839 | -0.823 | 85.5782 | 2007.2675 | -0.0096169
153 |  | 0.25447 | 12.4405 | 4187 | 0.011676 | 7.8839 | 7.8956 | -0.823 | 85.6444 | 2019.708 | -0.0096095
154 |  | 0.25447 | 12.4309 | 4187 | 0.011667 | 7.8956 | 7.9073 | -0.823 | 85.7106 | 2032.139 | -0.0096021
155 |  | 0.25447 | 12.4213 | 4187 | 0.011658 | 7.9073 | 7.9189 | -0.823 | 85.7768 | 2044.5603 | -0.0095947
156 |  | 0.25447 | 12.4117 | 4187 | 0.011649 | 7.9189 | 7.9306 | -0.823 | 85.8431 | 2056.972 | -0.0095873
157 |  | 0.25447 | 12.4021 | 4187 | 0.01164 | 7.9306 | 7.9422 | -0.823 | 85.9095 | 2069.3742 | -0.0095799
158 |  | 0.25447 | 12.3926 | 4187 | 0.011631 | 7.9422 | 7.9539 | -0.823 | 85.9759 | 2081.7667 | -0.0095725
159 |  | 0.25447 | 12.383 | 4187 | 0.011622 | 7.9539 | 7.9655 | -0.823 | 86.0424 | 2094.1497 | -0.0095651
160 |  | 0.25447 | 12.3734 | 4187 | 0.011613 | 7.9655 | 7.9771 | -0.823 | 86.1089 | 2106.5231 | -0.0095577
161 |  | 0.25447 | 12.3639 | 4187 | 0.011604 | 7.9771 | 7.9887 | -0.823 | 86.1754 | 2118.887 | -0.0095503
162 |  | 0.25447 | 12.3543 | 4187 | 0.011595 | 7.9887 | 8.0003 | -0.823 | 86.2421 | 2131.2413 | -0.0095429
163 |  | 0.25447 | 12.3448 | 4187 | 0.011586 | 8.0003 | 8.0119 | -0.823 | 86.3087 | 2143.5861 | -0.0095356
164 |  | 0.25447 | 12.3352 | 4187 | 0.011577 | 8.0119 | 8.0235 | -0.823 | 86.3754 | 2155.9213 | -0.0095282
165 |  | 0.25447 | 12.3257 | 4187 | 0.011568 | 8.0235 | 8.035 | -0.823 | 86.4422 | 2168.247 | -0.0095208
166 |  | 0.25447 | 12.3162 | 4187 | 0.011559 | 8.035 | 8.0466 | -0.823 | 86.509 | 2180.5632 | -0.0095135
167 |  | 0.25447 | 12.3067 | 4187 | 0.011551 | 8.0466 | 8.0581 | -0.823 | 86.5759 | 2192.8699 | -0.0095061
168 |  | 0.25447 | 12.2972 | 4187 | 0.011542 | 8.0581 | 8.0697 | -0.823 | 86.6428 | 2205.1671 | -0.0094988
169 |  | 0.25447 | 12.2877 | 4187 | 0.011533 | 8.0697 | 8.0812 | -0.823 | 86.7098 | 2217.4547 | -0.0094914
170 |  | 0.25447 | 12.2782 | 4187 | 0.011524 | 8.0812 | 8.0927 | -0.823 | 86.7768 | 2229.7329 | -0.0094841
171 |  | 0.25447 | 12.2687 | 4187 | 0.011515 | 8.0927 | 8.1043 | -0.823 | 86.8439 | 2242.0016 | -0.0094768
172 |  | 0.25447 | 12.2592 | 4187 | 0.011506 | 8.1043 | 8.1158 | -0.823 | 86.9111 | 2254.2608 | -0.0094695
173 |  | 0.25447 | 12.2497 | 4187 | 0.011497 | 8.1158 | 8.1273 | -0.823 | 86.9782 | 2266.5106 | -0.0094622
174 |  | 0.25447 | 12.2403 | 4187 | 0.011488 | 8.1273 | 8.1387 | -0.823 | 87.0455 | 2278.7509 | -0.0094548
175 |  | 0.25447 | 12.2308 | 4187 | 0.011479 | 8.1387 | 8.1502 | -0.823 | 87.1128 | 2290.9817 | -0.0094475
176 |  | 0.25447 | 12.2214 | 4187 | 0.011471 | 8.1502 | 8.1617 | -0.823 | 87.1801 | 2303.2031 | -0.0094402
177 |  | 0.25447 | 12.2119 | 4187 | 0.011462 | 8.1617 | 8.1732 | -0.823 | 87.2475 | 2315.415 | -0.0094329
178 |  | 0.25447 | 12.2025 | 4187 | 0.011453 | 8.1732 | 8.1846 | -0.823 | 87.315 | 2327.6176 | -0.0094257
179 |  | 0.25447 | 12.1931 | 4187 | 0.011444 | 8.1846 | 8.1961 | -0.823 | 87.3825 | 2339.8106 | -0.0094184
180 |  | 0.25447 | 12.1837 | 4187 | 0.011435 | 8.1961 | 8.2075 | -0.823 | 87.45 | 2351.9943 | -0.0094111
181 |  | 0.25447 | 12.1743 | 4187 | 0.011426 | 8.2075 | 8.2189 | -0.823 | 87.5176 | 2364.1686 | -0.0094038
182 |  | 0.25447 | 12.1649 | 4187 | 0.011417 | 8.2189 | 8.2303 | -0.823 | 87.5853 | 2376.3334 | -0.0093966
183 |  | 0.25447 | 12.1555 | 4187 | 0.011409 | 8.2303 | 8.2417 | -0.823 | 87.653 | 2388.4889 | -0.0093893
184 |  | 0.25447 | 12.1461 | 4187 | 0.0114 | 8.2417 | 8.2531 | -0.823 | 87.7207 | 2400.6349 | -0.0093821
185 |  | 0.25447 | 12.1367 | 4187 | 0.011391 | 8.2531 | 8.2645 | -0.823 | 87.7885 | 2412.7716 | -0.0093748
186 |  | 0.25447 | 12.1273 | 4187 | 0.011382 | 8.2645 | 8.2759 | -0.823 | 87.8564 | 2424.8989 | -0.0093676
187 |  | 0.25447 | 12.1179 | 4187 | 0.011373 | 8.2759 | 8.2873 | -0.823 | 87.9243 | 2437.0169 | -0.0093603
188 |  | 0.25447 | 12.1086 | 4187 | 0.011365 | 8.2873 | 8.2987 | -0.823 | 87.9923 | 2449.1255 | -0.0093531
189 |  | 0.25447 | 12.0992 | 4187 | 0.011356 | 8.2987 | 8.31 | -0.823 | 88.0603 | 2461.2247 | -0.0093459
190 |  | 0.25447 | 12.0899 | 4187 | 0.011347 | 8.31 | 8.3214 | -0.823 | 88.1284 | 2473.3146 | -0.0093387
191 |  | 0.25447 | 12.0805 | 4187 | 0.011338 | 8.3214 | 8.3327 | -0.823 | 88.1965 | 2485.3951 | -0.0093315
192 |  | 0.25447 | 12.0712 | 4187 | 0.01133 | 8.3327 | 8.344 | -0.823 | 88.2647 | 2497.4663 | -0.0093242
193 |  | 0.25447 | 12.0619 | 4187 | 0.011321 | 8.344 | 8.3553 | -0.823 | 88.3329 | 2509.5282 | -0.009317
194 |  | 0.25447 | 12.0526 | 4187 | 0.011312 | 8.3553 | 8.3667 | -0.823 | 88.4012 | 2521.5808 | -0.0093098
195 |  | 0.25447 | 12.0433 | 4187 | 0.011303 | 8.3667 | 8.378 | -0.823 | 88.4695 | 2533.624 | -0.0093027
196 |  | 0.25447 | 12.034 | 4187 | 0.011295 | 8.378 | 8.3893 | -0.823 | 88.5379 | 2545.658 | -0.0092955
197 |  | 0.25447 | 12.0247 | 4187 | 0.011286 | 8.3893 | 8.4005 | -0.823 | 88.6064 | 2557.6827 | -0.0092883
198 |  | 0.25447 | 12.0154 | 4187 | 0.011277 | 8.4005 | 8.4118 | -0.823 | 88.6749 | 2569.698 | -0.0092811
199 |  | 0.25447 | 12.0061 | 4187 | 0.011268 | 8.4118 | 8.4231 | -0.823 | 88.7434 | 2581.7041 | -0.0092739
200 |  | 0.25447 | 11.9968 | 4187 | 0.01126 | 8.4231 | 8.4343 | -0.823 | 88.812 | 2593.701 | -0.0092668
201 |  | 0.25447 | 11.9876 | 4187 | 0.011251 | 8.4343 | 8.4456 | -0.823 | 88.8807 | 2605.6885 | -0.0092596
202 |  | 0.25447 | 11.9783 | 4187 | 0.011242 | 8.4456 | 8.4568 | -0.823 | 88.9494 | 2617.6668 | -0.0092525
203 |  | 0.25447 | 11.969 | 4187 | 0.011234 | 8.4568 | 8.4681 | -0.823 | 89.0181 | 2629.6358 | -0.0092453
204 |  | 0.25447 | 11.9598 | 4187 | 0.011225 | 8.4681 | 8.4793 | -0.823 | 89.0869 | 2641.5956 | -0.0092382
205 |  | 0.25447 | 11.9506 | 4187 | 0.011216 | 8.4793 | 8.4905 | -0.823 | 89.1558 | 2653.5462 | -0.009231
206 |  | 0.25447 | 11.9413 | 4187 | 0.011208 | 8.4905 | 8.5017 | -0.823 | 89.2247 | 2665.4875 | -0.0092239
207 |  | 0.25447 | 11.9321 | 4187 | 0.011199 | 8.5017 | 8.5129 | -0.823 | 89.2937 | 2677.4196 | -0.0092168
208 |  | 0.25447 | 11.9229 | 4187 | 0.01119 | 8.5129 | 8.5241 | -0.823 | 89.3627 | 2689.3425 | -0.0092097
209 |  | 0.25447 | 11.9137 | 4187 | 0.011182 | 8.5241 | 8.5353 | -0.823 | 89.4318 | 2701.2562 | -0.0092026
210 |  | 0.25447 | 11.9045 | 4187 | 0.011173 | 8.5353 | 8.5465 | -0.823 | 89.501 | 2713.1607 | -0.0091954
211 |  | 0.25447 | 11.8953 | 4187 | 0.011164 | 8.5465 | 8.5576 | -0.823 | 89.5701 | 2725.0559 | -0.0091883
212 |  | 0.25447 | 11.8861 | 4187 | 0.011156 | 8.5576 | 8.5688 | -0.823 | 89.6394 | 2736.942 | -0.0091812
213 |  | 0.25447 | 11.8769 | 4187 | 0.011147 | 8.5688 | 8.5799 | -0.823 | 89.7087 | 2748.8189 | -0.0091742
214 |  | 0.25447 | 11.8677 | 4187 | 0.011139 | 8.5799 | 8.5911 | -0.823 | 89.778 | 2760.6867 | -0.0091671
215 |  | 0.25447 | 11.8586 | 4187 | 0.01113 | 8.5911 | 8.6022 | -0.823 | 89.8474 | 2772.5452 | -0.00916
216 |  | 0.25447 | 11.8494 | 4187 | 0.011121 | 8.6022 | 8.6133 | -0.823 | 89.9169 | 2784.3946 | -0.0091529
217 |  | 0.25447 | 11.8403 | 4187 | 0.011113 | 8.6133 | 8.6244 | -0.823 | 89.9864 | 2796.2349 | -0.0091458
218 |  | 0.25447 | 11.8311 | 4187 | 0.011104 | 8.6244 | 8.6355 | -0.823 | 90.0559 | 2808.066 | -0.0091388
219 |  | 0.25447 | 11.822 | 4187 | 0.011096 | 8.6355 | 8.6466 | -0.823 | 90.1256 | 2819.888 | -0.0091317
220 |  | 0.25447 | 11.8128 | 4187 | 0.011087 | 8.6466 | 8.6577 | -0.823 | 90.1952 | 2831.7008 | -0.0091247
221 |  | 0.25447 | 11.8037 | 4187 | 0.011078 | 8.6577 | 8.6688 | -0.823 | 90.265 | 2843.5045 | -0.0091176
222 |  | 0.25447 | 11.7946 | 4187 | 0.01107 | 8.6688 | 8.6799 | -0.823 | 90.3347 | 2855.2991 | -0.0091106
223 |  | 0.25447 | 11.7855 | 4187 | 0.011061 | 8.6799 | 8.6909 | -0.823 | 90.4046 | 2867.0846 | -0.0091035
224 |  | 0.25447 | 11.7764 | 4187 | 0.011053 | 8.6909 | 8.702 | -0.823 | 90.4745 | 2878.861 | -0.0090965
225 |  | 0.25447 | 11.7673 | 4187 | 0.011044 | 8.702 | 8.713 | -0.823 | 90.5444 | 2890.6283 | -0.0090895
226 |  | 0.25447 | 11.7582 | 4187 | 0.011036 | 8.713 | 8.7241 | -0.823 | 90.6144 | 2902.3865 | -0.0090825
227 |  | 0.25447 | 11.7491 | 4187 | 0.011027 | 8.7241 | 8.7351 | -0.823 | 90.6844 | 2914.1356 | -0.0090754
228 |  | 0.25447 | 11.74 | 4187 | 0.011019 | 8.7351 | 8.7461 | -0.823 | 90.7545 | 2925.8756 | -0.0090684
229 |  | 0.25447 | 11.731 | 4187 | 0.01101 | 8.7461 | 8.7571 | -0.823 | 90.8247 | 2937.6066 | -0.0090614
230 |  | 0.25447 | 11.7219 | 4187 | 0.011002 | 8.7571 | 8.7681 | -0.823 | 90.8949 | 2949.3285 | -0.0090544
231 |  | 0.25447 | 11.7129 | 4187 | 0.010993 | 8.7681 | 8.7791 | -0.823 | 90.9652 | 2961.0414 | -0.0090474
232 |  | 0.25447 | 11.7038 | 4187 | 0.010985 | 8.7791 | 8.7901 | -0.823 | 91.0355 | 2972.7452 | -0.0090404
233 |  | 0.25447 | 11.6948 | 4187 | 0.010976 | 8.7901 | 8.8011 | -0.823 | 91.1059 | 2984.4399 | -0.0090335
234 |  | 0.25447 | 11.6857 | 4187 | 0.010968 | 8.8011 | 8.812 | -0.823 | 91.1763 | 2996.1257 | -0.0090265
235 |  | 0.25447 | 11.6767 | 4187 | 0.010959 | 8.812 | 8.823 | -0.823 | 91.2468 | 3007.8024 | -0.0090195
236 |  | 0.25447 | 11.6677 | 4187 | 0.010951 | 8.823 | 8.834 | -0.823 | 91.3173 | 3019.4701 | -0.0090125

## 32
|  |  | buis | verlies W/M | L /°C/sec
diam | wandikte |  | inhoud l/m |  | W/M
32 | 2.9 | 3.1416 | 0.53913 | 19.1554 | 4187
[8 empty] | J/sec/mtr | aantal mtr. | verlies
|  | buis | verlies W/M | L /°C/sec | verlies temp | begintemp | eindtemp | verlies | bij 1°C | totaal J/sec
|  | inhoud L |  | W/M | °C per M | °C | °C | per m°C | daling | aantal mtr
1 | 32 | 0.53913 | 19.1554 | 4187 | 0.0084859 | 6 | 6.0085 | -1.1268 | 117.843 | 19.1554 | -0.0095618
2 |  | 0.53913 | 19.1459 | 4187 | 0.0084816 | 6.0085 | 6.017 | -1.1268 | 117.9018 | 38.3013 | -0.009557
3 |  | 0.53913 | 19.1363 | 4187 | 0.0084774 | 6.017 | 6.0254 | -1.1268 | 117.9607 | 57.4376 | -0.0095522
4 |  | 0.53913 | 19.1268 | 4187 | 0.0084732 | 6.0254 | 6.0339 | -1.1268 | 118.0196 | 76.5643 | -0.0095475
5 |  | 0.53913 | 19.1172 | 4187 | 0.0084689 | 6.0339 | 6.0424 | -1.1268 | 118.0786 | 95.6815 | -0.0095427
6 |  | 0.53913 | 19.1077 | 4187 | 0.0084647 | 6.0424 | 6.0509 | -1.1268 | 118.1375 | 114.7892 | -0.0095379
7 |  | 0.53913 | 19.0981 | 4187 | 0.0084605 | 6.0509 | 6.0593 | -1.1268 | 118.1965 | 133.8873 | -0.0095332
8 |  | 0.53913 | 19.0886 | 4187 | 0.0084563 | 6.0593 | 6.0678 | -1.1268 | 118.2556 | 152.9759 | -0.0095284
9 |  | 0.53913 | 19.0791 | 4187 | 0.008452 | 6.0678 | 6.0762 | -1.1268 | 118.3146 | 172.055 | -0.0095237
10 |  | 0.53913 | 19.0695 | 4187 | 0.0084478 | 6.0762 | 6.0847 | -1.1268 | 118.3737 | 191.1245 | -0.0095189
11 |  | 0.53913 | 19.06 | 4187 | 0.0084436 | 6.0847 | 6.0931 | -1.1268 | 118.4328 | 210.1845 | -0.0095142
12 |  | 0.53913 | 19.0505 | 4187 | 0.0084394 | 6.0931 | 6.1016 | -1.1268 | 118.492 | 229.235 | -0.0095094
13 |  | 0.53913 | 19.041 | 4187 | 0.0084352 | 6.1016 | 6.11 | -1.1268 | 118.5512 | 248.276 | -0.0095047
14 |  | 0.53913 | 19.0315 | 4187 | 0.008431 | 6.11 | 6.1184 | -1.1268 | 118.6104 | 267.3075 | -0.0094999
15 |  | 0.53913 | 19.022 | 4187 | 0.0084268 | 6.1184 | 6.1268 | -1.1268 | 118.6696 | 286.3295 | -0.0094952
16 |  | 0.53913 | 19.0125 | 4187 | 0.0084226 | 6.1268 | 6.1353 | -1.1268 | 118.7289 | 305.342 | -0.0094904
17 |  | 0.53913 | 19.003 | 4187 | 0.0084183 | 6.1353 | 6.1437 | -1.1268 | 118.7882 | 324.345 | -0.0094857
18 |  | 0.53913 | 18.9935 | 4187 | 0.0084141 | 6.1437 | 6.1521 | -1.1268 | 118.8475 | 343.3385 | -0.009481
19 |  | 0.53913 | 18.984 | 4187 | 0.0084099 | 6.1521 | 6.1605 | -1.1268 | 118.9068 | 362.3226 | -0.0094762
20 |  | 0.53913 | 18.9746 | 4187 | 0.0084057 | 6.1605 | 6.1689 | -1.1268 | 118.9662 | 381.2971 | -0.0094715
21 |  | 0.53913 | 18.9651 | 4187 | 0.0084016 | 6.1689 | 6.1773 | -1.1268 | 119.0256 | 400.2622 | -0.0094668
22 |  | 0.53913 | 18.9556 | 4187 | 0.0083974 | 6.1773 | 6.1857 | -1.1268 | 119.0851 | 419.2178 | -0.0094621
23 |  | 0.53913 | 18.9462 | 4187 | 0.0083932 | 6.1857 | 6.1941 | -1.1268 | 119.1446 | 438.164 | -0.0094573
24 |  | 0.53913 | 18.9367 | 4187 | 0.008389 | 6.1941 | 6.2025 | -1.1268 | 119.2041 | 457.1007 | -0.0094526
25 |  | 0.53913 | 18.9273 | 4187 | 0.0083848 | 6.2025 | 6.2109 | -1.1268 | 119.2636 | 476.0279 | -0.0094479
26 |  | 0.53913 | 18.9178 | 4187 | 0.0083806 | 6.2109 | 6.2193 | -1.1268 | 119.3232 | 494.9457 | -0.0094432
27 |  | 0.53913 | 18.9084 | 4187 | 0.0083764 | 6.2193 | 6.2276 | -1.1268 | 119.3827 | 513.8541 | -0.0094385
28 |  | 0.53913 | 18.8989 | 4187 | 0.0083722 | 6.2276 | 6.236 | -1.1268 | 119.4424 | 532.753 | -0.0094338
29 |  | 0.53913 | 18.8895 | 4187 | 0.0083681 | 6.236 | 6.2444 | -1.1268 | 119.502 | 551.6425 | -0.009429
30 |  | 0.53913 | 18.8801 | 4187 | 0.0083639 | 6.2444 | 6.2527 | -1.1268 | 119.5617 | 570.5226 | -0.0094243
31 |  | 0.53913 | 18.8706 | 4187 | 0.0083597 | 6.2527 | 6.2611 | -1.1268 | 119.6214 | 589.3932 | -0.0094196
32 |  | 0.53913 | 18.8612 | 4187 | 0.0083555 | 6.2611 | 6.2695 | -1.1268 | 119.6812 | 608.2544 | -0.0094149
33 |  | 0.53913 | 18.8518 | 4187 | 0.0083514 | 6.2695 | 6.2778 | -1.1268 | 119.7409 | 627.1062 | -0.0094102
34 |  | 0.53913 | 18.8424 | 4187 | 0.0083472 | 6.2778 | 6.2862 | -1.1268 | 119.8007 | 645.9486 | -0.0094055
35 |  | 0.53913 | 18.833 | 4187 | 0.008343 | 6.2862 | 6.2945 | -1.1268 | 119.8606 | 664.7816 | -0.0094008
36 |  | 0.53913 | 18.8236 | 4187 | 0.0083389 | 6.2945 | 6.3028 | -1.1268 | 119.9204 | 683.6052 | -0.0093961
37 |  | 0.53913 | 18.8142 | 4187 | 0.0083347 | 6.3028 | 6.3112 | -1.1268 | 119.9803 | 702.4194 | -0.0093915
38 |  | 0.53913 | 18.8048 | 4187 | 0.0083305 | 6.3112 | 6.3195 | -1.1268 | 120.0402 | 721.2242 | -0.0093868
39 |  | 0.53913 | 18.7954 | 4187 | 0.0083264 | 6.3195 | 6.3278 | -1.1268 | 120.1002 | 740.0196 | -0.0093821
40 |  | 0.53913 | 18.786 | 4187 | 0.0083222 | 6.3278 | 6.3362 | -1.1268 | 120.1602 | 758.8056 | -0.0093774
41 |  | 0.53913 | 18.7766 | 4187 | 0.0083181 | 6.3362 | 6.3445 | -1.1268 | 120.2202 | 777.5822 | -0.0093727
42 |  | 0.53913 | 18.7673 | 4187 | 0.0083139 | 6.3445 | 6.3528 | -1.1268 | 120.2802 | 796.3495 | -0.009368
43 |  | 0.53913 | 18.7579 | 4187 | 0.0083098 | 6.3528 | 6.3611 | -1.1268 | 120.3403 | 815.1074 | -0.0093634
44 |  | 0.53913 | 18.7485 | 4187 | 0.0083056 | 6.3611 | 6.3694 | -1.1268 | 120.4004 | 833.856 | -0.0093587
45 |  | 0.53913 | 18.7392 | 4187 | 0.0083015 | 6.3694 | 6.3777 | -1.1268 | 120.4605 | 852.5952 | -0.009354
46 |  | 0.53913 | 18.7298 | 4187 | 0.0082973 | 6.3777 | 6.386 | -1.1268 | 120.5207 | 871.325 | -0.0093493
47 |  | 0.53913 | 18.7205 | 4187 | 0.0082932 | 6.386 | 6.3943 | -1.1268 | 120.5809 | 890.0455 | -0.0093447
48 |  | 0.53913 | 18.7111 | 4187 | 0.0082891 | 6.3943 | 6.4026 | -1.1268 | 120.6411 | 908.7566 | -0.00934
49 |  | 0.53913 | 18.7018 | 4187 | 0.0082849 | 6.4026 | 6.4109 | -1.1268 | 120.7013 | 927.4584 | -0.0093354
50 |  | 0.53913 | 18.6925 | 4187 | 0.0082808 | 6.4109 | 6.4191 | -1.1268 | 120.7616 | 946.1509 | -0.0093307
51 |  | 0.53913 | 18.6831 | 4187 | 0.0082766 | 6.4191 | 6.4274 | -1.1268 | 120.8219 | 964.834 | -0.009326
52 |  | 0.53913 | 18.6738 | 4187 | 0.0082725 | 6.4274 | 6.4357 | -1.1268 | 120.8823 | 983.5078 | -0.0093214
53 |  | 0.53913 | 18.6645 | 4187 | 0.0082684 | 6.4357 | 6.444 | -1.1268 | 120.9426 | 1002.1723 | -0.0093167
54 |  | 0.53913 | 18.6552 | 4187 | 0.0082643 | 6.444 | 6.4522 | -1.1268 | 121.003 | 1020.8275 | -0.0093121
55 |  | 0.53913 | 18.6459 | 4187 | 0.0082601 | 6.4522 | 6.4605 | -1.1268 | 121.0635 | 1039.4733 | -0.0093074
56 |  | 0.53913 | 18.6365 | 4187 | 0.008256 | 6.4605 | 6.4687 | -1.1268 | 121.1239 | 1058.1099 | -0.0093028
57 |  | 0.53913 | 18.6272 | 4187 | 0.0082519 | 6.4687 | 6.477 | -1.1268 | 121.1844 | 1076.7371 | -0.0092981
58 |  | 0.53913 | 18.6179 | 4187 | 0.0082478 | 6.477 | 6.4852 | -1.1268 | 121.2449 | 1095.3551 | -0.0092935
59 |  | 0.53913 | 18.6087 | 4187 | 0.0082436 | 6.4852 | 6.4935 | -1.1268 | 121.3055 | 1113.9637 | -0.0092889
60 |  | 0.53913 | 18.5994 | 4187 | 0.0082395 | 6.4935 | 6.5017 | -1.1268 | 121.3661 | 1132.5631 | -0.0092842
61 |  | 0.53913 | 18.5901 | 4187 | 0.0082354 | 6.5017 | 6.51 | -1.1268 | 121.4267 | 1151.1532 | -0.0092796
62 |  | 0.53913 | 18.5808 | 4187 | 0.0082313 | 6.51 | 6.5182 | -1.1268 | 121.4873 | 1169.734 | -0.009275
63 |  | 0.53913 | 18.5715 | 4187 | 0.0082272 | 6.5182 | 6.5264 | -1.1268 | 121.548 | 1188.3055 | -0.0092703
64 |  | 0.53913 | 18.5623 | 4187 | 0.0082231 | 6.5264 | 6.5346 | -1.1268 | 121.6087 | 1206.8677 | -0.0092657
65 |  | 0.53913 | 18.553 | 4187 | 0.008219 | 6.5346 | 6.5429 | -1.1268 | 121.6694 | 1225.4207 | -0.0092611
66 |  | 0.53913 | 18.5437 | 4187 | 0.0082149 | 6.5429 | 6.5511 | -1.1268 | 121.7302 | 1243.9645 | -0.0092564
67 |  | 0.53913 | 18.5345 | 4187 | 0.0082108 | 6.5511 | 6.5593 | -1.1268 | 121.791 | 1262.4989 | -0.0092518
68 |  | 0.53913 | 18.5252 | 4187 | 0.0082067 | 6.5593 | 6.5675 | -1.1268 | 121.8518 | 1281.0242 | -0.0092472
69 |  | 0.53913 | 18.516 | 4187 | 0.0082026 | 6.5675 | 6.5757 | -1.1268 | 121.9127 | 1299.5401 | -0.0092426
70 |  | 0.53913 | 18.5067 | 4187 | 0.0081985 | 6.5757 | 6.5839 | -1.1268 | 121.9736 | 1318.0469 | -0.009238
71 |  | 0.53913 | 18.4975 | 4187 | 0.0081944 | 6.5839 | 6.5921 | -1.1268 | 122.0345 | 1336.5444 | -0.0092334
72 |  | 0.53913 | 18.4883 | 4187 | 0.0081903 | 6.5921 | 6.6003 | -1.1268 | 122.0954 | 1355.0326 | -0.0092288
73 |  | 0.53913 | 18.479 | 4187 | 0.0081862 | 6.6003 | 6.6085 | -1.1268 | 122.1564 | 1373.5116 | -0.0092242
74 |  | 0.53913 | 18.4698 | 4187 | 0.0081821 | 6.6085 | 6.6166 | -1.1268 | 122.2174 | 1391.9815 | -0.0092195
75 |  | 0.53913 | 18.4606 | 4187 | 0.0081781 | 6.6166 | 6.6248 | -1.1268 | 122.2784 | 1410.442 | -0.0092149
76 |  | 0.53913 | 18.4514 | 4187 | 0.008174 | 6.6248 | 6.633 | -1.1268 | 122.3395 | 1428.8934 | -0.0092103
77 |  | 0.53913 | 18.4422 | 4187 | 0.0081699 | 6.633 | 6.6412 | -1.1268 | 122.4006 | 1447.3356 | -0.0092058
78 |  | 0.53913 | 18.433 | 4187 | 0.0081658 | 6.6412 | 6.6493 | -1.1268 | 122.4617 | 1465.7685 | -0.0092012
79 |  | 0.53913 | 18.4238 | 4187 | 0.0081617 | 6.6493 | 6.6575 | -1.1268 | 122.5229 | 1484.1923 | -0.0091966
80 |  | 0.53913 | 18.4146 | 4187 | 0.0081577 | 6.6575 | 6.6657 | -1.1268 | 122.5841 | 1502.6068 | -0.009192
81 |  | 0.53913 | 18.4054 | 4187 | 0.0081536 | 6.6657 | 6.6738 | -1.1268 | 122.6453 | 1521.0122 | -0.0091874
82 |  | 0.53913 | 18.3962 | 4187 | 0.0081495 | 6.6738 | 6.682 | -1.1268 | 122.7066 | 1539.4084 | -0.0091828
83 |  | 0.53913 | 18.387 | 4187 | 0.0081455 | 6.682 | 6.6901 | -1.1268 | 122.7678 | 1557.7954 | -0.0091782
84 |  | 0.53913 | 18.3778 | 4187 | 0.0081414 | 6.6901 | 6.6982 | -1.1268 | 122.8292 | 1576.1732 | -0.0091736
85 |  | 0.53913 | 18.3686 | 4187 | 0.0081373 | 6.6982 | 6.7064 | -1.1268 | 122.8905 | 1594.5419 | -0.0091691
86 |  | 0.53913 | 18.3595 | 4187 | 0.0081333 | 6.7064 | 6.7145 | -1.1268 | 122.9519 | 1612.9013 | -0.0091645
87 |  | 0.53913 | 18.3503 | 4187 | 0.0081292 | 6.7145 | 6.7226 | -1.1268 | 123.0133 | 1631.2516 | -0.0091599
88 |  | 0.53913 | 18.3412 | 4187 | 0.0081251 | 6.7226 | 6.7308 | -1.1268 | 123.0747 | 1649.5928 | -0.0091553
89 |  | 0.53913 | 18.332 | 4187 | 0.0081211 | 6.7308 | 6.7389 | -1.1268 | 123.1362 | 1667.9248 | -0.0091508
90 |  | 0.53913 | 18.3228 | 4187 | 0.008117 | 6.7389 | 6.747 | -1.1268 | 123.1977 | 1686.2476 | -0.0091462
91 |  | 0.53913 | 18.3137 | 4187 | 0.008113 | 6.747 | 6.7551 | -1.1268 | 123.2592 | 1704.5613 | -0.0091416
92 |  | 0.53913 | 18.3046 | 4187 | 0.0081089 | 6.7551 | 6.7632 | -1.1268 | 123.3208 | 1722.8659 | -0.0091371
93 |  | 0.53913 | 18.2954 | 4187 | 0.0081049 | 6.7632 | 6.7713 | -1.1268 | 123.3823 | 1741.1613 | -0.0091325
94 |  | 0.53913 | 18.2863 | 4187 | 0.0081008 | 6.7713 | 6.7794 | -1.1268 | 123.444 | 1759.4476 | -0.0091279
95 |  | 0.53913 | 18.2772 | 4187 | 0.0080968 | 6.7794 | 6.7875 | -1.1268 | 123.5056 | 1777.7248 | -0.0091234
96 |  | 0.53913 | 18.268 | 4187 | 0.0080928 | 6.7875 | 6.7956 | -1.1268 | 123.5673 | 1795.9928 | -0.0091188
97 |  | 0.53913 | 18.2589 | 4187 | 0.0080887 | 6.7956 | 6.8037 | -1.1268 | 123.629 | 1814.2517 | -0.0091143
98 |  | 0.53913 | 18.2498 | 4187 | 0.0080847 | 6.8037 | 6.8118 | -1.1268 | 123.6908 | 1832.5015 | -0.0091097
99 |  | 0.53913 | 18.2407 | 4187 | 0.0080806 | 6.8118 | 6.8199 | -1.1268 | 123.7525 | 1850.7422 | -0.0091052
100 |  | 0.53913 | 18.2316 | 4187 | 0.0080766 | 6.8199 | 6.828 | -1.1268 | 123.8143 | 1868.9738 | -0.0091006
101 |  | 0.53913 | 18.2225 | 4187 | 0.0080726 | 6.828 | 6.836 | -1.1268 | 123.8762 | 1887.1963 | -0.0090961
102 |  | 0.53913 | 18.2134 | 4187 | 0.0080685 | 6.836 | 6.8441 | -1.1268 | 123.938 | 1905.4097 | -0.0090916
103 |  | 0.53913 | 18.2043 | 4187 | 0.0080645 | 6.8441 | 6.8522 | -1.1268 | 123.9999 | 1923.614 | -0.009087
104 |  | 0.53913 | 18.1952 | 4187 | 0.0080605 | 6.8522 | 6.8602 | -1.1268 | 124.0619 | 1941.8092 | -0.0090825
105 |  | 0.53913 | 18.1861 | 4187 | 0.0080565 | 6.8602 | 6.8683 | -1.1268 | 124.1238 | 1959.9953 | -0.0090779
106 |  | 0.53913 | 18.1771 | 4187 | 0.0080525 | 6.8683 | 6.8763 | -1.1268 | 124.1858 | 1978.1724 | -0.0090734
107 |  | 0.53913 | 18.168 | 4187 | 0.0080484 | 6.8763 | 6.8844 | -1.1268 | 124.2478 | 1996.3404 | -0.0090689
108 |  | 0.53913 | 18.1589 | 4187 | 0.0080444 | 6.8844 | 6.8924 | -1.1268 | 124.3099 | 2014.4993 | -0.0090644
109 |  | 0.53913 | 18.1498 | 4187 | 0.0080404 | 6.8924 | 6.9005 | -1.1268 | 124.372 | 2032.6491 | -0.0090598
110 |  | 0.53913 | 18.1408 | 4187 | 0.0080364 | 6.9005 | 6.9085 | -1.1268 | 124.4341 | 2050.7899 | -0.0090553
111 |  | 0.53913 | 18.1317 | 4187 | 0.0080324 | 6.9085 | 6.9165 | -1.1268 | 124.4962 | 2068.9216 | -0.0090508
112 |  | 0.53913 | 18.1227 | 4187 | 0.0080284 | 6.9165 | 6.9246 | -1.1268 | 124.5584 | 2087.0443 | -0.0090463
113 |  | 0.53913 | 18.1136 | 4187 | 0.0080244 | 6.9246 | 6.9326 | -1.1268 | 124.6206 | 2105.1579 | -0.0090418
114 |  | 0.53913 | 18.1046 | 4187 | 0.0080203 | 6.9326 | 6.9406 | -1.1268 | 124.6828 | 2123.2625 | -0.0090372
115 |  | 0.53913 | 18.0956 | 4187 | 0.0080163 | 6.9406 | 6.9486 | -1.1268 | 124.7451 | 2141.3581 | -0.0090327
116 |  | 0.53913 | 18.0865 | 4187 | 0.0080123 | 6.9486 | 6.9566 | -1.1268 | 124.8074 | 2159.4446 | -0.0090282
117 |  | 0.53913 | 18.0775 | 4187 | 0.0080083 | 6.9566 | 6.9646 | -1.1268 | 124.8697 | 2177.5221 | -0.0090237
118 |  | 0.53913 | 18.0685 | 4187 | 0.0080043 | 6.9646 | 6.9726 | -1.1268 | 124.9321 | 2195.5906 | -0.0090192
119 |  | 0.53913 | 18.0595 | 4187 | 0.0080004 | 6.9726 | 6.9806 | -1.1268 | 124.9945 | 2213.65 | -0.0090147
120 |  | 0.53913 | 18.0504 | 4187 | 0.0079964 | 6.9806 | 6.9886 | -1.1268 | 125.0569 | 2231.7005 | -0.0090102
121 |  | 0.53913 | 18.0414 | 4187 | 0.0079924 | 6.9886 | 6.9966 | -1.1268 | 125.1194 | 2249.7419 | -0.0090057
122 |  | 0.53913 | 18.0324 | 4187 | 0.0079884 | 6.9966 | 7.0046 | -1.1268 | 125.1819 | 2267.7743 | -0.0090012
123 |  | 0.53913 | 18.0234 | 4187 | 0.0079844 | 7.0046 | 7.0126 | -1.1268 | 125.2444 | 2285.7977 | -0.0089967
124 |  | 0.53913 | 18.0144 | 4187 | 0.0079804 | 7.0126 | 7.0206 | -1.1268 | 125.3069 | 2303.8122 | -0.0089922
125 |  | 0.53913 | 18.0054 | 4187 | 0.0079764 | 7.0206 | 7.0286 | -1.1268 | 125.3695 | 2321.8176 | -0.0089877
126 |  | 0.53913 | 17.9964 | 4187 | 0.0079724 | 7.0286 | 7.0365 | -1.1268 | 125.4321 | 2339.814 | -0.0089833
127 |  | 0.53913 | 17.9875 | 4187 | 0.0079685 | 7.0365 | 7.0445 | -1.1268 | 125.4948 | 2357.8015 | -0.0089788
128 |  | 0.53913 | 17.9785 | 4187 | 0.0079645 | 7.0445 | 7.0525 | -1.1268 | 125.5574 | 2375.78 | -0.0089743
129 |  | 0.53913 | 17.9695 | 4187 | 0.0079605 | 7.0525 | 7.0604 | -1.1268 | 125.6201 | 2393.7495 | -0.0089698
130 |  | 0.53913 | 17.9605 | 4187 | 0.0079565 | 7.0604 | 7.0684 | -1.1268 | 125.6829 | 2411.71 | -0.0089653
131 |  | 0.53913 | 17.9516 | 4187 | 0.0079526 | 7.0684 | 7.0763 | -1.1268 | 125.7456 | 2429.6616 | -0.0089609
132 |  | 0.53913 | 17.9426 | 4187 | 0.0079486 | 7.0763 | 7.0843 | -1.1268 | 125.8084 | 2447.6042 | -0.0089564
133 |  | 0.53913 | 17.9337 | 4187 | 0.0079446 | 7.0843 | 7.0922 | -1.1268 | 125.8713 | 2465.5378 | -0.0089519
134 |  | 0.53913 | 17.9247 | 4187 | 0.0079407 | 7.0922 | 7.1002 | -1.1268 | 125.9341 | 2483.4625 | -0.0089475
135 |  | 0.53913 | 17.9158 | 4187 | 0.0079367 | 7.1002 | 7.1081 | -1.1268 | 125.997 | 2501.3783 | -0.008943
136 |  | 0.53913 | 17.9068 | 4187 | 0.0079327 | 7.1081 | 7.116 | -1.1268 | 126.06 | 2519.2851 | -0.0089385
137 |  | 0.53913 | 17.8979 | 4187 | 0.0079288 | 7.116 | 7.124 | -1.1268 | 126.1229 | 2537.183 | -0.0089341
138 |  | 0.53913 | 17.8889 | 4187 | 0.0079248 | 7.124 | 7.1319 | -1.1268 | 126.1859 | 2555.0719 | -0.0089296
139 |  | 0.53913 | 17.88 | 4187 | 0.0079209 | 7.1319 | 7.1398 | -1.1268 | 126.2489 | 2572.9519 | -0.0089251
140 |  | 0.53913 | 17.8711 | 4187 | 0.0079169 | 7.1398 | 7.1477 | -1.1268 | 126.312 | 2590.823 | -0.0089207
141 |  | 0.53913 | 17.8622 | 4187 | 0.007913 | 7.1477 | 7.1556 | -1.1268 | 126.3751 | 2608.6852 | -0.0089162
142 |  | 0.53913 | 17.8532 | 4187 | 0.007909 | 7.1556 | 7.1636 | -1.1268 | 126.4382 | 2626.5384 | -0.0089118
143 |  | 0.53913 | 17.8443 | 4187 | 0.0079051 | 7.1636 | 7.1715 | -1.1268 | 126.5013 | 2644.3828 | -0.0089073
144 |  | 0.53913 | 17.8354 | 4187 | 0.0079011 | 7.1715 | 7.1794 | -1.1268 | 126.5645 | 2662.2182 | -0.0089029
145 |  | 0.53913 | 17.8265 | 4187 | 0.0078972 | 7.1794 | 7.1873 | -1.1268 | 126.6277 | 2680.0447 | -0.0088984
146 |  | 0.53913 | 17.8176 | 4187 | 0.0078932 | 7.1873 | 7.1952 | -1.1268 | 126.6909 | 2697.8623 | -0.008894
147 |  | 0.53913 | 17.8087 | 4187 | 0.0078893 | 7.1952 | 7.203 | -1.1268 | 126.7542 | 2715.6711 | -0.0088896
148 |  | 0.53913 | 17.7998 | 4187 | 0.0078853 | 7.203 | 7.2109 | -1.1268 | 126.8175 | 2733.4709 | -0.0088851
149 |  | 0.53913 | 17.791 | 4187 | 0.0078814 | 7.2109 | 7.2188 | -1.1268 | 126.8809 | 2751.2619 | -0.0088807
150 |  | 0.53913 | 17.7821 | 4187 | 0.0078775 | 7.2188 | 7.2267 | -1.1268 | 126.9442 | 2769.0439 | -0.0088763
151 |  | 0.53913 | 17.7732 | 4187 | 0.0078735 | 7.2267 | 7.2346 | -1.1268 | 127.0076 | 2786.8171 | -0.0088718
152 |  | 0.53913 | 17.7643 | 4187 | 0.0078696 | 7.2346 | 7.2424 | -1.1268 | 127.071 | 2804.5815 | -0.0088674
153 |  | 0.53913 | 17.7555 | 4187 | 0.0078657 | 7.2424 | 7.2503 | -1.1268 | 127.1345 | 2822.3369 | -0.008863
154 |  | 0.53913 | 17.7466 | 4187 | 0.0078618 | 7.2503 | 7.2582 | -1.1268 | 127.198 | 2840.0835 | -0.0088585
155 |  | 0.53913 | 17.7377 | 4187 | 0.0078578 | 7.2582 | 7.266 | -1.1268 | 127.2615 | 2857.8213 | -0.0088541
156 |  | 0.53913 | 17.7289 | 4187 | 0.0078539 | 7.266 | 7.2739 | -1.1268 | 127.3251 | 2875.5502 | -0.0088497
157 |  | 0.53913 | 17.72 | 4187 | 0.00785 | 7.2739 | 7.2817 | -1.1268 | 127.3887 | 2893.2702 | -0.0088453
158 |  | 0.53913 | 17.7112 | 4187 | 0.0078461 | 7.2817 | 7.2896 | -1.1268 | 127.4523 | 2910.9814 | -0.0088409
159 |  | 0.53913 | 17.7024 | 4187 | 0.0078422 | 7.2896 | 7.2974 | -1.1268 | 127.5159 | 2928.6837 | -0.0088365
160 |  | 0.53913 | 17.6935 | 4187 | 0.0078382 | 7.2974 | 7.3052 | -1.1268 | 127.5796 | 2946.3773 | -0.008832
161 |  | 0.53913 | 17.6847 | 4187 | 0.0078343 | 7.3052 | 7.3131 | -1.1268 | 127.6433 | 2964.0619 | -0.0088276
162 |  | 0.53913 | 17.6759 | 4187 | 0.0078304 | 7.3131 | 7.3209 | -1.1268 | 127.7071 | 2981.7378 | -0.0088232
163 |  | 0.53913 | 17.667 | 4187 | 0.0078265 | 7.3209 | 7.3287 | -1.1268 | 127.7709 | 2999.4048 | -0.0088188
164 |  | 0.53913 | 17.6582 | 4187 | 0.0078226 | 7.3287 | 7.3366 | -1.1268 | 127.8347 | 3017.063 | -0.0088144
165 |  | 0.53913 | 17.6494 | 4187 | 0.0078187 | 7.3366 | 7.3444 | -1.1268 | 127.8985 | 3034.7124 | -0.00881
166 |  | 0.53913 | 17.6406 | 4187 | 0.0078148 | 7.3444 | 7.3522 | -1.1268 | 127.9624 | 3052.353 | -0.0088056
167 |  | 0.53913 | 17.6318 | 4187 | 0.0078109 | 7.3522 | 7.36 | -1.1268 | 128.0263 | 3069.9848 | -0.0088012
168 |  | 0.53913 | 17.623 | 4187 | 0.007807 | 7.36 | 7.3678 | -1.1268 | 128.0902 | 3087.6078 | -0.0087968
169 |  | 0.53913 | 17.6142 | 4187 | 0.0078031 | 7.3678 | 7.3756 | -1.1268 | 128.1542 | 3105.222 | -0.0087924
170 |  | 0.53913 | 17.6054 | 4187 | 0.0077992 | 7.3756 | 7.3834 | -1.1268 | 128.2182 | 3122.8274 | -0.0087881
171 |  | 0.53913 | 17.5966 | 4187 | 0.0077953 | 7.3834 | 7.3912 | -1.1268 | 128.2823 | 3140.424 | -0.0087837
172 |  | 0.53913 | 17.5878 | 4187 | 0.0077914 | 7.3912 | 7.399 | -1.1268 | 128.3463 | 3158.0118 | -0.0087793
173 |  | 0.53913 | 17.579 | 4187 | 0.0077875 | 7.399 | 7.4068 | -1.1268 | 128.4104 | 3175.5908 | -0.0087749
174 |  | 0.53913 | 17.5703 | 4187 | 0.0077836 | 7.4068 | 7.4146 | -1.1268 | 128.4745 | 3193.1611 | -0.0087705
175 |  | 0.53913 | 17.5615 | 4187 | 0.0077798 | 7.4146 | 7.4224 | -1.1268 | 128.5387 | 3210.7226 | -0.0087661
176 |  | 0.53913 | 17.5527 | 4187 | 0.0077759 | 7.4224 | 7.4301 | -1.1268 | 128.6029 | 3228.2753 | -0.0087618
177 |  | 0.53913 | 17.544 | 4187 | 0.007772 | 7.4301 | 7.4379 | -1.1268 | 128.6671 | 3245.8193 | -0.0087574
178 |  | 0.53913 | 17.5352 | 4187 | 0.0077681 | 7.4379 | 7.4457 | -1.1268 | 128.7314 | 3263.3545 | -0.008753
179 |  | 0.53913 | 17.5265 | 4187 | 0.0077642 | 7.4457 | 7.4534 | -1.1268 | 128.7957 | 3280.8809 | -0.0087487
180 |  | 0.53913 | 17.5177 | 4187 | 0.0077604 | 7.4534 | 7.4612 | -1.1268 | 128.86 | 3298.3987 | -0.0087443
181 |  | 0.53913 | 17.509 | 4187 | 0.0077565 | 7.4612 | 7.4689 | -1.1268 | 128.9244 | 3315.9076 | -0.0087399
182 |  | 0.53913 | 17.5002 | 4187 | 0.0077526 | 7.4689 | 7.4767 | -1.1268 | 128.9887 | 3333.4078 | -0.0087356
183 |  | 0.53913 | 17.4915 | 4187 | 0.0077487 | 7.4767 | 7.4845 | -1.1268 | 129.0532 | 3350.8993 | -0.0087312
184 |  | 0.53913 | 17.4828 | 4187 | 0.0077449 | 7.4845 | 7.4922 | -1.1268 | 129.1176 | 3368.3821 | -0.0087268
185 |  | 0.53913 | 17.474 | 4187 | 0.007741 | 7.4922 | 7.4999 | -1.1268 | 129.1821 | 3385.8561 | -0.0087225
186 |  | 0.53913 | 17.4653 | 4187 | 0.0077371 | 7.4999 | 7.5077 | -1.1268 | 129.2466 | 3403.3214 | -0.0087181
187 |  | 0.53913 | 17.4566 | 4187 | 0.0077333 | 7.5077 | 7.5154 | -1.1268 | 129.3112 | 3420.778 | -0.0087138
188 |  | 0.53913 | 17.4479 | 4187 | 0.0077294 | 7.5154 | 7.5231 | -1.1268 | 129.3757 | 3438.2259 | -0.0087094
189 |  | 0.53913 | 17.4392 | 4187 | 0.0077256 | 7.5231 | 7.5309 | -1.1268 | 129.4404 | 3455.6651 | -0.0087051
190 |  | 0.53913 | 17.4305 | 4187 | 0.0077217 | 7.5309 | 7.5386 | -1.1268 | 129.505 | 3473.0955 | -0.0087007
191 |  | 0.53913 | 17.4218 | 4187 | 0.0077179 | 7.5386 | 7.5463 | -1.1268 | 129.5697 | 3490.5173 | -0.0086964
192 |  | 0.53913 | 17.4131 | 4187 | 0.007714 | 7.5463 | 7.554 | -1.1268 | 129.6344 | 3507.9303 | -0.0086921
193 |  | 0.53913 | 17.4044 | 4187 | 0.0077102 | 7.554 | 7.5617 | -1.1268 | 129.6991 | 3525.3347 | -0.0086877
194 |  | 0.53913 | 17.3957 | 4187 | 0.0077063 | 7.5617 | 7.5694 | -1.1268 | 129.7639 | 3542.7304 | -0.0086834
195 |  | 0.53913 | 17.387 | 4187 | 0.0077025 | 7.5694 | 7.5771 | -1.1268 | 129.8287 | 3560.1174 | -0.008679
196 |  | 0.53913 | 17.3783 | 4187 | 0.0076986 | 7.5771 | 7.5848 | -1.1268 | 129.8936 | 3577.4957 | -0.0086747
197 |  | 0.53913 | 17.3696 | 4187 | 0.0076948 | 7.5848 | 7.5925 | -1.1268 | 129.9584 | 3594.8654 | -0.0086704
198 |  | 0.53913 | 17.361 | 4187 | 0.0076909 | 7.5925 | 7.6002 | -1.1268 | 130.0233 | 3612.2263 | -0.0086661
199 |  | 0.53913 | 17.3523 | 4187 | 0.0076871 | 7.6002 | 7.6079 | -1.1268 | 130.0883 | 3629.5787 | -0.0086617
200 |  | 0.53913 | 17.3436 | 4187 | 0.0076833 | 7.6079 | 7.6156 | -1.1268 | 130.1532 | 3646.9223 | -0.0086574
201 |  | 0.53913 | 17.335 | 4187 | 0.0076794 | 7.6156 | 7.6233 | -1.1268 | 130.2182 | 3664.2573 | -0.0086531
202 |  | 0.53913 | 17.3263 | 4187 | 0.0076756 | 7.6233 | 7.6309 | -1.1268 | 130.2833 | 3681.5836 | -0.0086488
203 |  | 0.53913 | 17.3177 | 4187 | 0.0076718 | 7.6309 | 7.6386 | -1.1268 | 130.3483 | 3698.9013 | -0.0086444
204 |  | 0.53913 | 17.309 | 4187 | 0.0076679 | 7.6386 | 7.6463 | -1.1268 | 130.4134 | 3716.2104 | -0.0086401
205 |  | 0.53913 | 17.3004 | 4187 | 0.0076641 | 7.6463 | 7.6539 | -1.1268 | 130.4786 | 3733.5108 | -0.0086358
206 |  | 0.53913 | 17.2918 | 4187 | 0.0076603 | 7.6539 | 7.6616 | -1.1268 | 130.5437 | 3750.8025 | -0.0086315
207 |  | 0.53913 | 17.2831 | 4187 | 0.0076564 | 7.6616 | 7.6693 | -1.1268 | 130.6089 | 3768.0857 | -0.0086272
208 |  | 0.53913 | 17.2745 | 4187 | 0.0076526 | 7.6693 | 7.6769 | -1.1268 | 130.6741 | 3785.3602 | -0.0086229
209 |  | 0.53913 | 17.2659 | 4187 | 0.0076488 | 7.6769 | 7.6846 | -1.1268 | 130.7394 | 3802.6261 | -0.0086186
210 |  | 0.53913 | 17.2573 | 4187 | 0.007645 | 7.6846 | 7.6922 | -1.1268 | 130.8047 | 3819.8833 | -0.0086143
211 |  | 0.53913 | 17.2487 | 4187 | 0.0076412 | 7.6922 | 7.6999 | -1.1268 | 130.87 | 3837.132 | -0.00861
212 |  | 0.53913 | 17.24 | 4187 | 0.0076374 | 7.6999 | 7.7075 | -1.1268 | 130.9354 | 3854.372 | -0.0086057
213 |  | 0.53913 | 17.2314 | 4187 | 0.0076335 | 7.7075 | 7.7151 | -1.1268 | 131.0008 | 3871.6035 | -0.0086014
214 |  | 0.53913 | 17.2228 | 4187 | 0.0076297 | 7.7151 | 7.7228 | -1.1268 | 131.0662 | 3888.8263 | -0.0085971
215 |  | 0.53913 | 17.2142 | 4187 | 0.0076259 | 7.7228 | 7.7304 | -1.1268 | 131.1317 | 3906.0406 | -0.0085928
216 |  | 0.53913 | 17.2056 | 4187 | 0.0076221 | 7.7304 | 7.738 | -1.1268 | 131.1971 | 3923.2462 | -0.0085885
217 |  | 0.53913 | 17.1971 | 4187 | 0.0076183 | 7.738 | 7.7456 | -1.1268 | 131.2627 | 3940.4433 | -0.0085842
218 |  | 0.53913 | 17.1885 | 4187 | 0.0076145 | 7.7456 | 7.7532 | -1.1268 | 131.3282 | 3957.6317 | -0.0085799
219 |  | 0.53913 | 17.1799 | 4187 | 0.0076107 | 7.7532 | 7.7608 | -1.1268 | 131.3938 | 3974.8116 | -0.0085757
220 |  | 0.53913 | 17.1713 | 4187 | 0.0076069 | 7.7608 | 7.7685 | -1.1268 | 131.4594 | 3991.983 | -0.0085714
221 |  | 0.53913 | 17.1627 | 4187 | 0.0076031 | 7.7685 | 7.7761 | -1.1268 | 131.5251 | 4009.1457 | -0.0085671
222 |  | 0.53913 | 17.1542 | 4187 | 0.0075993 | 7.7761 | 7.7837 | -1.1268 | 131.5908 | 4026.2999 | -0.0085628
223 |  | 0.53913 | 17.1456 | 4187 | 0.0075955 | 7.7837 | 7.7912 | -1.1268 | 131.6565 | 4043.4455 | -0.0085586
224 |  | 0.53913 | 17.1371 | 4187 | 0.0075917 | 7.7912 | 7.7988 | -1.1268 | 131.7222 | 4060.5826 | -0.0085543
225 |  | 0.53913 | 17.1285 | 4187 | 0.0075879 | 7.7988 | 7.8064 | -1.1268 | 131.788 | 4077.7111 | -0.00855
226 |  | 0.53913 | 17.12 | 4187 | 0.0075842 | 7.8064 | 7.814 | -1.1268 | 131.8538 | 4094.831 | -0.0085457
227 |  | 0.53913 | 17.1114 | 4187 | 0.0075804 | 7.814 | 7.8216 | -1.1268 | 131.9197 | 4111.9424 | -0.0085415
228 |  | 0.53913 | 17.1029 | 4187 | 0.0075766 | 7.8216 | 7.8292 | -1.1268 | 131.9856 | 4129.0453 | -0.0085372
229 |  | 0.53913 | 17.0943 | 4187 | 0.0075728 | 7.8292 | 7.8367 | -1.1268 | 132.0515 | 4146.1396 | -0.008533
230 |  | 0.53913 | 17.0858 | 4187 | 0.007569 | 7.8367 | 7.8443 | -1.1268 | 132.1174 | 4163.2254 | -0.0085287
231 |  | 0.53913 | 17.0773 | 4187 | 0.0075652 | 7.8443 | 7.8519 | -1.1268 | 132.1834 | 4180.3027 | -0.0085244
232 |  | 0.53913 | 17.0687 | 4187 | 0.0075615 | 7.8519 | 7.8594 | -1.1268 | 132.2494 | 4197.3715 | -0.0085202
233 |  | 0.53913 | 17.0602 | 4187 | 0.0075577 | 7.8594 | 7.867 | -1.1268 | 132.3155 | 4214.4317 | -0.0085159
234 |  | 0.53913 | 17.0517 | 4187 | 0.0075539 | 7.867 | 7.8746 | -1.1268 | 132.3816 | 4231.4834 | -0.0085117
235 |  | 0.53913 | 17.0432 | 4187 | 0.0075502 | 7.8746 | 7.8821 | -1.1268 | 132.4477 | 4248.5266 | -0.0085074
236 |  | 0.53913 | 17.0347 | 4187 | 0.0075464 | 7.8821 | 7.8896 | -1.1268 | 132.5138 | 4265.5613 | -0.0085032

## 40
|  |  | buis | verlies W/M | L /°C/sec
diam | wandikte |  | inhoud l/m |  | W/M
40 | 3.7 | 3.1416 | 0.83469 | 22.4472 | 4187
[8 empty] | J/sec/mtr | aantal mtr. | verlies
|  | buis | verlies W/M | L /°C/sec | verlies temp | begintemp | eindtemp | verlies | bij 1°C | totaal J/sec
|  | inhoud L |  | W/M | °C per M | °C | °C | per m°C | daling | aantal mtr
1 | 40 | 0.83469 | 22.4472 | 4187 | 0.0064229 | 6 | 6.0064 | -1.3204 | 155.692 | 22.4472 | -0.008481
2 |  | 0.83469 | 22.4387 | 4187 | 0.0064205 | 6.0064 | 6.0128 | -1.3204 | 155.7509 | 44.8859 | -0.0084778
3 |  | 0.83469 | 22.4302 | 4187 | 0.0064181 | 6.0128 | 6.0193 | -1.3204 | 155.8098 | 67.3161 | -0.0084746
4 |  | 0.83469 | 22.4217 | 4187 | 0.0064157 | 6.0193 | 6.0257 | -1.3204 | 155.8686 | 89.7378 | -0.0084714
5 |  | 0.83469 | 22.4133 | 4187 | 0.0064132 | 6.0257 | 6.0321 | -1.3204 | 155.9276 | 112.1511 | -0.0084682
6 |  | 0.83469 | 22.4048 | 4187 | 0.0064108 | 6.0321 | 6.0385 | -1.3204 | 155.9865 | 134.5559 | -0.008465
7 |  | 0.83469 | 22.3963 | 4187 | 0.0064084 | 6.0385 | 6.0449 | -1.3204 | 156.0455 | 156.9522 | -0.0084618
8 |  | 0.83469 | 22.3879 | 4187 | 0.006406 | 6.0449 | 6.0513 | -1.3204 | 156.1044 | 179.3401 | -0.0084586
9 |  | 0.83469 | 22.3794 | 4187 | 0.0064035 | 6.0513 | 6.0577 | -1.3204 | 156.1634 | 201.7195 | -0.0084554
10 |  | 0.83469 | 22.371 | 4187 | 0.0064011 | 6.0577 | 6.0641 | -1.3204 | 156.2225 | 224.0905 | -0.0084522
11 |  | 0.83469 | 22.3625 | 4187 | 0.0063987 | 6.0641 | 6.0705 | -1.3204 | 156.2815 | 246.453 | -0.008449
12 |  | 0.83469 | 22.3541 | 4187 | 0.0063963 | 6.0705 | 6.0769 | -1.3204 | 156.3406 | 268.807 | -0.0084458
13 |  | 0.83469 | 22.3456 | 4187 | 0.0063939 | 6.0769 | 6.0833 | -1.3204 | 156.3997 | 291.1526 | -0.0084426
14 |  | 0.83469 | 22.3372 | 4187 | 0.0063915 | 6.0833 | 6.0897 | -1.3204 | 156.4588 | 313.4898 | -0.0084394
15 |  | 0.83469 | 22.3287 | 4187 | 0.006389 | 6.0897 | 6.0961 | -1.3204 | 156.5179 | 335.8185 | -0.0084362
16 |  | 0.83469 | 22.3203 | 4187 | 0.0063866 | 6.0961 | 6.1025 | -1.3204 | 156.5771 | 358.1388 | -0.008433
17 |  | 0.83469 | 22.3119 | 4187 | 0.0063842 | 6.1025 | 6.1089 | -1.3204 | 156.6362 | 380.4507 | -0.0084299
18 |  | 0.83469 | 22.3034 | 4187 | 0.0063818 | 6.1089 | 6.1152 | -1.3204 | 156.6955 | 402.7541 | -0.0084267
19 |  | 0.83469 | 22.295 | 4187 | 0.0063794 | 6.1152 | 6.1216 | -1.3204 | 156.7547 | 425.0491 | -0.0084235
20 |  | 0.83469 | 22.2866 | 4187 | 0.006377 | 6.1216 | 6.128 | -1.3204 | 156.8139 | 447.3357 | -0.0084203
21 |  | 0.83469 | 22.2782 | 4187 | 0.0063746 | 6.128 | 6.1344 | -1.3204 | 156.8732 | 469.6138 | -0.0084171
22 |  | 0.83469 | 22.2697 | 4187 | 0.0063722 | 6.1344 | 6.1407 | -1.3204 | 156.9325 | 491.8836 | -0.0084139
23 |  | 0.83469 | 22.2613 | 4187 | 0.0063698 | 6.1407 | 6.1471 | -1.3204 | 156.9918 | 514.1449 | -0.0084108
24 |  | 0.83469 | 22.2529 | 4187 | 0.0063674 | 6.1471 | 6.1535 | -1.3204 | 157.0511 | 536.3978 | -0.0084076
25 |  | 0.83469 | 22.2445 | 4187 | 0.0063649 | 6.1535 | 6.1598 | -1.3204 | 157.1105 | 558.6423 | -0.0084044
26 |  | 0.83469 | 22.2361 | 4187 | 0.0063625 | 6.1598 | 6.1662 | -1.3204 | 157.1699 | 580.8784 | -0.0084012
27 |  | 0.83469 | 22.2277 | 4187 | 0.0063601 | 6.1662 | 6.1726 | -1.3204 | 157.2293 | 603.1062 | -0.0083981
28 |  | 0.83469 | 22.2193 | 4187 | 0.0063577 | 6.1726 | 6.1789 | -1.3204 | 157.2887 | 625.3255 | -0.0083949
29 |  | 0.83469 | 22.2109 | 4187 | 0.0063553 | 6.1789 | 6.1853 | -1.3204 | 157.3482 | 647.5364 | -0.0083917
30 |  | 0.83469 | 22.2025 | 4187 | 0.0063529 | 6.1853 | 6.1916 | -1.3204 | 157.4076 | 669.7389 | -0.0083886
31 |  | 0.83469 | 22.1941 | 4187 | 0.0063505 | 6.1916 | 6.198 | -1.3204 | 157.4671 | 691.933 | -0.0083854
32 |  | 0.83469 | 22.1857 | 4187 | 0.0063481 | 6.198 | 6.2043 | -1.3204 | 157.5266 | 714.1188 | -0.0083822
33 |  | 0.83469 | 22.1774 | 4187 | 0.0063457 | 6.2043 | 6.2107 | -1.3204 | 157.5862 | 736.2961 | -0.008379
34 |  | 0.83469 | 22.169 | 4187 | 0.0063433 | 6.2107 | 6.217 | -1.3204 | 157.6457 | 758.4651 | -0.0083759
35 |  | 0.83469 | 22.1606 | 4187 | 0.0063409 | 6.217 | 6.2234 | -1.3204 | 157.7053 | 780.6257 | -0.0083727
36 |  | 0.83469 | 22.1522 | 4187 | 0.0063385 | 6.2234 | 6.2297 | -1.3204 | 157.7649 | 802.778 | -0.0083696
37 |  | 0.83469 | 22.1439 | 4187 | 0.0063361 | 6.2297 | 6.236 | -1.3204 | 157.8246 | 824.9218 | -0.0083664
38 |  | 0.83469 | 22.1355 | 4187 | 0.0063338 | 6.236 | 6.2424 | -1.3204 | 157.8842 | 847.0573 | -0.0083632
39 |  | 0.83469 | 22.1271 | 4187 | 0.0063314 | 6.2424 | 6.2487 | -1.3204 | 157.9439 | 869.1845 | -0.0083601
40 |  | 0.83469 | 22.1188 | 4187 | 0.006329 | 6.2487 | 6.255 | -1.3204 | 158.0036 | 891.3032 | -0.0083569
41 |  | 0.83469 | 22.1104 | 4187 | 0.0063266 | 6.255 | 6.2614 | -1.3204 | 158.0633 | 913.4137 | -0.0083538
42 |  | 0.83469 | 22.1021 | 4187 | 0.0063242 | 6.2614 | 6.2677 | -1.3204 | 158.123 | 935.5157 | -0.0083506
43 |  | 0.83469 | 22.0937 | 4187 | 0.0063218 | 6.2677 | 6.274 | -1.3204 | 158.1828 | 957.6094 | -0.0083474
44 |  | 0.83469 | 22.0854 | 4187 | 0.0063194 | 6.274 | 6.2803 | -1.3204 | 158.2426 | 979.6948 | -0.0083443
45 |  | 0.83469 | 22.077 | 4187 | 0.006317 | 6.2803 | 6.2866 | -1.3204 | 158.3024 | 1001.7718 | -0.0083411
46 |  | 0.83469 | 22.0687 | 4187 | 0.0063146 | 6.2866 | 6.293 | -1.3204 | 158.3622 | 1023.8405 | -0.008338
47 |  | 0.83469 | 22.0603 | 4187 | 0.0063123 | 6.293 | 6.2993 | -1.3204 | 158.4221 | 1045.9009 | -0.0083348
48 |  | 0.83469 | 22.052 | 4187 | 0.0063099 | 6.2993 | 6.3056 | -1.3204 | 158.482 | 1067.9529 | -0.0083317
49 |  | 0.83469 | 22.0437 | 4187 | 0.0063075 | 6.3056 | 6.3119 | -1.3204 | 158.5419 | 1089.9965 | -0.0083285
50 |  | 0.83469 | 22.0353 | 4187 | 0.0063051 | 6.3119 | 6.3182 | -1.3204 | 158.6018 | 1112.0319 | -0.0083254
51 |  | 0.83469 | 22.027 | 4187 | 0.0063027 | 6.3182 | 6.3245 | -1.3204 | 158.6617 | 1134.0589 | -0.0083222
52 |  | 0.83469 | 22.0187 | 4187 | 0.0063003 | 6.3245 | 6.3308 | -1.3204 | 158.7217 | 1156.0776 | -0.0083191
53 |  | 0.83469 | 22.0104 | 4187 | 0.006298 | 6.3308 | 6.3371 | -1.3204 | 158.7817 | 1178.088 | -0.008316
54 |  | 0.83469 | 22.0021 | 4187 | 0.0062956 | 6.3371 | 6.3434 | -1.3204 | 158.8417 | 1200.0901 | -0.0083128
55 |  | 0.83469 | 21.9938 | 4187 | 0.0062932 | 6.3434 | 6.3497 | -1.3204 | 158.9018 | 1222.0838 | -0.0083097
56 |  | 0.83469 | 21.9854 | 4187 | 0.0062908 | 6.3497 | 6.356 | -1.3204 | 158.9618 | 1244.0693 | -0.0083065
57 |  | 0.83469 | 21.9771 | 4187 | 0.0062884 | 6.356 | 6.3623 | -1.3204 | 159.0219 | 1266.0464 | -0.0083034
58 |  | 0.83469 | 21.9688 | 4187 | 0.0062861 | 6.3623 | 6.3685 | -1.3204 | 159.082 | 1288.0152 | -0.0083003
59 |  | 0.83469 | 21.9605 | 4187 | 0.0062837 | 6.3685 | 6.3748 | -1.3204 | 159.1421 | 1309.9758 | -0.0082971
60 |  | 0.83469 | 21.9522 | 4187 | 0.0062813 | 6.3748 | 6.3811 | -1.3204 | 159.2023 | 1331.928 | -0.008294
61 |  | 0.83469 | 21.9439 | 4187 | 0.0062789 | 6.3811 | 6.3874 | -1.3204 | 159.2624 | 1353.8719 | -0.0082909
62 |  | 0.83469 | 21.9357 | 4187 | 0.0062766 | 6.3874 | 6.3937 | -1.3204 | 159.3226 | 1375.8076 | -0.0082877
63 |  | 0.83469 | 21.9274 | 4187 | 0.0062742 | 6.3937 | 6.3999 | -1.3204 | 159.3829 | 1397.735 | -0.0082846
64 |  | 0.83469 | 21.9191 | 4187 | 0.0062718 | 6.3999 | 6.4062 | -1.3204 | 159.4431 | 1419.654 | -0.0082815
65 |  | 0.83469 | 21.9108 | 4187 | 0.0062695 | 6.4062 | 6.4125 | -1.3204 | 159.5034 | 1441.5648 | -0.0082783
66 |  | 0.83469 | 21.9025 | 4187 | 0.0062671 | 6.4125 | 6.4188 | -1.3204 | 159.5636 | 1463.4674 | -0.0082752
67 |  | 0.83469 | 21.8942 | 4187 | 0.0062647 | 6.4188 | 6.425 | -1.3204 | 159.624 | 1485.3616 | -0.0082721
68 |  | 0.83469 | 21.886 | 4187 | 0.0062624 | 6.425 | 6.4313 | -1.3204 | 159.6843 | 1507.2476 | -0.008269
69 |  | 0.83469 | 21.8777 | 4187 | 0.00626 | 6.4313 | 6.4375 | -1.3204 | 159.7446 | 1529.1253 | -0.0082658
70 |  | 0.83469 | 21.8694 | 4187 | 0.0062576 | 6.4375 | 6.4438 | -1.3204 | 159.805 | 1550.9947 | -0.0082627
71 |  | 0.83469 | 21.8612 | 4187 | 0.0062553 | 6.4438 | 6.4501 | -1.3204 | 159.8654 | 1572.8559 | -0.0082596
72 |  | 0.83469 | 21.8529 | 4187 | 0.0062529 | 6.4501 | 6.4563 | -1.3204 | 159.9258 | 1594.7088 | -0.0082565
73 |  | 0.83469 | 21.8447 | 4187 | 0.0062505 | 6.4563 | 6.4626 | -1.3204 | 159.9863 | 1616.5535 | -0.0082533
74 |  | 0.83469 | 21.8364 | 4187 | 0.0062482 | 6.4626 | 6.4688 | -1.3204 | 160.0468 | 1638.3899 | -0.0082502
75 |  | 0.83469 | 21.8282 | 4187 | 0.0062458 | 6.4688 | 6.475 | -1.3204 | 160.1073 | 1660.218 | -0.0082471
76 |  | 0.83469 | 21.8199 | 4187 | 0.0062435 | 6.475 | 6.4813 | -1.3204 | 160.1678 | 1682.0379 | -0.008244
77 |  | 0.83469 | 21.8117 | 4187 | 0.0062411 | 6.4813 | 6.4875 | -1.3204 | 160.2283 | 1703.8496 | -0.0082409
78 |  | 0.83469 | 21.8034 | 4187 | 0.0062387 | 6.4875 | 6.4938 | -1.3204 | 160.2889 | 1725.653 | -0.0082378
79 |  | 0.83469 | 21.7952 | 4187 | 0.0062364 | 6.4938 | 6.5 | -1.3204 | 160.3494 | 1747.4482 | -0.0082347
80 |  | 0.83469 | 21.787 | 4187 | 0.006234 | 6.5 | 6.5062 | -1.3204 | 160.4101 | 1769.2352 | -0.0082315
81 |  | 0.83469 | 21.7787 | 4187 | 0.0062317 | 6.5062 | 6.5125 | -1.3204 | 160.4707 | 1791.0139 | -0.0082284
82 |  | 0.83469 | 21.7705 | 4187 | 0.0062293 | 6.5125 | 6.5187 | -1.3204 | 160.5313 | 1812.7844 | -0.0082253
83 |  | 0.83469 | 21.7623 | 4187 | 0.006227 | 6.5187 | 6.5249 | -1.3204 | 160.592 | 1834.5466 | -0.0082222
84 |  | 0.83469 | 21.754 | 4187 | 0.0062246 | 6.5249 | 6.5312 | -1.3204 | 160.6527 | 1856.3007 | -0.0082191
85 |  | 0.83469 | 21.7458 | 4187 | 0.0062223 | 6.5312 | 6.5374 | -1.3204 | 160.7134 | 1878.0465 | -0.008216
86 |  | 0.83469 | 21.7376 | 4187 | 0.0062199 | 6.5374 | 6.5436 | -1.3204 | 160.7742 | 1899.7841 | -0.0082129
87 |  | 0.83469 | 21.7294 | 4187 | 0.0062176 | 6.5436 | 6.5498 | -1.3204 | 160.8349 | 1921.5135 | -0.0082098
88 |  | 0.83469 | 21.7212 | 4187 | 0.0062152 | 6.5498 | 6.556 | -1.3204 | 160.8957 | 1943.2347 | -0.0082067
89 |  | 0.83469 | 21.713 | 4187 | 0.0062129 | 6.556 | 6.5622 | -1.3204 | 160.9565 | 1964.9477 | -0.0082036
90 |  | 0.83469 | 21.7048 | 4187 | 0.0062105 | 6.5622 | 6.5685 | -1.3204 | 161.0174 | 1986.6524 | -0.0082005
91 |  | 0.83469 | 21.6966 | 4187 | 0.0062082 | 6.5685 | 6.5747 | -1.3204 | 161.0782 | 2008.349 | -0.0081974
92 |  | 0.83469 | 21.6884 | 4187 | 0.0062058 | 6.5747 | 6.5809 | -1.3204 | 161.1391 | 2030.0374 | -0.0081943
93 |  | 0.83469 | 21.6802 | 4187 | 0.0062035 | 6.5809 | 6.5871 | -1.3204 | 161.2 | 2051.7176 | -0.0081912
94 |  | 0.83469 | 21.672 | 4187 | 0.0062011 | 6.5871 | 6.5933 | -1.3204 | 161.2609 | 2073.3896 | -0.0081881
95 |  | 0.83469 | 21.6638 | 4187 | 0.0061988 | 6.5933 | 6.5995 | -1.3204 | 161.3219 | 2095.0534 | -0.008185
96 |  | 0.83469 | 21.6556 | 4187 | 0.0061964 | 6.5995 | 6.6057 | -1.3204 | 161.3829 | 2116.709 | -0.0081819
97 |  | 0.83469 | 21.6474 | 4187 | 0.0061941 | 6.6057 | 6.6119 | -1.3204 | 161.4439 | 2138.3564 | -0.0081788
98 |  | 0.83469 | 21.6393 | 4187 | 0.0061918 | 6.6119 | 6.6181 | -1.3204 | 161.5049 | 2159.9957 | -0.0081757
99 |  | 0.83469 | 21.6311 | 4187 | 0.0061894 | 6.6181 | 6.6242 | -1.3204 | 161.5659 | 2181.6268 | -0.0081727
100 |  | 0.83469 | 21.6229 | 4187 | 0.0061871 | 6.6242 | 6.6304 | -1.3204 | 161.627 | 2203.2497 | -0.0081696
101 |  | 0.83469 | 21.6147 | 4187 | 0.0061847 | 6.6304 | 6.6366 | -1.3204 | 161.6881 | 2224.8644 | -0.0081665
102 |  | 0.83469 | 21.6066 | 4187 | 0.0061824 | 6.6366 | 6.6428 | -1.3204 | 161.7492 | 2246.471 | -0.0081634
103 |  | 0.83469 | 21.5984 | 4187 | 0.0061801 | 6.6428 | 6.649 | -1.3204 | 161.8103 | 2268.0694 | -0.0081603
104 |  | 0.83469 | 21.5902 | 4187 | 0.0061777 | 6.649 | 6.6552 | -1.3204 | 161.8715 | 2289.6597 | -0.0081572
105 |  | 0.83469 | 21.5821 | 4187 | 0.0061754 | 6.6552 | 6.6613 | -1.3204 | 161.9327 | 2311.2418 | -0.0081541
106 |  | 0.83469 | 21.5739 | 4187 | 0.0061731 | 6.6613 | 6.6675 | -1.3204 | 161.9939 | 2332.8157 | -0.0081511
107 |  | 0.83469 | 21.5658 | 4187 | 0.0061707 | 6.6675 | 6.6737 | -1.3204 | 162.0551 | 2354.3815 | -0.008148
108 |  | 0.83469 | 21.5576 | 4187 | 0.0061684 | 6.6737 | 6.6798 | -1.3204 | 162.1164 | 2375.9391 | -0.0081449
109 |  | 0.83469 | 21.5495 | 4187 | 0.0061661 | 6.6798 | 6.686 | -1.3204 | 162.1776 | 2397.4886 | -0.0081418
110 |  | 0.83469 | 21.5414 | 4187 | 0.0061637 | 6.686 | 6.6922 | -1.3204 | 162.2389 | 2419.03 | -0.0081387
111 |  | 0.83469 | 21.5332 | 4187 | 0.0061614 | 6.6922 | 6.6983 | -1.3204 | 162.3002 | 2440.5632 | -0.0081357
112 |  | 0.83469 | 21.5251 | 4187 | 0.0061591 | 6.6983 | 6.7045 | -1.3204 | 162.3616 | 2462.0883 | -0.0081326
113 |  | 0.83469 | 21.5169 | 4187 | 0.0061568 | 6.7045 | 6.7106 | -1.3204 | 162.423 | 2483.6052 | -0.0081295
114 |  | 0.83469 | 21.5088 | 4187 | 0.0061544 | 6.7106 | 6.7168 | -1.3204 | 162.4843 | 2505.114 | -0.0081265
115 |  | 0.83469 | 21.5007 | 4187 | 0.0061521 | 6.7168 | 6.723 | -1.3204 | 162.5458 | 2526.6147 | -0.0081234
116 |  | 0.83469 | 21.4926 | 4187 | 0.0061498 | 6.723 | 6.7291 | -1.3204 | 162.6072 | 2548.1073 | -0.0081203
117 |  | 0.83469 | 21.4844 | 4187 | 0.0061475 | 6.7291 | 6.7353 | -1.3204 | 162.6687 | 2569.5917 | -0.0081172
118 |  | 0.83469 | 21.4763 | 4187 | 0.0061451 | 6.7353 | 6.7414 | -1.3204 | 162.7301 | 2591.0681 | -0.0081142
119 |  | 0.83469 | 21.4682 | 4187 | 0.0061428 | 6.7414 | 6.7475 | -1.3204 | 162.7916 | 2612.5363 | -0.0081111
120 |  | 0.83469 | 21.4601 | 4187 | 0.0061405 | 6.7475 | 6.7537 | -1.3204 | 162.8532 | 2633.9964 | -0.0081081
121 |  | 0.83469 | 21.452 | 4187 | 0.0061382 | 6.7537 | 6.7598 | -1.3204 | 162.9147 | 2655.4484 | -0.008105
122 |  | 0.83469 | 21.4439 | 4187 | 0.0061359 | 6.7598 | 6.766 | -1.3204 | 162.9763 | 2676.8923 | -0.0081019
123 |  | 0.83469 | 21.4358 | 4187 | 0.0061335 | 6.766 | 6.7721 | -1.3204 | 163.0379 | 2698.328 | -0.0080989
124 |  | 0.83469 | 21.4277 | 4187 | 0.0061312 | 6.7721 | 6.7782 | -1.3204 | 163.0995 | 2719.7557 | -0.0080958
125 |  | 0.83469 | 21.4196 | 4187 | 0.0061289 | 6.7782 | 6.7843 | -1.3204 | 163.1612 | 2741.1753 | -0.0080927
126 |  | 0.83469 | 21.4115 | 4187 | 0.0061266 | 6.7843 | 6.7905 | -1.3204 | 163.2228 | 2762.5868 | -0.0080897
127 |  | 0.83469 | 21.4034 | 4187 | 0.0061243 | 6.7905 | 6.7966 | -1.3204 | 163.2845 | 2783.9902 | -0.0080866
128 |  | 0.83469 | 21.3953 | 4187 | 0.006122 | 6.7966 | 6.8027 | -1.3204 | 163.3462 | 2805.3856 | -0.0080836
129 |  | 0.83469 | 21.3872 | 4187 | 0.0061197 | 6.8027 | 6.8088 | -1.3204 | 163.408 | 2826.7728 | -0.0080805
130 |  | 0.83469 | 21.3792 | 4187 | 0.0061173 | 6.8088 | 6.815 | -1.3204 | 163.4697 | 2848.152 | -0.0080775
131 |  | 0.83469 | 21.3711 | 4187 | 0.006115 | 6.815 | 6.8211 | -1.3204 | 163.5315 | 2869.5231 | -0.0080744
132 |  | 0.83469 | 21.363 | 4187 | 0.0061127 | 6.8211 | 6.8272 | -1.3204 | 163.5933 | 2890.8861 | -0.0080714
133 |  | 0.83469 | 21.3549 | 4187 | 0.0061104 | 6.8272 | 6.8333 | -1.3204 | 163.6552 | 2912.241 | -0.0080683
134 |  | 0.83469 | 21.3469 | 4187 | 0.0061081 | 6.8333 | 6.8394 | -1.3204 | 163.717 | 2933.5879 | -0.0080653
135 |  | 0.83469 | 21.3388 | 4187 | 0.0061058 | 6.8394 | 6.8455 | -1.3204 | 163.7789 | 2954.9267 | -0.0080622
136 |  | 0.83469 | 21.3307 | 4187 | 0.0061035 | 6.8455 | 6.8516 | -1.3204 | 163.8408 | 2976.2574 | -0.0080592
137 |  | 0.83469 | 21.3227 | 4187 | 0.0061012 | 6.8516 | 6.8577 | -1.3204 | 163.9027 | 2997.5801 | -0.0080561
138 |  | 0.83469 | 21.3146 | 4187 | 0.0060989 | 6.8577 | 6.8638 | -1.3204 | 163.9647 | 3018.8947 | -0.0080531
139 |  | 0.83469 | 21.3066 | 4187 | 0.0060966 | 6.8638 | 6.8699 | -1.3204 | 164.0267 | 3040.2013 | -0.00805
140 |  | 0.83469 | 21.2985 | 4187 | 0.0060943 | 6.8699 | 6.876 | -1.3204 | 164.0887 | 3061.4998 | -0.008047
141 |  | 0.83469 | 21.2905 | 4187 | 0.006092 | 6.876 | 6.8821 | -1.3204 | 164.1507 | 3082.7903 | -0.008044
142 |  | 0.83469 | 21.2824 | 4187 | 0.0060897 | 6.8821 | 6.8882 | -1.3204 | 164.2127 | 3104.0727 | -0.0080409
143 |  | 0.83469 | 21.2744 | 4187 | 0.0060874 | 6.8882 | 6.8943 | -1.3204 | 164.2748 | 3125.3471 | -0.0080379
144 |  | 0.83469 | 21.2664 | 4187 | 0.0060851 | 6.8943 | 6.9004 | -1.3204 | 164.3369 | 3146.6135 | -0.0080348
145 |  | 0.83469 | 21.2583 | 4187 | 0.0060828 | 6.9004 | 6.9064 | -1.3204 | 164.399 | 3167.8718 | -0.0080318
146 |  | 0.83469 | 21.2503 | 4187 | 0.0060805 | 6.9064 | 6.9125 | -1.3204 | 164.4611 | 3189.1221 | -0.0080288
147 |  | 0.83469 | 21.2423 | 4187 | 0.0060782 | 6.9125 | 6.9186 | -1.3204 | 164.5233 | 3210.3643 | -0.0080257
148 |  | 0.83469 | 21.2342 | 4187 | 0.0060759 | 6.9186 | 6.9247 | -1.3204 | 164.5855 | 3231.5986 | -0.0080227
149 |  | 0.83469 | 21.2262 | 4187 | 0.0060736 | 6.9247 | 6.9307 | -1.3204 | 164.6477 | 3252.8248 | -0.0080197
150 |  | 0.83469 | 21.2182 | 4187 | 0.0060713 | 6.9307 | 6.9368 | -1.3204 | 164.7099 | 3274.043 | -0.0080167
151 |  | 0.83469 | 21.2102 | 4187 | 0.006069 | 6.9368 | 6.9429 | -1.3204 | 164.7722 | 3295.2531 | -0.0080136
152 |  | 0.83469 | 21.2022 | 4187 | 0.0060667 | 6.9429 | 6.949 | -1.3204 | 164.8344 | 3316.4553 | -0.0080106
153 |  | 0.83469 | 21.1941 | 4187 | 0.0060644 | 6.949 | 6.955 | -1.3204 | 164.8967 | 3337.6495 | -0.0080076
154 |  | 0.83469 | 21.1861 | 4187 | 0.0060621 | 6.955 | 6.9611 | -1.3204 | 164.9591 | 3358.8356 | -0.0080045
155 |  | 0.83469 | 21.1781 | 4187 | 0.0060598 | 6.9611 | 6.9671 | -1.3204 | 165.0214 | 3380.0137 | -0.0080015
156 |  | 0.83469 | 21.1701 | 4187 | 0.0060575 | 6.9671 | 6.9732 | -1.3204 | 165.0838 | 3401.1839 | -0.0079985
157 |  | 0.83469 | 21.1621 | 4187 | 0.0060552 | 6.9732 | 6.9793 | -1.3204 | 165.1462 | 3422.346 | -0.0079955
158 |  | 0.83469 | 21.1541 | 4187 | 0.006053 | 6.9793 | 6.9853 | -1.3204 | 165.2086 | 3443.5001 | -0.0079925
159 |  | 0.83469 | 21.1461 | 4187 | 0.0060507 | 6.9853 | 6.9914 | -1.3204 | 165.271 | 3464.6463 | -0.0079894
160 |  | 0.83469 | 21.1382 | 4187 | 0.0060484 | 6.9914 | 6.9974 | -1.3204 | 165.3335 | 3485.7845 | -0.0079864
161 |  | 0.83469 | 21.1302 | 4187 | 0.0060461 | 6.9974 | 7.0035 | -1.3204 | 165.396 | 3506.9146 | -0.0079834
162 |  | 0.83469 | 21.1222 | 4187 | 0.0060438 | 7.0035 | 7.0095 | -1.3204 | 165.4585 | 3528.0368 | -0.0079804
163 |  | 0.83469 | 21.1142 | 4187 | 0.0060415 | 7.0095 | 7.0155 | -1.3204 | 165.521 | 3549.151 | -0.0079774
164 |  | 0.83469 | 21.1062 | 4187 | 0.0060392 | 7.0155 | 7.0216 | -1.3204 | 165.5836 | 3570.2573 | -0.0079744
165 |  | 0.83469 | 21.0983 | 4187 | 0.006037 | 7.0216 | 7.0276 | -1.3204 | 165.6462 | 3591.3555 | -0.0079713
166 |  | 0.83469 | 21.0903 | 4187 | 0.0060347 | 7.0276 | 7.0336 | -1.3204 | 165.7088 | 3612.4458 | -0.0079683
167 |  | 0.83469 | 21.0823 | 4187 | 0.0060324 | 7.0336 | 7.0397 | -1.3204 | 165.7714 | 3633.5281 | -0.0079653
168 |  | 0.83469 | 21.0744 | 4187 | 0.0060301 | 7.0397 | 7.0457 | -1.3204 | 165.8341 | 3654.6025 | -0.0079623
169 |  | 0.83469 | 21.0664 | 4187 | 0.0060278 | 7.0457 | 7.0517 | -1.3204 | 165.8968 | 3675.6689 | -0.0079593
170 |  | 0.83469 | 21.0584 | 4187 | 0.0060256 | 7.0517 | 7.0578 | -1.3204 | 165.9595 | 3696.7273 | -0.0079563
171 |  | 0.83469 | 21.0505 | 4187 | 0.0060233 | 7.0578 | 7.0638 | -1.3204 | 166.0222 | 3717.7778 | -0.0079533
172 |  | 0.83469 | 21.0425 | 4187 | 0.006021 | 7.0638 | 7.0698 | -1.3204 | 166.0849 | 3738.8203 | -0.0079503
173 |  | 0.83469 | 21.0346 | 4187 | 0.0060187 | 7.0698 | 7.0758 | -1.3204 | 166.1477 | 3759.8549 | -0.0079473
174 |  | 0.83469 | 21.0266 | 4187 | 0.0060165 | 7.0758 | 7.0818 | -1.3204 | 166.2105 | 3780.8815 | -0.0079443
175 |  | 0.83469 | 21.0187 | 4187 | 0.0060142 | 7.0818 | 7.0879 | -1.3204 | 166.2733 | 3801.9002 | -0.0079413
176 |  | 0.83469 | 21.0107 | 4187 | 0.0060119 | 7.0879 | 7.0939 | -1.3204 | 166.3362 | 3822.9109 | -0.0079383
177 |  | 0.83469 | 21.0028 | 4187 | 0.0060096 | 7.0939 | 7.0999 | -1.3204 | 166.399 | 3843.9137 | -0.0079353
178 |  | 0.83469 | 20.9949 | 4187 | 0.0060074 | 7.0999 | 7.1059 | -1.3204 | 166.4619 | 3864.9086 | -0.0079323
179 |  | 0.83469 | 20.9869 | 4187 | 0.0060051 | 7.1059 | 7.1119 | -1.3204 | 166.5249 | 3885.8955 | -0.0079293
180 |  | 0.83469 | 20.979 | 4187 | 0.0060028 | 7.1119 | 7.1179 | -1.3204 | 166.5878 | 3906.8745 | -0.0079263
181 |  | 0.83469 | 20.9711 | 4187 | 0.0060006 | 7.1179 | 7.1239 | -1.3204 | 166.6508 | 3927.8456 | -0.0079233
182 |  | 0.83469 | 20.9632 | 4187 | 0.0059983 | 7.1239 | 7.1299 | -1.3204 | 166.7138 | 3948.8087 | -0.0079203
183 |  | 0.83469 | 20.9552 | 4187 | 0.005996 | 7.1299 | 7.1359 | -1.3204 | 166.7768 | 3969.764 | -0.0079173
184 |  | 0.83469 | 20.9473 | 4187 | 0.0059938 | 7.1359 | 7.1419 | -1.3204 | 166.8398 | 3990.7113 | -0.0079143
185 |  | 0.83469 | 20.9394 | 4187 | 0.0059915 | 7.1419 | 7.1479 | -1.3204 | 166.9029 | 4011.6507 | -0.0079113
186 |  | 0.83469 | 20.9315 | 4187 | 0.0059892 | 7.1479 | 7.1539 | -1.3204 | 166.9659 | 4032.5822 | -0.0079083
187 |  | 0.83469 | 20.9236 | 4187 | 0.005987 | 7.1539 | 7.1599 | -1.3204 | 167.029 | 4053.5058 | -0.0079053
188 |  | 0.83469 | 20.9157 | 4187 | 0.0059847 | 7.1599 | 7.1658 | -1.3204 | 167.0922 | 4074.4214 | -0.0079024
189 |  | 0.83469 | 20.9078 | 4187 | 0.0059825 | 7.1658 | 7.1718 | -1.3204 | 167.1553 | 4095.3292 | -0.0078994
190 |  | 0.83469 | 20.8999 | 4187 | 0.0059802 | 7.1718 | 7.1778 | -1.3204 | 167.2185 | 4116.2291 | -0.0078964
191 |  | 0.83469 | 20.892 | 4187 | 0.0059779 | 7.1778 | 7.1838 | -1.3204 | 167.2817 | 4137.1211 | -0.0078934
192 |  | 0.83469 | 20.8841 | 4187 | 0.0059757 | 7.1838 | 7.1898 | -1.3204 | 167.3449 | 4158.0051 | -0.0078904
193 |  | 0.83469 | 20.8762 | 4187 | 0.0059734 | 7.1898 | 7.1957 | -1.3204 | 167.4082 | 4178.8813 | -0.0078874
194 |  | 0.83469 | 20.8683 | 4187 | 0.0059712 | 7.1957 | 7.2017 | -1.3204 | 167.4715 | 4199.7497 | -0.0078845
195 |  | 0.83469 | 20.8604 | 4187 | 0.0059689 | 7.2017 | 7.2077 | -1.3204 | 167.5348 | 4220.6101 | -0.0078815
196 |  | 0.83469 | 20.8525 | 4187 | 0.0059667 | 7.2077 | 7.2136 | -1.3204 | 167.5981 | 4241.4626 | -0.0078785
197 |  | 0.83469 | 20.8447 | 4187 | 0.0059644 | 7.2136 | 7.2196 | -1.3204 | 167.6614 | 4262.3073 | -0.0078755
198 |  | 0.83469 | 20.8368 | 4187 | 0.0059621 | 7.2196 | 7.2256 | -1.3204 | 167.7248 | 4283.1441 | -0.0078725
199 |  | 0.83469 | 20.8289 | 4187 | 0.0059599 | 7.2256 | 7.2315 | -1.3204 | 167.7882 | 4303.973 | -0.0078696
200 |  | 0.83469 | 20.821 | 4187 | 0.0059576 | 7.2315 | 7.2375 | -1.3204 | 167.8516 | 4324.794 | -0.0078666
201 |  | 0.83469 | 20.8132 | 4187 | 0.0059554 | 7.2375 | 7.2434 | -1.3204 | 167.9151 | 4345.6072 | -0.0078636
202 |  | 0.83469 | 20.8053 | 4187 | 0.0059531 | 7.2434 | 7.2494 | -1.3204 | 167.9785 | 4366.4125 | -0.0078607
203 |  | 0.83469 | 20.7975 | 4187 | 0.0059509 | 7.2494 | 7.2553 | -1.3204 | 168.042 | 4387.21 | -0.0078577
204 |  | 0.83469 | 20.7896 | 4187 | 0.0059486 | 7.2553 | 7.2613 | -1.3204 | 168.1055 | 4407.9996 | -0.0078547
205 |  | 0.83469 | 20.7817 | 4187 | 0.0059464 | 7.2613 | 7.2672 | -1.3204 | 168.1691 | 4428.7813 | -0.0078518
206 |  | 0.83469 | 20.7739 | 4187 | 0.0059442 | 7.2672 | 7.2732 | -1.3204 | 168.2326 | 4449.5552 | -0.0078488
207 |  | 0.83469 | 20.766 | 4187 | 0.0059419 | 7.2732 | 7.2791 | -1.3204 | 168.2962 | 4470.3212 | -0.0078458
208 |  | 0.83469 | 20.7582 | 4187 | 0.0059397 | 7.2791 | 7.2851 | -1.3204 | 168.3598 | 4491.0794 | -0.0078429
209 |  | 0.83469 | 20.7504 | 4187 | 0.0059374 | 7.2851 | 7.291 | -1.3204 | 168.4234 | 4511.8298 | -0.0078399
210 |  | 0.83469 | 20.7425 | 4187 | 0.0059352 | 7.291 | 7.2969 | -1.3204 | 168.4871 | 4532.5723 | -0.0078369
211 |  | 0.83469 | 20.7347 | 4187 | 0.0059329 | 7.2969 | 7.3029 | -1.3204 | 168.5508 | 4553.307 | -0.007834
212 |  | 0.83469 | 20.7268 | 4187 | 0.0059307 | 7.3029 | 7.3088 | -1.3204 | 168.6145 | 4574.0338 | -0.007831
213 |  | 0.83469 | 20.719 | 4187 | 0.0059284 | 7.3088 | 7.3147 | -1.3204 | 168.6782 | 4594.7528 | -0.0078281
214 |  | 0.83469 | 20.7112 | 4187 | 0.0059262 | 7.3147 | 7.3206 | -1.3204 | 168.742 | 4615.464 | -0.0078251
215 |  | 0.83469 | 20.7034 | 4187 | 0.005924 | 7.3206 | 7.3266 | -1.3204 | 168.8058 | 4636.1674 | -0.0078221
216 |  | 0.83469 | 20.6955 | 4187 | 0.0059217 | 7.3266 | 7.3325 | -1.3204 | 168.8696 | 4656.8629 | -0.0078192
217 |  | 0.83469 | 20.6877 | 4187 | 0.0059195 | 7.3325 | 7.3384 | -1.3204 | 168.9334 | 4677.5506 | -0.0078162
218 |  | 0.83469 | 20.6799 | 4187 | 0.0059173 | 7.3384 | 7.3443 | -1.3204 | 168.9972 | 4698.2305 | -0.0078133
219 |  | 0.83469 | 20.6721 | 4187 | 0.005915 | 7.3443 | 7.3502 | -1.3204 | 169.0611 | 4718.9026 | -0.0078103
220 |  | 0.83469 | 20.6643 | 4187 | 0.0059128 | 7.3502 | 7.3562 | -1.3204 | 169.125 | 4739.5669 | -0.0078074
221 |  | 0.83469 | 20.6565 | 4187 | 0.0059106 | 7.3562 | 7.3621 | -1.3204 | 169.1889 | 4760.2234 | -0.0078044
222 |  | 0.83469 | 20.6487 | 4187 | 0.0059083 | 7.3621 | 7.368 | -1.3204 | 169.2529 | 4780.872 | -0.0078015
223 |  | 0.83469 | 20.6409 | 4187 | 0.0059061 | 7.368 | 7.3739 | -1.3204 | 169.3168 | 4801.5129 | -0.0077985
224 |  | 0.83469 | 20.6331 | 4187 | 0.0059039 | 7.3739 | 7.3798 | -1.3204 | 169.3808 | 4822.146 | -0.0077956
225 |  | 0.83469 | 20.6253 | 4187 | 0.0059016 | 7.3798 | 7.3857 | -1.3204 | 169.4449 | 4842.7712 | -0.0077926
226 |  | 0.83469 | 20.6175 | 4187 | 0.0058994 | 7.3857 | 7.3916 | -1.3204 | 169.5089 | 4863.3887 | -0.0077897
227 |  | 0.83469 | 20.6097 | 4187 | 0.0058972 | 7.3916 | 7.3975 | -1.3204 | 169.573 | 4883.9984 | -0.0077867
228 |  | 0.83469 | 20.6019 | 4187 | 0.0058949 | 7.3975 | 7.4034 | -1.3204 | 169.6371 | 4904.6003 | -0.0077838
229 |  | 0.83469 | 20.5941 | 4187 | 0.0058927 | 7.4034 | 7.4093 | -1.3204 | 169.7012 | 4925.1944 | -0.0077809
230 |  | 0.83469 | 20.5863 | 4187 | 0.0058905 | 7.4093 | 7.4152 | -1.3204 | 169.7653 | 4945.7807 | -0.0077779
231 |  | 0.83469 | 20.5786 | 4187 | 0.0058883 | 7.4152 | 7.4211 | -1.3204 | 169.8295 | 4966.3593 | -0.007775
232 |  | 0.83469 | 20.5708 | 4187 | 0.005886 | 7.4211 | 7.4269 | -1.3204 | 169.8937 | 4986.9301 | -0.007772
233 |  | 0.83469 | 20.563 | 4187 | 0.0058838 | 7.4269 | 7.4328 | -1.3204 | 169.9579 | 5007.4931 | -0.0077691
234 |  | 0.83469 | 20.5552 | 4187 | 0.0058816 | 7.4328 | 7.4387 | -1.3204 | 170.0221 | 5028.0483 | -0.0077662
235 |  | 0.83469 | 20.5475 | 4187 | 0.0058794 | 7.4387 | 7.4446 | -1.3204 | 170.0864 | 5048.5958 | -0.0077632
236 |  | 0.83469 | 20.5397 | 4187 | 0.0058771 | 7.4446 | 7.4505 | -1.3204 | 170.1507 | 5069.1355 | -0.0077603

## 50
|  |  | buis | verlies W/M | L /°C/sec
diam | wandikte |  | inhoud l/m |  | W/M
50 | 4.6 | 3.1416 | 1.3074 | 26.2359 | 4187
[8 empty] | J/sec/mtr | aantal mtr. | verlies
|  | buis | verlies W/M | L /°C/sec | verlies temp | begintemp | eindtemp | verlies | bij 1°C | totaal J/sec
|  | inhoud L |  | W/M | °C per M | °C | °C | per m°C | daling | aantal mtr
1 | 50 | 1.3074 | 26.2359 | 4187 | 0.0047927 | 6 | 6.0048 | -1.5433 | 208.6494 | 26.2359 | -0.0073966
2 |  | 1.3074 | 26.2285 | 4187 | 0.0047914 | 6.0048 | 6.0096 | -1.5433 | 208.7082 | 52.4644 | -0.0073945
3 |  | 1.3074 | 26.2211 | 4187 | 0.00479 | 6.0096 | 6.0144 | -1.5433 | 208.7671 | 78.6855 | -0.0073924
4 |  | 1.3074 | 26.2137 | 4187 | 0.0047887 | 6.0144 | 6.0192 | -1.5433 | 208.8259 | 104.8993 | -0.0073903
5 |  | 1.3074 | 26.2063 | 4187 | 0.0047873 | 6.0192 | 6.024 | -1.5433 | 208.8848 | 131.1056 | -0.0073882
6 |  | 1.3074 | 26.1989 | 4187 | 0.004786 | 6.024 | 6.0287 | -1.5433 | 208.9437 | 157.3046 | -0.0073861
7 |  | 1.3074 | 26.1916 | 4187 | 0.0047846 | 6.0287 | 6.0335 | -1.5433 | 209.0026 | 183.4961 | -0.0073841
8 |  | 1.3074 | 26.1842 | 4187 | 0.0047833 | 6.0335 | 6.0383 | -1.5433 | 209.0616 | 209.6803 | -0.007382
9 |  | 1.3074 | 26.1768 | 4187 | 0.0047819 | 6.0383 | 6.0431 | -1.5433 | 209.1205 | 235.8571 | -0.0073799
10 |  | 1.3074 | 26.1694 | 4187 | 0.0047806 | 6.0431 | 6.0479 | -1.5433 | 209.1795 | 262.0265 | -0.0073778
11 |  | 1.3074 | 26.162 | 4187 | 0.0047792 | 6.0479 | 6.0526 | -1.5433 | 209.2385 | 288.1885 | -0.0073757
12 |  | 1.3074 | 26.1547 | 4187 | 0.0047779 | 6.0526 | 6.0574 | -1.5433 | 209.2975 | 314.3432 | -0.0073737
13 |  | 1.3074 | 26.1473 | 4187 | 0.0047765 | 6.0574 | 6.0622 | -1.5433 | 209.3565 | 340.4905 | -0.0073716
14 |  | 1.3074 | 26.1399 | 4187 | 0.0047752 | 6.0622 | 6.067 | -1.5433 | 209.4156 | 366.6304 | -0.0073695
15 |  | 1.3074 | 26.1325 | 4187 | 0.0047738 | 6.067 | 6.0717 | -1.5433 | 209.4746 | 392.763 | -0.0073674
16 |  | 1.3074 | 26.1252 | 4187 | 0.0047725 | 6.0717 | 6.0765 | -1.5433 | 209.5337 | 418.8881 | -0.0073653
17 |  | 1.3074 | 26.1178 | 4187 | 0.0047712 | 6.0765 | 6.0813 | -1.5433 | 209.5928 | 445.0059 | -0.0073633
18 |  | 1.3074 | 26.1105 | 4187 | 0.0047698 | 6.0813 | 6.0861 | -1.5433 | 209.6519 | 471.1164 | -0.0073612
19 |  | 1.3074 | 26.1031 | 4187 | 0.0047685 | 6.0861 | 6.0908 | -1.5433 | 209.711 | 497.2195 | -0.0073591
20 |  | 1.3074 | 26.0957 | 4187 | 0.0047671 | 6.0908 | 6.0956 | -1.5433 | 209.7702 | 523.3152 | -0.007357
21 |  | 1.3074 | 26.0884 | 4187 | 0.0047658 | 6.0956 | 6.1004 | -1.5433 | 209.8293 | 549.4036 | -0.007355
22 |  | 1.3074 | 26.081 | 4187 | 0.0047644 | 6.1004 | 6.1051 | -1.5433 | 209.8885 | 575.4846 | -0.0073529
23 |  | 1.3074 | 26.0737 | 4187 | 0.0047631 | 6.1051 | 6.1099 | -1.5433 | 209.9477 | 601.5583 | -0.0073508
24 |  | 1.3074 | 26.0663 | 4187 | 0.0047617 | 6.1099 | 6.1147 | -1.5433 | 210.0069 | 627.6246 | -0.0073488
25 |  | 1.3074 | 26.059 | 4187 | 0.0047604 | 6.1147 | 6.1194 | -1.5433 | 210.0661 | 653.6836 | -0.0073467
26 |  | 1.3074 | 26.0516 | 4187 | 0.0047591 | 6.1194 | 6.1242 | -1.5433 | 210.1253 | 679.7352 | -0.0073446
27 |  | 1.3074 | 26.0443 | 4187 | 0.0047577 | 6.1242 | 6.1289 | -1.5433 | 210.1846 | 705.7795 | -0.0073425
28 |  | 1.3074 | 26.0369 | 4187 | 0.0047564 | 6.1289 | 6.1337 | -1.5433 | 210.2439 | 731.8164 | -0.0073405
29 |  | 1.3074 | 26.0296 | 4187 | 0.004755 | 6.1337 | 6.1384 | -1.5433 | 210.3032 | 757.846 | -0.0073384
30 |  | 1.3074 | 26.0223 | 4187 | 0.0047537 | 6.1384 | 6.1432 | -1.5433 | 210.3625 | 783.8682 | -0.0073363
31 |  | 1.3074 | 26.0149 | 4187 | 0.0047524 | 6.1432 | 6.1479 | -1.5433 | 210.4218 | 809.8831 | -0.0073343
32 |  | 1.3074 | 26.0076 | 4187 | 0.004751 | 6.1479 | 6.1527 | -1.5433 | 210.4811 | 835.8907 | -0.0073322
33 |  | 1.3074 | 26.0003 | 4187 | 0.0047497 | 6.1527 | 6.1574 | -1.5433 | 210.5405 | 861.891 | -0.0073301
34 |  | 1.3074 | 25.9929 | 4187 | 0.0047483 | 6.1574 | 6.1622 | -1.5433 | 210.5999 | 887.8839 | -0.0073281
35 |  | 1.3074 | 25.9856 | 4187 | 0.004747 | 6.1622 | 6.1669 | -1.5433 | 210.6593 | 913.8695 | -0.007326
36 |  | 1.3074 | 25.9783 | 4187 | 0.0047457 | 6.1669 | 6.1717 | -1.5433 | 210.7187 | 939.8478 | -0.0073239
37 |  | 1.3074 | 25.9709 | 4187 | 0.0047443 | 6.1717 | 6.1764 | -1.5433 | 210.7781 | 965.8187 | -0.0073219
38 |  | 1.3074 | 25.9636 | 4187 | 0.004743 | 6.1764 | 6.1812 | -1.5433 | 210.8375 | 991.7823 | -0.0073198
39 |  | 1.3074 | 25.9563 | 4187 | 0.0047417 | 6.1812 | 6.1859 | -1.5433 | 210.897 | 1017.7386 | -0.0073177
40 |  | 1.3074 | 25.949 | 4187 | 0.0047403 | 6.1859 | 6.1907 | -1.5433 | 210.9565 | 1043.6876 | -0.0073157
41 |  | 1.3074 | 25.9417 | 4187 | 0.004739 | 6.1907 | 6.1954 | -1.5433 | 211.0159 | 1069.6293 | -0.0073136
42 |  | 1.3074 | 25.9344 | 4187 | 0.0047376 | 6.1954 | 6.2001 | -1.5433 | 211.0755 | 1095.5636 | -0.0073116
43 |  | 1.3074 | 25.927 | 4187 | 0.0047363 | 6.2001 | 6.2049 | -1.5433 | 211.135 | 1121.4907 | -0.0073095
44 |  | 1.3074 | 25.9197 | 4187 | 0.004735 | 6.2049 | 6.2096 | -1.5433 | 211.1945 | 1147.4104 | -0.0073074
45 |  | 1.3074 | 25.9124 | 4187 | 0.0047336 | 6.2096 | 6.2143 | -1.5433 | 211.2541 | 1173.3228 | -0.0073054
46 |  | 1.3074 | 25.9051 | 4187 | 0.0047323 | 6.2143 | 6.2191 | -1.5433 | 211.3137 | 1199.228 | -0.0073033
47 |  | 1.3074 | 25.8978 | 4187 | 0.004731 | 6.2191 | 6.2238 | -1.5433 | 211.3732 | 1225.1258 | -0.0073012
48 |  | 1.3074 | 25.8905 | 4187 | 0.0047296 | 6.2238 | 6.2285 | -1.5433 | 211.4329 | 1251.0163 | -0.0072992
49 |  | 1.3074 | 25.8832 | 4187 | 0.0047283 | 6.2285 | 6.2333 | -1.5433 | 211.4925 | 1276.8995 | -0.0072971
50 |  | 1.3074 | 25.8759 | 4187 | 0.004727 | 6.2333 | 6.238 | -1.5433 | 211.5521 | 1302.7754 | -0.0072951
51 |  | 1.3074 | 25.8686 | 4187 | 0.0047256 | 6.238 | 6.2427 | -1.5433 | 211.6118 | 1328.644 | -0.007293
52 |  | 1.3074 | 25.8613 | 4187 | 0.0047243 | 6.2427 | 6.2474 | -1.5433 | 211.6715 | 1354.5054 | -0.007291
53 |  | 1.3074 | 25.854 | 4187 | 0.004723 | 6.2474 | 6.2522 | -1.5433 | 211.7311 | 1380.3594 | -0.0072889
54 |  | 1.3074 | 25.8468 | 4187 | 0.0047216 | 6.2522 | 6.2569 | -1.5433 | 211.7909 | 1406.2062 | -0.0072869
55 |  | 1.3074 | 25.8395 | 4187 | 0.0047203 | 6.2569 | 6.2616 | -1.5433 | 211.8506 | 1432.0456 | -0.0072848
56 |  | 1.3074 | 25.8322 | 4187 | 0.004719 | 6.2616 | 6.2663 | -1.5433 | 211.9103 | 1457.8778 | -0.0072827
57 |  | 1.3074 | 25.8249 | 4187 | 0.0047176 | 6.2663 | 6.271 | -1.5433 | 211.9701 | 1483.7027 | -0.0072807
58 |  | 1.3074 | 25.8176 | 4187 | 0.0047163 | 6.271 | 6.2758 | -1.5433 | 212.0299 | 1509.5203 | -0.0072786
59 |  | 1.3074 | 25.8103 | 4187 | 0.004715 | 6.2758 | 6.2805 | -1.5433 | 212.0897 | 1535.3307 | -0.0072766
60 |  | 1.3074 | 25.8031 | 4187 | 0.0047137 | 6.2805 | 6.2852 | -1.5433 | 212.1495 | 1561.1337 | -0.0072745
61 |  | 1.3074 | 25.7958 | 4187 | 0.0047123 | 6.2852 | 6.2899 | -1.5433 | 212.2093 | 1586.9295 | -0.0072725
62 |  | 1.3074 | 25.7885 | 4187 | 0.004711 | 6.2899 | 6.2946 | -1.5433 | 212.2691 | 1612.718 | -0.0072704
63 |  | 1.3074 | 25.7812 | 4187 | 0.0047097 | 6.2946 | 6.2993 | -1.5433 | 212.329 | 1638.4993 | -0.0072684
64 |  | 1.3074 | 25.774 | 4187 | 0.0047083 | 6.2993 | 6.304 | -1.5433 | 212.3889 | 1664.2732 | -0.0072663
65 |  | 1.3074 | 25.7667 | 4187 | 0.004707 | 6.304 | 6.3087 | -1.5433 | 212.4488 | 1690.0399 | -0.0072643
66 |  | 1.3074 | 25.7594 | 4187 | 0.0047057 | 6.3087 | 6.3134 | -1.5433 | 212.5087 | 1715.7994 | -0.0072622
67 |  | 1.3074 | 25.7522 | 4187 | 0.0047044 | 6.3134 | 6.3181 | -1.5433 | 212.5686 | 1741.5516 | -0.0072602
68 |  | 1.3074 | 25.7449 | 4187 | 0.004703 | 6.3181 | 6.3228 | -1.5433 | 212.6286 | 1767.2965 | -0.0072581
69 |  | 1.3074 | 25.7377 | 4187 | 0.0047017 | 6.3228 | 6.3275 | -1.5433 | 212.6885 | 1793.0342 | -0.0072561
70 |  | 1.3074 | 25.7304 | 4187 | 0.0047004 | 6.3275 | 6.3322 | -1.5433 | 212.7485 | 1818.7646 | -0.0072541
71 |  | 1.3074 | 25.7232 | 4187 | 0.0046991 | 6.3322 | 6.3369 | -1.5433 | 212.8085 | 1844.4877 | -0.007252
72 |  | 1.3074 | 25.7159 | 4187 | 0.0046977 | 6.3369 | 6.3416 | -1.5433 | 212.8685 | 1870.2036 | -0.00725
73 |  | 1.3074 | 25.7087 | 4187 | 0.0046964 | 6.3416 | 6.3463 | -1.5433 | 212.9285 | 1895.9123 | -0.0072479
74 |  | 1.3074 | 25.7014 | 4187 | 0.0046951 | 6.3463 | 6.351 | -1.5433 | 212.9886 | 1921.6137 | -0.0072459
75 |  | 1.3074 | 25.6942 | 4187 | 0.0046938 | 6.351 | 6.3557 | -1.5433 | 213.0486 | 1947.3078 | -0.0072438
76 |  | 1.3074 | 25.6869 | 4187 | 0.0046924 | 6.3557 | 6.3604 | -1.5433 | 213.1087 | 1972.9948 | -0.0072418
77 |  | 1.3074 | 25.6797 | 4187 | 0.0046911 | 6.3604 | 6.3651 | -1.5433 | 213.1688 | 1998.6744 | -0.0072397
78 |  | 1.3074 | 25.6724 | 4187 | 0.0046898 | 6.3651 | 6.3698 | -1.5433 | 213.2289 | 2024.3469 | -0.0072377
79 |  | 1.3074 | 25.6652 | 4187 | 0.0046885 | 6.3698 | 6.3745 | -1.5433 | 213.2891 | 2050.0121 | -0.0072357
80 |  | 1.3074 | 25.658 | 4187 | 0.0046872 | 6.3745 | 6.3792 | -1.5433 | 213.3492 | 2075.67 | -0.0072336
81 |  | 1.3074 | 25.6507 | 4187 | 0.0046858 | 6.3792 | 6.3839 | -1.5433 | 213.4094 | 2101.3207 | -0.0072316
82 |  | 1.3074 | 25.6435 | 4187 | 0.0046845 | 6.3839 | 6.3886 | -1.5433 | 213.4696 | 2126.9642 | -0.0072295
83 |  | 1.3074 | 25.6363 | 4187 | 0.0046832 | 6.3886 | 6.3932 | -1.5433 | 213.5298 | 2152.6005 | -0.0072275
84 |  | 1.3074 | 25.629 | 4187 | 0.0046819 | 6.3932 | 6.3979 | -1.5433 | 213.59 | 2178.2295 | -0.0072255
85 |  | 1.3074 | 25.6218 | 4187 | 0.0046805 | 6.3979 | 6.4026 | -1.5433 | 213.6502 | 2203.8513 | -0.0072234
86 |  | 1.3074 | 25.6146 | 4187 | 0.0046792 | 6.4026 | 6.4073 | -1.5433 | 213.7105 | 2229.4659 | -0.0072214
87 |  | 1.3074 | 25.6074 | 4187 | 0.0046779 | 6.4073 | 6.412 | -1.5433 | 213.7707 | 2255.0733 | -0.0072194
88 |  | 1.3074 | 25.6001 | 4187 | 0.0046766 | 6.412 | 6.4166 | -1.5433 | 213.831 | 2280.6734 | -0.0072173
89 |  | 1.3074 | 25.5929 | 4187 | 0.0046753 | 6.4166 | 6.4213 | -1.5433 | 213.8913 | 2306.2664 | -0.0072153
90 |  | 1.3074 | 25.5857 | 4187 | 0.004674 | 6.4213 | 6.426 | -1.5433 | 213.9516 | 2331.8521 | -0.0072133
91 |  | 1.3074 | 25.5785 | 4187 | 0.0046726 | 6.426 | 6.4307 | -1.5433 | 214.012 | 2357.4306 | -0.0072112
92 |  | 1.3074 | 25.5713 | 4187 | 0.0046713 | 6.4307 | 6.4353 | -1.5433 | 214.0723 | 2383.0019 | -0.0072092
93 |  | 1.3074 | 25.5641 | 4187 | 0.00467 | 6.4353 | 6.44 | -1.5433 | 214.1327 | 2408.566 | -0.0072072
94 |  | 1.3074 | 25.5569 | 4187 | 0.0046687 | 6.44 | 6.4447 | -1.5433 | 214.1931 | 2434.1228 | -0.0072051
95 |  | 1.3074 | 25.5497 | 4187 | 0.0046674 | 6.4447 | 6.4493 | -1.5433 | 214.2535 | 2459.6725 | -0.0072031
96 |  | 1.3074 | 25.5425 | 4187 | 0.0046661 | 6.4493 | 6.454 | -1.5433 | 214.3139 | 2485.215 | -0.0072011
97 |  | 1.3074 | 25.5353 | 4187 | 0.0046647 | 6.454 | 6.4587 | -1.5433 | 214.3743 | 2510.7502 | -0.007199
98 |  | 1.3074 | 25.5281 | 4187 | 0.0046634 | 6.4587 | 6.4633 | -1.5433 | 214.4348 | 2536.2783 | -0.007197
99 |  | 1.3074 | 25.5209 | 4187 | 0.0046621 | 6.4633 | 6.468 | -1.5433 | 214.4953 | 2561.7992 | -0.007195
100 |  | 1.3074 | 25.5137 | 4187 | 0.0046608 | 6.468 | 6.4726 | -1.5433 | 214.5558 | 2587.3128 | -0.0071929
101 |  | 1.3074 | 25.5065 | 4187 | 0.0046595 | 6.4726 | 6.4773 | -1.5433 | 214.6163 | 2612.8193 | -0.0071909
102 |  | 1.3074 | 25.4993 | 4187 | 0.0046582 | 6.4773 | 6.482 | -1.5433 | 214.6768 | 2638.3186 | -0.0071889
103 |  | 1.3074 | 25.4921 | 4187 | 0.0046569 | 6.482 | 6.4866 | -1.5433 | 214.7373 | 2663.8107 | -0.0071869
104 |  | 1.3074 | 25.4849 | 4187 | 0.0046555 | 6.4866 | 6.4913 | -1.5433 | 214.7979 | 2689.2956 | -0.0071848
105 |  | 1.3074 | 25.4777 | 4187 | 0.0046542 | 6.4913 | 6.4959 | -1.5433 | 214.8585 | 2714.7734 | -0.0071828
106 |  | 1.3074 | 25.4705 | 4187 | 0.0046529 | 6.4959 | 6.5006 | -1.5433 | 214.919 | 2740.2439 | -0.0071808
107 |  | 1.3074 | 25.4634 | 4187 | 0.0046516 | 6.5006 | 6.5052 | -1.5433 | 214.9797 | 2765.7073 | -0.0071788
108 |  | 1.3074 | 25.4562 | 4187 | 0.0046503 | 6.5052 | 6.5099 | -1.5433 | 215.0403 | 2791.1635 | -0.0071767
109 |  | 1.3074 | 25.449 | 4187 | 0.004649 | 6.5099 | 6.5145 | -1.5433 | 215.1009 | 2816.6125 | -0.0071747
110 |  | 1.3074 | 25.4418 | 4187 | 0.0046477 | 6.5145 | 6.5192 | -1.5433 | 215.1616 | 2842.0543 | -0.0071727
111 |  | 1.3074 | 25.4347 | 4187 | 0.0046464 | 6.5192 | 6.5238 | -1.5433 | 215.2223 | 2867.489 | -0.0071707
112 |  | 1.3074 | 25.4275 | 4187 | 0.004645 | 6.5238 | 6.5285 | -1.5433 | 215.283 | 2892.9165 | -0.0071687
113 |  | 1.3074 | 25.4203 | 4187 | 0.0046437 | 6.5285 | 6.5331 | -1.5433 | 215.3437 | 2918.3368 | -0.0071666
114 |  | 1.3074 | 25.4132 | 4187 | 0.0046424 | 6.5331 | 6.5378 | -1.5433 | 215.4044 | 2943.7499 | -0.0071646
115 |  | 1.3074 | 25.406 | 4187 | 0.0046411 | 6.5378 | 6.5424 | -1.5433 | 215.4651 | 2969.1559 | -0.0071626
116 |  | 1.3074 | 25.3988 | 4187 | 0.0046398 | 6.5424 | 6.547 | -1.5433 | 215.5259 | 2994.5548 | -0.0071606
117 |  | 1.3074 | 25.3917 | 4187 | 0.0046385 | 6.547 | 6.5517 | -1.5433 | 215.5867 | 3019.9464 | -0.0071586
118 |  | 1.3074 | 25.3845 | 4187 | 0.0046372 | 6.5517 | 6.5563 | -1.5433 | 215.6475 | 3045.3309 | -0.0071565
119 |  | 1.3074 | 25.3774 | 4187 | 0.0046359 | 6.5563 | 6.561 | -1.5433 | 215.7083 | 3070.7083 | -0.0071545
120 |  | 1.3074 | 25.3702 | 4187 | 0.0046346 | 6.561 | 6.5656 | -1.5433 | 215.7691 | 3096.0785 | -0.0071525
121 |  | 1.3074 | 25.363 | 4187 | 0.0046333 | 6.5656 | 6.5702 | -1.5433 | 215.83 | 3121.4415 | -0.0071505
122 |  | 1.3074 | 25.3559 | 4187 | 0.004632 | 6.5702 | 6.5749 | -1.5433 | 215.8908 | 3146.7974 | -0.0071485
123 |  | 1.3074 | 25.3487 | 4187 | 0.0046307 | 6.5749 | 6.5795 | -1.5433 | 215.9517 | 3172.1462 | -0.0071465
124 |  | 1.3074 | 25.3416 | 4187 | 0.0046294 | 6.5795 | 6.5841 | -1.5433 | 216.0126 | 3197.4878 | -0.0071444
125 |  | 1.3074 | 25.3345 | 4187 | 0.0046281 | 6.5841 | 6.5887 | -1.5433 | 216.0735 | 3222.8222 | -0.0071424
126 |  | 1.3074 | 25.3273 | 4187 | 0.0046267 | 6.5887 | 6.5934 | -1.5433 | 216.1345 | 3248.1496 | -0.0071404
127 |  | 1.3074 | 25.3202 | 4187 | 0.0046254 | 6.5934 | 6.598 | -1.5433 | 216.1954 | 3273.4697 | -0.0071384
128 |  | 1.3074 | 25.313 | 4187 | 0.0046241 | 6.598 | 6.6026 | -1.5433 | 216.2564 | 3298.7828 | -0.0071364
129 |  | 1.3074 | 25.3059 | 4187 | 0.0046228 | 6.6026 | 6.6072 | -1.5433 | 216.3174 | 3324.0887 | -0.0071344
130 |  | 1.3074 | 25.2988 | 4187 | 0.0046215 | 6.6072 | 6.6119 | -1.5433 | 216.3784 | 3349.3874 | -0.0071324
131 |  | 1.3074 | 25.2916 | 4187 | 0.0046202 | 6.6119 | 6.6165 | -1.5433 | 216.4394 | 3374.6791 | -0.0071304
132 |  | 1.3074 | 25.2845 | 4187 | 0.0046189 | 6.6165 | 6.6211 | -1.5433 | 216.5004 | 3399.9636 | -0.0071283
133 |  | 1.3074 | 25.2774 | 4187 | 0.0046176 | 6.6211 | 6.6257 | -1.5433 | 216.5615 | 3425.2409 | -0.0071263
134 |  | 1.3074 | 25.2702 | 4187 | 0.0046163 | 6.6257 | 6.6303 | -1.5433 | 216.6226 | 3450.5112 | -0.0071243
135 |  | 1.3074 | 25.2631 | 4187 | 0.004615 | 6.6303 | 6.6349 | -1.5433 | 216.6836 | 3475.7743 | -0.0071223
136 |  | 1.3074 | 25.256 | 4187 | 0.0046137 | 6.6349 | 6.6396 | -1.5433 | 216.7447 | 3501.0303 | -0.0071203
137 |  | 1.3074 | 25.2489 | 4187 | 0.0046124 | 6.6396 | 6.6442 | -1.5433 | 216.8059 | 3526.2792 | -0.0071183
138 |  | 1.3074 | 25.2418 | 4187 | 0.0046111 | 6.6442 | 6.6488 | -1.5433 | 216.867 | 3551.521 | -0.0071163
139 |  | 1.3074 | 25.2346 | 4187 | 0.0046098 | 6.6488 | 6.6534 | -1.5433 | 216.9282 | 3576.7556 | -0.0071143
140 |  | 1.3074 | 25.2275 | 4187 | 0.0046085 | 6.6534 | 6.658 | -1.5433 | 216.9893 | 3601.9831 | -0.0071123
141 |  | 1.3074 | 25.2204 | 4187 | 0.0046072 | 6.658 | 6.6626 | -1.5433 | 217.0505 | 3627.2035 | -0.0071103
142 |  | 1.3074 | 25.2133 | 4187 | 0.0046059 | 6.6626 | 6.6672 | -1.5433 | 217.1117 | 3652.4169 | -0.0071083
143 |  | 1.3074 | 25.2062 | 4187 | 0.0046046 | 6.6672 | 6.6718 | -1.5433 | 217.173 | 3677.6231 | -0.0071063
144 |  | 1.3074 | 25.1991 | 4187 | 0.0046033 | 6.6718 | 6.6764 | -1.5433 | 217.2342 | 3702.8222 | -0.0071043
145 |  | 1.3074 | 25.192 | 4187 | 0.004602 | 6.6764 | 6.681 | -1.5433 | 217.2955 | 3728.0141 | -0.0071023
146 |  | 1.3074 | 25.1849 | 4187 | 0.0046007 | 6.681 | 6.6856 | -1.5433 | 217.3568 | 3753.199 | -0.0071003
147 |  | 1.3074 | 25.1778 | 4187 | 0.0045994 | 6.6856 | 6.6902 | -1.5433 | 217.4181 | 3778.3768 | -0.0070983
148 |  | 1.3074 | 25.1707 | 4187 | 0.0045981 | 6.6902 | 6.6948 | -1.5433 | 217.4794 | 3803.5475 | -0.0070963
149 |  | 1.3074 | 25.1636 | 4187 | 0.0045968 | 6.6948 | 6.6994 | -1.5433 | 217.5407 | 3828.7111 | -0.0070943
150 |  | 1.3074 | 25.1565 | 4187 | 0.0045955 | 6.6994 | 6.704 | -1.5433 | 217.602 | 3853.8676 | -0.0070923
151 |  | 1.3074 | 25.1494 | 4187 | 0.0045942 | 6.704 | 6.7086 | -1.5433 | 217.6634 | 3879.017 | -0.0070903
152 |  | 1.3074 | 25.1423 | 4187 | 0.004593 | 6.7086 | 6.7132 | -1.5433 | 217.7248 | 3904.1593 | -0.0070883
153 |  | 1.3074 | 25.1352 | 4187 | 0.0045917 | 6.7132 | 6.7178 | -1.5433 | 217.7862 | 3929.2946 | -0.0070863
154 |  | 1.3074 | 25.1281 | 4187 | 0.0045904 | 6.7178 | 6.7224 | -1.5433 | 217.8476 | 3954.4227 | -0.0070843
155 |  | 1.3074 | 25.1211 | 4187 | 0.0045891 | 6.7224 | 6.727 | -1.5433 | 217.909 | 3979.5438 | -0.0070823
156 |  | 1.3074 | 25.114 | 4187 | 0.0045878 | 6.727 | 6.7316 | -1.5433 | 217.9705 | 4004.6577 | -0.0070803
157 |  | 1.3074 | 25.1069 | 4187 | 0.0045865 | 6.7316 | 6.7362 | -1.5433 | 218.032 | 4029.7646 | -0.0070783
158 |  | 1.3074 | 25.0998 | 4187 | 0.0045852 | 6.7362 | 6.7407 | -1.5433 | 218.0934 | 4054.8644 | -0.0070763
159 |  | 1.3074 | 25.0927 | 4187 | 0.0045839 | 6.7407 | 6.7453 | -1.5433 | 218.1549 | 4079.9572 | -0.0070743
160 |  | 1.3074 | 25.0857 | 4187 | 0.0045826 | 6.7453 | 6.7499 | -1.5433 | 218.2165 | 4105.0428 | -0.0070723
161 |  | 1.3074 | 25.0786 | 4187 | 0.0045813 | 6.7499 | 6.7545 | -1.5433 | 218.278 | 4130.1214 | -0.0070703
162 |  | 1.3074 | 25.0715 | 4187 | 0.00458 | 6.7545 | 6.7591 | -1.5433 | 218.3396 | 4155.193 | -0.0070683
163 |  | 1.3074 | 25.0645 | 4187 | 0.0045787 | 6.7591 | 6.7636 | -1.5433 | 218.4011 | 4180.2574 | -0.0070663
164 |  | 1.3074 | 25.0574 | 4187 | 0.0045774 | 6.7636 | 6.7682 | -1.5433 | 218.4627 | 4205.3148 | -0.0070643
165 |  | 1.3074 | 25.0503 | 4187 | 0.0045761 | 6.7682 | 6.7728 | -1.5433 | 218.5243 | 4230.3651 | -0.0070623
166 |  | 1.3074 | 25.0433 | 4187 | 0.0045749 | 6.7728 | 6.7774 | -1.5433 | 218.586 | 4255.4084 | -0.0070603
167 |  | 1.3074 | 25.0362 | 4187 | 0.0045736 | 6.7774 | 6.7819 | -1.5433 | 218.6476 | 4280.4446 | -0.0070583
168 |  | 1.3074 | 25.0291 | 4187 | 0.0045723 | 6.7819 | 6.7865 | -1.5433 | 218.7093 | 4305.4737 | -0.0070563
169 |  | 1.3074 | 25.0221 | 4187 | 0.004571 | 6.7865 | 6.7911 | -1.5433 | 218.7709 | 4330.4958 | -0.0070544
170 |  | 1.3074 | 25.015 | 4187 | 0.0045697 | 6.7911 | 6.7957 | -1.5433 | 218.8326 | 4355.5109 | -0.0070524
171 |  | 1.3074 | 25.008 | 4187 | 0.0045684 | 6.7957 | 6.8002 | -1.5433 | 218.8943 | 4380.5188 | -0.0070504
172 |  | 1.3074 | 25.0009 | 4187 | 0.0045671 | 6.8002 | 6.8048 | -1.5433 | 218.9561 | 4405.5198 | -0.0070484
173 |  | 1.3074 | 24.9939 | 4187 | 0.0045658 | 6.8048 | 6.8094 | -1.5433 | 219.0178 | 4430.5137 | -0.0070464
174 |  | 1.3074 | 24.9868 | 4187 | 0.0045646 | 6.8094 | 6.8139 | -1.5433 | 219.0796 | 4455.5005 | -0.0070444
175 |  | 1.3074 | 24.9798 | 4187 | 0.0045633 | 6.8139 | 6.8185 | -1.5433 | 219.1414 | 4480.4803 | -0.0070424
176 |  | 1.3074 | 24.9727 | 4187 | 0.004562 | 6.8185 | 6.823 | -1.5433 | 219.2032 | 4505.453 | -0.0070404
177 |  | 1.3074 | 24.9657 | 4187 | 0.0045607 | 6.823 | 6.8276 | -1.5433 | 219.265 | 4530.4187 | -0.0070385
178 |  | 1.3074 | 24.9587 | 4187 | 0.0045594 | 6.8276 | 6.8322 | -1.5433 | 219.3268 | 4555.3774 | -0.0070365
179 |  | 1.3074 | 24.9516 | 4187 | 0.0045581 | 6.8322 | 6.8367 | -1.5433 | 219.3887 | 4580.329 | -0.0070345
180 |  | 1.3074 | 24.9446 | 4187 | 0.0045568 | 6.8367 | 6.8413 | -1.5433 | 219.4505 | 4605.2736 | -0.0070325
181 |  | 1.3074 | 24.9376 | 4187 | 0.0045556 | 6.8413 | 6.8458 | -1.5433 | 219.5124 | 4630.2112 | -0.0070305
182 |  | 1.3074 | 24.9305 | 4187 | 0.0045543 | 6.8458 | 6.8504 | -1.5433 | 219.5743 | 4655.1417 | -0.0070285
183 |  | 1.3074 | 24.9235 | 4187 | 0.004553 | 6.8504 | 6.8549 | -1.5433 | 219.6362 | 4680.0653 | -0.0070266
184 |  | 1.3074 | 24.9165 | 4187 | 0.0045517 | 6.8549 | 6.8595 | -1.5433 | 219.6982 | 4704.9817 | -0.0070246
185 |  | 1.3074 | 24.9095 | 4187 | 0.0045504 | 6.8595 | 6.864 | -1.5433 | 219.7601 | 4729.8912 | -0.0070226
186 |  | 1.3074 | 24.9024 | 4187 | 0.0045491 | 6.864 | 6.8686 | -1.5433 | 219.8221 | 4754.7936 | -0.0070206
187 |  | 1.3074 | 24.8954 | 4187 | 0.0045479 | 6.8686 | 6.8731 | -1.5433 | 219.8841 | 4779.689 | -0.0070186
188 |  | 1.3074 | 24.8884 | 4187 | 0.0045466 | 6.8731 | 6.8777 | -1.5433 | 219.9461 | 4804.5774 | -0.0070167
189 |  | 1.3074 | 24.8814 | 4187 | 0.0045453 | 6.8777 | 6.8822 | -1.5433 | 220.0081 | 4829.4588 | -0.0070147
190 |  | 1.3074 | 24.8744 | 4187 | 0.004544 | 6.8822 | 6.8868 | -1.5433 | 220.0702 | 4854.3332 | -0.0070127
191 |  | 1.3074 | 24.8674 | 4187 | 0.0045427 | 6.8868 | 6.8913 | -1.5433 | 220.1322 | 4879.2005 | -0.0070107
192 |  | 1.3074 | 24.8603 | 4187 | 0.0045414 | 6.8913 | 6.8959 | -1.5433 | 220.1943 | 4904.0609 | -0.0070088
193 |  | 1.3074 | 24.8533 | 4187 | 0.0045402 | 6.8959 | 6.9004 | -1.5433 | 220.2564 | 4928.9142 | -0.0070068
194 |  | 1.3074 | 24.8463 | 4187 | 0.0045389 | 6.9004 | 6.9049 | -1.5433 | 220.3185 | 4953.7605 | -0.0070048
195 |  | 1.3074 | 24.8393 | 4187 | 0.0045376 | 6.9049 | 6.9095 | -1.5433 | 220.3807 | 4978.5998 | -0.0070028
196 |  | 1.3074 | 24.8323 | 4187 | 0.0045363 | 6.9095 | 6.914 | -1.5433 | 220.4428 | 5003.4322 | -0.0070009
197 |  | 1.3074 | 24.8253 | 4187 | 0.004535 | 6.914 | 6.9186 | -1.5433 | 220.505 | 5028.2575 | -0.0069989
198 |  | 1.3074 | 24.8183 | 4187 | 0.0045338 | 6.9186 | 6.9231 | -1.5433 | 220.5672 | 5053.0758 | -0.0069969
199 |  | 1.3074 | 24.8113 | 4187 | 0.0045325 | 6.9231 | 6.9276 | -1.5433 | 220.6294 | 5077.8871 | -0.0069949
200 |  | 1.3074 | 24.8043 | 4187 | 0.0045312 | 6.9276 | 6.9322 | -1.5433 | 220.6916 | 5102.6914 | -0.006993
201 |  | 1.3074 | 24.7973 | 4187 | 0.0045299 | 6.9322 | 6.9367 | -1.5433 | 220.7538 | 5127.4888 | -0.006991
202 |  | 1.3074 | 24.7903 | 4187 | 0.0045287 | 6.9367 | 6.9412 | -1.5433 | 220.8161 | 5152.2791 | -0.006989
203 |  | 1.3074 | 24.7834 | 4187 | 0.0045274 | 6.9412 | 6.9457 | -1.5433 | 220.8783 | 5177.0625 | -0.0069871
204 |  | 1.3074 | 24.7764 | 4187 | 0.0045261 | 6.9457 | 6.9503 | -1.5433 | 220.9406 | 5201.8388 | -0.0069851
205 |  | 1.3074 | 24.7694 | 4187 | 0.0045248 | 6.9503 | 6.9548 | -1.5433 | 221.0029 | 5226.6082 | -0.0069831
206 |  | 1.3074 | 24.7624 | 4187 | 0.0045236 | 6.9548 | 6.9593 | -1.5433 | 221.0653 | 5251.3706 | -0.0069811
207 |  | 1.3074 | 24.7554 | 4187 | 0.0045223 | 6.9593 | 6.9638 | -1.5433 | 221.1276 | 5276.126 | -0.0069792
208 |  | 1.3074 | 24.7484 | 4187 | 0.004521 | 6.9638 | 6.9684 | -1.5433 | 221.19 | 5300.8744 | -0.0069772
209 |  | 1.3074 | 24.7415 | 4187 | 0.0045197 | 6.9684 | 6.9729 | -1.5433 | 221.2523 | 5325.6159 | -0.0069752
210 |  | 1.3074 | 24.7345 | 4187 | 0.0045185 | 6.9729 | 6.9774 | -1.5433 | 221.3147 | 5350.3504 | -0.0069733
211 |  | 1.3074 | 24.7275 | 4187 | 0.0045172 | 6.9774 | 6.9819 | -1.5433 | 221.3771 | 5375.0779 | -0.0069713
212 |  | 1.3074 | 24.7205 | 4187 | 0.0045159 | 6.9819 | 6.9864 | -1.5433 | 221.4396 | 5399.7984 | -0.0069693
213 |  | 1.3074 | 24.7136 | 4187 | 0.0045146 | 6.9864 | 6.9909 | -1.5433 | 221.502 | 5424.512 | -0.0069674
214 |  | 1.3074 | 24.7066 | 4187 | 0.0045134 | 6.9909 | 6.9955 | -1.5433 | 221.5645 | 5449.2186 | -0.0069654
215 |  | 1.3074 | 24.6996 | 4187 | 0.0045121 | 6.9955 | 7 | -1.5433 | 221.627 | 5473.9182 | -0.0069635
216 |  | 1.3074 | 24.6927 | 4187 | 0.0045108 | 7 | 7.0045 | -1.5433 | 221.6895 | 5498.6109 | -0.0069615
217 |  | 1.3074 | 24.6857 | 4187 | 0.0045095 | 7.0045 | 7.009 | -1.5433 | 221.752 | 5523.2966 | -0.0069595
218 |  | 1.3074 | 24.6788 | 4187 | 0.0045083 | 7.009 | 7.0135 | -1.5433 | 221.8145 | 5547.9754 | -0.0069576
219 |  | 1.3074 | 24.6718 | 4187 | 0.004507 | 7.0135 | 7.018 | -1.5433 | 221.8771 | 5572.6472 | -0.0069556
220 |  | 1.3074 | 24.6648 | 4187 | 0.0045057 | 7.018 | 7.0225 | -1.5433 | 221.9396 | 5597.312 | -0.0069536
221 |  | 1.3074 | 24.6579 | 4187 | 0.0045045 | 7.0225 | 7.027 | -1.5433 | 222.0022 | 5621.9699 | -0.0069517
222 |  | 1.3074 | 24.6509 | 4187 | 0.0045032 | 7.027 | 7.0315 | -1.5433 | 222.0648 | 5646.6208 | -0.0069497
223 |  | 1.3074 | 24.644 | 4187 | 0.0045019 | 7.0315 | 7.036 | -1.5433 | 222.1275 | 5671.2648 | -0.0069478
224 |  | 1.3074 | 24.637 | 4187 | 0.0045007 | 7.036 | 7.0405 | -1.5433 | 222.1901 | 5695.9019 | -0.0069458
225 |  | 1.3074 | 24.6301 | 4187 | 0.0044994 | 7.0405 | 7.045 | -1.5433 | 222.2528 | 5720.532 | -0.0069438
226 |  | 1.3074 | 24.6231 | 4187 | 0.0044981 | 7.045 | 7.0495 | -1.5433 | 222.3154 | 5745.1551 | -0.0069419
227 |  | 1.3074 | 24.6162 | 4187 | 0.0044968 | 7.0495 | 7.054 | -1.5433 | 222.3781 | 5769.7713 | -0.0069399
228 |  | 1.3074 | 24.6093 | 4187 | 0.0044956 | 7.054 | 7.0585 | -1.5433 | 222.4408 | 5794.3806 | -0.006938
229 |  | 1.3074 | 24.6023 | 4187 | 0.0044943 | 7.0585 | 7.063 | -1.5433 | 222.5036 | 5818.9829 | -0.006936
230 |  | 1.3074 | 24.5954 | 4187 | 0.004493 | 7.063 | 7.0675 | -1.5433 | 222.5663 | 5843.5783 | -0.0069341
231 |  | 1.3074 | 24.5885 | 4187 | 0.0044918 | 7.0675 | 7.072 | -1.5433 | 222.6291 | 5868.1667 | -0.0069321
232 |  | 1.3074 | 24.5815 | 4187 | 0.0044905 | 7.072 | 7.0765 | -1.5433 | 222.6919 | 5892.7483 | -0.0069302
233 |  | 1.3074 | 24.5746 | 4187 | 0.0044892 | 7.0765 | 7.081 | -1.5433 | 222.7547 | 5917.3229 | -0.0069282
234 |  | 1.3074 | 24.5677 | 4187 | 0.004488 | 7.081 | 7.0855 | -1.5433 | 222.8175 | 5941.8905 | -0.0069262
235 |  | 1.3074 | 24.5607 | 4187 | 0.0044867 | 7.0855 | 7.0899 | -1.5433 | 222.8803 | 5966.4513 | -0.0069243
236 |  | 1.3074 | 24.5538 | 4187 | 0.0044854 | 7.0899 | 7.0944 | -1.5433 | 222.9432 | 5991.0051 | -0.0069223

## 63
|  |  | buis | verlies W/M | L /°C/sec
diam | wandikte |  | inhoud l/m |  | W/M
63 | 5.8 | 3.1416 | 2.075 | 30.4144 | 4187
|  |  |  | 6 |  |  |  | J/sec/mtr | aantal mtr. | verlies
|  | buis | verlies W/M | L /°C/sec | verlies temp | begintemp | eindtemp | verlies | bij 1°C | totaal J/sec
|  | inhoud L |  | W/M | °C per M | °C | °C | per m°C | daling | aantal mtr
1 | 63 | 2.075 | 30.4144 | 4187 | 0.0035007 | 6 | 6.0035 | -1.7891 | 285.6536 | 30.4144 | -0.0062631
2 |  | 2.075 | 30.4081 | 4187 | 0.0035 | 6.0035 | 6.007 | -1.7891 | 285.7125 | 60.8225 | -0.0062618
3 |  | 2.075 | 30.4019 | 4187 | 0.0034993 | 6.007 | 6.0105 | -1.7891 | 285.7713 | 91.2244 | -0.0062605
4 |  | 2.075 | 30.3956 | 4187 | 0.0034986 | 6.0105 | 6.014 | -1.7891 | 285.8302 | 121.62 | -0.0062593
5 |  | 2.075 | 30.3894 | 4187 | 0.0034979 | 6.014 | 6.0175 | -1.7891 | 285.8891 | 152.0094 | -0.006258
6 |  | 2.075 | 30.3831 | 4187 | 0.0034971 | 6.0175 | 6.021 | -1.7891 | 285.9479 | 182.3925 | -0.0062567
7 |  | 2.075 | 30.3768 | 4187 | 0.0034964 | 6.021 | 6.0245 | -1.7891 | 286.0068 | 212.7694 | -0.0062554
8 |  | 2.075 | 30.3706 | 4187 | 0.0034957 | 6.0245 | 6.028 | -1.7891 | 286.0657 | 243.1399 | -0.0062541
9 |  | 2.075 | 30.3643 | 4187 | 0.003495 | 6.028 | 6.0315 | -1.7891 | 286.1247 | 273.5043 | -0.0062528
10 |  | 2.075 | 30.3581 | 4187 | 0.0034943 | 6.0315 | 6.035 | -1.7891 | 286.1836 | 303.8624 | -0.0062515
11 |  | 2.075 | 30.3518 | 4187 | 0.0034935 | 6.035 | 6.0385 | -1.7891 | 286.2425 | 334.2142 | -0.0062502
12 |  | 2.075 | 30.3456 | 4187 | 0.0034928 | 6.0385 | 6.042 | -1.7891 | 286.3015 | 364.5598 | -0.0062489
13 |  | 2.075 | 30.3393 | 4187 | 0.0034921 | 6.042 | 6.0455 | -1.7891 | 286.3605 | 394.8991 | -0.0062477
14 |  | 2.075 | 30.3331 | 4187 | 0.0034914 | 6.0455 | 6.0489 | -1.7891 | 286.4194 | 425.2322 | -0.0062464
15 |  | 2.075 | 30.3268 | 4187 | 0.0034907 | 6.0489 | 6.0524 | -1.7891 | 286.4784 | 455.559 | -0.0062451
16 |  | 2.075 | 30.3206 | 4187 | 0.0034899 | 6.0524 | 6.0559 | -1.7891 | 286.5374 | 485.8796 | -0.0062438
17 |  | 2.075 | 30.3143 | 4187 | 0.0034892 | 6.0559 | 6.0594 | -1.7891 | 286.5965 | 516.194 | -0.0062425
18 |  | 2.075 | 30.3081 | 4187 | 0.0034885 | 6.0594 | 6.0629 | -1.7891 | 286.6555 | 546.5021 | -0.0062412
19 |  | 2.075 | 30.3019 | 4187 | 0.0034878 | 6.0629 | 6.0664 | -1.7891 | 286.7145 | 576.8039 | -0.0062399
20 |  | 2.075 | 30.2956 | 4187 | 0.0034871 | 6.0664 | 6.0699 | -1.7891 | 286.7736 | 607.0996 | -0.0062387
21 |  | 2.075 | 30.2894 | 4187 | 0.0034864 | 6.0699 | 6.0734 | -1.7891 | 286.8327 | 637.389 | -0.0062374
22 |  | 2.075 | 30.2831 | 4187 | 0.0034856 | 6.0734 | 6.0769 | -1.7891 | 286.8917 | 667.6721 | -0.0062361
23 |  | 2.075 | 30.2769 | 4187 | 0.0034849 | 6.0769 | 6.0803 | -1.7891 | 286.9508 | 697.949 | -0.0062348
24 |  | 2.075 | 30.2707 | 4187 | 0.0034842 | 6.0803 | 6.0838 | -1.7891 | 287.0099 | 728.2197 | -0.0062335
25 |  | 2.075 | 30.2644 | 4187 | 0.0034835 | 6.0838 | 6.0873 | -1.7891 | 287.069 | 758.4841 | -0.0062322
26 |  | 2.075 | 30.2582 | 4187 | 0.0034828 | 6.0873 | 6.0908 | -1.7891 | 287.1282 | 788.7424 | -0.006231
27 |  | 2.075 | 30.252 | 4187 | 0.003482 | 6.0908 | 6.0943 | -1.7891 | 287.1873 | 818.9943 | -0.0062297
28 |  | 2.075 | 30.2458 | 4187 | 0.0034813 | 6.0943 | 6.0977 | -1.7891 | 287.2465 | 849.2401 | -0.0062284
29 |  | 2.075 | 30.2395 | 4187 | 0.0034806 | 6.0977 | 6.1012 | -1.7891 | 287.3056 | 879.4796 | -0.0062271
30 |  | 2.075 | 30.2333 | 4187 | 0.0034799 | 6.1012 | 6.1047 | -1.7891 | 287.3648 | 909.7129 | -0.0062258
31 |  | 2.075 | 30.2271 | 4187 | 0.0034792 | 6.1047 | 6.1082 | -1.7891 | 287.424 | 939.94 | -0.0062245
32 |  | 2.075 | 30.2208 | 4187 | 0.0034785 | 6.1082 | 6.1117 | -1.7891 | 287.4832 | 970.1608 | -0.0062233
33 |  | 2.075 | 30.2146 | 4187 | 0.0034777 | 6.1117 | 6.1151 | -1.7891 | 287.5424 | 1000.3754 | -0.006222
34 |  | 2.075 | 30.2084 | 4187 | 0.003477 | 6.1151 | 6.1186 | -1.7891 | 287.6016 | 1030.5838 | -0.0062207
35 |  | 2.075 | 30.2022 | 4187 | 0.0034763 | 6.1186 | 6.1221 | -1.7891 | 287.6609 | 1060.786 | -0.0062194
36 |  | 2.075 | 30.196 | 4187 | 0.0034756 | 6.1221 | 6.1256 | -1.7891 | 287.7201 | 1090.982 | -0.0062181
37 |  | 2.075 | 30.1897 | 4187 | 0.0034749 | 6.1256 | 6.129 | -1.7891 | 287.7794 | 1121.1717 | -0.0062169
38 |  | 2.075 | 30.1835 | 4187 | 0.0034742 | 6.129 | 6.1325 | -1.7891 | 287.8386 | 1151.3553 | -0.0062156
39 |  | 2.075 | 30.1773 | 4187 | 0.0034735 | 6.1325 | 6.136 | -1.7891 | 287.8979 | 1181.5326 | -0.0062143
40 |  | 2.075 | 30.1711 | 4187 | 0.0034727 | 6.136 | 6.1395 | -1.7891 | 287.9572 | 1211.7037 | -0.006213
41 |  | 2.075 | 30.1649 | 4187 | 0.003472 | 6.1395 | 6.1429 | -1.7891 | 288.0165 | 1241.8685 | -0.0062117
42 |  | 2.075 | 30.1587 | 4187 | 0.0034713 | 6.1429 | 6.1464 | -1.7891 | 288.0759 | 1272.0272 | -0.0062105
43 |  | 2.075 | 30.1525 | 4187 | 0.0034706 | 6.1464 | 6.1499 | -1.7891 | 288.1352 | 1302.1797 | -0.0062092
44 |  | 2.075 | 30.1463 | 4187 | 0.0034699 | 6.1499 | 6.1534 | -1.7891 | 288.1945 | 1332.3259 | -0.0062079
45 |  | 2.075 | 30.14 | 4187 | 0.0034692 | 6.1534 | 6.1568 | -1.7891 | 288.2539 | 1362.466 | -0.0062066
46 |  | 2.075 | 30.1338 | 4187 | 0.0034684 | 6.1568 | 6.1603 | -1.7891 | 288.3133 | 1392.5998 | -0.0062053
47 |  | 2.075 | 30.1276 | 4187 | 0.0034677 | 6.1603 | 6.1638 | -1.7891 | 288.3727 | 1422.7274 | -0.0062041
48 |  | 2.075 | 30.1214 | 4187 | 0.003467 | 6.1638 | 6.1672 | -1.7891 | 288.4321 | 1452.8489 | -0.0062028
49 |  | 2.075 | 30.1152 | 4187 | 0.0034663 | 6.1672 | 6.1707 | -1.7891 | 288.4915 | 1482.9641 | -0.0062015
50 |  | 2.075 | 30.109 | 4187 | 0.0034656 | 6.1707 | 6.1742 | -1.7891 | 288.5509 | 1513.0731 | -0.0062002
51 |  | 2.075 | 30.1028 | 4187 | 0.0034649 | 6.1742 | 6.1776 | -1.7891 | 288.6103 | 1543.1759 | -0.006199
52 |  | 2.075 | 30.0966 | 4187 | 0.0034642 | 6.1776 | 6.1811 | -1.7891 | 288.6698 | 1573.2726 | -0.0061977
53 |  | 2.075 | 30.0904 | 4187 | 0.0034635 | 6.1811 | 6.1845 | -1.7891 | 288.7292 | 1603.363 | -0.0061964
54 |  | 2.075 | 30.0842 | 4187 | 0.0034627 | 6.1845 | 6.188 | -1.7891 | 288.7887 | 1633.4472 | -0.0061951
55 |  | 2.075 | 30.078 | 4187 | 0.003462 | 6.188 | 6.1915 | -1.7891 | 288.8482 | 1663.5253 | -0.0061939
56 |  | 2.075 | 30.0718 | 4187 | 0.0034613 | 6.1915 | 6.1949 | -1.7891 | 288.9077 | 1693.5971 | -0.0061926
57 |  | 2.075 | 30.0656 | 4187 | 0.0034606 | 6.1949 | 6.1984 | -1.7891 | 288.9672 | 1723.6628 | -0.0061913
58 |  | 2.075 | 30.0595 | 4187 | 0.0034599 | 6.1984 | 6.2019 | -1.7891 | 289.0267 | 1753.7222 | -0.00619
59 |  | 2.075 | 30.0533 | 4187 | 0.0034592 | 6.2019 | 6.2053 | -1.7891 | 289.0862 | 1783.7755 | -0.0061888
60 |  | 2.075 | 30.0471 | 4187 | 0.0034585 | 6.2053 | 6.2088 | -1.7891 | 289.1458 | 1813.8226 | -0.0061875
61 |  | 2.075 | 30.0409 | 4187 | 0.0034578 | 6.2088 | 6.2122 | -1.7891 | 289.2053 | 1843.8634 | -0.0061862
62 |  | 2.075 | 30.0347 | 4187 | 0.003457 | 6.2122 | 6.2157 | -1.7891 | 289.2649 | 1873.8982 | -0.0061849
63 |  | 2.075 | 30.0285 | 4187 | 0.0034563 | 6.2157 | 6.2191 | -1.7891 | 289.3245 | 1903.9267 | -0.0061837
64 |  | 2.075 | 30.0223 | 4187 | 0.0034556 | 6.2191 | 6.2226 | -1.7891 | 289.3841 | 1933.949 | -0.0061824
65 |  | 2.075 | 30.0162 | 4187 | 0.0034549 | 6.2226 | 6.2261 | -1.7891 | 289.4437 | 1963.9652 | -0.0061811
66 |  | 2.075 | 30.01 | 4187 | 0.0034542 | 6.2261 | 6.2295 | -1.7891 | 289.5033 | 1993.9751 | -0.0061798
67 |  | 2.075 | 30.0038 | 4187 | 0.0034535 | 6.2295 | 6.233 | -1.7891 | 289.5629 | 2023.9789 | -0.0061786
68 |  | 2.075 | 29.9976 | 4187 | 0.0034528 | 6.233 | 6.2364 | -1.7891 | 289.6225 | 2053.9765 | -0.0061773
69 |  | 2.075 | 29.9914 | 4187 | 0.0034521 | 6.2364 | 6.2399 | -1.7891 | 289.6822 | 2083.968 | -0.006176
70 |  | 2.075 | 29.9853 | 4187 | 0.0034513 | 6.2399 | 6.2433 | -1.7891 | 289.7419 | 2113.9532 | -0.0061747
71 |  | 2.075 | 29.9791 | 4187 | 0.0034506 | 6.2433 | 6.2468 | -1.7891 | 289.8015 | 2143.9323 | -0.0061735
72 |  | 2.075 | 29.9729 | 4187 | 0.0034499 | 6.2468 | 6.2502 | -1.7891 | 289.8612 | 2173.9052 | -0.0061722
73 |  | 2.075 | 29.9667 | 4187 | 0.0034492 | 6.2502 | 6.2537 | -1.7891 | 289.9209 | 2203.872 | -0.0061709
74 |  | 2.075 | 29.9606 | 4187 | 0.0034485 | 6.2537 | 6.2571 | -1.7891 | 289.9806 | 2233.8326 | -0.0061697
75 |  | 2.075 | 29.9544 | 4187 | 0.0034478 | 6.2571 | 6.2606 | -1.7891 | 290.0404 | 2263.787 | -0.0061684
76 |  | 2.075 | 29.9482 | 4187 | 0.0034471 | 6.2606 | 6.264 | -1.7891 | 290.1001 | 2293.7352 | -0.0061671
77 |  | 2.075 | 29.9421 | 4187 | 0.0034464 | 6.264 | 6.2675 | -1.7891 | 290.1599 | 2323.6772 | -0.0061659
78 |  | 2.075 | 29.9359 | 4187 | 0.0034457 | 6.2675 | 6.2709 | -1.7891 | 290.2196 | 2353.6131 | -0.0061646
79 |  | 2.075 | 29.9297 | 4187 | 0.003445 | 6.2709 | 6.2743 | -1.7891 | 290.2794 | 2383.5429 | -0.0061633
80 |  | 2.075 | 29.9236 | 4187 | 0.0034442 | 6.2743 | 6.2778 | -1.7891 | 290.3392 | 2413.4665 | -0.006162
81 |  | 2.075 | 29.9174 | 4187 | 0.0034435 | 6.2778 | 6.2812 | -1.7891 | 290.399 | 2443.3839 | -0.0061608
82 |  | 2.075 | 29.9112 | 4187 | 0.0034428 | 6.2812 | 6.2847 | -1.7891 | 290.4588 | 2473.2951 | -0.0061595
83 |  | 2.075 | 29.9051 | 4187 | 0.0034421 | 6.2847 | 6.2881 | -1.7891 | 290.5186 | 2503.2002 | -0.0061582
84 |  | 2.075 | 29.8989 | 4187 | 0.0034414 | 6.2881 | 6.2916 | -1.7891 | 290.5785 | 2533.0991 | -0.006157
85 |  | 2.075 | 29.8928 | 4187 | 0.0034407 | 6.2916 | 6.295 | -1.7891 | 290.6383 | 2562.9919 | -0.0061557
86 |  | 2.075 | 29.8866 | 4187 | 0.00344 | 6.295 | 6.2984 | -1.7891 | 290.6982 | 2592.8785 | -0.0061544
87 |  | 2.075 | 29.8805 | 4187 | 0.0034393 | 6.2984 | 6.3019 | -1.7891 | 290.7581 | 2622.759 | -0.0061532
88 |  | 2.075 | 29.8743 | 4187 | 0.0034386 | 6.3019 | 6.3053 | -1.7891 | 290.8179 | 2652.6333 | -0.0061519
89 |  | 2.075 | 29.8682 | 4187 | 0.0034379 | 6.3053 | 6.3088 | -1.7891 | 290.8778 | 2682.5015 | -0.0061506
90 |  | 2.075 | 29.862 | 4187 | 0.0034372 | 6.3088 | 6.3122 | -1.7891 | 290.9378 | 2712.3635 | -0.0061494
91 |  | 2.075 | 29.8559 | 4187 | 0.0034365 | 6.3122 | 6.3156 | -1.7891 | 290.9977 | 2742.2193 | -0.0061481
92 |  | 2.075 | 29.8497 | 4187 | 0.0034357 | 6.3156 | 6.3191 | -1.7891 | 291.0576 | 2772.069 | -0.0061468
93 |  | 2.075 | 29.8436 | 4187 | 0.003435 | 6.3191 | 6.3225 | -1.7891 | 291.1176 | 2801.9126 | -0.0061456
94 |  | 2.075 | 29.8374 | 4187 | 0.0034343 | 6.3225 | 6.3259 | -1.7891 | 291.1775 | 2831.75 | -0.0061443
95 |  | 2.075 | 29.8313 | 4187 | 0.0034336 | 6.3259 | 6.3294 | -1.7891 | 291.2375 | 2861.5813 | -0.006143
96 |  | 2.075 | 29.8251 | 4187 | 0.0034329 | 6.3294 | 6.3328 | -1.7891 | 291.2975 | 2891.4064 | -0.0061418
97 |  | 2.075 | 29.819 | 4187 | 0.0034322 | 6.3328 | 6.3362 | -1.7891 | 291.3575 | 2921.2254 | -0.0061405
98 |  | 2.075 | 29.8128 | 4187 | 0.0034315 | 6.3362 | 6.3397 | -1.7891 | 291.4175 | 2951.0382 | -0.0061392
99 |  | 2.075 | 29.8067 | 4187 | 0.0034308 | 6.3397 | 6.3431 | -1.7891 | 291.4775 | 2980.845 | -0.006138
100 |  | 2.075 | 29.8006 | 4187 | 0.0034301 | 6.3431 | 6.3465 | -1.7891 | 291.5375 | 3010.6455 | -0.0061367
101 |  | 2.075 | 29.7944 | 4187 | 0.0034294 | 6.3465 | 6.35 | -1.7891 | 291.5976 | 3040.44 | -0.0061355
102 |  | 2.075 | 29.7883 | 4187 | 0.0034287 | 6.35 | 6.3534 | -1.7891 | 291.6577 | 3070.2283 | -0.0061342
103 |  | 2.075 | 29.7822 | 4187 | 0.003428 | 6.3534 | 6.3568 | -1.7891 | 291.7177 | 3100.0104 | -0.0061329
104 |  | 2.075 | 29.776 | 4187 | 0.0034273 | 6.3568 | 6.3602 | -1.7891 | 291.7778 | 3129.7865 | -0.0061317
105 |  | 2.075 | 29.7699 | 4187 | 0.0034266 | 6.3602 | 6.3637 | -1.7891 | 291.8379 | 3159.5564 | -0.0061304
106 |  | 2.075 | 29.7638 | 4187 | 0.0034259 | 6.3637 | 6.3671 | -1.7891 | 291.898 | 3189.3201 | -0.0061291
107 |  | 2.075 | 29.7576 | 4187 | 0.0034251 | 6.3671 | 6.3705 | -1.7891 | 291.9581 | 3219.0778 | -0.0061279
108 |  | 2.075 | 29.7515 | 4187 | 0.0034244 | 6.3705 | 6.3739 | -1.7891 | 292.0183 | 3248.8293 | -0.0061266
109 |  | 2.075 | 29.7454 | 4187 | 0.0034237 | 6.3739 | 6.3774 | -1.7891 | 292.0784 | 3278.5747 | -0.0061254
110 |  | 2.075 | 29.7393 | 4187 | 0.003423 | 6.3774 | 6.3808 | -1.7891 | 292.1386 | 3308.3139 | -0.0061241
111 |  | 2.075 | 29.7331 | 4187 | 0.0034223 | 6.3808 | 6.3842 | -1.7891 | 292.1988 | 3338.0471 | -0.0061228
112 |  | 2.075 | 29.727 | 4187 | 0.0034216 | 6.3842 | 6.3876 | -1.7891 | 292.2589 | 3367.7741 | -0.0061216
113 |  | 2.075 | 29.7209 | 4187 | 0.0034209 | 6.3876 | 6.3911 | -1.7891 | 292.3191 | 3397.495 | -0.0061203
114 |  | 2.075 | 29.7148 | 4187 | 0.0034202 | 6.3911 | 6.3945 | -1.7891 | 292.3793 | 3427.2097 | -0.006119
115 |  | 2.075 | 29.7087 | 4187 | 0.0034195 | 6.3945 | 6.3979 | -1.7891 | 292.4396 | 3456.9184 | -0.0061178
116 |  | 2.075 | 29.7025 | 4187 | 0.0034188 | 6.3979 | 6.4013 | -1.7891 | 292.4998 | 3486.6209 | -0.0061165
117 |  | 2.075 | 29.6964 | 4187 | 0.0034181 | 6.4013 | 6.4047 | -1.7891 | 292.56 | 3516.3173 | -0.0061153
118 |  | 2.075 | 29.6903 | 4187 | 0.0034174 | 6.4047 | 6.4082 | -1.7891 | 292.6203 | 3546.0076 | -0.006114
119 |  | 2.075 | 29.6842 | 4187 | 0.0034167 | 6.4082 | 6.4116 | -1.7891 | 292.6806 | 3575.6918 | -0.0061127
120 |  | 2.075 | 29.6781 | 4187 | 0.003416 | 6.4116 | 6.415 | -1.7891 | 292.7409 | 3605.3699 | -0.0061115
121 |  | 2.075 | 29.672 | 4187 | 0.0034153 | 6.415 | 6.4184 | -1.7891 | 292.8011 | 3635.0419 | -0.0061102
122 |  | 2.075 | 29.6659 | 4187 | 0.0034146 | 6.4184 | 6.4218 | -1.7891 | 292.8615 | 3664.7077 | -0.006109
123 |  | 2.075 | 29.6597 | 4187 | 0.0034139 | 6.4218 | 6.4252 | -1.7891 | 292.9218 | 3694.3675 | -0.0061077
124 |  | 2.075 | 29.6536 | 4187 | 0.0034132 | 6.4252 | 6.4286 | -1.7891 | 292.9821 | 3724.0211 | -0.0061065
125 |  | 2.075 | 29.6475 | 4187 | 0.0034125 | 6.4286 | 6.4321 | -1.7891 | 293.0425 | 3753.6686 | -0.0061052
126 |  | 2.075 | 29.6414 | 4187 | 0.0034118 | 6.4321 | 6.4355 | -1.7891 | 293.1028 | 3783.3101 | -0.0061039
127 |  | 2.075 | 29.6353 | 4187 | 0.0034111 | 6.4355 | 6.4389 | -1.7891 | 293.1632 | 3812.9454 | -0.0061027
128 |  | 2.075 | 29.6292 | 4187 | 0.0034104 | 6.4389 | 6.4423 | -1.7891 | 293.2236 | 3842.5746 | -0.0061014
129 |  | 2.075 | 29.6231 | 4187 | 0.0034097 | 6.4423 | 6.4457 | -1.7891 | 293.284 | 3872.1977 | -0.0061002
130 |  | 2.075 | 29.617 | 4187 | 0.003409 | 6.4457 | 6.4491 | -1.7891 | 293.3444 | 3901.8148 | -0.0060989
131 |  | 2.075 | 29.6109 | 4187 | 0.0034083 | 6.4491 | 6.4525 | -1.7891 | 293.4048 | 3931.4257 | -0.0060977
132 |  | 2.075 | 29.6048 | 4187 | 0.0034076 | 6.4525 | 6.4559 | -1.7891 | 293.4652 | 3961.0305 | -0.0060964
133 |  | 2.075 | 29.5987 | 4187 | 0.0034069 | 6.4559 | 6.4593 | -1.7891 | 293.5257 | 3990.6292 | -0.0060951
134 |  | 2.075 | 29.5926 | 4187 | 0.0034062 | 6.4593 | 6.4627 | -1.7891 | 293.5861 | 4020.2218 | -0.0060939
135 |  | 2.075 | 29.5865 | 4187 | 0.0034055 | 6.4627 | 6.4661 | -1.7891 | 293.6466 | 4049.8084 | -0.0060926
136 |  | 2.075 | 29.5804 | 4187 | 0.0034048 | 6.4661 | 6.4695 | -1.7891 | 293.7071 | 4079.3888 | -0.0060914
137 |  | 2.075 | 29.5744 | 4187 | 0.0034041 | 6.4695 | 6.4729 | -1.7891 | 293.7676 | 4108.9632 | -0.0060901
138 |  | 2.075 | 29.5683 | 4187 | 0.0034034 | 6.4729 | 6.4764 | -1.7891 | 293.8281 | 4138.5314 | -0.0060889
139 |  | 2.075 | 29.5622 | 4187 | 0.0034026 | 6.4764 | 6.4798 | -1.7891 | 293.8886 | 4168.0936 | -0.0060876
140 |  | 2.075 | 29.5561 | 4187 | 0.0034019 | 6.4798 | 6.4832 | -1.7891 | 293.9491 | 4197.6497 | -0.0060864
141 |  | 2.075 | 29.55 | 4187 | 0.0034012 | 6.4832 | 6.4866 | -1.7891 | 294.0097 | 4227.1997 | -0.0060851
142 |  | 2.075 | 29.5439 | 4187 | 0.0034005 | 6.4866 | 6.49 | -1.7891 | 294.0702 | 4256.7436 | -0.0060839
143 |  | 2.075 | 29.5378 | 4187 | 0.0033998 | 6.49 | 6.4934 | -1.7891 | 294.1308 | 4286.2814 | -0.0060826
144 |  | 2.075 | 29.5317 | 4187 | 0.0033991 | 6.4934 | 6.4968 | -1.7891 | 294.1914 | 4315.8132 | -0.0060814
145 |  | 2.075 | 29.5257 | 4187 | 0.0033984 | 6.4968 | 6.5002 | -1.7891 | 294.252 | 4345.3389 | -0.0060801
146 |  | 2.075 | 29.5196 | 4187 | 0.0033977 | 6.5002 | 6.5036 | -1.7891 | 294.3126 | 4374.8584 | -0.0060789
147 |  | 2.075 | 29.5135 | 4187 | 0.003397 | 6.5036 | 6.5069 | -1.7891 | 294.3732 | 4404.372 | -0.0060776
148 |  | 2.075 | 29.5074 | 4187 | 0.0033963 | 6.5069 | 6.5103 | -1.7891 | 294.4338 | 4433.8794 | -0.0060763
149 |  | 2.075 | 29.5014 | 4187 | 0.0033956 | 6.5103 | 6.5137 | -1.7891 | 294.4945 | 4463.3807 | -0.0060751
150 |  | 2.075 | 29.4953 | 4187 | 0.003395 | 6.5137 | 6.5171 | -1.7891 | 294.5551 | 4492.876 | -0.0060738
151 |  | 2.075 | 29.4892 | 4187 | 0.0033943 | 6.5171 | 6.5205 | -1.7891 | 294.6158 | 4522.3652 | -0.0060726
152 |  | 2.075 | 29.4831 | 4187 | 0.0033936 | 6.5205 | 6.5239 | -1.7891 | 294.6765 | 4551.8483 | -0.0060713
153 |  | 2.075 | 29.4771 | 4187 | 0.0033929 | 6.5239 | 6.5273 | -1.7891 | 294.7372 | 4581.3254 | -0.0060701
154 |  | 2.075 | 29.471 | 4187 | 0.0033922 | 6.5273 | 6.5307 | -1.7891 | 294.7979 | 4610.7964 | -0.0060688
155 |  | 2.075 | 29.4649 | 4187 | 0.0033915 | 6.5307 | 6.5341 | -1.7891 | 294.8586 | 4640.2613 | -0.0060676
156 |  | 2.075 | 29.4589 | 4187 | 0.0033908 | 6.5341 | 6.5375 | -1.7891 | 294.9193 | 4669.7202 | -0.0060663
157 |  | 2.075 | 29.4528 | 4187 | 0.0033901 | 6.5375 | 6.5409 | -1.7891 | 294.9801 | 4699.173 | -0.0060651
158 |  | 2.075 | 29.4467 | 4187 | 0.0033894 | 6.5409 | 6.5443 | -1.7891 | 295.0408 | 4728.6197 | -0.0060638
159 |  | 2.075 | 29.4407 | 4187 | 0.0033887 | 6.5443 | 6.5477 | -1.7891 | 295.1016 | 4758.0603 | -0.0060626
160 |  | 2.075 | 29.4346 | 4187 | 0.003388 | 6.5477 | 6.551 | -1.7891 | 295.1624 | 4787.4949 | -0.0060614
161 |  | 2.075 | 29.4285 | 4187 | 0.0033873 | 6.551 | 6.5544 | -1.7891 | 295.2232 | 4816.9235 | -0.0060601
162 |  | 2.075 | 29.4225 | 4187 | 0.0033866 | 6.5544 | 6.5578 | -1.7891 | 295.284 | 4846.3459 | -0.0060589
163 |  | 2.075 | 29.4164 | 4187 | 0.0033859 | 6.5578 | 6.5612 | -1.7891 | 295.3448 | 4875.7624 | -0.0060576
164 |  | 2.075 | 29.4104 | 4187 | 0.0033852 | 6.5612 | 6.5646 | -1.7891 | 295.4056 | 4905.1727 | -0.0060564
165 |  | 2.075 | 29.4043 | 4187 | 0.0033845 | 6.5646 | 6.568 | -1.7891 | 295.4665 | 4934.577 | -0.0060551
166 |  | 2.075 | 29.3982 | 4187 | 0.0033838 | 6.568 | 6.5714 | -1.7891 | 295.5273 | 4963.9753 | -0.0060539
167 |  | 2.075 | 29.3922 | 4187 | 0.0033831 | 6.5714 | 6.5747 | -1.7891 | 295.5882 | 4993.3675 | -0.0060526
168 |  | 2.075 | 29.3861 | 4187 | 0.0033824 | 6.5747 | 6.5781 | -1.7891 | 295.6491 | 5022.7536 | -0.0060514
169 |  | 2.075 | 29.3801 | 4187 | 0.0033817 | 6.5781 | 6.5815 | -1.7891 | 295.71 | 5052.1337 | -0.0060501
170 |  | 2.075 | 29.374 | 4187 | 0.003381 | 6.5815 | 6.5849 | -1.7891 | 295.7709 | 5081.5077 | -0.0060489
171 |  | 2.075 | 29.368 | 4187 | 0.0033803 | 6.5849 | 6.5883 | -1.7891 | 295.8318 | 5110.8757 | -0.0060476
172 |  | 2.075 | 29.3619 | 4187 | 0.0033796 | 6.5883 | 6.5916 | -1.7891 | 295.8927 | 5140.2377 | -0.0060464
173 |  | 2.075 | 29.3559 | 4187 | 0.0033789 | 6.5916 | 6.595 | -1.7891 | 295.9537 | 5169.5936 | -0.0060451
174 |  | 2.075 | 29.3499 | 4187 | 0.0033782 | 6.595 | 6.5984 | -1.7891 | 296.0146 | 5198.9434 | -0.0060439
175 |  | 2.075 | 29.3438 | 4187 | 0.0033775 | 6.5984 | 6.6018 | -1.7891 | 296.0756 | 5228.2872 | -0.0060427
176 |  | 2.075 | 29.3378 | 4187 | 0.0033768 | 6.6018 | 6.6052 | -1.7891 | 296.1366 | 5257.625 | -0.0060414
177 |  | 2.075 | 29.3317 | 4187 | 0.0033761 | 6.6052 | 6.6085 | -1.7891 | 296.1976 | 5286.9567 | -0.0060402
178 |  | 2.075 | 29.3257 | 4187 | 0.0033754 | 6.6085 | 6.6119 | -1.7891 | 296.2586 | 5316.2824 | -0.0060389
179 |  | 2.075 | 29.3196 | 4187 | 0.0033747 | 6.6119 | 6.6153 | -1.7891 | 296.3196 | 5345.602 | -0.0060377
180 |  | 2.075 | 29.3136 | 4187 | 0.003374 | 6.6153 | 6.6187 | -1.7891 | 296.3806 | 5374.9156 | -0.0060364
181 |  | 2.075 | 29.3076 | 4187 | 0.0033733 | 6.6187 | 6.622 | -1.7891 | 296.4417 | 5404.2232 | -0.0060352
182 |  | 2.075 | 29.3015 | 4187 | 0.0033727 | 6.622 | 6.6254 | -1.7891 | 296.5027 | 5433.5247 | -0.0060339
183 |  | 2.075 | 29.2955 | 4187 | 0.003372 | 6.6254 | 6.6288 | -1.7891 | 296.5638 | 5462.8202 | -0.0060327
184 |  | 2.075 | 29.2895 | 4187 | 0.0033713 | 6.6288 | 6.6321 | -1.7891 | 296.6249 | 5492.1097 | -0.0060315
185 |  | 2.075 | 29.2834 | 4187 | 0.0033706 | 6.6321 | 6.6355 | -1.7891 | 296.686 | 5521.3931 | -0.0060302
186 |  | 2.075 | 29.2774 | 4187 | 0.0033699 | 6.6355 | 6.6389 | -1.7891 | 296.7471 | 5550.6705 | -0.006029
187 |  | 2.075 | 29.2714 | 4187 | 0.0033692 | 6.6389 | 6.6423 | -1.7891 | 296.8082 | 5579.9419 | -0.0060277
188 |  | 2.075 | 29.2653 | 4187 | 0.0033685 | 6.6423 | 6.6456 | -1.7891 | 296.8694 | 5609.2073 | -0.0060265
189 |  | 2.075 | 29.2593 | 4187 | 0.0033678 | 6.6456 | 6.649 | -1.7891 | 296.9305 | 5638.4666 | -0.0060253
190 |  | 2.075 | 29.2533 | 4187 | 0.0033671 | 6.649 | 6.6524 | -1.7891 | 296.9917 | 5667.7199 | -0.006024
191 |  | 2.075 | 29.2473 | 4187 | 0.0033664 | 6.6524 | 6.6557 | -1.7891 | 297.0528 | 5696.9672 | -0.0060228
192 |  | 2.075 | 29.2413 | 4187 | 0.0033657 | 6.6557 | 6.6591 | -1.7891 | 297.114 | 5726.2084 | -0.0060215
193 |  | 2.075 | 29.2352 | 4187 | 0.003365 | 6.6591 | 6.6625 | -1.7891 | 297.1752 | 5755.4436 | -0.0060203
194 |  | 2.075 | 29.2292 | 4187 | 0.0033643 | 6.6625 | 6.6658 | -1.7891 | 297.2364 | 5784.6728 | -0.0060191
195 |  | 2.075 | 29.2232 | 4187 | 0.0033636 | 6.6658 | 6.6692 | -1.7891 | 297.2976 | 5813.896 | -0.0060178
196 |  | 2.075 | 29.2172 | 4187 | 0.0033629 | 6.6692 | 6.6726 | -1.7891 | 297.3589 | 5843.1132 | -0.0060166
197 |  | 2.075 | 29.2112 | 4187 | 0.0033622 | 6.6726 | 6.6759 | -1.7891 | 297.4201 | 5872.3244 | -0.0060153
198 |  | 2.075 | 29.2051 | 4187 | 0.0033616 | 6.6759 | 6.6793 | -1.7891 | 297.4814 | 5901.5295 | -0.0060141
199 |  | 2.075 | 29.1991 | 4187 | 0.0033609 | 6.6793 | 6.6826 | -1.7891 | 297.5427 | 5930.7286 | -0.0060129
200 |  | 2.075 | 29.1931 | 4187 | 0.0033602 | 6.6826 | 6.686 | -1.7891 | 297.6039 | 5959.9217 | -0.0060116
201 |  | 2.075 | 29.1871 | 4187 | 0.0033595 | 6.686 | 6.6894 | -1.7891 | 297.6652 | 5989.1088 | -0.0060104
202 |  | 2.075 | 29.1811 | 4187 | 0.0033588 | 6.6894 | 6.6927 | -1.7891 | 297.7265 | 6018.2899 | -0.0060091
203 |  | 2.075 | 29.1751 | 4187 | 0.0033581 | 6.6927 | 6.6961 | -1.7891 | 297.7879 | 6047.465 | -0.0060079
204 |  | 2.075 | 29.1691 | 4187 | 0.0033574 | 6.6961 | 6.6994 | -1.7891 | 297.8492 | 6076.6341 | -0.0060067
205 |  | 2.075 | 29.1631 | 4187 | 0.0033567 | 6.6994 | 6.7028 | -1.7891 | 297.9105 | 6105.7972 | -0.0060054
206 |  | 2.075 | 29.1571 | 4187 | 0.003356 | 6.7028 | 6.7061 | -1.7891 | 297.9719 | 6134.9542 | -0.0060042
207 |  | 2.075 | 29.1511 | 4187 | 0.0033553 | 6.7061 | 6.7095 | -1.7891 | 298.0333 | 6164.1053 | -0.006003
208 |  | 2.075 | 29.1451 | 4187 | 0.0033546 | 6.7095 | 6.7129 | -1.7891 | 298.0947 | 6193.2503 | -0.0060017
209 |  | 2.075 | 29.1391 | 4187 | 0.0033539 | 6.7129 | 6.7162 | -1.7891 | 298.1561 | 6222.3894 | -0.0060005
210 |  | 2.075 | 29.1331 | 4187 | 0.0033533 | 6.7162 | 6.7196 | -1.7891 | 298.2175 | 6251.5224 | -0.0059993
211 |  | 2.075 | 29.1271 | 4187 | 0.0033526 | 6.7196 | 6.7229 | -1.7891 | 298.2789 | 6280.6495 | -0.005998
212 |  | 2.075 | 29.1211 | 4187 | 0.0033519 | 6.7229 | 6.7263 | -1.7891 | 298.3403 | 6309.7705 | -0.0059968
213 |  | 2.075 | 29.1151 | 4187 | 0.0033512 | 6.7263 | 6.7296 | -1.7891 | 298.4018 | 6338.8856 | -0.0059955
214 |  | 2.075 | 29.1091 | 4187 | 0.0033505 | 6.7296 | 6.733 | -1.7891 | 298.4632 | 6367.9947 | -0.0059943
215 |  | 2.075 | 29.1031 | 4187 | 0.0033498 | 6.733 | 6.7363 | -1.7891 | 298.5247 | 6397.0977 | -0.0059931
216 |  | 2.075 | 29.0971 | 4187 | 0.0033491 | 6.7363 | 6.7397 | -1.7891 | 298.5862 | 6426.1948 | -0.0059918
217 |  | 2.075 | 29.0911 | 4187 | 0.0033484 | 6.7397 | 6.743 | -1.7891 | 298.6477 | 6455.2859 | -0.0059906
218 |  | 2.075 | 29.0851 | 4187 | 0.0033477 | 6.743 | 6.7464 | -1.7891 | 298.7092 | 6484.371 | -0.0059894
219 |  | 2.075 | 29.0791 | 4187 | 0.003347 | 6.7464 | 6.7497 | -1.7891 | 298.7707 | 6513.4501 | -0.0059881
220 |  | 2.075 | 29.0731 | 4187 | 0.0033464 | 6.7497 | 6.7531 | -1.7891 | 298.8323 | 6542.5232 | -0.0059869
221 |  | 2.075 | 29.0671 | 4187 | 0.0033457 | 6.7531 | 6.7564 | -1.7891 | 298.8938 | 6571.5903 | -0.0059857
222 |  | 2.075 | 29.0611 | 4187 | 0.003345 | 6.7564 | 6.7597 | -1.7891 | 298.9554 | 6600.6515 | -0.0059844
223 |  | 2.075 | 29.0552 | 4187 | 0.0033443 | 6.7597 | 6.7631 | -1.7891 | 299.017 | 6629.7066 | -0.0059832
224 |  | 2.075 | 29.0492 | 4187 | 0.0033436 | 6.7631 | 6.7664 | -1.7891 | 299.0786 | 6658.7558 | -0.005982
225 |  | 2.075 | 29.0432 | 4187 | 0.0033429 | 6.7664 | 6.7698 | -1.7891 | 299.1402 | 6687.799 | -0.0059808
226 |  | 2.075 | 29.0372 | 4187 | 0.0033422 | 6.7698 | 6.7731 | -1.7891 | 299.2018 | 6716.8362 | -0.0059795
227 |  | 2.075 | 29.0312 | 4187 | 0.0033415 | 6.7731 | 6.7765 | -1.7891 | 299.2634 | 6745.8675 | -0.0059783
228 |  | 2.075 | 29.0253 | 4187 | 0.0033408 | 6.7765 | 6.7798 | -1.7891 | 299.325 | 6774.8927 | -0.0059771
229 |  | 2.075 | 29.0193 | 4187 | 0.0033402 | 6.7798 | 6.7831 | -1.7891 | 299.3867 | 6803.912 | -0.0059758
230 |  | 2.075 | 29.0133 | 4187 | 0.0033395 | 6.7831 | 6.7865 | -1.7891 | 299.4484 | 6832.9253 | -0.0059746
231 |  | 2.075 | 29.0073 | 4187 | 0.0033388 | 6.7865 | 6.7898 | -1.7891 | 299.51 | 6861.9326 | -0.0059734
232 |  | 2.075 | 29.0014 | 4187 | 0.0033381 | 6.7898 | 6.7932 | -1.7891 | 299.5717 | 6890.934 | -0.0059721
233 |  | 2.075 | 28.9954 | 4187 | 0.0033374 | 6.7932 | 6.7965 | -1.7891 | 299.6334 | 6919.9293 | -0.0059709
234 |  | 2.075 | 28.9894 | 4187 | 0.0033367 | 6.7965 | 6.7998 | -1.7891 | 299.6951 | 6948.9188 | -0.0059697
235 |  | 2.075 | 28.9834 | 4187 | 0.003336 | 6.7998 | 6.8032 | -1.7891 | 299.7569 | 6977.9022 | -0.0059684
236 |  | 2.075 | 28.9775 | 4187 | 0.0033354 | 6.8032 | 6.8065 | -1.7891 | 299.8186 | 7006.8797 | -0.0059672

## 75
|  |  | buis | verlies W/M | L /°C/sec
diam | wandikte |  | inhoud l/m |  | W/M
75 | 6.8 | 3.1416 | 2.9609 | 33.9717 | 4187
[8 empty] | J/sec/mtr | aantal mtr. | verlies
|  | buis | verlies W/M | L /°C/sec | verlies temp | begintemp | eindtemp | verlies | bij 1°C | totaal J/sec
|  | inhoud L |  | W/M | °C per M | °C | °C | per m°C | daling | aantal mtr
1 | 75 | 2.9609 | 33.9717 | 4187 | 0.0027402 | 6 | 6.0027 | -1.9983 | 364.9322 | 33.9717 | -0.0054759
2 |  | 2.9609 | 33.9662 | 4187 | 0.0027398 | 6.0027 | 6.0055 | -1.9983 | 364.991 | 67.9379 | -0.005475
3 |  | 2.9609 | 33.9608 | 4187 | 0.0027394 | 6.0055 | 6.0082 | -1.9983 | 365.0499 | 101.8987 | -0.0054741
4 |  | 2.9609 | 33.9553 | 4187 | 0.0027389 | 6.0082 | 6.011 | -1.9983 | 365.1087 | 135.854 | -0.0054733
5 |  | 2.9609 | 33.9498 | 4187 | 0.0027385 | 6.011 | 6.0137 | -1.9983 | 365.1676 | 169.8038 | -0.0054724
6 |  | 2.9609 | 33.9443 | 4187 | 0.002738 | 6.0137 | 6.0164 | -1.9983 | 365.2265 | 203.7481 | -0.0054715
7 |  | 2.9609 | 33.9389 | 4187 | 0.0027376 | 6.0164 | 6.0192 | -1.9983 | 365.2853 | 237.687 | -0.0054706
8 |  | 2.9609 | 33.9334 | 4187 | 0.0027371 | 6.0192 | 6.0219 | -1.9983 | 365.3442 | 271.6204 | -0.0054697
9 |  | 2.9609 | 33.9279 | 4187 | 0.0027367 | 6.0219 | 6.0246 | -1.9983 | 365.4031 | 305.5483 | -0.0054689
10 |  | 2.9609 | 33.9225 | 4187 | 0.0027363 | 6.0246 | 6.0274 | -1.9983 | 365.462 | 339.4708 | -0.005468
11 |  | 2.9609 | 33.917 | 4187 | 0.0027358 | 6.0274 | 6.0301 | -1.9983 | 365.521 | 373.3878 | -0.0054671
12 |  | 2.9609 | 33.9115 | 4187 | 0.0027354 | 6.0301 | 6.0329 | -1.9983 | 365.5799 | 407.2993 | -0.0054662
13 |  | 2.9609 | 33.9061 | 4187 | 0.0027349 | 6.0329 | 6.0356 | -1.9983 | 365.6388 | 441.2053 | -0.0054653
14 |  | 2.9609 | 33.9006 | 4187 | 0.0027345 | 6.0356 | 6.0383 | -1.9983 | 365.6978 | 475.1059 | -0.0054644
15 |  | 2.9609 | 33.8951 | 4187 | 0.0027341 | 6.0383 | 6.0411 | -1.9983 | 365.7567 | 509.0011 | -0.0054636
16 |  | 2.9609 | 33.8897 | 4187 | 0.0027336 | 6.0411 | 6.0438 | -1.9983 | 365.8157 | 542.8907 | -0.0054627
17 |  | 2.9609 | 33.8842 | 4187 | 0.0027332 | 6.0438 | 6.0465 | -1.9983 | 365.8747 | 576.7749 | -0.0054618
18 |  | 2.9609 | 33.8787 | 4187 | 0.0027327 | 6.0465 | 6.0493 | -1.9983 | 365.9337 | 610.6537 | -0.0054609
19 |  | 2.9609 | 33.8733 | 4187 | 0.0027323 | 6.0493 | 6.052 | -1.9983 | 365.9926 | 644.5269 | -0.00546
20 |  | 2.9609 | 33.8678 | 4187 | 0.0027319 | 6.052 | 6.0547 | -1.9983 | 366.0517 | 678.3948 | -0.0054592
21 |  | 2.9609 | 33.8624 | 4187 | 0.0027314 | 6.0547 | 6.0575 | -1.9983 | 366.1107 | 712.2571 | -0.0054583
22 |  | 2.9609 | 33.8569 | 4187 | 0.002731 | 6.0575 | 6.0602 | -1.9983 | 366.1697 | 746.114 | -0.0054574
23 |  | 2.9609 | 33.8514 | 4187 | 0.0027305 | 6.0602 | 6.0629 | -1.9983 | 366.2287 | 779.9655 | -0.0054565
24 |  | 2.9609 | 33.846 | 4187 | 0.0027301 | 6.0629 | 6.0656 | -1.9983 | 366.2878 | 813.8114 | -0.0054556
25 |  | 2.9609 | 33.8405 | 4187 | 0.0027297 | 6.0656 | 6.0684 | -1.9983 | 366.3468 | 847.652 | -0.0054548
26 |  | 2.9609 | 33.8351 | 4187 | 0.0027292 | 6.0684 | 6.0711 | -1.9983 | 366.4059 | 881.4871 | -0.0054539
27 |  | 2.9609 | 33.8296 | 4187 | 0.0027288 | 6.0711 | 6.0738 | -1.9983 | 366.4649 | 915.3167 | -0.005453
28 |  | 2.9609 | 33.8242 | 4187 | 0.0027283 | 6.0738 | 6.0766 | -1.9983 | 366.524 | 949.1408 | -0.0054521
29 |  | 2.9609 | 33.8187 | 4187 | 0.0027279 | 6.0766 | 6.0793 | -1.9983 | 366.5831 | 982.9596 | -0.0054512
30 |  | 2.9609 | 33.8133 | 4187 | 0.0027275 | 6.0793 | 6.082 | -1.9983 | 366.6422 | 1016.7728 | -0.0054504
31 |  | 2.9609 | 33.8078 | 4187 | 0.002727 | 6.082 | 6.0847 | -1.9983 | 366.7013 | 1050.5806 | -0.0054495
32 |  | 2.9609 | 33.8024 | 4187 | 0.0027266 | 6.0847 | 6.0875 | -1.9983 | 366.7604 | 1084.383 | -0.0054486
33 |  | 2.9609 | 33.7969 | 4187 | 0.0027261 | 6.0875 | 6.0902 | -1.9983 | 366.8196 | 1118.1799 | -0.0054477
34 |  | 2.9609 | 33.7915 | 4187 | 0.0027257 | 6.0902 | 6.0929 | -1.9983 | 366.8787 | 1151.9714 | -0.0054469
35 |  | 2.9609 | 33.786 | 4187 | 0.0027253 | 6.0929 | 6.0956 | -1.9983 | 366.9379 | 1185.7574 | -0.005446
36 |  | 2.9609 | 33.7806 | 4187 | 0.0027248 | 6.0956 | 6.0984 | -1.9983 | 366.997 | 1219.538 | -0.0054451
37 |  | 2.9609 | 33.7751 | 4187 | 0.0027244 | 6.0984 | 6.1011 | -1.9983 | 367.0562 | 1253.3131 | -0.0054442
38 |  | 2.9609 | 33.7697 | 4187 | 0.0027239 | 6.1011 | 6.1038 | -1.9983 | 367.1154 | 1287.0828 | -0.0054433
39 |  | 2.9609 | 33.7642 | 4187 | 0.0027235 | 6.1038 | 6.1065 | -1.9983 | 367.1745 | 1320.8471 | -0.0054425
40 |  | 2.9609 | 33.7588 | 4187 | 0.0027231 | 6.1065 | 6.1093 | -1.9983 | 367.2337 | 1354.6059 | -0.0054416
41 |  | 2.9609 | 33.7534 | 4187 | 0.0027226 | 6.1093 | 6.112 | -1.9983 | 367.2929 | 1388.3592 | -0.0054407
42 |  | 2.9609 | 33.7479 | 4187 | 0.0027222 | 6.112 | 6.1147 | -1.9983 | 367.3522 | 1422.1071 | -0.0054398
43 |  | 2.9609 | 33.7425 | 4187 | 0.0027217 | 6.1147 | 6.1174 | -1.9983 | 367.4114 | 1455.8496 | -0.005439
44 |  | 2.9609 | 33.737 | 4187 | 0.0027213 | 6.1174 | 6.1202 | -1.9983 | 367.4706 | 1489.5867 | -0.0054381
45 |  | 2.9609 | 33.7316 | 4187 | 0.0027209 | 6.1202 | 6.1229 | -1.9983 | 367.5298 | 1523.3183 | -0.0054372
46 |  | 2.9609 | 33.7262 | 4187 | 0.0027204 | 6.1229 | 6.1256 | -1.9983 | 367.5891 | 1557.0444 | -0.0054363
47 |  | 2.9609 | 33.7207 | 4187 | 0.00272 | 6.1256 | 6.1283 | -1.9983 | 367.6484 | 1590.7652 | -0.0054355
48 |  | 2.9609 | 33.7153 | 4187 | 0.0027196 | 6.1283 | 6.131 | -1.9983 | 367.7076 | 1624.4804 | -0.0054346
49 |  | 2.9609 | 33.7099 | 4187 | 0.0027191 | 6.131 | 6.1338 | -1.9983 | 367.7669 | 1658.1903 | -0.0054337
50 |  | 2.9609 | 33.7044 | 4187 | 0.0027187 | 6.1338 | 6.1365 | -1.9983 | 367.8262 | 1691.8947 | -0.0054328
51 |  | 2.9609 | 33.699 | 4187 | 0.0027182 | 6.1365 | 6.1392 | -1.9983 | 367.8855 | 1725.5937 | -0.005432
52 |  | 2.9609 | 33.6936 | 4187 | 0.0027178 | 6.1392 | 6.1419 | -1.9983 | 367.9448 | 1759.2873 | -0.0054311
53 |  | 2.9609 | 33.6881 | 4187 | 0.0027174 | 6.1419 | 6.1446 | -1.9983 | 368.0041 | 1792.9754 | -0.0054302
54 |  | 2.9609 | 33.6827 | 4187 | 0.0027169 | 6.1446 | 6.1473 | -1.9983 | 368.0635 | 1826.6581 | -0.0054293
55 |  | 2.9609 | 33.6773 | 4187 | 0.0027165 | 6.1473 | 6.1501 | -1.9983 | 368.1228 | 1860.3354 | -0.0054284
56 |  | 2.9609 | 33.6718 | 4187 | 0.002716 | 6.1501 | 6.1528 | -1.9983 | 368.1821 | 1894.0072 | -0.0054276
57 |  | 2.9609 | 33.6664 | 4187 | 0.0027156 | 6.1528 | 6.1555 | -1.9983 | 368.2415 | 1927.6736 | -0.0054267
58 |  | 2.9609 | 33.661 | 4187 | 0.0027152 | 6.1555 | 6.1582 | -1.9983 | 368.3009 | 1961.3346 | -0.0054258
59 |  | 2.9609 | 33.6556 | 4187 | 0.0027147 | 6.1582 | 6.1609 | -1.9983 | 368.3602 | 1994.9902 | -0.0054249
60 |  | 2.9609 | 33.6501 | 4187 | 0.0027143 | 6.1609 | 6.1636 | -1.9983 | 368.4196 | 2028.6403 | -0.0054241
61 |  | 2.9609 | 33.6447 | 4187 | 0.0027139 | 6.1636 | 6.1663 | -1.9983 | 368.479 | 2062.285 | -0.0054232
62 |  | 2.9609 | 33.6393 | 4187 | 0.0027134 | 6.1663 | 6.1691 | -1.9983 | 368.5384 | 2095.9243 | -0.0054223
63 |  | 2.9609 | 33.6339 | 4187 | 0.002713 | 6.1691 | 6.1718 | -1.9983 | 368.5978 | 2129.5582 | -0.0054215
64 |  | 2.9609 | 33.6284 | 4187 | 0.0027125 | 6.1718 | 6.1745 | -1.9983 | 368.6573 | 2163.1866 | -0.0054206
65 |  | 2.9609 | 33.623 | 4187 | 0.0027121 | 6.1745 | 6.1772 | -1.9983 | 368.7167 | 2196.8097 | -0.0054197
66 |  | 2.9609 | 33.6176 | 4187 | 0.0027117 | 6.1772 | 6.1799 | -1.9983 | 368.7761 | 2230.4273 | -0.0054188
67 |  | 2.9609 | 33.6122 | 4187 | 0.0027112 | 6.1799 | 6.1826 | -1.9983 | 368.8356 | 2264.0394 | -0.005418
68 |  | 2.9609 | 33.6068 | 4187 | 0.0027108 | 6.1826 | 6.1853 | -1.9983 | 368.8951 | 2297.6462 | -0.0054171
69 |  | 2.9609 | 33.6014 | 4187 | 0.0027104 | 6.1853 | 6.188 | -1.9983 | 368.9545 | 2331.2476 | -0.0054162
70 |  | 2.9609 | 33.5959 | 4187 | 0.0027099 | 6.188 | 6.1908 | -1.9983 | 369.014 | 2364.8435 | -0.0054153
71 |  | 2.9609 | 33.5905 | 4187 | 0.0027095 | 6.1908 | 6.1935 | -1.9983 | 369.0735 | 2398.434 | -0.0054145
72 |  | 2.9609 | 33.5851 | 4187 | 0.0027091 | 6.1935 | 6.1962 | -1.9983 | 369.133 | 2432.0191 | -0.0054136
73 |  | 2.9609 | 33.5797 | 4187 | 0.0027086 | 6.1962 | 6.1989 | -1.9983 | 369.1925 | 2465.5988 | -0.0054127
74 |  | 2.9609 | 33.5743 | 4187 | 0.0027082 | 6.1989 | 6.2016 | -1.9983 | 369.252 | 2499.1731 | -0.0054118
75 |  | 2.9609 | 33.5689 | 4187 | 0.0027077 | 6.2016 | 6.2043 | -1.9983 | 369.3116 | 2532.742 | -0.005411
76 |  | 2.9609 | 33.5635 | 4187 | 0.0027073 | 6.2043 | 6.207 | -1.9983 | 369.3711 | 2566.3054 | -0.0054101
77 |  | 2.9609 | 33.558 | 4187 | 0.0027069 | 6.207 | 6.2097 | -1.9983 | 369.4307 | 2599.8635 | -0.0054092
78 |  | 2.9609 | 33.5526 | 4187 | 0.0027064 | 6.2097 | 6.2124 | -1.9983 | 369.4902 | 2633.4161 | -0.0054084
79 |  | 2.9609 | 33.5472 | 4187 | 0.002706 | 6.2124 | 6.2151 | -1.9983 | 369.5498 | 2666.9633 | -0.0054075
80 |  | 2.9609 | 33.5418 | 4187 | 0.0027056 | 6.2151 | 6.2178 | -1.9983 | 369.6094 | 2700.5051 | -0.0054066
81 |  | 2.9609 | 33.5364 | 4187 | 0.0027051 | 6.2178 | 6.2205 | -1.9983 | 369.6689 | 2734.0416 | -0.0054057
82 |  | 2.9609 | 33.531 | 4187 | 0.0027047 | 6.2205 | 6.2232 | -1.9983 | 369.7285 | 2767.5726 | -0.0054049
83 |  | 2.9609 | 33.5256 | 4187 | 0.0027043 | 6.2232 | 6.2259 | -1.9983 | 369.7881 | 2801.0982 | -0.005404
84 |  | 2.9609 | 33.5202 | 4187 | 0.0027038 | 6.2259 | 6.2286 | -1.9983 | 369.8478 | 2834.6184 | -0.0054031
85 |  | 2.9609 | 33.5148 | 4187 | 0.0027034 | 6.2286 | 6.2314 | -1.9983 | 369.9074 | 2868.1332 | -0.0054023
86 |  | 2.9609 | 33.5094 | 4187 | 0.0027029 | 6.2314 | 6.2341 | -1.9983 | 369.967 | 2901.6426 | -0.0054014
87 |  | 2.9609 | 33.504 | 4187 | 0.0027025 | 6.2341 | 6.2368 | -1.9983 | 370.0267 | 2935.1465 | -0.0054005
88 |  | 2.9609 | 33.4986 | 4187 | 0.0027021 | 6.2368 | 6.2395 | -1.9983 | 370.0863 | 2968.6451 | -0.0053996
89 |  | 2.9609 | 33.4932 | 4187 | 0.0027016 | 6.2395 | 6.2422 | -1.9983 | 370.146 | 3002.1383 | -0.0053988
90 |  | 2.9609 | 33.4878 | 4187 | 0.0027012 | 6.2422 | 6.2449 | -1.9983 | 370.2057 | 3035.6261 | -0.0053979
91 |  | 2.9609 | 33.4824 | 4187 | 0.0027008 | 6.2449 | 6.2476 | -1.9983 | 370.2653 | 3069.1085 | -0.005397
92 |  | 2.9609 | 33.477 | 4187 | 0.0027003 | 6.2476 | 6.2503 | -1.9983 | 370.325 | 3102.5855 | -0.0053962
93 |  | 2.9609 | 33.4716 | 4187 | 0.0026999 | 6.2503 | 6.253 | -1.9983 | 370.3847 | 3136.0571 | -0.0053953
94 |  | 2.9609 | 33.4662 | 4187 | 0.0026995 | 6.253 | 6.2557 | -1.9983 | 370.4444 | 3169.5233 | -0.0053944
95 |  | 2.9609 | 33.4608 | 4187 | 0.002699 | 6.2557 | 6.2584 | -1.9983 | 370.5042 | 3202.9841 | -0.0053936
96 |  | 2.9609 | 33.4554 | 4187 | 0.0026986 | 6.2584 | 6.2611 | -1.9983 | 370.5639 | 3236.4396 | -0.0053927
97 |  | 2.9609 | 33.45 | 4187 | 0.0026982 | 6.2611 | 6.2638 | -1.9983 | 370.6236 | 3269.8896 | -0.0053918
98 |  | 2.9609 | 33.4446 | 4187 | 0.0026977 | 6.2638 | 6.2665 | -1.9983 | 370.6834 | 3303.3342 | -0.005391
99 |  | 2.9609 | 33.4392 | 4187 | 0.0026973 | 6.2665 | 6.2692 | -1.9983 | 370.7432 | 3336.7735 | -0.0053901
100 |  | 2.9609 | 33.4339 | 4187 | 0.0026969 | 6.2692 | 6.2718 | -1.9983 | 370.8029 | 3370.2073 | -0.0053892
101 |  | 2.9609 | 33.4285 | 4187 | 0.0026964 | 6.2718 | 6.2745 | -1.9983 | 370.8627 | 3403.6358 | -0.0053883
102 |  | 2.9609 | 33.4231 | 4187 | 0.002696 | 6.2745 | 6.2772 | -1.9983 | 370.9225 | 3437.0589 | -0.0053875
103 |  | 2.9609 | 33.4177 | 4187 | 0.0026955 | 6.2772 | 6.2799 | -1.9983 | 370.9823 | 3470.4765 | -0.0053866
104 |  | 2.9609 | 33.4123 | 4187 | 0.0026951 | 6.2799 | 6.2826 | -1.9983 | 371.0421 | 3503.8888 | -0.0053857
105 |  | 2.9609 | 33.4069 | 4187 | 0.0026947 | 6.2826 | 6.2853 | -1.9983 | 371.1019 | 3537.2958 | -0.0053849
106 |  | 2.9609 | 33.4015 | 4187 | 0.0026942 | 6.2853 | 6.288 | -1.9983 | 371.1617 | 3570.6973 | -0.005384
107 |  | 2.9609 | 33.3961 | 4187 | 0.0026938 | 6.288 | 6.2907 | -1.9983 | 371.2216 | 3604.0934 | -0.0053831
108 |  | 2.9609 | 33.3908 | 4187 | 0.0026934 | 6.2907 | 6.2934 | -1.9983 | 371.2814 | 3637.4842 | -0.0053823
109 |  | 2.9609 | 33.3854 | 4187 | 0.0026929 | 6.2934 | 6.2961 | -1.9983 | 371.3413 | 3670.8696 | -0.0053814
110 |  | 2.9609 | 33.38 | 4187 | 0.0026925 | 6.2961 | 6.2988 | -1.9983 | 371.4012 | 3704.2496 | -0.0053805
111 |  | 2.9609 | 33.3746 | 4187 | 0.0026921 | 6.2988 | 6.3015 | -1.9983 | 371.461 | 3737.6242 | -0.0053797
112 |  | 2.9609 | 33.3692 | 4187 | 0.0026916 | 6.3015 | 6.3042 | -1.9983 | 371.5209 | 3770.9934 | -0.0053788
113 |  | 2.9609 | 33.3639 | 4187 | 0.0026912 | 6.3042 | 6.3069 | -1.9983 | 371.5808 | 3804.3573 | -0.0053779
114 |  | 2.9609 | 33.3585 | 4187 | 0.0026908 | 6.3069 | 6.3096 | -1.9983 | 371.6407 | 3837.7158 | -0.0053771
115 |  | 2.9609 | 33.3531 | 4187 | 0.0026903 | 6.3096 | 6.3122 | -1.9983 | 371.7006 | 3871.0689 | -0.0053762
116 |  | 2.9609 | 33.3477 | 4187 | 0.0026899 | 6.3122 | 6.3149 | -1.9983 | 371.7606 | 3904.4166 | -0.0053753
117 |  | 2.9609 | 33.3424 | 4187 | 0.0026895 | 6.3149 | 6.3176 | -1.9983 | 371.8205 | 3937.759 | -0.0053745
118 |  | 2.9609 | 33.337 | 4187 | 0.002689 | 6.3176 | 6.3203 | -1.9983 | 371.8804 | 3971.096 | -0.0053736
119 |  | 2.9609 | 33.3316 | 4187 | 0.0026886 | 6.3203 | 6.323 | -1.9983 | 371.9404 | 4004.4276 | -0.0053727
120 |  | 2.9609 | 33.3262 | 4187 | 0.0026882 | 6.323 | 6.3257 | -1.9983 | 372.0003 | 4037.7538 | -0.0053719
121 |  | 2.9609 | 33.3209 | 4187 | 0.0026877 | 6.3257 | 6.3284 | -1.9983 | 372.0603 | 4071.0747 | -0.005371
122 |  | 2.9609 | 33.3155 | 4187 | 0.0026873 | 6.3284 | 6.3311 | -1.9983 | 372.1203 | 4104.3902 | -0.0053701
123 |  | 2.9609 | 33.3101 | 4187 | 0.0026869 | 6.3311 | 6.3338 | -1.9983 | 372.1803 | 4137.7003 | -0.0053693
124 |  | 2.9609 | 33.3048 | 4187 | 0.0026864 | 6.3338 | 6.3364 | -1.9983 | 372.2403 | 4171.005 | -0.0053684
125 |  | 2.9609 | 33.2994 | 4187 | 0.002686 | 6.3364 | 6.3391 | -1.9983 | 372.3003 | 4204.3044 | -0.0053675
126 |  | 2.9609 | 33.294 | 4187 | 0.0026856 | 6.3391 | 6.3418 | -1.9983 | 372.3603 | 4237.5984 | -0.0053667
127 |  | 2.9609 | 33.2886 | 4187 | 0.0026851 | 6.3418 | 6.3445 | -1.9983 | 372.4204 | 4270.8871 | -0.0053658
128 |  | 2.9609 | 33.2833 | 4187 | 0.0026847 | 6.3445 | 6.3472 | -1.9983 | 372.4804 | 4304.1704 | -0.0053649
129 |  | 2.9609 | 33.2779 | 4187 | 0.0026843 | 6.3472 | 6.3499 | -1.9983 | 372.5404 | 4337.4483 | -0.0053641
130 |  | 2.9609 | 33.2726 | 4187 | 0.0026838 | 6.3499 | 6.3526 | -1.9983 | 372.6005 | 4370.7208 | -0.0053632
131 |  | 2.9609 | 33.2672 | 4187 | 0.0026834 | 6.3526 | 6.3552 | -1.9983 | 372.6606 | 4403.988 | -0.0053623
132 |  | 2.9609 | 33.2618 | 4187 | 0.002683 | 6.3552 | 6.3579 | -1.9983 | 372.7207 | 4437.2499 | -0.0053615
133 |  | 2.9609 | 33.2565 | 4187 | 0.0026825 | 6.3579 | 6.3606 | -1.9983 | 372.7807 | 4470.5063 | -0.0053606
134 |  | 2.9609 | 33.2511 | 4187 | 0.0026821 | 6.3606 | 6.3633 | -1.9983 | 372.8408 | 4503.7574 | -0.0053598
135 |  | 2.9609 | 33.2457 | 4187 | 0.0026817 | 6.3633 | 6.366 | -1.9983 | 372.9009 | 4537.0032 | -0.0053589
136 |  | 2.9609 | 33.2404 | 4187 | 0.0026812 | 6.366 | 6.3686 | -1.9983 | 372.9611 | 4570.2436 | -0.005358
137 |  | 2.9609 | 33.235 | 4187 | 0.0026808 | 6.3686 | 6.3713 | -1.9983 | 373.0212 | 4603.4786 | -0.0053572
138 |  | 2.9609 | 33.2297 | 4187 | 0.0026804 | 6.3713 | 6.374 | -1.9983 | 373.0813 | 4636.7083 | -0.0053563
139 |  | 2.9609 | 33.2243 | 4187 | 0.0026799 | 6.374 | 6.3767 | -1.9983 | 373.1415 | 4669.9326 | -0.0053554
140 |  | 2.9609 | 33.219 | 4187 | 0.0026795 | 6.3767 | 6.3794 | -1.9983 | 373.2016 | 4703.1515 | -0.0053546
141 |  | 2.9609 | 33.2136 | 4187 | 0.0026791 | 6.3794 | 6.382 | -1.9983 | 373.2618 | 4736.3652 | -0.0053537
142 |  | 2.9609 | 33.2083 | 4187 | 0.0026787 | 6.382 | 6.3847 | -1.9983 | 373.322 | 4769.5734 | -0.0053528
143 |  | 2.9609 | 33.2029 | 4187 | 0.0026782 | 6.3847 | 6.3874 | -1.9983 | 373.3822 | 4802.7763 | -0.005352
144 |  | 2.9609 | 33.1975 | 4187 | 0.0026778 | 6.3874 | 6.3901 | -1.9983 | 373.4424 | 4835.9739 | -0.0053511
145 |  | 2.9609 | 33.1922 | 4187 | 0.0026774 | 6.3901 | 6.3928 | -1.9983 | 373.5026 | 4869.1661 | -0.0053503
146 |  | 2.9609 | 33.1868 | 4187 | 0.0026769 | 6.3928 | 6.3954 | -1.9983 | 373.5628 | 4902.3529 | -0.0053494
147 |  | 2.9609 | 33.1815 | 4187 | 0.0026765 | 6.3954 | 6.3981 | -1.9983 | 373.623 | 4935.5344 | -0.0053485
148 |  | 2.9609 | 33.1761 | 4187 | 0.0026761 | 6.3981 | 6.4008 | -1.9983 | 373.6832 | 4968.7105 | -0.0053477
149 |  | 2.9609 | 33.1708 | 4187 | 0.0026756 | 6.4008 | 6.4035 | -1.9983 | 373.7435 | 5001.8813 | -0.0053468
150 |  | 2.9609 | 33.1655 | 4187 | 0.0026752 | 6.4035 | 6.4061 | -1.9983 | 373.8037 | 5035.0468 | -0.0053459
151 |  | 2.9609 | 33.1601 | 4187 | 0.0026748 | 6.4061 | 6.4088 | -1.9983 | 373.864 | 5068.2069 | -0.0053451
152 |  | 2.9609 | 33.1548 | 4187 | 0.0026743 | 6.4088 | 6.4115 | -1.9983 | 373.9243 | 5101.3617 | -0.0053442
153 |  | 2.9609 | 33.1494 | 4187 | 0.0026739 | 6.4115 | 6.4142 | -1.9983 | 373.9846 | 5134.5111 | -0.0053434
154 |  | 2.9609 | 33.1441 | 4187 | 0.0026735 | 6.4142 | 6.4168 | -1.9983 | 374.0448 | 5167.6552 | -0.0053425
155 |  | 2.9609 | 33.1387 | 4187 | 0.002673 | 6.4168 | 6.4195 | -1.9983 | 374.1051 | 5200.7939 | -0.0053416
156 |  | 2.9609 | 33.1334 | 4187 | 0.0026726 | 6.4195 | 6.4222 | -1.9983 | 374.1655 | 5233.9273 | -0.0053408
157 |  | 2.9609 | 33.1281 | 4187 | 0.0026722 | 6.4222 | 6.4249 | -1.9983 | 374.2258 | 5267.0553 | -0.0053399
158 |  | 2.9609 | 33.1227 | 4187 | 0.0026718 | 6.4249 | 6.4275 | -1.9983 | 374.2861 | 5300.1781 | -0.0053391
159 |  | 2.9609 | 33.1174 | 4187 | 0.0026713 | 6.4275 | 6.4302 | -1.9983 | 374.3465 | 5333.2954 | -0.0053382
160 |  | 2.9609 | 33.112 | 4187 | 0.0026709 | 6.4302 | 6.4329 | -1.9983 | 374.4068 | 5366.4075 | -0.0053373
161 |  | 2.9609 | 33.1067 | 4187 | 0.0026705 | 6.4329 | 6.4355 | -1.9983 | 374.4672 | 5399.5142 | -0.0053365
162 |  | 2.9609 | 33.1014 | 4187 | 0.00267 | 6.4355 | 6.4382 | -1.9983 | 374.5275 | 5432.6155 | -0.0053356
163 |  | 2.9609 | 33.096 | 4187 | 0.0026696 | 6.4382 | 6.4409 | -1.9983 | 374.5879 | 5465.7115 | -0.0053348
164 |  | 2.9609 | 33.0907 | 4187 | 0.0026692 | 6.4409 | 6.4435 | -1.9983 | 374.6483 | 5498.8022 | -0.0053339
165 |  | 2.9609 | 33.0854 | 4187 | 0.0026687 | 6.4435 | 6.4462 | -1.9983 | 374.7087 | 5531.8876 | -0.005333
166 |  | 2.9609 | 33.08 | 4187 | 0.0026683 | 6.4462 | 6.4489 | -1.9983 | 374.7691 | 5564.9676 | -0.0053322
167 |  | 2.9609 | 33.0747 | 4187 | 0.0026679 | 6.4489 | 6.4516 | -1.9983 | 374.8295 | 5598.0423 | -0.0053313
168 |  | 2.9609 | 33.0694 | 4187 | 0.0026674 | 6.4516 | 6.4542 | -1.9983 | 374.89 | 5631.1117 | -0.0053305
169 |  | 2.9609 | 33.064 | 4187 | 0.002667 | 6.4542 | 6.4569 | -1.9983 | 374.9504 | 5664.1757 | -0.0053296
170 |  | 2.9609 | 33.0587 | 4187 | 0.0026666 | 6.4569 | 6.4596 | -1.9983 | 375.0108 | 5697.2344 | -0.0053287
171 |  | 2.9609 | 33.0534 | 4187 | 0.0026662 | 6.4596 | 6.4622 | -1.9983 | 375.0713 | 5730.2878 | -0.0053279
172 |  | 2.9609 | 33.048 | 4187 | 0.0026657 | 6.4622 | 6.4649 | -1.9983 | 375.1318 | 5763.3358 | -0.005327
173 |  | 2.9609 | 33.0427 | 4187 | 0.0026653 | 6.4649 | 6.4675 | -1.9983 | 375.1922 | 5796.3785 | -0.0053262
174 |  | 2.9609 | 33.0374 | 4187 | 0.0026649 | 6.4675 | 6.4702 | -1.9983 | 375.2527 | 5829.4159 | -0.0053253
175 |  | 2.9609 | 33.0321 | 4187 | 0.0026644 | 6.4702 | 6.4729 | -1.9983 | 375.3132 | 5862.448 | -0.0053244
176 |  | 2.9609 | 33.0267 | 4187 | 0.002664 | 6.4729 | 6.4755 | -1.9983 | 375.3737 | 5895.4747 | -0.0053236
177 |  | 2.9609 | 33.0214 | 4187 | 0.0026636 | 6.4755 | 6.4782 | -1.9983 | 375.4343 | 5928.4961 | -0.0053227
178 |  | 2.9609 | 33.0161 | 4187 | 0.0026632 | 6.4782 | 6.4809 | -1.9983 | 375.4948 | 5961.5122 | -0.0053219
179 |  | 2.9609 | 33.0108 | 4187 | 0.0026627 | 6.4809 | 6.4835 | -1.9983 | 375.5553 | 5994.523 | -0.005321
180 |  | 2.9609 | 33.0055 | 4187 | 0.0026623 | 6.4835 | 6.4862 | -1.9983 | 375.6159 | 6027.5284 | -0.0053202
181 |  | 2.9609 | 33.0001 | 4187 | 0.0026619 | 6.4862 | 6.4889 | -1.9983 | 375.6764 | 6060.5286 | -0.0053193
182 |  | 2.9609 | 32.9948 | 4187 | 0.0026614 | 6.4889 | 6.4915 | -1.9983 | 375.737 | 6093.5234 | -0.0053184
183 |  | 2.9609 | 32.9895 | 4187 | 0.002661 | 6.4915 | 6.4942 | -1.9983 | 375.7976 | 6126.5129 | -0.0053176
184 |  | 2.9609 | 32.9842 | 4187 | 0.0026606 | 6.4942 | 6.4968 | -1.9983 | 375.8581 | 6159.497 | -0.0053167
185 |  | 2.9609 | 32.9789 | 4187 | 0.0026601 | 6.4968 | 6.4995 | -1.9983 | 375.9187 | 6192.4759 | -0.0053159
186 |  | 2.9609 | 32.9735 | 4187 | 0.0026597 | 6.4995 | 6.5022 | -1.9983 | 375.9793 | 6225.4494 | -0.005315
187 |  | 2.9609 | 32.9682 | 4187 | 0.0026593 | 6.5022 | 6.5048 | -1.9983 | 376.04 | 6258.4177 | -0.0053142
188 |  | 2.9609 | 32.9629 | 4187 | 0.0026589 | 6.5048 | 6.5075 | -1.9983 | 376.1006 | 6291.3806 | -0.0053133
189 |  | 2.9609 | 32.9576 | 4187 | 0.0026584 | 6.5075 | 6.5101 | -1.9983 | 376.1612 | 6324.3382 | -0.0053124
190 |  | 2.9609 | 32.9523 | 4187 | 0.002658 | 6.5101 | 6.5128 | -1.9983 | 376.2219 | 6357.2905 | -0.0053116
191 |  | 2.9609 | 32.947 | 4187 | 0.0026576 | 6.5128 | 6.5155 | -1.9983 | 376.2825 | 6390.2374 | -0.0053107
192 |  | 2.9609 | 32.9417 | 4187 | 0.0026571 | 6.5155 | 6.5181 | -1.9983 | 376.3432 | 6423.1791 | -0.0053099
193 |  | 2.9609 | 32.9364 | 4187 | 0.0026567 | 6.5181 | 6.5208 | -1.9983 | 376.4038 | 6456.1155 | -0.005309
194 |  | 2.9609 | 32.931 | 4187 | 0.0026563 | 6.5208 | 6.5234 | -1.9983 | 376.4645 | 6489.0465 | -0.0053082
195 |  | 2.9609 | 32.9257 | 4187 | 0.0026559 | 6.5234 | 6.5261 | -1.9983 | 376.5252 | 6521.9722 | -0.0053073
196 |  | 2.9609 | 32.9204 | 4187 | 0.0026554 | 6.5261 | 6.5287 | -1.9983 | 376.5859 | 6554.8927 | -0.0053065
197 |  | 2.9609 | 32.9151 | 4187 | 0.002655 | 6.5287 | 6.5314 | -1.9983 | 376.6466 | 6587.8078 | -0.0053056
198 |  | 2.9609 | 32.9098 | 4187 | 0.0026546 | 6.5314 | 6.534 | -1.9983 | 376.7074 | 6620.7176 | -0.0053047
199 |  | 2.9609 | 32.9045 | 4187 | 0.0026542 | 6.534 | 6.5367 | -1.9983 | 376.7681 | 6653.6221 | -0.0053039
200 |  | 2.9609 | 32.8992 | 4187 | 0.0026537 | 6.5367 | 6.5393 | -1.9983 | 376.8288 | 6686.5213 | -0.005303
201 |  | 2.9609 | 32.8939 | 4187 | 0.0026533 | 6.5393 | 6.542 | -1.9983 | 376.8896 | 6719.4152 | -0.0053022
202 |  | 2.9609 | 32.8886 | 4187 | 0.0026529 | 6.542 | 6.5447 | -1.9983 | 376.9503 | 6752.3039 | -0.0053013
203 |  | 2.9609 | 32.8833 | 4187 | 0.0026524 | 6.5447 | 6.5473 | -1.9983 | 377.0111 | 6785.1872 | -0.0053005
204 |  | 2.9609 | 32.878 | 4187 | 0.002652 | 6.5473 | 6.55 | -1.9983 | 377.0719 | 6818.0652 | -0.0052996
205 |  | 2.9609 | 32.8727 | 4187 | 0.0026516 | 6.55 | 6.5526 | -1.9983 | 377.1327 | 6850.9379 | -0.0052988
206 |  | 2.9609 | 32.8674 | 4187 | 0.0026512 | 6.5526 | 6.5553 | -1.9983 | 377.1935 | 6883.8053 | -0.0052979
207 |  | 2.9609 | 32.8621 | 4187 | 0.0026507 | 6.5553 | 6.5579 | -1.9983 | 377.2543 | 6916.6674 | -0.0052971
208 |  | 2.9609 | 32.8568 | 4187 | 0.0026503 | 6.5579 | 6.5606 | -1.9983 | 377.3151 | 6949.5242 | -0.0052962
209 |  | 2.9609 | 32.8515 | 4187 | 0.0026499 | 6.5606 | 6.5632 | -1.9983 | 377.3759 | 6982.3757 | -0.0052953
210 |  | 2.9609 | 32.8462 | 4187 | 0.0026495 | 6.5632 | 6.5659 | -1.9983 | 377.4368 | 7015.2219 | -0.0052945
211 |  | 2.9609 | 32.8409 | 4187 | 0.002649 | 6.5659 | 6.5685 | -1.9983 | 377.4976 | 7048.0628 | -0.0052936
212 |  | 2.9609 | 32.8356 | 4187 | 0.0026486 | 6.5685 | 6.5712 | -1.9983 | 377.5585 | 7080.8985 | -0.0052928
213 |  | 2.9609 | 32.8303 | 4187 | 0.0026482 | 6.5712 | 6.5738 | -1.9983 | 377.6194 | 7113.7288 | -0.0052919
214 |  | 2.9609 | 32.825 | 4187 | 0.0026477 | 6.5738 | 6.5765 | -1.9983 | 377.6802 | 7146.5538 | -0.0052911
215 |  | 2.9609 | 32.8198 | 4187 | 0.0026473 | 6.5765 | 6.5791 | -1.9983 | 377.7411 | 7179.3736 | -0.0052902
216 |  | 2.9609 | 32.8145 | 4187 | 0.0026469 | 6.5791 | 6.5818 | -1.9983 | 377.802 | 7212.1881 | -0.0052894
217 |  | 2.9609 | 32.8092 | 4187 | 0.0026465 | 6.5818 | 6.5844 | -1.9983 | 377.8629 | 7244.9972 | -0.0052885
218 |  | 2.9609 | 32.8039 | 4187 | 0.002646 | 6.5844 | 6.587 | -1.9983 | 377.9238 | 7277.8011 | -0.0052877
219 |  | 2.9609 | 32.7986 | 4187 | 0.0026456 | 6.587 | 6.5897 | -1.9983 | 377.9848 | 7310.5997 | -0.0052868
220 |  | 2.9609 | 32.7933 | 4187 | 0.0026452 | 6.5897 | 6.5923 | -1.9983 | 378.0457 | 7343.393 | -0.005286
221 |  | 2.9609 | 32.788 | 4187 | 0.0026448 | 6.5923 | 6.595 | -1.9983 | 378.1067 | 7376.1811 | -0.0052851
222 |  | 2.9609 | 32.7827 | 4187 | 0.0026443 | 6.595 | 6.5976 | -1.9983 | 378.1676 | 7408.9638 | -0.0052843
223 |  | 2.9609 | 32.7775 | 4187 | 0.0026439 | 6.5976 | 6.6003 | -1.9983 | 378.2286 | 7441.7413 | -0.0052834
224 |  | 2.9609 | 32.7722 | 4187 | 0.0026435 | 6.6003 | 6.6029 | -1.9983 | 378.2896 | 7474.5134 | -0.0052826
225 |  | 2.9609 | 32.7669 | 4187 | 0.0026431 | 6.6029 | 6.6056 | -1.9983 | 378.3505 | 7507.2803 | -0.0052817
226 |  | 2.9609 | 32.7616 | 4187 | 0.0026426 | 6.6056 | 6.6082 | -1.9983 | 378.4115 | 7540.0419 | -0.0052809
227 |  | 2.9609 | 32.7563 | 4187 | 0.0026422 | 6.6082 | 6.6108 | -1.9983 | 378.4725 | 7572.7983 | -0.00528
228 |  | 2.9609 | 32.751 | 4187 | 0.0026418 | 6.6108 | 6.6135 | -1.9983 | 378.5336 | 7605.5493 | -0.0052792
229 |  | 2.9609 | 32.7458 | 4187 | 0.0026413 | 6.6135 | 6.6161 | -1.9983 | 378.5946 | 7638.2951 | -0.0052783
230 |  | 2.9609 | 32.7405 | 4187 | 0.0026409 | 6.6161 | 6.6188 | -1.9983 | 378.6556 | 7671.0356 | -0.0052774
231 |  | 2.9609 | 32.7352 | 4187 | 0.0026405 | 6.6188 | 6.6214 | -1.9983 | 378.7167 | 7703.7708 | -0.0052766
232 |  | 2.9609 | 32.7299 | 4187 | 0.0026401 | 6.6214 | 6.624 | -1.9983 | 378.7777 | 7736.5007 | -0.0052757
233 |  | 2.9609 | 32.7247 | 4187 | 0.0026396 | 6.624 | 6.6267 | -1.9983 | 378.8388 | 7769.2254 | -0.0052749
234 |  | 2.9609 | 32.7194 | 4187 | 0.0026392 | 6.6267 | 6.6293 | -1.9983 | 378.8999 | 7801.9448 | -0.005274
235 |  | 2.9609 | 32.7141 | 4187 | 0.0026388 | 6.6293 | 6.632 | -1.9983 | 378.9609 | 7834.6589 | -0.0052732
236 |  | 2.9609 | 32.7088 | 4187 | 0.0026384 | 6.632 | 6.6346 | -1.9983 | 379.022 | 7867.3677 | -0.0052723

## 90
|  |  | buis | verlies W/M | L /°C/sec
diam | wandikte |  | inhoud l/m |  | W/M
90 | 8.2 | 3.1416 | 4.2545 | 37.4819 | 4187
[8 empty] | J/sec/mtr | aantal mtr. | verlies
|  | buis | verlies W/M | L /°C/sec | verlies temp | begintemp | eindtemp | verlies | bij 1°C | totaal J/sec
|  | inhoud L |  | W/M | °C per M | °C | °C | per m°C | daling | aantal mtr
1 | 90 | 4.2545 | 37.4819 | 4187 | 0.0021041 | 6 | 6.0021 | -2.2048 | 475.2556 | 37.4819 | -0.0046392
2 |  | 4.2545 | 37.4772 | 4187 | 0.0021039 | 6.0021 | 6.0042 | -2.2048 | 475.3145 | 74.9591 | -0.0046386
3 |  | 4.2545 | 37.4726 | 4187 | 0.0021036 | 6.0042 | 6.0063 | -2.2048 | 475.3733 | 112.4317 | -0.0046381
4 |  | 4.2545 | 37.4679 | 4187 | 0.0021033 | 6.0063 | 6.0084 | -2.2048 | 475.4321 | 149.8996 | -0.0046375
5 |  | 4.2545 | 37.4633 | 4187 | 0.0021031 | 6.0084 | 6.0105 | -2.2048 | 475.491 | 187.3629 | -0.0046369
6 |  | 4.2545 | 37.4587 | 4187 | 0.0021028 | 6.0105 | 6.0126 | -2.2048 | 475.5499 | 224.8216 | -0.0046364
7 |  | 4.2545 | 37.454 | 4187 | 0.0021026 | 6.0126 | 6.0147 | -2.2048 | 475.6087 | 262.2757 | -0.0046358
8 |  | 4.2545 | 37.4494 | 4187 | 0.0021023 | 6.0147 | 6.0168 | -2.2048 | 475.6676 | 299.7251 | -0.0046352
9 |  | 4.2545 | 37.4448 | 4187 | 0.002102 | 6.0168 | 6.0189 | -2.2048 | 475.7265 | 337.1698 | -0.0046346
10 |  | 4.2545 | 37.4401 | 4187 | 0.0021018 | 6.0189 | 6.021 | -2.2048 | 475.7854 | 374.61 | -0.0046341
11 |  | 4.2545 | 37.4355 | 4187 | 0.0021015 | 6.021 | 6.0231 | -2.2048 | 475.8443 | 412.0455 | -0.0046335
12 |  | 4.2545 | 37.4309 | 4187 | 0.0021013 | 6.0231 | 6.0252 | -2.2048 | 475.9032 | 449.4763 | -0.0046329
13 |  | 4.2545 | 37.4262 | 4187 | 0.002101 | 6.0252 | 6.0273 | -2.2048 | 475.9621 | 486.9026 | -0.0046323
14 |  | 4.2545 | 37.4216 | 4187 | 0.0021007 | 6.0273 | 6.0294 | -2.2048 | 476.021 | 524.3242 | -0.0046318
15 |  | 4.2545 | 37.417 | 4187 | 0.0021005 | 6.0294 | 6.0315 | -2.2048 | 476.0799 | 561.7411 | -0.0046312
16 |  | 4.2545 | 37.4123 | 4187 | 0.0021002 | 6.0315 | 6.0336 | -2.2048 | 476.1389 | 599.1535 | -0.0046306
17 |  | 4.2545 | 37.4077 | 4187 | 0.0021 | 6.0336 | 6.0357 | -2.2048 | 476.1978 | 636.5612 | -0.00463
18 |  | 4.2545 | 37.4031 | 4187 | 0.0020997 | 6.0357 | 6.0378 | -2.2048 | 476.2567 | 673.9642 | -0.0046295
19 |  | 4.2545 | 37.3984 | 4187 | 0.0020994 | 6.0378 | 6.0399 | -2.2048 | 476.3157 | 711.3627 | -0.0046289
20 |  | 4.2545 | 37.3938 | 4187 | 0.0020992 | 6.0399 | 6.042 | -2.2048 | 476.3747 | 748.7565 | -0.0046283
21 |  | 4.2545 | 37.3892 | 4187 | 0.0020989 | 6.042 | 6.0441 | -2.2048 | 476.4336 | 786.1457 | -0.0046277
22 |  | 4.2545 | 37.3846 | 4187 | 0.0020987 | 6.0441 | 6.0462 | -2.2048 | 476.4926 | 823.5303 | -0.0046272
23 |  | 4.2545 | 37.3799 | 4187 | 0.0020984 | 6.0462 | 6.0483 | -2.2048 | 476.5516 | 860.9102 | -0.0046266
24 |  | 4.2545 | 37.3753 | 4187 | 0.0020981 | 6.0483 | 6.0504 | -2.2048 | 476.6106 | 898.2855 | -0.004626
25 |  | 4.2545 | 37.3707 | 4187 | 0.0020979 | 6.0504 | 6.0525 | -2.2048 | 476.6696 | 935.6562 | -0.0046255
26 |  | 4.2545 | 37.3661 | 4187 | 0.0020976 | 6.0525 | 6.0546 | -2.2048 | 476.7286 | 973.0223 | -0.0046249
27 |  | 4.2545 | 37.3614 | 4187 | 0.0020974 | 6.0546 | 6.0567 | -2.2048 | 476.7876 | 1010.3837 | -0.0046243
28 |  | 4.2545 | 37.3568 | 4187 | 0.0020971 | 6.0567 | 6.0588 | -2.2048 | 476.8466 | 1047.7405 | -0.0046237
29 |  | 4.2545 | 37.3522 | 4187 | 0.0020969 | 6.0588 | 6.0609 | -2.2048 | 476.9056 | 1085.0927 | -0.0046232
30 |  | 4.2545 | 37.3476 | 4187 | 0.0020966 | 6.0609 | 6.063 | -2.2048 | 476.9647 | 1122.4402 | -0.0046226
31 |  | 4.2545 | 37.3429 | 4187 | 0.0020963 | 6.063 | 6.0651 | -2.2048 | 477.0237 | 1159.7832 | -0.004622
32 |  | 4.2545 | 37.3383 | 4187 | 0.0020961 | 6.0651 | 6.0672 | -2.2048 | 477.0828 | 1197.1215 | -0.0046215
33 |  | 4.2545 | 37.3337 | 4187 | 0.0020958 | 6.0672 | 6.0693 | -2.2048 | 477.1418 | 1234.4552 | -0.0046209
34 |  | 4.2545 | 37.3291 | 4187 | 0.0020956 | 6.0693 | 6.0714 | -2.2048 | 477.2009 | 1271.7843 | -0.0046203
35 |  | 4.2545 | 37.3245 | 4187 | 0.0020953 | 6.0714 | 6.0735 | -2.2048 | 477.26 | 1309.1087 | -0.0046197
36 |  | 4.2545 | 37.3198 | 4187 | 0.002095 | 6.0735 | 6.0756 | -2.2048 | 477.319 | 1346.4285 | -0.0046192
37 |  | 4.2545 | 37.3152 | 4187 | 0.0020948 | 6.0756 | 6.0777 | -2.2048 | 477.3781 | 1383.7438 | -0.0046186
38 |  | 4.2545 | 37.3106 | 4187 | 0.0020945 | 6.0777 | 6.0798 | -2.2048 | 477.4372 | 1421.0544 | -0.004618
39 |  | 4.2545 | 37.306 | 4187 | 0.0020943 | 6.0798 | 6.0819 | -2.2048 | 477.4963 | 1458.3603 | -0.0046175
40 |  | 4.2545 | 37.3014 | 4187 | 0.002094 | 6.0819 | 6.084 | -2.2048 | 477.5554 | 1495.6617 | -0.0046169
41 |  | 4.2545 | 37.2967 | 4187 | 0.0020937 | 6.084 | 6.0861 | -2.2048 | 477.6146 | 1532.9584 | -0.0046163
42 |  | 4.2545 | 37.2921 | 4187 | 0.0020935 | 6.0861 | 6.0881 | -2.2048 | 477.6737 | 1570.2506 | -0.0046157
43 |  | 4.2545 | 37.2875 | 4187 | 0.0020932 | 6.0881 | 6.0902 | -2.2048 | 477.7328 | 1607.5381 | -0.0046152
44 |  | 4.2545 | 37.2829 | 4187 | 0.002093 | 6.0902 | 6.0923 | -2.2048 | 477.7919 | 1644.821 | -0.0046146
45 |  | 4.2545 | 37.2783 | 4187 | 0.0020927 | 6.0923 | 6.0944 | -2.2048 | 477.8511 | 1682.0993 | -0.004614
46 |  | 4.2545 | 37.2737 | 4187 | 0.0020924 | 6.0944 | 6.0965 | -2.2048 | 477.9102 | 1719.3729 | -0.0046135
47 |  | 4.2545 | 37.2691 | 4187 | 0.0020922 | 6.0965 | 6.0986 | -2.2048 | 477.9694 | 1756.642 | -0.0046129
48 |  | 4.2545 | 37.2644 | 4187 | 0.0020919 | 6.0986 | 6.1007 | -2.2048 | 478.0286 | 1793.9064 | -0.0046123
49 |  | 4.2545 | 37.2598 | 4187 | 0.0020917 | 6.1007 | 6.1028 | -2.2048 | 478.0877 | 1831.1663 | -0.0046117
50 |  | 4.2545 | 37.2552 | 4187 | 0.0020914 | 6.1028 | 6.1049 | -2.2048 | 478.1469 | 1868.4215 | -0.0046112
51 |  | 4.2545 | 37.2506 | 4187 | 0.0020911 | 6.1049 | 6.107 | -2.2048 | 478.2061 | 1905.6721 | -0.0046106
52 |  | 4.2545 | 37.246 | 4187 | 0.0020909 | 6.107 | 6.1091 | -2.2048 | 478.2653 | 1942.9181 | -0.00461
53 |  | 4.2545 | 37.2414 | 4187 | 0.0020906 | 6.1091 | 6.1112 | -2.2048 | 478.3245 | 1980.1595 | -0.0046095
54 |  | 4.2545 | 37.2368 | 4187 | 0.0020904 | 6.1112 | 6.1133 | -2.2048 | 478.3837 | 2017.3962 | -0.0046089
55 |  | 4.2545 | 37.2322 | 4187 | 0.0020901 | 6.1133 | 6.1153 | -2.2048 | 478.4429 | 2054.6284 | -0.0046083
56 |  | 4.2545 | 37.2276 | 4187 | 0.0020899 | 6.1153 | 6.1174 | -2.2048 | 478.5022 | 2091.856 | -0.0046077
57 |  | 4.2545 | 37.223 | 4187 | 0.0020896 | 6.1174 | 6.1195 | -2.2048 | 478.5614 | 2129.0789 | -0.0046072
58 |  | 4.2545 | 37.2183 | 4187 | 0.0020893 | 6.1195 | 6.1216 | -2.2048 | 478.6206 | 2166.2973 | -0.0046066
59 |  | 4.2545 | 37.2137 | 4187 | 0.0020891 | 6.1216 | 6.1237 | -2.2048 | 478.6799 | 2203.511 | -0.004606
60 |  | 4.2545 | 37.2091 | 4187 | 0.0020888 | 6.1237 | 6.1258 | -2.2048 | 478.7391 | 2240.7201 | -0.0046055
61 |  | 4.2545 | 37.2045 | 4187 | 0.0020886 | 6.1258 | 6.1279 | -2.2048 | 478.7984 | 2277.9247 | -0.0046049
62 |  | 4.2545 | 37.1999 | 4187 | 0.0020883 | 6.1279 | 6.13 | -2.2048 | 478.8577 | 2315.1246 | -0.0046043
63 |  | 4.2545 | 37.1953 | 4187 | 0.002088 | 6.13 | 6.1321 | -2.2048 | 478.9169 | 2352.3199 | -0.0046038
64 |  | 4.2545 | 37.1907 | 4187 | 0.0020878 | 6.1321 | 6.1341 | -2.2048 | 478.9762 | 2389.5106 | -0.0046032
65 |  | 4.2545 | 37.1861 | 4187 | 0.0020875 | 6.1341 | 6.1362 | -2.2048 | 479.0355 | 2426.6967 | -0.0046026
66 |  | 4.2545 | 37.1815 | 4187 | 0.0020873 | 6.1362 | 6.1383 | -2.2048 | 479.0948 | 2463.8782 | -0.004602
67 |  | 4.2545 | 37.1769 | 4187 | 0.002087 | 6.1383 | 6.1404 | -2.2048 | 479.1541 | 2501.0551 | -0.0046015
68 |  | 4.2545 | 37.1723 | 4187 | 0.0020868 | 6.1404 | 6.1425 | -2.2048 | 479.2134 | 2538.2274 | -0.0046009
69 |  | 4.2545 | 37.1677 | 4187 | 0.0020865 | 6.1425 | 6.1446 | -2.2048 | 479.2728 | 2575.3951 | -0.0046003
70 |  | 4.2545 | 37.1631 | 4187 | 0.0020862 | 6.1446 | 6.1467 | -2.2048 | 479.3321 | 2612.5582 | -0.0045998
71 |  | 4.2545 | 37.1585 | 4187 | 0.002086 | 6.1467 | 6.1487 | -2.2048 | 479.3914 | 2649.7167 | -0.0045992
72 |  | 4.2545 | 37.1539 | 4187 | 0.0020857 | 6.1487 | 6.1508 | -2.2048 | 479.4508 | 2686.8707 | -0.0045986
73 |  | 4.2545 | 37.1493 | 4187 | 0.0020855 | 6.1508 | 6.1529 | -2.2048 | 479.5101 | 2724.02 | -0.0045981
74 |  | 4.2545 | 37.1447 | 4187 | 0.0020852 | 6.1529 | 6.155 | -2.2048 | 479.5695 | 2761.1647 | -0.0045975
75 |  | 4.2545 | 37.1401 | 4187 | 0.0020849 | 6.155 | 6.1571 | -2.2048 | 479.6288 | 2798.3048 | -0.0045969
76 |  | 4.2545 | 37.1355 | 4187 | 0.0020847 | 6.1571 | 6.1592 | -2.2048 | 479.6882 | 2835.4403 | -0.0045964
77 |  | 4.2545 | 37.1309 | 4187 | 0.0020844 | 6.1592 | 6.1613 | -2.2048 | 479.7476 | 2872.5712 | -0.0045958
78 |  | 4.2545 | 37.1263 | 4187 | 0.0020842 | 6.1613 | 6.1633 | -2.2048 | 479.807 | 2909.6975 | -0.0045952
79 |  | 4.2545 | 37.1217 | 4187 | 0.0020839 | 6.1633 | 6.1654 | -2.2048 | 479.8664 | 2946.8192 | -0.0045946
80 |  | 4.2545 | 37.1171 | 4187 | 0.0020837 | 6.1654 | 6.1675 | -2.2048 | 479.9258 | 2983.9364 | -0.0045941
81 |  | 4.2545 | 37.1125 | 4187 | 0.0020834 | 6.1675 | 6.1696 | -2.2048 | 479.9852 | 3021.0489 | -0.0045935
82 |  | 4.2545 | 37.1079 | 4187 | 0.0020831 | 6.1696 | 6.1717 | -2.2048 | 480.0446 | 3058.1569 | -0.0045929
83 |  | 4.2545 | 37.1034 | 4187 | 0.0020829 | 6.1717 | 6.1738 | -2.2048 | 480.104 | 3095.2602 | -0.0045924
84 |  | 4.2545 | 37.0988 | 4187 | 0.0020826 | 6.1738 | 6.1758 | -2.2048 | 480.1635 | 3132.359 | -0.0045918
85 |  | 4.2545 | 37.0942 | 4187 | 0.0020824 | 6.1758 | 6.1779 | -2.2048 | 480.2229 | 3169.4531 | -0.0045912
86 |  | 4.2545 | 37.0896 | 4187 | 0.0020821 | 6.1779 | 6.18 | -2.2048 | 480.2823 | 3206.5427 | -0.0045907
87 |  | 4.2545 | 37.085 | 4187 | 0.0020819 | 6.18 | 6.1821 | -2.2048 | 480.3418 | 3243.6277 | -0.0045901
88 |  | 4.2545 | 37.0804 | 4187 | 0.0020816 | 6.1821 | 6.1842 | -2.2048 | 480.4013 | 3280.7081 | -0.0045895
89 |  | 4.2545 | 37.0758 | 4187 | 0.0020813 | 6.1842 | 6.1863 | -2.2048 | 480.4607 | 3317.7839 | -0.004589
90 |  | 4.2545 | 37.0712 | 4187 | 0.0020811 | 6.1863 | 6.1883 | -2.2048 | 480.5202 | 3354.8551 | -0.0045884
91 |  | 4.2545 | 37.0666 | 4187 | 0.0020808 | 6.1883 | 6.1904 | -2.2048 | 480.5797 | 3391.9217 | -0.0045878
92 |  | 4.2545 | 37.062 | 4187 | 0.0020806 | 6.1904 | 6.1925 | -2.2048 | 480.6392 | 3428.9838 | -0.0045873
93 |  | 4.2545 | 37.0575 | 4187 | 0.0020803 | 6.1925 | 6.1946 | -2.2048 | 480.6987 | 3466.0412 | -0.0045867
94 |  | 4.2545 | 37.0529 | 4187 | 0.00208 | 6.1946 | 6.1967 | -2.2048 | 480.7582 | 3503.0941 | -0.0045861
95 |  | 4.2545 | 37.0483 | 4187 | 0.0020798 | 6.1967 | 6.1987 | -2.2048 | 480.8177 | 3540.1424 | -0.0045856
96 |  | 4.2545 | 37.0437 | 4187 | 0.0020795 | 6.1987 | 6.2008 | -2.2048 | 480.8772 | 3577.1861 | -0.004585
97 |  | 4.2545 | 37.0391 | 4187 | 0.0020793 | 6.2008 | 6.2029 | -2.2048 | 480.9367 | 3614.2252 | -0.0045844
98 |  | 4.2545 | 37.0345 | 4187 | 0.002079 | 6.2029 | 6.205 | -2.2048 | 480.9963 | 3651.2597 | -0.0045839
99 |  | 4.2545 | 37.0299 | 4187 | 0.0020788 | 6.205 | 6.2071 | -2.2048 | 481.0558 | 3688.2896 | -0.0045833
100 |  | 4.2545 | 37.0254 | 4187 | 0.0020785 | 6.2071 | 6.2091 | -2.2048 | 481.1154 | 3725.315 | -0.0045827
101 |  | 4.2545 | 37.0208 | 4187 | 0.0020782 | 6.2091 | 6.2112 | -2.2048 | 481.1749 | 3762.3358 | -0.0045822
102 |  | 4.2545 | 37.0162 | 4187 | 0.002078 | 6.2112 | 6.2133 | -2.2048 | 481.2345 | 3799.352 | -0.0045816
103 |  | 4.2545 | 37.0116 | 4187 | 0.0020777 | 6.2133 | 6.2154 | -2.2048 | 481.294 | 3836.3636 | -0.004581
104 |  | 4.2545 | 37.007 | 4187 | 0.0020775 | 6.2154 | 6.2174 | -2.2048 | 481.3536 | 3873.3706 | -0.0045804
105 |  | 4.2545 | 37.0024 | 4187 | 0.0020772 | 6.2174 | 6.2195 | -2.2048 | 481.4132 | 3910.3731 | -0.0045799
106 |  | 4.2545 | 36.9979 | 4187 | 0.002077 | 6.2195 | 6.2216 | -2.2048 | 481.4728 | 3947.3709 | -0.0045793
107 |  | 4.2545 | 36.9933 | 4187 | 0.0020767 | 6.2216 | 6.2237 | -2.2048 | 481.5324 | 3984.3642 | -0.0045787
108 |  | 4.2545 | 36.9887 | 4187 | 0.0020764 | 6.2237 | 6.2257 | -2.2048 | 481.592 | 4021.3529 | -0.0045782
109 |  | 4.2545 | 36.9841 | 4187 | 0.0020762 | 6.2257 | 6.2278 | -2.2048 | 481.6516 | 4058.3371 | -0.0045776
110 |  | 4.2545 | 36.9796 | 4187 | 0.0020759 | 6.2278 | 6.2299 | -2.2048 | 481.7112 | 4095.3166 | -0.004577
111 |  | 4.2545 | 36.975 | 4187 | 0.0020757 | 6.2299 | 6.232 | -2.2048 | 481.7709 | 4132.2916 | -0.0045765
112 |  | 4.2545 | 36.9704 | 4187 | 0.0020754 | 6.232 | 6.2341 | -2.2048 | 481.8305 | 4169.262 | -0.0045759
113 |  | 4.2545 | 36.9658 | 4187 | 0.0020752 | 6.2341 | 6.2361 | -2.2048 | 481.8902 | 4206.2278 | -0.0045753
114 |  | 4.2545 | 36.9613 | 4187 | 0.0020749 | 6.2361 | 6.2382 | -2.2048 | 481.9498 | 4243.1891 | -0.0045748
115 |  | 4.2545 | 36.9567 | 4187 | 0.0020746 | 6.2382 | 6.2403 | -2.2048 | 482.0095 | 4280.1457 | -0.0045742
116 |  | 4.2545 | 36.9521 | 4187 | 0.0020744 | 6.2403 | 6.2424 | -2.2048 | 482.0691 | 4317.0978 | -0.0045737
117 |  | 4.2545 | 36.9475 | 4187 | 0.0020741 | 6.2424 | 6.2444 | -2.2048 | 482.1288 | 4354.0454 | -0.0045731
118 |  | 4.2545 | 36.943 | 4187 | 0.0020739 | 6.2444 | 6.2465 | -2.2048 | 482.1885 | 4390.9883 | -0.0045725
119 |  | 4.2545 | 36.9384 | 4187 | 0.0020736 | 6.2465 | 6.2486 | -2.2048 | 482.2482 | 4427.9267 | -0.004572
120 |  | 4.2545 | 36.9338 | 4187 | 0.0020734 | 6.2486 | 6.2506 | -2.2048 | 482.3079 | 4464.8605 | -0.0045714
121 |  | 4.2545 | 36.9292 | 4187 | 0.0020731 | 6.2506 | 6.2527 | -2.2048 | 482.3676 | 4501.7898 | -0.0045708
122 |  | 4.2545 | 36.9247 | 4187 | 0.0020729 | 6.2527 | 6.2548 | -2.2048 | 482.4273 | 4538.7144 | -0.0045703
123 |  | 4.2545 | 36.9201 | 4187 | 0.0020726 | 6.2548 | 6.2569 | -2.2048 | 482.487 | 4575.6345 | -0.0045697
124 |  | 4.2545 | 36.9155 | 4187 | 0.0020723 | 6.2569 | 6.2589 | -2.2048 | 482.5467 | 4612.5501 | -0.0045691
125 |  | 4.2545 | 36.911 | 4187 | 0.0020721 | 6.2589 | 6.261 | -2.2048 | 482.6065 | 4649.461 | -0.0045686
126 |  | 4.2545 | 36.9064 | 4187 | 0.0020718 | 6.261 | 6.2631 | -2.2048 | 482.6662 | 4686.3674 | -0.004568
127 |  | 4.2545 | 36.9018 | 4187 | 0.0020716 | 6.2631 | 6.2652 | -2.2048 | 482.726 | 4723.2692 | -0.0045674
128 |  | 4.2545 | 36.8973 | 4187 | 0.0020713 | 6.2652 | 6.2672 | -2.2048 | 482.7857 | 4760.1665 | -0.0045669
129 |  | 4.2545 | 36.8927 | 4187 | 0.0020711 | 6.2672 | 6.2693 | -2.2048 | 482.8455 | 4797.0592 | -0.0045663
130 |  | 4.2545 | 36.8881 | 4187 | 0.0020708 | 6.2693 | 6.2714 | -2.2048 | 482.9052 | 4833.9473 | -0.0045657
131 |  | 4.2545 | 36.8836 | 4187 | 0.0020705 | 6.2714 | 6.2734 | -2.2048 | 482.965 | 4870.8309 | -0.0045652
132 |  | 4.2545 | 36.879 | 4187 | 0.0020703 | 6.2734 | 6.2755 | -2.2048 | 483.0248 | 4907.7098 | -0.0045646
133 |  | 4.2545 | 36.8744 | 4187 | 0.00207 | 6.2755 | 6.2776 | -2.2048 | 483.0846 | 4944.5843 | -0.004564
134 |  | 4.2545 | 36.8699 | 4187 | 0.0020698 | 6.2776 | 6.2796 | -2.2048 | 483.1444 | 4981.4541 | -0.0045635
135 |  | 4.2545 | 36.8653 | 4187 | 0.0020695 | 6.2796 | 6.2817 | -2.2048 | 483.2042 | 5018.3194 | -0.0045629
136 |  | 4.2545 | 36.8607 | 4187 | 0.0020693 | 6.2817 | 6.2838 | -2.2048 | 483.264 | 5055.1802 | -0.0045623
137 |  | 4.2545 | 36.8562 | 4187 | 0.002069 | 6.2838 | 6.2859 | -2.2048 | 483.3238 | 5092.0363 | -0.0045618
138 |  | 4.2545 | 36.8516 | 4187 | 0.0020688 | 6.2859 | 6.2879 | -2.2048 | 483.3837 | 5128.888 | -0.0045612
139 |  | 4.2545 | 36.8471 | 4187 | 0.0020685 | 6.2879 | 6.29 | -2.2048 | 483.4435 | 5165.735 | -0.0045606
140 |  | 4.2545 | 36.8425 | 4187 | 0.0020682 | 6.29 | 6.2921 | -2.2048 | 483.5034 | 5202.5775 | -0.0045601
141 |  | 4.2545 | 36.8379 | 4187 | 0.002068 | 6.2921 | 6.2941 | -2.2048 | 483.5632 | 5239.4154 | -0.0045595
142 |  | 4.2545 | 36.8334 | 4187 | 0.0020677 | 6.2941 | 6.2962 | -2.2048 | 483.6231 | 5276.2488 | -0.004559
143 |  | 4.2545 | 36.8288 | 4187 | 0.0020675 | 6.2962 | 6.2983 | -2.2048 | 483.6829 | 5313.0776 | -0.0045584
144 |  | 4.2545 | 36.8243 | 4187 | 0.0020672 | 6.2983 | 6.3003 | -2.2048 | 483.7428 | 5349.9019 | -0.0045578
145 |  | 4.2545 | 36.8197 | 4187 | 0.002067 | 6.3003 | 6.3024 | -2.2048 | 483.8027 | 5386.7216 | -0.0045573
146 |  | 4.2545 | 36.8151 | 4187 | 0.0020667 | 6.3024 | 6.3045 | -2.2048 | 483.8626 | 5423.5367 | -0.0045567
147 |  | 4.2545 | 36.8106 | 4187 | 0.0020664 | 6.3045 | 6.3065 | -2.2048 | 483.9225 | 5460.3473 | -0.0045561
148 |  | 4.2545 | 36.806 | 4187 | 0.0020662 | 6.3065 | 6.3086 | -2.2048 | 483.9824 | 5497.1533 | -0.0045556
149 |  | 4.2545 | 36.8015 | 4187 | 0.0020659 | 6.3086 | 6.3107 | -2.2048 | 484.0423 | 5533.9548 | -0.004555
150 |  | 4.2545 | 36.7969 | 4187 | 0.0020657 | 6.3107 | 6.3127 | -2.2048 | 484.1022 | 5570.7517 | -0.0045544
151 |  | 4.2545 | 36.7924 | 4187 | 0.0020654 | 6.3127 | 6.3148 | -2.2048 | 484.1621 | 5607.544 | -0.0045539
152 |  | 4.2545 | 36.7878 | 4187 | 0.0020652 | 6.3148 | 6.3169 | -2.2048 | 484.2221 | 5644.3319 | -0.0045533
153 |  | 4.2545 | 36.7833 | 4187 | 0.0020649 | 6.3169 | 6.3189 | -2.2048 | 484.282 | 5681.1151 | -0.0045528
154 |  | 4.2545 | 36.7787 | 4187 | 0.0020647 | 6.3189 | 6.321 | -2.2048 | 484.342 | 5717.8938 | -0.0045522
155 |  | 4.2545 | 36.7741 | 4187 | 0.0020644 | 6.321 | 6.3231 | -2.2048 | 484.4019 | 5754.668 | -0.0045516
156 |  | 4.2545 | 36.7696 | 4187 | 0.0020641 | 6.3231 | 6.3251 | -2.2048 | 484.4619 | 5791.4375 | -0.0045511
157 |  | 4.2545 | 36.765 | 4187 | 0.0020639 | 6.3251 | 6.3272 | -2.2048 | 484.5218 | 5828.2026 | -0.0045505
158 |  | 4.2545 | 36.7605 | 4187 | 0.0020636 | 6.3272 | 6.3292 | -2.2048 | 484.5818 | 5864.9631 | -0.0045499
159 |  | 4.2545 | 36.7559 | 4187 | 0.0020634 | 6.3292 | 6.3313 | -2.2048 | 484.6418 | 5901.719 | -0.0045494
160 |  | 4.2545 | 36.7514 | 4187 | 0.0020631 | 6.3313 | 6.3334 | -2.2048 | 484.7018 | 5938.4704 | -0.0045488
161 |  | 4.2545 | 36.7468 | 4187 | 0.0020629 | 6.3334 | 6.3354 | -2.2048 | 484.7618 | 5975.2173 | -0.0045482
162 |  | 4.2545 | 36.7423 | 4187 | 0.0020626 | 6.3354 | 6.3375 | -2.2048 | 484.8218 | 6011.9596 | -0.0045477
163 |  | 4.2545 | 36.7378 | 4187 | 0.0020624 | 6.3375 | 6.3396 | -2.2048 | 484.8818 | 6048.6973 | -0.0045471
164 |  | 4.2545 | 36.7332 | 4187 | 0.0020621 | 6.3396 | 6.3416 | -2.2048 | 484.9418 | 6085.4305 | -0.0045466
165 |  | 4.2545 | 36.7287 | 4187 | 0.0020618 | 6.3416 | 6.3437 | -2.2048 | 485.0019 | 6122.1592 | -0.004546
166 |  | 4.2545 | 36.7241 | 4187 | 0.0020616 | 6.3437 | 6.3457 | -2.2048 | 485.0619 | 6158.8833 | -0.0045454
167 |  | 4.2545 | 36.7196 | 4187 | 0.0020613 | 6.3457 | 6.3478 | -2.2048 | 485.122 | 6195.6029 | -0.0045449
168 |  | 4.2545 | 36.715 | 4187 | 0.0020611 | 6.3478 | 6.3499 | -2.2048 | 485.182 | 6232.3179 | -0.0045443
169 |  | 4.2545 | 36.7105 | 4187 | 0.0020608 | 6.3499 | 6.3519 | -2.2048 | 485.2421 | 6269.0284 | -0.0045437
170 |  | 4.2545 | 36.7059 | 4187 | 0.0020606 | 6.3519 | 6.354 | -2.2048 | 485.3021 | 6305.7343 | -0.0045432
171 |  | 4.2545 | 36.7014 | 4187 | 0.0020603 | 6.354 | 6.356 | -2.2048 | 485.3622 | 6342.4357 | -0.0045426
172 |  | 4.2545 | 36.6968 | 4187 | 0.0020601 | 6.356 | 6.3581 | -2.2048 | 485.4223 | 6379.1325 | -0.0045421
173 |  | 4.2545 | 36.6923 | 4187 | 0.0020598 | 6.3581 | 6.3602 | -2.2048 | 485.4824 | 6415.8248 | -0.0045415
174 |  | 4.2545 | 36.6878 | 4187 | 0.0020596 | 6.3602 | 6.3622 | -2.2048 | 485.5425 | 6452.5126 | -0.0045409
175 |  | 4.2545 | 36.6832 | 4187 | 0.0020593 | 6.3622 | 6.3643 | -2.2048 | 485.6026 | 6489.1958 | -0.0045404
176 |  | 4.2545 | 36.6787 | 4187 | 0.002059 | 6.3643 | 6.3663 | -2.2048 | 485.6627 | 6525.8745 | -0.0045398
177 |  | 4.2545 | 36.6741 | 4187 | 0.0020588 | 6.3663 | 6.3684 | -2.2048 | 485.7228 | 6562.5486 | -0.0045392
178 |  | 4.2545 | 36.6696 | 4187 | 0.0020585 | 6.3684 | 6.3705 | -2.2048 | 485.7829 | 6599.2183 | -0.0045387
179 |  | 4.2545 | 36.6651 | 4187 | 0.0020583 | 6.3705 | 6.3725 | -2.2048 | 485.8431 | 6635.8833 | -0.0045381
180 |  | 4.2545 | 36.6605 | 4187 | 0.002058 | 6.3725 | 6.3746 | -2.2048 | 485.9032 | 6672.5438 | -0.0045376
181 |  | 4.2545 | 36.656 | 4187 | 0.0020578 | 6.3746 | 6.3766 | -2.2048 | 485.9634 | 6709.1998 | -0.004537
182 |  | 4.2545 | 36.6515 | 4187 | 0.0020575 | 6.3766 | 6.3787 | -2.2048 | 486.0235 | 6745.8513 | -0.0045364
183 |  | 4.2545 | 36.6469 | 4187 | 0.0020573 | 6.3787 | 6.3808 | -2.2048 | 486.0837 | 6782.4982 | -0.0045359
184 |  | 4.2545 | 36.6424 | 4187 | 0.002057 | 6.3808 | 6.3828 | -2.2048 | 486.1439 | 6819.1406 | -0.0045353
185 |  | 4.2545 | 36.6378 | 4187 | 0.0020567 | 6.3828 | 6.3849 | -2.2048 | 486.204 | 6855.7784 | -0.0045348
186 |  | 4.2545 | 36.6333 | 4187 | 0.0020565 | 6.3849 | 6.3869 | -2.2048 | 486.2642 | 6892.4117 | -0.0045342
187 |  | 4.2545 | 36.6288 | 4187 | 0.0020562 | 6.3869 | 6.389 | -2.2048 | 486.3244 | 6929.0405 | -0.0045336
188 |  | 4.2545 | 36.6242 | 4187 | 0.002056 | 6.389 | 6.391 | -2.2048 | 486.3846 | 6965.6647 | -0.0045331
189 |  | 4.2545 | 36.6197 | 4187 | 0.0020557 | 6.391 | 6.3931 | -2.2048 | 486.4448 | 7002.2845 | -0.0045325
190 |  | 4.2545 | 36.6152 | 4187 | 0.0020555 | 6.3931 | 6.3951 | -2.2048 | 486.505 | 7038.8996 | -0.0045319
191 |  | 4.2545 | 36.6106 | 4187 | 0.0020552 | 6.3951 | 6.3972 | -2.2048 | 486.5653 | 7075.5103 | -0.0045314
192 |  | 4.2545 | 36.6061 | 4187 | 0.002055 | 6.3972 | 6.3993 | -2.2048 | 486.6255 | 7112.1164 | -0.0045308
193 |  | 4.2545 | 36.6016 | 4187 | 0.0020547 | 6.3993 | 6.4013 | -2.2048 | 486.6857 | 7148.718 | -0.0045303
194 |  | 4.2545 | 36.5971 | 4187 | 0.0020545 | 6.4013 | 6.4034 | -2.2048 | 486.746 | 7185.315 | -0.0045297
195 |  | 4.2545 | 36.5925 | 4187 | 0.0020542 | 6.4034 | 6.4054 | -2.2048 | 486.8062 | 7221.9075 | -0.0045291
196 |  | 4.2545 | 36.588 | 4187 | 0.002054 | 6.4054 | 6.4075 | -2.2048 | 486.8665 | 7258.4955 | -0.0045286
197 |  | 4.2545 | 36.5835 | 4187 | 0.0020537 | 6.4075 | 6.4095 | -2.2048 | 486.9268 | 7295.079 | -0.004528
198 |  | 4.2545 | 36.5789 | 4187 | 0.0020534 | 6.4095 | 6.4116 | -2.2048 | 486.987 | 7331.6579 | -0.0045275
199 |  | 4.2545 | 36.5744 | 4187 | 0.0020532 | 6.4116 | 6.4136 | -2.2048 | 487.0473 | 7368.2323 | -0.0045269
200 |  | 4.2545 | 36.5699 | 4187 | 0.0020529 | 6.4136 | 6.4157 | -2.2048 | 487.1076 | 7404.8022 | -0.0045263
201 |  | 4.2545 | 36.5654 | 4187 | 0.0020527 | 6.4157 | 6.4177 | -2.2048 | 487.1679 | 7441.3676 | -0.0045258
202 |  | 4.2545 | 36.5608 | 4187 | 0.0020524 | 6.4177 | 6.4198 | -2.2048 | 487.2282 | 7477.9284 | -0.0045252
203 |  | 4.2545 | 36.5563 | 4187 | 0.0020522 | 6.4198 | 6.4218 | -2.2048 | 487.2885 | 7514.4847 | -0.0045247
204 |  | 4.2545 | 36.5518 | 4187 | 0.0020519 | 6.4218 | 6.4239 | -2.2048 | 487.3488 | 7551.0365 | -0.0045241
205 |  | 4.2545 | 36.5473 | 4187 | 0.0020517 | 6.4239 | 6.4259 | -2.2048 | 487.4092 | 7587.5838 | -0.0045235
206 |  | 4.2545 | 36.5427 | 4187 | 0.0020514 | 6.4259 | 6.428 | -2.2048 | 487.4695 | 7624.1265 | -0.004523
207 |  | 4.2545 | 36.5382 | 4187 | 0.0020512 | 6.428 | 6.43 | -2.2048 | 487.5299 | 7660.6647 | -0.0045224
208 |  | 4.2545 | 36.5337 | 4187 | 0.0020509 | 6.43 | 6.4321 | -2.2048 | 487.5902 | 7697.1984 | -0.0045219
209 |  | 4.2545 | 36.5292 | 4187 | 0.0020506 | 6.4321 | 6.4342 | -2.2048 | 487.6506 | 7733.7275 | -0.0045213
210 |  | 4.2545 | 36.5246 | 4187 | 0.0020504 | 6.4342 | 6.4362 | -2.2048 | 487.7109 | 7770.2522 | -0.0045207
211 |  | 4.2545 | 36.5201 | 4187 | 0.0020501 | 6.4362 | 6.4383 | -2.2048 | 487.7713 | 7806.7723 | -0.0045202
212 |  | 4.2545 | 36.5156 | 4187 | 0.0020499 | 6.4383 | 6.4403 | -2.2048 | 487.8317 | 7843.2879 | -0.0045196
213 |  | 4.2545 | 36.5111 | 4187 | 0.0020496 | 6.4403 | 6.4424 | -2.2048 | 487.8921 | 7879.799 | -0.0045191
214 |  | 4.2545 | 36.5066 | 4187 | 0.0020494 | 6.4424 | 6.4444 | -2.2048 | 487.9525 | 7916.3056 | -0.0045185
215 |  | 4.2545 | 36.502 | 4187 | 0.0020491 | 6.4444 | 6.4464 | -2.2048 | 488.0129 | 7952.8076 | -0.0045179
216 |  | 4.2545 | 36.4975 | 4187 | 0.0020489 | 6.4464 | 6.4485 | -2.2048 | 488.0733 | 7989.3051 | -0.0045174
217 |  | 4.2545 | 36.493 | 4187 | 0.0020486 | 6.4485 | 6.4505 | -2.2048 | 488.1337 | 8025.7981 | -0.0045168
218 |  | 4.2545 | 36.4885 | 4187 | 0.0020484 | 6.4505 | 6.4526 | -2.2048 | 488.1941 | 8062.2866 | -0.0045163
219 |  | 4.2545 | 36.484 | 4187 | 0.0020481 | 6.4526 | 6.4546 | -2.2048 | 488.2545 | 8098.7706 | -0.0045157
220 |  | 4.2545 | 36.4795 | 4187 | 0.0020479 | 6.4546 | 6.4567 | -2.2048 | 488.315 | 8135.2501 | -0.0045152
221 |  | 4.2545 | 36.4749 | 4187 | 0.0020476 | 6.4567 | 6.4587 | -2.2048 | 488.3754 | 8171.725 | -0.0045146
222 |  | 4.2545 | 36.4704 | 4187 | 0.0020474 | 6.4587 | 6.4608 | -2.2048 | 488.4359 | 8208.1955 | -0.004514
223 |  | 4.2545 | 36.4659 | 4187 | 0.0020471 | 6.4608 | 6.4628 | -2.2048 | 488.4964 | 8244.6614 | -0.0045135
224 |  | 4.2545 | 36.4614 | 4187 | 0.0020468 | 6.4628 | 6.4649 | -2.2048 | 488.5568 | 8281.1228 | -0.0045129
225 |  | 4.2545 | 36.4569 | 4187 | 0.0020466 | 6.4649 | 6.4669 | -2.2048 | 488.6173 | 8317.5797 | -0.0045124
226 |  | 4.2545 | 36.4524 | 4187 | 0.0020463 | 6.4669 | 6.469 | -2.2048 | 488.6778 | 8354.0321 | -0.0045118
227 |  | 4.2545 | 36.4479 | 4187 | 0.0020461 | 6.469 | 6.471 | -2.2048 | 488.7383 | 8390.4799 | -0.0045112
228 |  | 4.2545 | 36.4434 | 4187 | 0.0020458 | 6.471 | 6.4731 | -2.2048 | 488.7988 | 8426.9233 | -0.0045107
229 |  | 4.2545 | 36.4388 | 4187 | 0.0020456 | 6.4731 | 6.4751 | -2.2048 | 488.8593 | 8463.3621 | -0.0045101
230 |  | 4.2545 | 36.4343 | 4187 | 0.0020453 | 6.4751 | 6.4772 | -2.2048 | 488.9198 | 8499.7965 | -0.0045096
231 |  | 4.2545 | 36.4298 | 4187 | 0.0020451 | 6.4772 | 6.4792 | -2.2048 | 488.9803 | 8536.2263 | -0.004509
232 |  | 4.2545 | 36.4253 | 4187 | 0.0020448 | 6.4792 | 6.4812 | -2.2048 | 489.0408 | 8572.6516 | -0.0045084
233 |  | 4.2545 | 36.4208 | 4187 | 0.0020446 | 6.4812 | 6.4833 | -2.2048 | 489.1014 | 8609.0724 | -0.0045079
234 |  | 4.2545 | 36.4163 | 4187 | 0.0020443 | 6.4833 | 6.4853 | -2.2048 | 489.1619 | 8645.4887 | -0.0045073
235 |  | 4.2545 | 36.4118 | 4187 | 0.0020441 | 6.4853 | 6.4874 | -2.2048 | 489.2225 | 8681.9005 | -0.0045068
236 |  | 4.2545 | 36.4073 | 4187 | 0.0020438 | 6.4874 | 6.4894 | -2.2048 | 489.283 | 8718.3078 | -0.0045062

## 110
|  |  | buis | verlies W/M | L /°C/sec
diam | wandikte |  | inhoud l/m |  | W/M
110 | 10 | 3.1416 | 6.3617 | 41.5272 | 4187
[8 empty] | J/sec/mtr | aantal mtr. | verlies
|  | buis | verlies W/M | L /°C/sec | verlies temp | begintemp | eindtemp | verlies | bij 1°C | totaal J/sec
|  | inhoud L |  | W/M | °C per M | °C | °C | per m°C | daling | aantal mtr
1 | 110 | 6.3617 | 41.5272 | 4187 | 0.001559 | 6 | 6.0016 | -2.4428 | 641.4243 | 41.5272 | -0.0038084
2 |  | 6.3617 | 41.5234 | 4187 | 0.0015589 | 6.0016 | 6.0031 | -2.4428 | 641.4831 | 83.0506 | -0.003808
3 |  | 6.3617 | 41.5196 | 4187 | 0.0015587 | 6.0031 | 6.0047 | -2.4428 | 641.542 | 124.5701 | -0.0038077
4 |  | 6.3617 | 41.5158 | 4187 | 0.0015586 | 6.0047 | 6.0062 | -2.4428 | 641.6008 | 166.0859 | -0.0038073
5 |  | 6.3617 | 41.512 | 4187 | 0.0015585 | 6.0062 | 6.0078 | -2.4428 | 641.6596 | 207.5978 | -0.003807
6 |  | 6.3617 | 41.5081 | 4187 | 0.0015583 | 6.0078 | 6.0094 | -2.4428 | 641.7185 | 249.106 | -0.0038066
7 |  | 6.3617 | 41.5043 | 4187 | 0.0015582 | 6.0094 | 6.0109 | -2.4428 | 641.7773 | 290.6103 | -0.0038063
8 |  | 6.3617 | 41.5005 | 4187 | 0.001558 | 6.0109 | 6.0125 | -2.4428 | 641.8362 | 332.1108 | -0.0038059
9 |  | 6.3617 | 41.4967 | 4187 | 0.0015579 | 6.0125 | 6.014 | -2.4428 | 641.8951 | 373.6076 | -0.0038056
10 |  | 6.3617 | 41.4929 | 4187 | 0.0015577 | 6.014 | 6.0156 | -2.4428 | 641.9539 | 415.1005 | -0.0038052
11 |  | 6.3617 | 41.4891 | 4187 | 0.0015576 | 6.0156 | 6.0171 | -2.4428 | 642.0128 | 456.5896 | -0.0038049
12 |  | 6.3617 | 41.4853 | 4187 | 0.0015575 | 6.0171 | 6.0187 | -2.4428 | 642.0717 | 498.0749 | -0.0038045
13 |  | 6.3617 | 41.4815 | 4187 | 0.0015573 | 6.0187 | 6.0203 | -2.4428 | 642.1306 | 539.5564 | -0.0038042
14 |  | 6.3617 | 41.4777 | 4187 | 0.0015572 | 6.0203 | 6.0218 | -2.4428 | 642.1895 | 581.0341 | -0.0038038
15 |  | 6.3617 | 41.4739 | 4187 | 0.001557 | 6.0218 | 6.0234 | -2.4428 | 642.2484 | 622.508 | -0.0038035
16 |  | 6.3617 | 41.4701 | 4187 | 0.0015569 | 6.0234 | 6.0249 | -2.4428 | 642.3073 | 663.9781 | -0.0038031
17 |  | 6.3617 | 41.4663 | 4187 | 0.0015567 | 6.0249 | 6.0265 | -2.4428 | 642.3662 | 705.4444 | -0.0038028
18 |  | 6.3617 | 41.4625 | 4187 | 0.0015566 | 6.0265 | 6.028 | -2.4428 | 642.4251 | 746.9069 | -0.0038024
19 |  | 6.3617 | 41.4587 | 4187 | 0.0015565 | 6.028 | 6.0296 | -2.4428 | 642.484 | 788.3656 | -0.0038021
20 |  | 6.3617 | 41.4549 | 4187 | 0.0015563 | 6.0296 | 6.0312 | -2.4428 | 642.543 | 829.8204 | -0.0038017
21 |  | 6.3617 | 41.4511 | 4187 | 0.0015562 | 6.0312 | 6.0327 | -2.4428 | 642.6019 | 871.2715 | -0.0038014
22 |  | 6.3617 | 41.4473 | 4187 | 0.001556 | 6.0327 | 6.0343 | -2.4428 | 642.6608 | 912.7188 | -0.003801
23 |  | 6.3617 | 41.4435 | 4187 | 0.0015559 | 6.0343 | 6.0358 | -2.4428 | 642.7198 | 954.1623 | -0.0038007
24 |  | 6.3617 | 41.4397 | 4187 | 0.0015557 | 6.0358 | 6.0374 | -2.4428 | 642.7787 | 995.602 | -0.0038003
25 |  | 6.3617 | 41.4359 | 4187 | 0.0015556 | 6.0374 | 6.0389 | -2.4428 | 642.8377 | 1037.0378 | -0.0038
26 |  | 6.3617 | 41.4321 | 4187 | 0.0015555 | 6.0389 | 6.0405 | -2.4428 | 642.8966 | 1078.4699 | -0.0037996
27 |  | 6.3617 | 41.4283 | 4187 | 0.0015553 | 6.0405 | 6.042 | -2.4428 | 642.9556 | 1119.8982 | -0.0037993
28 |  | 6.3617 | 41.4245 | 4187 | 0.0015552 | 6.042 | 6.0436 | -2.4428 | 643.0146 | 1161.3227 | -0.0037989
29 |  | 6.3617 | 41.4207 | 4187 | 0.001555 | 6.0436 | 6.0452 | -2.4428 | 643.0735 | 1202.7433 | -0.0037986
30 |  | 6.3617 | 41.4169 | 4187 | 0.0015549 | 6.0452 | 6.0467 | -2.4428 | 643.1325 | 1244.1602 | -0.0037982
31 |  | 6.3617 | 41.4131 | 4187 | 0.0015547 | 6.0467 | 6.0483 | -2.4428 | 643.1915 | 1285.5733 | -0.0037979
32 |  | 6.3617 | 41.4093 | 4187 | 0.0015546 | 6.0483 | 6.0498 | -2.4428 | 643.2505 | 1326.9826 | -0.0037975
33 |  | 6.3617 | 41.4055 | 4187 | 0.0015545 | 6.0498 | 6.0514 | -2.4428 | 643.3095 | 1368.3881 | -0.0037972
34 |  | 6.3617 | 41.4017 | 4187 | 0.0015543 | 6.0514 | 6.0529 | -2.4428 | 643.3685 | 1409.7898 | -0.0037969
35 |  | 6.3617 | 41.3979 | 4187 | 0.0015542 | 6.0529 | 6.0545 | -2.4428 | 643.4275 | 1451.1877 | -0.0037965
36 |  | 6.3617 | 41.3941 | 4187 | 0.001554 | 6.0545 | 6.056 | -2.4428 | 643.4865 | 1492.5818 | -0.0037962
37 |  | 6.3617 | 41.3903 | 4187 | 0.0015539 | 6.056 | 6.0576 | -2.4428 | 643.5455 | 1533.9721 | -0.0037958
38 |  | 6.3617 | 41.3865 | 4187 | 0.0015537 | 6.0576 | 6.0591 | -2.4428 | 643.6046 | 1575.3586 | -0.0037955
39 |  | 6.3617 | 41.3827 | 4187 | 0.0015536 | 6.0591 | 6.0607 | -2.4428 | 643.6636 | 1616.7413 | -0.0037951
40 |  | 6.3617 | 41.3789 | 4187 | 0.0015535 | 6.0607 | 6.0622 | -2.4428 | 643.7226 | 1658.1202 | -0.0037948
41 |  | 6.3617 | 41.3751 | 4187 | 0.0015533 | 6.0622 | 6.0638 | -2.4428 | 643.7817 | 1699.4953 | -0.0037944
42 |  | 6.3617 | 41.3713 | 4187 | 0.0015532 | 6.0638 | 6.0654 | -2.4428 | 643.8407 | 1740.8666 | -0.0037941
43 |  | 6.3617 | 41.3675 | 4187 | 0.001553 | 6.0654 | 6.0669 | -2.4428 | 643.8998 | 1782.2342 | -0.0037937
44 |  | 6.3617 | 41.3637 | 4187 | 0.0015529 | 6.0669 | 6.0685 | -2.4428 | 643.9588 | 1823.5979 | -0.0037934
45 |  | 6.3617 | 41.3599 | 4187 | 0.0015528 | 6.0685 | 6.07 | -2.4428 | 644.0179 | 1864.9578 | -0.003793
46 |  | 6.3617 | 41.3562 | 4187 | 0.0015526 | 6.07 | 6.0716 | -2.4428 | 644.0769 | 1906.314 | -0.0037927
47 |  | 6.3617 | 41.3524 | 4187 | 0.0015525 | 6.0716 | 6.0731 | -2.4428 | 644.136 | 1947.6664 | -0.0037923
48 |  | 6.3617 | 41.3486 | 4187 | 0.0015523 | 6.0731 | 6.0747 | -2.4428 | 644.1951 | 1989.0149 | -0.003792
49 |  | 6.3617 | 41.3448 | 4187 | 0.0015522 | 6.0747 | 6.0762 | -2.4428 | 644.2542 | 2030.3597 | -0.0037916
50 |  | 6.3617 | 41.341 | 4187 | 0.001552 | 6.0762 | 6.0778 | -2.4428 | 644.3133 | 2071.7007 | -0.0037913
51 |  | 6.3617 | 41.3372 | 4187 | 0.0015519 | 6.0778 | 6.0793 | -2.4428 | 644.3724 | 2113.0379 | -0.0037909
52 |  | 6.3617 | 41.3334 | 4187 | 0.0015518 | 6.0793 | 6.0809 | -2.4428 | 644.4315 | 2154.3713 | -0.0037906
53 |  | 6.3617 | 41.3296 | 4187 | 0.0015516 | 6.0809 | 6.0824 | -2.4428 | 644.4906 | 2195.7009 | -0.0037902
54 |  | 6.3617 | 41.3258 | 4187 | 0.0015515 | 6.0824 | 6.084 | -2.4428 | 644.5497 | 2237.0267 | -0.0037899
55 |  | 6.3617 | 41.322 | 4187 | 0.0015513 | 6.084 | 6.0855 | -2.4428 | 644.6088 | 2278.3487 | -0.0037895
56 |  | 6.3617 | 41.3182 | 4187 | 0.0015512 | 6.0855 | 6.0871 | -2.4428 | 644.6679 | 2319.667 | -0.0037892
57 |  | 6.3617 | 41.3145 | 4187 | 0.001551 | 6.0871 | 6.0886 | -2.4428 | 644.727 | 2360.9814 | -0.0037889
58 |  | 6.3617 | 41.3107 | 4187 | 0.0015509 | 6.0886 | 6.0902 | -2.4428 | 644.7862 | 2402.2921 | -0.0037885
59 |  | 6.3617 | 41.3069 | 4187 | 0.0015508 | 6.0902 | 6.0917 | -2.4428 | 644.8453 | 2443.5989 | -0.0037882
60 |  | 6.3617 | 41.3031 | 4187 | 0.0015506 | 6.0917 | 6.0933 | -2.4428 | 644.9044 | 2484.902 | -0.0037878
61 |  | 6.3617 | 41.2993 | 4187 | 0.0015505 | 6.0933 | 6.0948 | -2.4428 | 644.9636 | 2526.2013 | -0.0037875
62 |  | 6.3617 | 41.2955 | 4187 | 0.0015503 | 6.0948 | 6.0964 | -2.4428 | 645.0227 | 2567.4968 | -0.0037871
63 |  | 6.3617 | 41.2917 | 4187 | 0.0015502 | 6.0964 | 6.0979 | -2.4428 | 645.0819 | 2608.7886 | -0.0037868
64 |  | 6.3617 | 41.2879 | 4187 | 0.00155 | 6.0979 | 6.0995 | -2.4428 | 645.1411 | 2650.0765 | -0.0037864
65 |  | 6.3617 | 41.2841 | 4187 | 0.0015499 | 6.0995 | 6.101 | -2.4428 | 645.2002 | 2691.3606 | -0.0037861
66 |  | 6.3617 | 41.2804 | 4187 | 0.0015498 | 6.101 | 6.1026 | -2.4428 | 645.2594 | 2732.641 | -0.0037857
67 |  | 6.3617 | 41.2766 | 4187 | 0.0015496 | 6.1026 | 6.1041 | -2.4428 | 645.3186 | 2773.9176 | -0.0037854
68 |  | 6.3617 | 41.2728 | 4187 | 0.0015495 | 6.1041 | 6.1057 | -2.4428 | 645.3778 | 2815.1904 | -0.003785
69 |  | 6.3617 | 41.269 | 4187 | 0.0015493 | 6.1057 | 6.1072 | -2.4428 | 645.437 | 2856.4594 | -0.0037847
70 |  | 6.3617 | 41.2652 | 4187 | 0.0015492 | 6.1072 | 6.1088 | -2.4428 | 645.4962 | 2897.7246 | -0.0037843
71 |  | 6.3617 | 41.2614 | 4187 | 0.0015491 | 6.1088 | 6.1103 | -2.4428 | 645.5554 | 2938.986 | -0.003784
72 |  | 6.3617 | 41.2577 | 4187 | 0.0015489 | 6.1103 | 6.1119 | -2.4428 | 645.6146 | 2980.2437 | -0.0037836
73 |  | 6.3617 | 41.2539 | 4187 | 0.0015488 | 6.1119 | 6.1134 | -2.4428 | 645.6738 | 3021.4976 | -0.0037833
74 |  | 6.3617 | 41.2501 | 4187 | 0.0015486 | 6.1134 | 6.115 | -2.4428 | 645.733 | 3062.7477 | -0.0037829
75 |  | 6.3617 | 41.2463 | 4187 | 0.0015485 | 6.115 | 6.1165 | -2.4428 | 645.7922 | 3103.994 | -0.0037826
76 |  | 6.3617 | 41.2425 | 4187 | 0.0015483 | 6.1165 | 6.1181 | -2.4428 | 645.8515 | 3145.2365 | -0.0037823
77 |  | 6.3617 | 41.2387 | 4187 | 0.0015482 | 6.1181 | 6.1196 | -2.4428 | 645.9107 | 3186.4752 | -0.0037819
78 |  | 6.3617 | 41.235 | 4187 | 0.0015481 | 6.1196 | 6.1212 | -2.4428 | 645.9699 | 3227.7102 | -0.0037816
79 |  | 6.3617 | 41.2312 | 4187 | 0.0015479 | 6.1212 | 6.1227 | -2.4428 | 646.0292 | 3268.9414 | -0.0037812
80 |  | 6.3617 | 41.2274 | 4187 | 0.0015478 | 6.1227 | 6.1243 | -2.4428 | 646.0884 | 3310.1687 | -0.0037809
81 |  | 6.3617 | 41.2236 | 4187 | 0.0015476 | 6.1243 | 6.1258 | -2.4428 | 646.1477 | 3351.3924 | -0.0037805
82 |  | 6.3617 | 41.2198 | 4187 | 0.0015475 | 6.1258 | 6.1274 | -2.4428 | 646.207 | 3392.6122 | -0.0037802
83 |  | 6.3617 | 41.2161 | 4187 | 0.0015473 | 6.1274 | 6.1289 | -2.4428 | 646.2662 | 3433.8282 | -0.0037798
84 |  | 6.3617 | 41.2123 | 4187 | 0.0015472 | 6.1289 | 6.1305 | -2.4428 | 646.3255 | 3475.0405 | -0.0037795
85 |  | 6.3617 | 41.2085 | 4187 | 0.0015471 | 6.1305 | 6.132 | -2.4428 | 646.3848 | 3516.249 | -0.0037791
86 |  | 6.3617 | 41.2047 | 4187 | 0.0015469 | 6.132 | 6.1336 | -2.4428 | 646.4441 | 3557.4537 | -0.0037788
87 |  | 6.3617 | 41.2009 | 4187 | 0.0015468 | 6.1336 | 6.1351 | -2.4428 | 646.5034 | 3598.6547 | -0.0037784
88 |  | 6.3617 | 41.1972 | 4187 | 0.0015466 | 6.1351 | 6.1366 | -2.4428 | 646.5626 | 3639.8518 | -0.0037781
89 |  | 6.3617 | 41.1934 | 4187 | 0.0015465 | 6.1366 | 6.1382 | -2.4428 | 646.6219 | 3681.0452 | -0.0037777
90 |  | 6.3617 | 41.1896 | 4187 | 0.0015464 | 6.1382 | 6.1397 | -2.4428 | 646.6813 | 3722.2348 | -0.0037774
91 |  | 6.3617 | 41.1858 | 4187 | 0.0015462 | 6.1397 | 6.1413 | -2.4428 | 646.7406 | 3763.4206 | -0.0037771
92 |  | 6.3617 | 41.182 | 4187 | 0.0015461 | 6.1413 | 6.1428 | -2.4428 | 646.7999 | 3804.6027 | -0.0037767
93 |  | 6.3617 | 41.1783 | 4187 | 0.0015459 | 6.1428 | 6.1444 | -2.4428 | 646.8592 | 3845.7809 | -0.0037764
94 |  | 6.3617 | 41.1745 | 4187 | 0.0015458 | 6.1444 | 6.1459 | -2.4428 | 646.9185 | 3886.9554 | -0.003776
95 |  | 6.3617 | 41.1707 | 4187 | 0.0015456 | 6.1459 | 6.1475 | -2.4428 | 646.9779 | 3928.1262 | -0.0037757
96 |  | 6.3617 | 41.1669 | 4187 | 0.0015455 | 6.1475 | 6.149 | -2.4428 | 647.0372 | 3969.2931 | -0.0037753
97 |  | 6.3617 | 41.1632 | 4187 | 0.0015454 | 6.149 | 6.1506 | -2.4428 | 647.0965 | 4010.4563 | -0.003775
98 |  | 6.3617 | 41.1594 | 4187 | 0.0015452 | 6.1506 | 6.1521 | -2.4428 | 647.1559 | 4051.6157 | -0.0037746
99 |  | 6.3617 | 41.1556 | 4187 | 0.0015451 | 6.1521 | 6.1537 | -2.4428 | 647.2152 | 4092.7713 | -0.0037743
100 |  | 6.3617 | 41.1518 | 4187 | 0.0015449 | 6.1537 | 6.1552 | -2.4428 | 647.2746 | 4133.9231 | -0.0037739
101 |  | 6.3617 | 41.1481 | 4187 | 0.0015448 | 6.1552 | 6.1567 | -2.4428 | 647.334 | 4175.0712 | -0.0037736
102 |  | 6.3617 | 41.1443 | 4187 | 0.0015447 | 6.1567 | 6.1583 | -2.4428 | 647.3933 | 4216.2155 | -0.0037732
103 |  | 6.3617 | 41.1405 | 4187 | 0.0015445 | 6.1583 | 6.1598 | -2.4428 | 647.4527 | 4257.356 | -0.0037729
104 |  | 6.3617 | 41.1367 | 4187 | 0.0015444 | 6.1598 | 6.1614 | -2.4428 | 647.5121 | 4298.4928 | -0.0037726
105 |  | 6.3617 | 41.133 | 4187 | 0.0015442 | 6.1614 | 6.1629 | -2.4428 | 647.5715 | 4339.6257 | -0.0037722
106 |  | 6.3617 | 41.1292 | 4187 | 0.0015441 | 6.1629 | 6.1645 | -2.4428 | 647.6309 | 4380.7549 | -0.0037719
107 |  | 6.3617 | 41.1254 | 4187 | 0.0015439 | 6.1645 | 6.166 | -2.4428 | 647.6903 | 4421.8804 | -0.0037715
108 |  | 6.3617 | 41.1217 | 4187 | 0.0015438 | 6.166 | 6.1676 | -2.4428 | 647.7497 | 4463.002 | -0.0037712
109 |  | 6.3617 | 41.1179 | 4187 | 0.0015437 | 6.1676 | 6.1691 | -2.4428 | 647.8091 | 4504.1199 | -0.0037708
110 |  | 6.3617 | 41.1141 | 4187 | 0.0015435 | 6.1691 | 6.1706 | -2.4428 | 647.8685 | 4545.234 | -0.0037705
111 |  | 6.3617 | 41.1103 | 4187 | 0.0015434 | 6.1706 | 6.1722 | -2.4428 | 647.9279 | 4586.3444 | -0.0037701
112 |  | 6.3617 | 41.1066 | 4187 | 0.0015432 | 6.1722 | 6.1737 | -2.4428 | 647.9874 | 4627.451 | -0.0037698
113 |  | 6.3617 | 41.1028 | 4187 | 0.0015431 | 6.1737 | 6.1753 | -2.4428 | 648.0468 | 4668.5538 | -0.0037694
114 |  | 6.3617 | 41.099 | 4187 | 0.001543 | 6.1753 | 6.1768 | -2.4428 | 648.1062 | 4709.6528 | -0.0037691
115 |  | 6.3617 | 41.0953 | 4187 | 0.0015428 | 6.1768 | 6.1784 | -2.4428 | 648.1657 | 4750.7481 | -0.0037688
116 |  | 6.3617 | 41.0915 | 4187 | 0.0015427 | 6.1784 | 6.1799 | -2.4428 | 648.2251 | 4791.8396 | -0.0037684
117 |  | 6.3617 | 41.0877 | 4187 | 0.0015425 | 6.1799 | 6.1814 | -2.4428 | 648.2846 | 4832.9273 | -0.0037681
118 |  | 6.3617 | 41.084 | 4187 | 0.0015424 | 6.1814 | 6.183 | -2.4428 | 648.344 | 4874.0113 | -0.0037677
119 |  | 6.3617 | 41.0802 | 4187 | 0.0015422 | 6.183 | 6.1845 | -2.4428 | 648.4035 | 4915.0915 | -0.0037674
120 |  | 6.3617 | 41.0764 | 4187 | 0.0015421 | 6.1845 | 6.1861 | -2.4428 | 648.463 | 4956.1679 | -0.003767
121 |  | 6.3617 | 41.0727 | 4187 | 0.001542 | 6.1861 | 6.1876 | -2.4428 | 648.5224 | 4997.2406 | -0.0037667
122 |  | 6.3617 | 41.0689 | 4187 | 0.0015418 | 6.1876 | 6.1892 | -2.4428 | 648.5819 | 5038.3095 | -0.0037663
123 |  | 6.3617 | 41.0651 | 4187 | 0.0015417 | 6.1892 | 6.1907 | -2.4428 | 648.6414 | 5079.3746 | -0.003766
124 |  | 6.3617 | 41.0614 | 4187 | 0.0015415 | 6.1907 | 6.1922 | -2.4428 | 648.7009 | 5120.436 | -0.0037656
125 |  | 6.3617 | 41.0576 | 4187 | 0.0015414 | 6.1922 | 6.1938 | -2.4428 | 648.7604 | 5161.4936 | -0.0037653
126 |  | 6.3617 | 41.0538 | 4187 | 0.0015413 | 6.1938 | 6.1953 | -2.4428 | 648.8199 | 5202.5474 | -0.003765
127 |  | 6.3617 | 41.0501 | 4187 | 0.0015411 | 6.1953 | 6.1969 | -2.4428 | 648.8794 | 5243.5975 | -0.0037646
128 |  | 6.3617 | 41.0463 | 4187 | 0.001541 | 6.1969 | 6.1984 | -2.4428 | 648.9389 | 5284.6438 | -0.0037643
129 |  | 6.3617 | 41.0425 | 4187 | 0.0015408 | 6.1984 | 6.1999 | -2.4428 | 648.9984 | 5325.6863 | -0.0037639
130 |  | 6.3617 | 41.0388 | 4187 | 0.0015407 | 6.1999 | 6.2015 | -2.4428 | 649.0579 | 5366.7251 | -0.0037636
131 |  | 6.3617 | 41.035 | 4187 | 0.0015406 | 6.2015 | 6.203 | -2.4428 | 649.1175 | 5407.7601 | -0.0037632
132 |  | 6.3617 | 41.0312 | 4187 | 0.0015404 | 6.203 | 6.2046 | -2.4428 | 649.177 | 5448.7913 | -0.0037629
133 |  | 6.3617 | 41.0275 | 4187 | 0.0015403 | 6.2046 | 6.2061 | -2.4428 | 649.2365 | 5489.8188 | -0.0037625
134 |  | 6.3617 | 41.0237 | 4187 | 0.0015401 | 6.2061 | 6.2076 | -2.4428 | 649.2961 | 5530.8426 | -0.0037622
135 |  | 6.3617 | 41.02 | 4187 | 0.00154 | 6.2076 | 6.2092 | -2.4428 | 649.3556 | 5571.8625 | -0.0037618
136 |  | 6.3617 | 41.0162 | 4187 | 0.0015398 | 6.2092 | 6.2107 | -2.4428 | 649.4152 | 5612.8787 | -0.0037615
137 |  | 6.3617 | 41.0124 | 4187 | 0.0015397 | 6.2107 | 6.2123 | -2.4428 | 649.4748 | 5653.8912 | -0.0037612
138 |  | 6.3617 | 41.0087 | 4187 | 0.0015396 | 6.2123 | 6.2138 | -2.4428 | 649.5343 | 5694.8998 | -0.0037608
139 |  | 6.3617 | 41.0049 | 4187 | 0.0015394 | 6.2138 | 6.2153 | -2.4428 | 649.5939 | 5735.9047 | -0.0037605
140 |  | 6.3617 | 41.0012 | 4187 | 0.0015393 | 6.2153 | 6.2169 | -2.4428 | 649.6535 | 5776.9059 | -0.0037601
141 |  | 6.3617 | 40.9974 | 4187 | 0.0015391 | 6.2169 | 6.2184 | -2.4428 | 649.7131 | 5817.9033 | -0.0037598
142 |  | 6.3617 | 40.9936 | 4187 | 0.001539 | 6.2184 | 6.22 | -2.4428 | 649.7727 | 5858.8969 | -0.0037594
143 |  | 6.3617 | 40.9899 | 4187 | 0.0015389 | 6.22 | 6.2215 | -2.4428 | 649.8322 | 5899.8868 | -0.0037591
144 |  | 6.3617 | 40.9861 | 4187 | 0.0015387 | 6.2215 | 6.223 | -2.4428 | 649.8918 | 5940.8729 | -0.0037587
145 |  | 6.3617 | 40.9824 | 4187 | 0.0015386 | 6.223 | 6.2246 | -2.4428 | 649.9515 | 5981.8553 | -0.0037584
146 |  | 6.3617 | 40.9786 | 4187 | 0.0015384 | 6.2246 | 6.2261 | -2.4428 | 650.0111 | 6022.8339 | -0.0037581
147 |  | 6.3617 | 40.9748 | 4187 | 0.0015383 | 6.2261 | 6.2276 | -2.4428 | 650.0707 | 6063.8087 | -0.0037577
148 |  | 6.3617 | 40.9711 | 4187 | 0.0015382 | 6.2276 | 6.2292 | -2.4428 | 650.1303 | 6104.7798 | -0.0037574
149 |  | 6.3617 | 40.9673 | 4187 | 0.001538 | 6.2292 | 6.2307 | -2.4428 | 650.1899 | 6145.7471 | -0.003757
150 |  | 6.3617 | 40.9636 | 4187 | 0.0015379 | 6.2307 | 6.2323 | -2.4428 | 650.2496 | 6186.7107 | -0.0037567
151 |  | 6.3617 | 40.9598 | 4187 | 0.0015377 | 6.2323 | 6.2338 | -2.4428 | 650.3092 | 6227.6705 | -0.0037563
152 |  | 6.3617 | 40.9561 | 4187 | 0.0015376 | 6.2338 | 6.2353 | -2.4428 | 650.3688 | 6268.6266 | -0.003756
153 |  | 6.3617 | 40.9523 | 4187 | 0.0015374 | 6.2353 | 6.2369 | -2.4428 | 650.4285 | 6309.5789 | -0.0037556
154 |  | 6.3617 | 40.9485 | 4187 | 0.0015373 | 6.2369 | 6.2384 | -2.4428 | 650.4881 | 6350.5274 | -0.0037553
155 |  | 6.3617 | 40.9448 | 4187 | 0.0015372 | 6.2384 | 6.24 | -2.4428 | 650.5478 | 6391.4722 | -0.003755
156 |  | 6.3617 | 40.941 | 4187 | 0.001537 | 6.24 | 6.2415 | -2.4428 | 650.6075 | 6432.4132 | -0.0037546
157 |  | 6.3617 | 40.9373 | 4187 | 0.0015369 | 6.2415 | 6.243 | -2.4428 | 650.6671 | 6473.3505 | -0.0037543
158 |  | 6.3617 | 40.9335 | 4187 | 0.0015367 | 6.243 | 6.2446 | -2.4428 | 650.7268 | 6514.284 | -0.0037539
159 |  | 6.3617 | 40.9298 | 4187 | 0.0015366 | 6.2446 | 6.2461 | -2.4428 | 650.7865 | 6555.2138 | -0.0037536
160 |  | 6.3617 | 40.926 | 4187 | 0.0015365 | 6.2461 | 6.2476 | -2.4428 | 650.8462 | 6596.1398 | -0.0037532
161 |  | 6.3617 | 40.9223 | 4187 | 0.0015363 | 6.2476 | 6.2492 | -2.4428 | 650.9059 | 6637.0621 | -0.0037529
162 |  | 6.3617 | 40.9185 | 4187 | 0.0015362 | 6.2492 | 6.2507 | -2.4428 | 650.9656 | 6677.9806 | -0.0037525
163 |  | 6.3617 | 40.9148 | 4187 | 0.001536 | 6.2507 | 6.2522 | -2.4428 | 651.0253 | 6718.8954 | -0.0037522
164 |  | 6.3617 | 40.911 | 4187 | 0.0015359 | 6.2522 | 6.2538 | -2.4428 | 651.085 | 6759.8064 | -0.0037519
165 |  | 6.3617 | 40.9073 | 4187 | 0.0015358 | 6.2538 | 6.2553 | -2.4428 | 651.1447 | 6800.7136 | -0.0037515
166 |  | 6.3617 | 40.9035 | 4187 | 0.0015356 | 6.2553 | 6.2569 | -2.4428 | 651.2044 | 6841.6171 | -0.0037512
167 |  | 6.3617 | 40.8998 | 4187 | 0.0015355 | 6.2569 | 6.2584 | -2.4428 | 651.2642 | 6882.5169 | -0.0037508
168 |  | 6.3617 | 40.896 | 4187 | 0.0015353 | 6.2584 | 6.2599 | -2.4428 | 651.3239 | 6923.4129 | -0.0037505
169 |  | 6.3617 | 40.8923 | 4187 | 0.0015352 | 6.2599 | 6.2615 | -2.4428 | 651.3836 | 6964.3051 | -0.0037501
170 |  | 6.3617 | 40.8885 | 4187 | 0.0015351 | 6.2615 | 6.263 | -2.4428 | 651.4434 | 7005.1936 | -0.0037498
171 |  | 6.3617 | 40.8848 | 4187 | 0.0015349 | 6.263 | 6.2645 | -2.4428 | 651.5031 | 7046.0784 | -0.0037494
172 |  | 6.3617 | 40.881 | 4187 | 0.0015348 | 6.2645 | 6.2661 | -2.4428 | 651.5629 | 7086.9594 | -0.0037491
173 |  | 6.3617 | 40.8773 | 4187 | 0.0015346 | 6.2661 | 6.2676 | -2.4428 | 651.6226 | 7127.8367 | -0.0037488
174 |  | 6.3617 | 40.8735 | 4187 | 0.0015345 | 6.2676 | 6.2691 | -2.4428 | 651.6824 | 7168.7102 | -0.0037484
175 |  | 6.3617 | 40.8698 | 4187 | 0.0015343 | 6.2691 | 6.2707 | -2.4428 | 651.7422 | 7209.5799 | -0.0037481
176 |  | 6.3617 | 40.866 | 4187 | 0.0015342 | 6.2707 | 6.2722 | -2.4428 | 651.8019 | 7250.4459 | -0.0037477
177 |  | 6.3617 | 40.8623 | 4187 | 0.0015341 | 6.2722 | 6.2737 | -2.4428 | 651.8617 | 7291.3082 | -0.0037474
178 |  | 6.3617 | 40.8585 | 4187 | 0.0015339 | 6.2737 | 6.2753 | -2.4428 | 651.9215 | 7332.1667 | -0.003747
179 |  | 6.3617 | 40.8548 | 4187 | 0.0015338 | 6.2753 | 6.2768 | -2.4428 | 651.9813 | 7373.0215 | -0.0037467
180 |  | 6.3617 | 40.851 | 4187 | 0.0015336 | 6.2768 | 6.2783 | -2.4428 | 652.0411 | 7413.8725 | -0.0037464
181 |  | 6.3617 | 40.8473 | 4187 | 0.0015335 | 6.2783 | 6.2799 | -2.4428 | 652.1009 | 7454.7197 | -0.003746
182 |  | 6.3617 | 40.8435 | 4187 | 0.0015334 | 6.2799 | 6.2814 | -2.4428 | 652.1607 | 7495.5633 | -0.0037457
183 |  | 6.3617 | 40.8398 | 4187 | 0.0015332 | 6.2814 | 6.2829 | -2.4428 | 652.2205 | 7536.4031 | -0.0037453
184 |  | 6.3617 | 40.836 | 4187 | 0.0015331 | 6.2829 | 6.2845 | -2.4428 | 652.2803 | 7577.2391 | -0.003745
185 |  | 6.3617 | 40.8323 | 4187 | 0.0015329 | 6.2845 | 6.286 | -2.4428 | 652.3402 | 7618.0714 | -0.0037446
186 |  | 6.3617 | 40.8285 | 4187 | 0.0015328 | 6.286 | 6.2875 | -2.4428 | 652.4 | 7658.8999 | -0.0037443
187 |  | 6.3617 | 40.8248 | 4187 | 0.0015327 | 6.2875 | 6.2891 | -2.4428 | 652.4598 | 7699.7247 | -0.0037439
188 |  | 6.3617 | 40.8211 | 4187 | 0.0015325 | 6.2891 | 6.2906 | -2.4428 | 652.5197 | 7740.5458 | -0.0037436
189 |  | 6.3617 | 40.8173 | 4187 | 0.0015324 | 6.2906 | 6.2921 | -2.4428 | 652.5795 | 7781.3631 | -0.0037433
190 |  | 6.3617 | 40.8136 | 4187 | 0.0015322 | 6.2921 | 6.2937 | -2.4428 | 652.6394 | 7822.1767 | -0.0037429
191 |  | 6.3617 | 40.8098 | 4187 | 0.0015321 | 6.2937 | 6.2952 | -2.4428 | 652.6992 | 7862.9865 | -0.0037426
192 |  | 6.3617 | 40.8061 | 4187 | 0.001532 | 6.2952 | 6.2967 | -2.4428 | 652.7591 | 7903.7926 | -0.0037422
193 |  | 6.3617 | 40.8023 | 4187 | 0.0015318 | 6.2967 | 6.2983 | -2.4428 | 652.819 | 7944.5949 | -0.0037419
194 |  | 6.3617 | 40.7986 | 4187 | 0.0015317 | 6.2983 | 6.2998 | -2.4428 | 652.8788 | 7985.3935 | -0.0037415
195 |  | 6.3617 | 40.7949 | 4187 | 0.0015315 | 6.2998 | 6.3013 | -2.4428 | 652.9387 | 8026.1884 | -0.0037412
196 |  | 6.3617 | 40.7911 | 4187 | 0.0015314 | 6.3013 | 6.3029 | -2.4428 | 652.9986 | 8066.9795 | -0.0037409
197 |  | 6.3617 | 40.7874 | 4187 | 0.0015313 | 6.3029 | 6.3044 | -2.4428 | 653.0585 | 8107.7669 | -0.0037405
198 |  | 6.3617 | 40.7836 | 4187 | 0.0015311 | 6.3044 | 6.3059 | -2.4428 | 653.1184 | 8148.5505 | -0.0037402
199 |  | 6.3617 | 40.7799 | 4187 | 0.001531 | 6.3059 | 6.3074 | -2.4428 | 653.1783 | 8189.3304 | -0.0037398
200 |  | 6.3617 | 40.7762 | 4187 | 0.0015308 | 6.3074 | 6.309 | -2.4428 | 653.2382 | 8230.1066 | -0.0037395
201 |  | 6.3617 | 40.7724 | 4187 | 0.0015307 | 6.309 | 6.3105 | -2.4428 | 653.2981 | 8270.879 | -0.0037391
202 |  | 6.3617 | 40.7687 | 4187 | 0.0015306 | 6.3105 | 6.312 | -2.4428 | 653.358 | 8311.6477 | -0.0037388
203 |  | 6.3617 | 40.7649 | 4187 | 0.0015304 | 6.312 | 6.3136 | -2.4428 | 653.4179 | 8352.4126 | -0.0037385
204 |  | 6.3617 | 40.7612 | 4187 | 0.0015303 | 6.3136 | 6.3151 | -2.4428 | 653.4779 | 8393.1738 | -0.0037381
205 |  | 6.3617 | 40.7575 | 4187 | 0.0015301 | 6.3151 | 6.3166 | -2.4428 | 653.5378 | 8433.9313 | -0.0037378
206 |  | 6.3617 | 40.7537 | 4187 | 0.00153 | 6.3166 | 6.3182 | -2.4428 | 653.5977 | 8474.685 | -0.0037374
207 |  | 6.3617 | 40.75 | 4187 | 0.0015299 | 6.3182 | 6.3197 | -2.4428 | 653.6577 | 8515.435 | -0.0037371
208 |  | 6.3617 | 40.7463 | 4187 | 0.0015297 | 6.3197 | 6.3212 | -2.4428 | 653.7176 | 8556.1812 | -0.0037367
209 |  | 6.3617 | 40.7425 | 4187 | 0.0015296 | 6.3212 | 6.3227 | -2.4428 | 653.7776 | 8596.9238 | -0.0037364
210 |  | 6.3617 | 40.7388 | 4187 | 0.0015294 | 6.3227 | 6.3243 | -2.4428 | 653.8376 | 8637.6625 | -0.0037361
211 |  | 6.3617 | 40.735 | 4187 | 0.0015293 | 6.3243 | 6.3258 | -2.4428 | 653.8975 | 8678.3976 | -0.0037357
212 |  | 6.3617 | 40.7313 | 4187 | 0.0015292 | 6.3258 | 6.3273 | -2.4428 | 653.9575 | 8719.1289 | -0.0037354
213 |  | 6.3617 | 40.7276 | 4187 | 0.001529 | 6.3273 | 6.3289 | -2.4428 | 654.0175 | 8759.8565 | -0.003735
214 |  | 6.3617 | 40.7238 | 4187 | 0.0015289 | 6.3289 | 6.3304 | -2.4428 | 654.0775 | 8800.5803 | -0.0037347
215 |  | 6.3617 | 40.7201 | 4187 | 0.0015287 | 6.3304 | 6.3319 | -2.4428 | 654.1375 | 8841.3004 | -0.0037343
216 |  | 6.3617 | 40.7164 | 4187 | 0.0015286 | 6.3319 | 6.3335 | -2.4428 | 654.1974 | 8882.0168 | -0.003734
217 |  | 6.3617 | 40.7126 | 4187 | 0.0015285 | 6.3335 | 6.335 | -2.4428 | 654.2574 | 8922.7294 | -0.0037337
218 |  | 6.3617 | 40.7089 | 4187 | 0.0015283 | 6.335 | 6.3365 | -2.4428 | 654.3175 | 8963.4383 | -0.0037333
219 |  | 6.3617 | 40.7052 | 4187 | 0.0015282 | 6.3365 | 6.338 | -2.4428 | 654.3775 | 9004.1435 | -0.003733
220 |  | 6.3617 | 40.7014 | 4187 | 0.001528 | 6.338 | 6.3396 | -2.4428 | 654.4375 | 9044.8449 | -0.0037326
221 |  | 6.3617 | 40.6977 | 4187 | 0.0015279 | 6.3396 | 6.3411 | -2.4428 | 654.4975 | 9085.5426 | -0.0037323
222 |  | 6.3617 | 40.694 | 4187 | 0.0015277 | 6.3411 | 6.3426 | -2.4428 | 654.5575 | 9126.2366 | -0.0037319
223 |  | 6.3617 | 40.6902 | 4187 | 0.0015276 | 6.3426 | 6.3441 | -2.4428 | 654.6176 | 9166.9268 | -0.0037316
224 |  | 6.3617 | 40.6865 | 4187 | 0.0015275 | 6.3441 | 6.3457 | -2.4428 | 654.6776 | 9207.6133 | -0.0037313
225 |  | 6.3617 | 40.6828 | 4187 | 0.0015273 | 6.3457 | 6.3472 | -2.4428 | 654.7377 | 9248.2961 | -0.0037309
226 |  | 6.3617 | 40.679 | 4187 | 0.0015272 | 6.3472 | 6.3487 | -2.4428 | 654.7977 | 9288.9751 | -0.0037306
227 |  | 6.3617 | 40.6753 | 4187 | 0.001527 | 6.3487 | 6.3503 | -2.4428 | 654.8578 | 9329.6504 | -0.0037302
228 |  | 6.3617 | 40.6716 | 4187 | 0.0015269 | 6.3503 | 6.3518 | -2.4428 | 654.9178 | 9370.322 | -0.0037299
229 |  | 6.3617 | 40.6679 | 4187 | 0.0015268 | 6.3518 | 6.3533 | -2.4428 | 654.9779 | 9410.9898 | -0.0037296
230 |  | 6.3617 | 40.6641 | 4187 | 0.0015266 | 6.3533 | 6.3548 | -2.4428 | 655.038 | 9451.654 | -0.0037292
231 |  | 6.3617 | 40.6604 | 4187 | 0.0015265 | 6.3548 | 6.3564 | -2.4428 | 655.098 | 9492.3144 | -0.0037289
232 |  | 6.3617 | 40.6567 | 4187 | 0.0015263 | 6.3564 | 6.3579 | -2.4428 | 655.1581 | 9532.971 | -0.0037285
233 |  | 6.3617 | 40.6529 | 4187 | 0.0015262 | 6.3579 | 6.3594 | -2.4428 | 655.2182 | 9573.624 | -0.0037282
234 |  | 6.3617 | 40.6492 | 4187 | 0.0015261 | 6.3594 | 6.3609 | -2.4428 | 655.2783 | 9614.2732 | -0.0037278
235 |  | 6.3617 | 40.6455 | 4187 | 0.0015259 | 6.3609 | 6.3625 | -2.4428 | 655.3384 | 9654.9186 | -0.0037275
236 |  | 6.3617 | 40.6418 | 4187 | 0.0015258 | 6.3625 | 6.364 | -2.4428 | 655.3985 | 9695.5604 | -0.0037272

## 125
|  |  | buis | verlies W/M | L /°C/sec
diam | wandikte |  | inhoud l/m |  | W/M
125 | 11.4 | 3.1416 | 8.2034 | 43.9784 | 4187
[8 empty] | J/sec/mtr | aantal mtr. | verlies
|  | buis | verlies W/M | L /°C/sec | verlies temp | begintemp | eindtemp | verlies | bij 1°C | totaal J/sec
|  | inhoud L |  | W/M | °C per M | °C | °C | per m°C | daling | aantal mtr
1 | 125 | 8.2034 | 43.9784 | 4187 | 0.0012804 | 6 | 6.0013 | -2.587 | 781.0071 | 43.9784 | -0.0033123
2 |  | 8.2034 | 43.9751 | 4187 | 0.0012803 | 6.0013 | 6.0026 | -2.587 | 781.0659 | 87.9535 | -0.0033121
3 |  | 8.2034 | 43.9718 | 4187 | 0.0012802 | 6.0026 | 6.0038 | -2.587 | 781.1247 | 131.9253 | -0.0033118
4 |  | 8.2034 | 43.9685 | 4187 | 0.0012801 | 6.0038 | 6.0051 | -2.587 | 781.1836 | 175.8938 | -0.0033116
5 |  | 8.2034 | 43.9652 | 4187 | 0.00128 | 6.0051 | 6.0064 | -2.587 | 781.2424 | 219.859 | -0.0033113
6 |  | 8.2034 | 43.9619 | 4187 | 0.0012799 | 6.0064 | 6.0077 | -2.587 | 781.3012 | 263.8209 | -0.0033111
7 |  | 8.2034 | 43.9586 | 4187 | 0.0012798 | 6.0077 | 6.009 | -2.587 | 781.3601 | 307.7794 | -0.0033109
8 |  | 8.2034 | 43.9552 | 4187 | 0.0012797 | 6.009 | 6.0102 | -2.587 | 781.419 | 351.7347 | -0.0033106
9 |  | 8.2034 | 43.9519 | 4187 | 0.0012796 | 6.0102 | 6.0115 | -2.587 | 781.4778 | 395.6866 | -0.0033104
10 |  | 8.2034 | 43.9486 | 4187 | 0.0012795 | 6.0115 | 6.0128 | -2.587 | 781.5367 | 439.6352 | -0.0033101
11 |  | 8.2034 | 43.9453 | 4187 | 0.0012794 | 6.0128 | 6.0141 | -2.587 | 781.5955 | 483.5805 | -0.0033099
12 |  | 8.2034 | 43.942 | 4187 | 0.0012793 | 6.0141 | 6.0154 | -2.587 | 781.6544 | 527.5225 | -0.0033096
13 |  | 8.2034 | 43.9387 | 4187 | 0.0012792 | 6.0154 | 6.0166 | -2.587 | 781.7133 | 571.4612 | -0.0033094
14 |  | 8.2034 | 43.9354 | 4187 | 0.0012791 | 6.0166 | 6.0179 | -2.587 | 781.7722 | 615.3966 | -0.0033091
15 |  | 8.2034 | 43.9321 | 4187 | 0.001279 | 6.0179 | 6.0192 | -2.587 | 781.8311 | 659.3287 | -0.0033089
16 |  | 8.2034 | 43.9288 | 4187 | 0.001279 | 6.0192 | 6.0205 | -2.587 | 781.8899 | 703.2575 | -0.0033086
17 |  | 8.2034 | 43.9255 | 4187 | 0.0012789 | 6.0205 | 6.0218 | -2.587 | 781.9488 | 747.1829 | -0.0033084
18 |  | 8.2034 | 43.9221 | 4187 | 0.0012788 | 6.0218 | 6.023 | -2.587 | 782.0077 | 791.1051 | -0.0033081
19 |  | 8.2034 | 43.9188 | 4187 | 0.0012787 | 6.023 | 6.0243 | -2.587 | 782.0666 | 835.0239 | -0.0033079
20 |  | 8.2034 | 43.9155 | 4187 | 0.0012786 | 6.0243 | 6.0256 | -2.587 | 782.1256 | 878.9394 | -0.0033076
21 |  | 8.2034 | 43.9122 | 4187 | 0.0012785 | 6.0256 | 6.0269 | -2.587 | 782.1845 | 922.8517 | -0.0033074
22 |  | 8.2034 | 43.9089 | 4187 | 0.0012784 | 6.0269 | 6.0281 | -2.587 | 782.2434 | 966.7606 | -0.0033071
23 |  | 8.2034 | 43.9056 | 4187 | 0.0012783 | 6.0281 | 6.0294 | -2.587 | 782.3023 | 1010.6662 | -0.0033069
24 |  | 8.2034 | 43.9023 | 4187 | 0.0012782 | 6.0294 | 6.0307 | -2.587 | 782.3612 | 1054.5685 | -0.0033066
25 |  | 8.2034 | 43.899 | 4187 | 0.0012781 | 6.0307 | 6.032 | -2.587 | 782.4202 | 1098.4675 | -0.0033064
26 |  | 8.2034 | 43.8957 | 4187 | 0.001278 | 6.032 | 6.0333 | -2.587 | 782.4791 | 1142.3632 | -0.0033061
27 |  | 8.2034 | 43.8924 | 4187 | 0.0012779 | 6.0333 | 6.0345 | -2.587 | 782.538 | 1186.2556 | -0.0033059
28 |  | 8.2034 | 43.8891 | 4187 | 0.0012778 | 6.0345 | 6.0358 | -2.587 | 782.597 | 1230.1447 | -0.0033056
29 |  | 8.2034 | 43.8858 | 4187 | 0.0012777 | 6.0358 | 6.0371 | -2.587 | 782.6559 | 1274.0304 | -0.0033054
30 |  | 8.2034 | 43.8825 | 4187 | 0.0012776 | 6.0371 | 6.0384 | -2.587 | 782.7149 | 1317.9129 | -0.0033051
31 |  | 8.2034 | 43.8792 | 4187 | 0.0012775 | 6.0384 | 6.0396 | -2.587 | 782.7738 | 1361.7921 | -0.0033049
32 |  | 8.2034 | 43.8759 | 4187 | 0.0012774 | 6.0396 | 6.0409 | -2.587 | 782.8328 | 1405.6679 | -0.0033046
33 |  | 8.2034 | 43.8726 | 4187 | 0.0012773 | 6.0409 | 6.0422 | -2.587 | 782.8918 | 1449.5405 | -0.0033044
34 |  | 8.2034 | 43.8692 | 4187 | 0.0012772 | 6.0422 | 6.0435 | -2.587 | 782.9507 | 1493.4097 | -0.0033041
35 |  | 8.2034 | 43.8659 | 4187 | 0.0012771 | 6.0435 | 6.0448 | -2.587 | 783.0097 | 1537.2757 | -0.0033039
36 |  | 8.2034 | 43.8626 | 4187 | 0.001277 | 6.0448 | 6.046 | -2.587 | 783.0687 | 1581.1383 | -0.0033036
37 |  | 8.2034 | 43.8593 | 4187 | 0.0012769 | 6.046 | 6.0473 | -2.587 | 783.1277 | 1624.9976 | -0.0033034
38 |  | 8.2034 | 43.856 | 4187 | 0.0012768 | 6.0473 | 6.0486 | -2.587 | 783.1867 | 1668.8537 | -0.0033031
39 |  | 8.2034 | 43.8527 | 4187 | 0.0012767 | 6.0486 | 6.0499 | -2.587 | 783.2456 | 1712.7064 | -0.0033029
40 |  | 8.2034 | 43.8494 | 4187 | 0.0012766 | 6.0499 | 6.0511 | -2.587 | 783.3046 | 1756.5558 | -0.0033026
41 |  | 8.2034 | 43.8461 | 4187 | 0.0012765 | 6.0511 | 6.0524 | -2.587 | 783.3636 | 1800.402 | -0.0033024
42 |  | 8.2034 | 43.8428 | 4187 | 0.0012765 | 6.0524 | 6.0537 | -2.587 | 783.4226 | 1844.2448 | -0.0033021
43 |  | 8.2034 | 43.8395 | 4187 | 0.0012764 | 6.0537 | 6.055 | -2.587 | 783.4817 | 1888.0843 | -0.0033019
44 |  | 8.2034 | 43.8362 | 4187 | 0.0012763 | 6.055 | 6.0562 | -2.587 | 783.5407 | 1931.9205 | -0.0033016
45 |  | 8.2034 | 43.8329 | 4187 | 0.0012762 | 6.0562 | 6.0575 | -2.587 | 783.5997 | 1975.7534 | -0.0033014
46 |  | 8.2034 | 43.8296 | 4187 | 0.0012761 | 6.0575 | 6.0588 | -2.587 | 783.6587 | 2019.5831 | -0.0033011
47 |  | 8.2034 | 43.8263 | 4187 | 0.001276 | 6.0588 | 6.0601 | -2.587 | 783.7177 | 2063.4094 | -0.0033009
48 |  | 8.2034 | 43.823 | 4187 | 0.0012759 | 6.0601 | 6.0614 | -2.587 | 783.7768 | 2107.2324 | -0.0033006
49 |  | 8.2034 | 43.8197 | 4187 | 0.0012758 | 6.0614 | 6.0626 | -2.587 | 783.8358 | 2151.0521 | -0.0033004
50 |  | 8.2034 | 43.8164 | 4187 | 0.0012757 | 6.0626 | 6.0639 | -2.587 | 783.8949 | 2194.8685 | -0.0033001
51 |  | 8.2034 | 43.8131 | 4187 | 0.0012756 | 6.0639 | 6.0652 | -2.587 | 783.9539 | 2238.6816 | -0.0032999
52 |  | 8.2034 | 43.8098 | 4187 | 0.0012755 | 6.0652 | 6.0665 | -2.587 | 784.0129 | 2282.4914 | -0.0032996
53 |  | 8.2034 | 43.8065 | 4187 | 0.0012754 | 6.0665 | 6.0677 | -2.587 | 784.072 | 2326.298 | -0.0032994
54 |  | 8.2034 | 43.8032 | 4187 | 0.0012753 | 6.0677 | 6.069 | -2.587 | 784.1311 | 2370.1012 | -0.0032992
55 |  | 8.2034 | 43.7999 | 4187 | 0.0012752 | 6.069 | 6.0703 | -2.587 | 784.1901 | 2413.9011 | -0.0032989
56 |  | 8.2034 | 43.7966 | 4187 | 0.0012751 | 6.0703 | 6.0716 | -2.587 | 784.2492 | 2457.6977 | -0.0032987
57 |  | 8.2034 | 43.7933 | 4187 | 0.001275 | 6.0716 | 6.0728 | -2.587 | 784.3083 | 2501.491 | -0.0032984
58 |  | 8.2034 | 43.79 | 4187 | 0.0012749 | 6.0728 | 6.0741 | -2.587 | 784.3673 | 2545.281 | -0.0032982
59 |  | 8.2034 | 43.7867 | 4187 | 0.0012748 | 6.0741 | 6.0754 | -2.587 | 784.4264 | 2589.0678 | -0.0032979
60 |  | 8.2034 | 43.7834 | 4187 | 0.0012747 | 6.0754 | 6.0767 | -2.587 | 784.4855 | 2632.8512 | -0.0032977
61 |  | 8.2034 | 43.7801 | 4187 | 0.0012746 | 6.0767 | 6.0779 | -2.587 | 784.5446 | 2676.6313 | -0.0032974
62 |  | 8.2034 | 43.7768 | 4187 | 0.0012745 | 6.0779 | 6.0792 | -2.587 | 784.6037 | 2720.4081 | -0.0032972
63 |  | 8.2034 | 43.7735 | 4187 | 0.0012744 | 6.0792 | 6.0805 | -2.587 | 784.6628 | 2764.1817 | -0.0032969
64 |  | 8.2034 | 43.7702 | 4187 | 0.0012743 | 6.0805 | 6.0818 | -2.587 | 784.7219 | 2807.9519 | -0.0032967
65 |  | 8.2034 | 43.7669 | 4187 | 0.0012742 | 6.0818 | 6.083 | -2.587 | 784.781 | 2851.7188 | -0.0032964
66 |  | 8.2034 | 43.7636 | 4187 | 0.0012741 | 6.083 | 6.0843 | -2.587 | 784.8401 | 2895.4825 | -0.0032962
67 |  | 8.2034 | 43.7603 | 4187 | 0.001274 | 6.0843 | 6.0856 | -2.587 | 784.8992 | 2939.2428 | -0.0032959
68 |  | 8.2034 | 43.757 | 4187 | 0.001274 | 6.0856 | 6.0868 | -2.587 | 784.9583 | 2982.9999 | -0.0032957
69 |  | 8.2034 | 43.7538 | 4187 | 0.0012739 | 6.0868 | 6.0881 | -2.587 | 785.0175 | 3026.7536 | -0.0032954
70 |  | 8.2034 | 43.7505 | 4187 | 0.0012738 | 6.0881 | 6.0894 | -2.587 | 785.0766 | 3070.5041 | -0.0032952
71 |  | 8.2034 | 43.7472 | 4187 | 0.0012737 | 6.0894 | 6.0907 | -2.587 | 785.1357 | 3114.2512 | -0.0032949
72 |  | 8.2034 | 43.7439 | 4187 | 0.0012736 | 6.0907 | 6.0919 | -2.587 | 785.1949 | 3157.9951 | -0.0032947
73 |  | 8.2034 | 43.7406 | 4187 | 0.0012735 | 6.0919 | 6.0932 | -2.587 | 785.254 | 3201.7357 | -0.0032944
74 |  | 8.2034 | 43.7373 | 4187 | 0.0012734 | 6.0932 | 6.0945 | -2.587 | 785.3132 | 3245.473 | -0.0032942
75 |  | 8.2034 | 43.734 | 4187 | 0.0012733 | 6.0945 | 6.0958 | -2.587 | 785.3723 | 3289.2069 | -0.0032939
76 |  | 8.2034 | 43.7307 | 4187 | 0.0012732 | 6.0958 | 6.097 | -2.587 | 785.4315 | 3332.9376 | -0.0032937
77 |  | 8.2034 | 43.7274 | 4187 | 0.0012731 | 6.097 | 6.0983 | -2.587 | 785.4906 | 3376.665 | -0.0032934
78 |  | 8.2034 | 43.7241 | 4187 | 0.001273 | 6.0983 | 6.0996 | -2.587 | 785.5498 | 3420.3891 | -0.0032932
79 |  | 8.2034 | 43.7208 | 4187 | 0.0012729 | 6.0996 | 6.1009 | -2.587 | 785.609 | 3464.1099 | -0.0032929
80 |  | 8.2034 | 43.7175 | 4187 | 0.0012728 | 6.1009 | 6.1021 | -2.587 | 785.6682 | 3507.8275 | -0.0032927
81 |  | 8.2034 | 43.7142 | 4187 | 0.0012727 | 6.1021 | 6.1034 | -2.587 | 785.7273 | 3551.5417 | -0.0032924
82 |  | 8.2034 | 43.7109 | 4187 | 0.0012726 | 6.1034 | 6.1047 | -2.587 | 785.7865 | 3595.2526 | -0.0032922
83 |  | 8.2034 | 43.7076 | 4187 | 0.0012725 | 6.1047 | 6.1059 | -2.587 | 785.8457 | 3638.9603 | -0.003292
84 |  | 8.2034 | 43.7043 | 4187 | 0.0012724 | 6.1059 | 6.1072 | -2.587 | 785.9049 | 3682.6646 | -0.0032917
85 |  | 8.2034 | 43.7011 | 4187 | 0.0012723 | 6.1072 | 6.1085 | -2.587 | 785.9641 | 3726.3657 | -0.0032915
86 |  | 8.2034 | 43.6978 | 4187 | 0.0012722 | 6.1085 | 6.1098 | -2.587 | 786.0233 | 3770.0634 | -0.0032912
87 |  | 8.2034 | 43.6945 | 4187 | 0.0012721 | 6.1098 | 6.111 | -2.587 | 786.0825 | 3813.7579 | -0.003291
88 |  | 8.2034 | 43.6912 | 4187 | 0.001272 | 6.111 | 6.1123 | -2.587 | 786.1417 | 3857.4491 | -0.0032907
89 |  | 8.2034 | 43.6879 | 4187 | 0.0012719 | 6.1123 | 6.1136 | -2.587 | 786.2009 | 3901.137 | -0.0032905
90 |  | 8.2034 | 43.6846 | 4187 | 0.0012718 | 6.1136 | 6.1149 | -2.587 | 786.2601 | 3944.8216 | -0.0032902
91 |  | 8.2034 | 43.6813 | 4187 | 0.0012717 | 6.1149 | 6.1161 | -2.587 | 786.3194 | 3988.5029 | -0.00329
92 |  | 8.2034 | 43.678 | 4187 | 0.0012717 | 6.1161 | 6.1174 | -2.587 | 786.3786 | 4032.1809 | -0.0032897
93 |  | 8.2034 | 43.6747 | 4187 | 0.0012716 | 6.1174 | 6.1187 | -2.587 | 786.4378 | 4075.8556 | -0.0032895
94 |  | 8.2034 | 43.6714 | 4187 | 0.0012715 | 6.1187 | 6.1199 | -2.587 | 786.4971 | 4119.5271 | -0.0032892
95 |  | 8.2034 | 43.6682 | 4187 | 0.0012714 | 6.1199 | 6.1212 | -2.587 | 786.5563 | 4163.1952 | -0.003289
96 |  | 8.2034 | 43.6649 | 4187 | 0.0012713 | 6.1212 | 6.1225 | -2.587 | 786.6156 | 4206.8601 | -0.0032887
97 |  | 8.2034 | 43.6616 | 4187 | 0.0012712 | 6.1225 | 6.1238 | -2.587 | 786.6748 | 4250.5217 | -0.0032885
98 |  | 8.2034 | 43.6583 | 4187 | 0.0012711 | 6.1238 | 6.125 | -2.587 | 786.7341 | 4294.1799 | -0.0032882
99 |  | 8.2034 | 43.655 | 4187 | 0.001271 | 6.125 | 6.1263 | -2.587 | 786.7933 | 4337.8349 | -0.003288
100 |  | 8.2034 | 43.6517 | 4187 | 0.0012709 | 6.1263 | 6.1276 | -2.587 | 786.8526 | 4381.4867 | -0.0032877
101 |  | 8.2034 | 43.6484 | 4187 | 0.0012708 | 6.1276 | 6.1288 | -2.587 | 786.9118 | 4425.1351 | -0.0032875
102 |  | 8.2034 | 43.6451 | 4187 | 0.0012707 | 6.1288 | 6.1301 | -2.587 | 786.9711 | 4468.7802 | -0.0032872
103 |  | 8.2034 | 43.6418 | 4187 | 0.0012706 | 6.1301 | 6.1314 | -2.587 | 787.0304 | 4512.4221 | -0.003287
104 |  | 8.2034 | 43.6386 | 4187 | 0.0012705 | 6.1314 | 6.1326 | -2.587 | 787.0897 | 4556.0606 | -0.0032867
105 |  | 8.2034 | 43.6353 | 4187 | 0.0012704 | 6.1326 | 6.1339 | -2.587 | 787.149 | 4599.6959 | -0.0032865
106 |  | 8.2034 | 43.632 | 4187 | 0.0012703 | 6.1339 | 6.1352 | -2.587 | 787.2083 | 4643.3279 | -0.0032863
107 |  | 8.2034 | 43.6287 | 4187 | 0.0012702 | 6.1352 | 6.1365 | -2.587 | 787.2676 | 4686.9566 | -0.003286
108 |  | 8.2034 | 43.6254 | 4187 | 0.0012701 | 6.1365 | 6.1377 | -2.587 | 787.3269 | 4730.582 | -0.0032858
109 |  | 8.2034 | 43.6221 | 4187 | 0.00127 | 6.1377 | 6.139 | -2.587 | 787.3862 | 4774.2041 | -0.0032855
110 |  | 8.2034 | 43.6188 | 4187 | 0.0012699 | 6.139 | 6.1403 | -2.587 | 787.4455 | 4817.823 | -0.0032853
111 |  | 8.2034 | 43.6156 | 4187 | 0.0012698 | 6.1403 | 6.1415 | -2.587 | 787.5048 | 4861.4385 | -0.003285
112 |  | 8.2034 | 43.6123 | 4187 | 0.0012697 | 6.1415 | 6.1428 | -2.587 | 787.5641 | 4905.0508 | -0.0032848
113 |  | 8.2034 | 43.609 | 4187 | 0.0012696 | 6.1428 | 6.1441 | -2.587 | 787.6234 | 4948.6598 | -0.0032845
114 |  | 8.2034 | 43.6057 | 4187 | 0.0012695 | 6.1441 | 6.1453 | -2.587 | 787.6827 | 4992.2655 | -0.0032843
115 |  | 8.2034 | 43.6024 | 4187 | 0.0012695 | 6.1453 | 6.1466 | -2.587 | 787.7421 | 5035.8679 | -0.003284
116 |  | 8.2034 | 43.5991 | 4187 | 0.0012694 | 6.1466 | 6.1479 | -2.587 | 787.8014 | 5079.4671 | -0.0032838
117 |  | 8.2034 | 43.5959 | 4187 | 0.0012693 | 6.1479 | 6.1492 | -2.587 | 787.8607 | 5123.0629 | -0.0032835
118 |  | 8.2034 | 43.5926 | 4187 | 0.0012692 | 6.1492 | 6.1504 | -2.587 | 787.9201 | 5166.6555 | -0.0032833
119 |  | 8.2034 | 43.5893 | 4187 | 0.0012691 | 6.1504 | 6.1517 | -2.587 | 787.9794 | 5210.2448 | -0.003283
120 |  | 8.2034 | 43.586 | 4187 | 0.001269 | 6.1517 | 6.153 | -2.587 | 788.0388 | 5253.8308 | -0.0032828
121 |  | 8.2034 | 43.5827 | 4187 | 0.0012689 | 6.153 | 6.1542 | -2.587 | 788.0982 | 5297.4135 | -0.0032825
122 |  | 8.2034 | 43.5794 | 4187 | 0.0012688 | 6.1542 | 6.1555 | -2.587 | 788.1575 | 5340.9929 | -0.0032823
123 |  | 8.2034 | 43.5762 | 4187 | 0.0012687 | 6.1555 | 6.1568 | -2.587 | 788.2169 | 5384.5691 | -0.003282
124 |  | 8.2034 | 43.5729 | 4187 | 0.0012686 | 6.1568 | 6.158 | -2.587 | 788.2763 | 5428.1419 | -0.0032818
125 |  | 8.2034 | 43.5696 | 4187 | 0.0012685 | 6.158 | 6.1593 | -2.587 | 788.3356 | 5471.7115 | -0.0032816
126 |  | 8.2034 | 43.5663 | 4187 | 0.0012684 | 6.1593 | 6.1606 | -2.587 | 788.395 | 5515.2778 | -0.0032813
127 |  | 8.2034 | 43.563 | 4187 | 0.0012683 | 6.1606 | 6.1618 | -2.587 | 788.4544 | 5558.8409 | -0.0032811
128 |  | 8.2034 | 43.5597 | 4187 | 0.0012682 | 6.1618 | 6.1631 | -2.587 | 788.5138 | 5602.4006 | -0.0032808
129 |  | 8.2034 | 43.5565 | 4187 | 0.0012681 | 6.1631 | 6.1644 | -2.587 | 788.5732 | 5645.9571 | -0.0032806
130 |  | 8.2034 | 43.5532 | 4187 | 0.001268 | 6.1644 | 6.1656 | -2.587 | 788.6326 | 5689.5103 | -0.0032803
131 |  | 8.2034 | 43.5499 | 4187 | 0.0012679 | 6.1656 | 6.1669 | -2.587 | 788.692 | 5733.0602 | -0.0032801
132 |  | 8.2034 | 43.5466 | 4187 | 0.0012678 | 6.1669 | 6.1682 | -2.587 | 788.7514 | 5776.6068 | -0.0032798
133 |  | 8.2034 | 43.5433 | 4187 | 0.0012677 | 6.1682 | 6.1694 | -2.587 | 788.8108 | 5820.1501 | -0.0032796
134 |  | 8.2034 | 43.5401 | 4187 | 0.0012676 | 6.1694 | 6.1707 | -2.587 | 788.8702 | 5863.6902 | -0.0032793
135 |  | 8.2034 | 43.5368 | 4187 | 0.0012675 | 6.1707 | 6.172 | -2.587 | 788.9296 | 5907.227 | -0.0032791
136 |  | 8.2034 | 43.5335 | 4187 | 0.0012674 | 6.172 | 6.1733 | -2.587 | 788.9891 | 5950.7605 | -0.0032788
137 |  | 8.2034 | 43.5302 | 4187 | 0.0012673 | 6.1733 | 6.1745 | -2.587 | 789.0485 | 5994.2907 | -0.0032786
138 |  | 8.2034 | 43.5269 | 4187 | 0.0012673 | 6.1745 | 6.1758 | -2.587 | 789.1079 | 6037.8177 | -0.0032783
139 |  | 8.2034 | 43.5237 | 4187 | 0.0012672 | 6.1758 | 6.1771 | -2.587 | 789.1674 | 6081.3414 | -0.0032781
140 |  | 8.2034 | 43.5204 | 4187 | 0.0012671 | 6.1771 | 6.1783 | -2.587 | 789.2268 | 6124.8617 | -0.0032778
141 |  | 8.2034 | 43.5171 | 4187 | 0.001267 | 6.1783 | 6.1796 | -2.587 | 789.2862 | 6168.3789 | -0.0032776
142 |  | 8.2034 | 43.5138 | 4187 | 0.0012669 | 6.1796 | 6.1809 | -2.587 | 789.3457 | 6211.8927 | -0.0032774
143 |  | 8.2034 | 43.5106 | 4187 | 0.0012668 | 6.1809 | 6.1821 | -2.587 | 789.4051 | 6255.4033 | -0.0032771
144 |  | 8.2034 | 43.5073 | 4187 | 0.0012667 | 6.1821 | 6.1834 | -2.587 | 789.4646 | 6298.9105 | -0.0032769
145 |  | 8.2034 | 43.504 | 4187 | 0.0012666 | 6.1834 | 6.1847 | -2.587 | 789.5241 | 6342.4146 | -0.0032766
146 |  | 8.2034 | 43.5007 | 4187 | 0.0012665 | 6.1847 | 6.1859 | -2.587 | 789.5835 | 6385.9153 | -0.0032764
147 |  | 8.2034 | 43.4975 | 4187 | 0.0012664 | 6.1859 | 6.1872 | -2.587 | 789.643 | 6429.4127 | -0.0032761
148 |  | 8.2034 | 43.4942 | 4187 | 0.0012663 | 6.1872 | 6.1885 | -2.587 | 789.7025 | 6472.9069 | -0.0032759
149 |  | 8.2034 | 43.4909 | 4187 | 0.0012662 | 6.1885 | 6.1897 | -2.587 | 789.762 | 6516.3978 | -0.0032756
150 |  | 8.2034 | 43.4876 | 4187 | 0.0012661 | 6.1897 | 6.191 | -2.587 | 789.8215 | 6559.8854 | -0.0032754
151 |  | 8.2034 | 43.4844 | 4187 | 0.001266 | 6.191 | 6.1923 | -2.587 | 789.881 | 6603.3698 | -0.0032751
152 |  | 8.2034 | 43.4811 | 4187 | 0.0012659 | 6.1923 | 6.1935 | -2.587 | 789.9405 | 6646.8509 | -0.0032749
153 |  | 8.2034 | 43.4778 | 4187 | 0.0012658 | 6.1935 | 6.1948 | -2.587 | 790 | 6690.3287 | -0.0032746
154 |  | 8.2034 | 43.4745 | 4187 | 0.0012657 | 6.1948 | 6.196 | -2.587 | 790.0595 | 6733.8032 | -0.0032744
155 |  | 8.2034 | 43.4713 | 4187 | 0.0012656 | 6.196 | 6.1973 | -2.587 | 790.119 | 6777.2744 | -0.0032741
156 |  | 8.2034 | 43.468 | 4187 | 0.0012655 | 6.1973 | 6.1986 | -2.587 | 790.1785 | 6820.7424 | -0.0032739
157 |  | 8.2034 | 43.4647 | 4187 | 0.0012654 | 6.1986 | 6.1998 | -2.587 | 790.238 | 6864.2071 | -0.0032737
158 |  | 8.2034 | 43.4614 | 4187 | 0.0012653 | 6.1998 | 6.2011 | -2.587 | 790.2975 | 6907.6686 | -0.0032734
159 |  | 8.2034 | 43.4582 | 4187 | 0.0012653 | 6.2011 | 6.2024 | -2.587 | 790.3571 | 6951.1267 | -0.0032732
160 |  | 8.2034 | 43.4549 | 4187 | 0.0012652 | 6.2024 | 6.2036 | -2.587 | 790.4166 | 6994.5816 | -0.0032729
161 |  | 8.2034 | 43.4516 | 4187 | 0.0012651 | 6.2036 | 6.2049 | -2.587 | 790.4761 | 7038.0332 | -0.0032727
162 |  | 8.2034 | 43.4483 | 4187 | 0.001265 | 6.2049 | 6.2062 | -2.587 | 790.5357 | 7081.4815 | -0.0032724
163 |  | 8.2034 | 43.4451 | 4187 | 0.0012649 | 6.2062 | 6.2074 | -2.587 | 790.5952 | 7124.9266 | -0.0032722
164 |  | 8.2034 | 43.4418 | 4187 | 0.0012648 | 6.2074 | 6.2087 | -2.587 | 790.6548 | 7168.3684 | -0.0032719
165 |  | 8.2034 | 43.4385 | 4187 | 0.0012647 | 6.2087 | 6.21 | -2.587 | 790.7143 | 7211.8069 | -0.0032717
166 |  | 8.2034 | 43.4352 | 4187 | 0.0012646 | 6.21 | 6.2112 | -2.587 | 790.7739 | 7255.2422 | -0.0032714
167 |  | 8.2034 | 43.432 | 4187 | 0.0012645 | 6.2112 | 6.2125 | -2.587 | 790.8334 | 7298.6741 | -0.0032712
168 |  | 8.2034 | 43.4287 | 4187 | 0.0012644 | 6.2125 | 6.2138 | -2.587 | 790.893 | 7342.1029 | -0.0032709
169 |  | 8.2034 | 43.4254 | 4187 | 0.0012643 | 6.2138 | 6.215 | -2.587 | 790.9526 | 7385.5283 | -0.0032707
170 |  | 8.2034 | 43.4222 | 4187 | 0.0012642 | 6.215 | 6.2163 | -2.587 | 791.0122 | 7428.9505 | -0.0032705
171 |  | 8.2034 | 43.4189 | 4187 | 0.0012641 | 6.2163 | 6.2176 | -2.587 | 791.0717 | 7472.3694 | -0.0032702
172 |  | 8.2034 | 43.4156 | 4187 | 0.001264 | 6.2176 | 6.2188 | -2.587 | 791.1313 | 7515.785 | -0.00327
173 |  | 8.2034 | 43.4124 | 4187 | 0.0012639 | 6.2188 | 6.2201 | -2.587 | 791.1909 | 7559.1973 | -0.0032697
174 |  | 8.2034 | 43.4091 | 4187 | 0.0012638 | 6.2201 | 6.2213 | -2.587 | 791.2505 | 7602.6064 | -0.0032695
175 |  | 8.2034 | 43.4058 | 4187 | 0.0012637 | 6.2213 | 6.2226 | -2.587 | 791.3101 | 7646.0122 | -0.0032692
176 |  | 8.2034 | 43.4025 | 4187 | 0.0012636 | 6.2226 | 6.2239 | -2.587 | 791.3697 | 7689.4148 | -0.003269
177 |  | 8.2034 | 43.3993 | 4187 | 0.0012635 | 6.2239 | 6.2251 | -2.587 | 791.4293 | 7732.8141 | -0.0032687
178 |  | 8.2034 | 43.396 | 4187 | 0.0012634 | 6.2251 | 6.2264 | -2.587 | 791.4889 | 7776.2101 | -0.0032685
179 |  | 8.2034 | 43.3927 | 4187 | 0.0012633 | 6.2264 | 6.2277 | -2.587 | 791.5486 | 7819.6028 | -0.0032682
180 |  | 8.2034 | 43.3895 | 4187 | 0.0012633 | 6.2277 | 6.2289 | -2.587 | 791.6082 | 7862.9923 | -0.003268
181 |  | 8.2034 | 43.3862 | 4187 | 0.0012632 | 6.2289 | 6.2302 | -2.587 | 791.6678 | 7906.3785 | -0.0032677
182 |  | 8.2034 | 43.3829 | 4187 | 0.0012631 | 6.2302 | 6.2315 | -2.587 | 791.7274 | 7949.7614 | -0.0032675
183 |  | 8.2034 | 43.3797 | 4187 | 0.001263 | 6.2315 | 6.2327 | -2.587 | 791.7871 | 7993.1411 | -0.0032672
184 |  | 8.2034 | 43.3764 | 4187 | 0.0012629 | 6.2327 | 6.234 | -2.587 | 791.8467 | 8036.5175 | -0.003267
185 |  | 8.2034 | 43.3731 | 4187 | 0.0012628 | 6.234 | 6.2352 | -2.587 | 791.9064 | 8079.8906 | -0.0032668
186 |  | 8.2034 | 43.3699 | 4187 | 0.0012627 | 6.2352 | 6.2365 | -2.587 | 791.966 | 8123.2605 | -0.0032665
187 |  | 8.2034 | 43.3666 | 4187 | 0.0012626 | 6.2365 | 6.2378 | -2.587 | 792.0257 | 8166.6271 | -0.0032663
188 |  | 8.2034 | 43.3633 | 4187 | 0.0012625 | 6.2378 | 6.239 | -2.587 | 792.0853 | 8209.9904 | -0.003266
189 |  | 8.2034 | 43.3601 | 4187 | 0.0012624 | 6.239 | 6.2403 | -2.587 | 792.145 | 8253.3505 | -0.0032658
190 |  | 8.2034 | 43.3568 | 4187 | 0.0012623 | 6.2403 | 6.2416 | -2.587 | 792.2046 | 8296.7073 | -0.0032655
191 |  | 8.2034 | 43.3535 | 4187 | 0.0012622 | 6.2416 | 6.2428 | -2.587 | 792.2643 | 8340.0608 | -0.0032653
192 |  | 8.2034 | 43.3503 | 4187 | 0.0012621 | 6.2428 | 6.2441 | -2.587 | 792.324 | 8383.4111 | -0.003265
193 |  | 8.2034 | 43.347 | 4187 | 0.001262 | 6.2441 | 6.2453 | -2.587 | 792.3837 | 8426.7581 | -0.0032648
194 |  | 8.2034 | 43.3437 | 4187 | 0.0012619 | 6.2453 | 6.2466 | -2.587 | 792.4434 | 8470.1019 | -0.0032645
195 |  | 8.2034 | 43.3405 | 4187 | 0.0012618 | 6.2466 | 6.2479 | -2.587 | 792.503 | 8513.4423 | -0.0032643
196 |  | 8.2034 | 43.3372 | 4187 | 0.0012617 | 6.2479 | 6.2491 | -2.587 | 792.5627 | 8556.7795 | -0.0032641
197 |  | 8.2034 | 43.3339 | 4187 | 0.0012616 | 6.2491 | 6.2504 | -2.587 | 792.6224 | 8600.1135 | -0.0032638
198 |  | 8.2034 | 43.3307 | 4187 | 0.0012615 | 6.2504 | 6.2516 | -2.587 | 792.6821 | 8643.4442 | -0.0032636
199 |  | 8.2034 | 43.3274 | 4187 | 0.0012614 | 6.2516 | 6.2529 | -2.587 | 792.7418 | 8686.7716 | -0.0032633
200 |  | 8.2034 | 43.3242 | 4187 | 0.0012613 | 6.2529 | 6.2542 | -2.587 | 792.8016 | 8730.0958 | -0.0032631
201 |  | 8.2034 | 43.3209 | 4187 | 0.0012613 | 6.2542 | 6.2554 | -2.587 | 792.8613 | 8773.4167 | -0.0032628
202 |  | 8.2034 | 43.3176 | 4187 | 0.0012612 | 6.2554 | 6.2567 | -2.587 | 792.921 | 8816.7343 | -0.0032626
203 |  | 8.2034 | 43.3144 | 4187 | 0.0012611 | 6.2567 | 6.258 | -2.587 | 792.9807 | 8860.0487 | -0.0032623
204 |  | 8.2034 | 43.3111 | 4187 | 0.001261 | 6.258 | 6.2592 | -2.587 | 793.0405 | 8903.3598 | -0.0032621
205 |  | 8.2034 | 43.3078 | 4187 | 0.0012609 | 6.2592 | 6.2605 | -2.587 | 793.1002 | 8946.6676 | -0.0032618
206 |  | 8.2034 | 43.3046 | 4187 | 0.0012608 | 6.2605 | 6.2617 | -2.587 | 793.1599 | 8989.9722 | -0.0032616
207 |  | 8.2034 | 43.3013 | 4187 | 0.0012607 | 6.2617 | 6.263 | -2.587 | 793.2197 | 9033.2735 | -0.0032613
208 |  | 8.2034 | 43.2981 | 4187 | 0.0012606 | 6.263 | 6.2643 | -2.587 | 793.2794 | 9076.5716 | -0.0032611
209 |  | 8.2034 | 43.2948 | 4187 | 0.0012605 | 6.2643 | 6.2655 | -2.587 | 793.3392 | 9119.8664 | -0.0032609
210 |  | 8.2034 | 43.2915 | 4187 | 0.0012604 | 6.2655 | 6.2668 | -2.587 | 793.3989 | 9163.1579 | -0.0032606
211 |  | 8.2034 | 43.2883 | 4187 | 0.0012603 | 6.2668 | 6.268 | -2.587 | 793.4587 | 9206.4462 | -0.0032604
212 |  | 8.2034 | 43.285 | 4187 | 0.0012602 | 6.268 | 6.2693 | -2.587 | 793.5185 | 9249.7312 | -0.0032601
213 |  | 8.2034 | 43.2818 | 4187 | 0.0012601 | 6.2693 | 6.2706 | -2.587 | 793.5782 | 9293.013 | -0.0032599
214 |  | 8.2034 | 43.2785 | 4187 | 0.00126 | 6.2706 | 6.2718 | -2.587 | 793.638 | 9336.2915 | -0.0032596
215 |  | 8.2034 | 43.2752 | 4187 | 0.0012599 | 6.2718 | 6.2731 | -2.587 | 793.6978 | 9379.5667 | -0.0032594
216 |  | 8.2034 | 43.272 | 4187 | 0.0012598 | 6.2731 | 6.2743 | -2.587 | 793.7576 | 9422.8387 | -0.0032591
217 |  | 8.2034 | 43.2687 | 4187 | 0.0012597 | 6.2743 | 6.2756 | -2.587 | 793.8173 | 9466.1074 | -0.0032589
218 |  | 8.2034 | 43.2655 | 4187 | 0.0012596 | 6.2756 | 6.2769 | -2.587 | 793.8771 | 9509.3729 | -0.0032586
219 |  | 8.2034 | 43.2622 | 4187 | 0.0012595 | 6.2769 | 6.2781 | -2.587 | 793.9369 | 9552.6351 | -0.0032584
220 |  | 8.2034 | 43.2589 | 4187 | 0.0012595 | 6.2781 | 6.2794 | -2.587 | 793.9967 | 9595.894 | -0.0032582
221 |  | 8.2034 | 43.2557 | 4187 | 0.0012594 | 6.2794 | 6.2806 | -2.587 | 794.0565 | 9639.1497 | -0.0032579
222 |  | 8.2034 | 43.2524 | 4187 | 0.0012593 | 6.2806 | 6.2819 | -2.587 | 794.1164 | 9682.4021 | -0.0032577
223 |  | 8.2034 | 43.2492 | 4187 | 0.0012592 | 6.2819 | 6.2832 | -2.587 | 794.1762 | 9725.6513 | -0.0032574
224 |  | 8.2034 | 43.2459 | 4187 | 0.0012591 | 6.2832 | 6.2844 | -2.587 | 794.236 | 9768.8972 | -0.0032572
225 |  | 8.2034 | 43.2427 | 4187 | 0.001259 | 6.2844 | 6.2857 | -2.587 | 794.2958 | 9812.1399 | -0.0032569
226 |  | 8.2034 | 43.2394 | 4187 | 0.0012589 | 6.2857 | 6.2869 | -2.587 | 794.3556 | 9855.3793 | -0.0032567
227 |  | 8.2034 | 43.2361 | 4187 | 0.0012588 | 6.2869 | 6.2882 | -2.587 | 794.4155 | 9898.6154 | -0.0032564
228 |  | 8.2034 | 43.2329 | 4187 | 0.0012587 | 6.2882 | 6.2894 | -2.587 | 794.4753 | 9941.8483 | -0.0032562
229 |  | 8.2034 | 43.2296 | 4187 | 0.0012586 | 6.2894 | 6.2907 | -2.587 | 794.5352 | 9985.0779 | -0.0032559
230 |  | 8.2034 | 43.2264 | 4187 | 0.0012585 | 6.2907 | 6.292 | -2.587 | 794.595 | 10028.3043 | -0.0032557
231 |  | 8.2034 | 43.2231 | 4187 | 0.0012584 | 6.292 | 6.2932 | -2.587 | 794.6549 | 10071.5274 | -0.0032555
232 |  | 8.2034 | 43.2199 | 4187 | 0.0012583 | 6.2932 | 6.2945 | -2.587 | 794.7147 | 10114.7473 | -0.0032552
233 |  | 8.2034 | 43.2166 | 4187 | 0.0012582 | 6.2945 | 6.2957 | -2.587 | 794.7746 | 10157.9639 | -0.003255
234 |  | 8.2034 | 43.2134 | 4187 | 0.0012581 | 6.2957 | 6.297 | -2.587 | 794.8344 | 10201.1772 | -0.0032547
235 |  | 8.2034 | 43.2101 | 4187 | 0.001258 | 6.297 | 6.2983 | -2.587 | 794.8943 | 10244.3873 | -0.0032545
236 |  | 8.2034 | 43.2068 | 4187 | 0.0012579 | 6.2983 | 6.2995 | -2.587 | 794.9542 | 10287.5942 | -0.0032542

## 160
|  |  | buis | verlies W/M | L /°C/sec
diam | wandikte |  | inhoud l/m |  | W/M
160 | 14.6 | 3.1416 | 13.4371 | 48.7293 | 4187
[8 empty] | J/sec/mtr | aantal mtr. | verlies
|  | buis | verlies W/M | L /°C/sec | verlies temp | begintemp | eindtemp | verlies | bij 1°C | totaal J/sec
|  | inhoud L |  | W/M | °C per M | °C | °C | per m°C | daling | aantal mtr
1 | 160 | 13.4371 | 48.7293 | 4187 | 0.00086613 | 6 | 6.0009 | -2.8664 | 1154.5633 | 48.7293 | -0.0024827
2 |  | 13.4371 | 48.7269 | 4187 | 0.00086608 | 6.0009 | 6.0017 | -2.8664 | 1154.6221 | 97.4562 | -0.0024826
3 |  | 13.4371 | 48.7244 | 4187 | 0.00086604 | 6.0017 | 6.0026 | -2.8664 | 1154.681 | 146.1806 | -0.0024824
4 |  | 13.4371 | 48.7219 | 4187 | 0.000866 | 6.0026 | 6.0035 | -2.8664 | 1154.7398 | 194.9025 | -0.0024823
5 |  | 13.4371 | 48.7194 | 4187 | 0.00086595 | 6.0035 | 6.0043 | -2.8664 | 1154.7986 | 243.6219 | -0.0024822
6 |  | 13.4371 | 48.7169 | 4187 | 0.00086591 | 6.0043 | 6.0052 | -2.8664 | 1154.8575 | 292.3388 | -0.0024821
7 |  | 13.4371 | 48.7145 | 4187 | 0.00086586 | 6.0052 | 6.0061 | -2.8664 | 1154.9163 | 341.0533 | -0.0024819
8 |  | 13.4371 | 48.712 | 4187 | 0.00086582 | 6.0061 | 6.0069 | -2.8664 | 1154.9752 | 389.7653 | -0.0024818
9 |  | 13.4371 | 48.7095 | 4187 | 0.00086578 | 6.0069 | 6.0078 | -2.8664 | 1155.034 | 438.4747 | -0.0024817
10 |  | 13.4371 | 48.707 | 4187 | 0.00086573 | 6.0078 | 6.0087 | -2.8664 | 1155.0929 | 487.1817 | -0.0024816
11 |  | 13.4371 | 48.7045 | 4187 | 0.00086569 | 6.0087 | 6.0095 | -2.8664 | 1155.1517 | 535.8863 | -0.0024814
12 |  | 13.4371 | 48.702 | 4187 | 0.00086564 | 6.0095 | 6.0104 | -2.8664 | 1155.2106 | 584.5883 | -0.0024813
13 |  | 13.4371 | 48.6996 | 4187 | 0.0008656 | 6.0104 | 6.0113 | -2.8664 | 1155.2694 | 633.2879 | -0.0024812
14 |  | 13.4371 | 48.6971 | 4187 | 0.00086555 | 6.0113 | 6.0121 | -2.8664 | 1155.3283 | 681.985 | -0.0024811
15 |  | 13.4371 | 48.6946 | 4187 | 0.00086551 | 6.0121 | 6.013 | -2.8664 | 1155.3872 | 730.6796 | -0.0024809
16 |  | 13.4371 | 48.6921 | 4187 | 0.00086547 | 6.013 | 6.0139 | -2.8664 | 1155.446 | 779.3717 | -0.0024808
17 |  | 13.4371 | 48.6896 | 4187 | 0.00086542 | 6.0139 | 6.0147 | -2.8664 | 1155.5049 | 828.0613 | -0.0024807
18 |  | 13.4371 | 48.6872 | 4187 | 0.00086538 | 6.0147 | 6.0156 | -2.8664 | 1155.5638 | 876.7485 | -0.0024805
19 |  | 13.4371 | 48.6847 | 4187 | 0.00086533 | 6.0156 | 6.0164 | -2.8664 | 1155.6227 | 925.4331 | -0.0024804
20 |  | 13.4371 | 48.6822 | 4187 | 0.00086529 | 6.0164 | 6.0173 | -2.8664 | 1155.6815 | 974.1153 | -0.0024803
21 |  | 13.4371 | 48.6797 | 4187 | 0.00086525 | 6.0173 | 6.0182 | -2.8664 | 1155.7404 | 1022.7951 | -0.0024802
22 |  | 13.4371 | 48.6772 | 4187 | 0.0008652 | 6.0182 | 6.019 | -2.8664 | 1155.7993 | 1071.4723 | -0.00248
23 |  | 13.4371 | 48.6748 | 4187 | 0.00086516 | 6.019 | 6.0199 | -2.8664 | 1155.8582 | 1120.147 | -0.0024799
24 |  | 13.4371 | 48.6723 | 4187 | 0.00086511 | 6.0199 | 6.0208 | -2.8664 | 1155.9171 | 1168.8193 | -0.0024798
25 |  | 13.4371 | 48.6698 | 4187 | 0.00086507 | 6.0208 | 6.0216 | -2.8664 | 1155.976 | 1217.4891 | -0.0024797
26 |  | 13.4371 | 48.6673 | 4187 | 0.00086503 | 6.0216 | 6.0225 | -2.8664 | 1156.0349 | 1266.1564 | -0.0024795
27 |  | 13.4371 | 48.6648 | 4187 | 0.00086498 | 6.0225 | 6.0234 | -2.8664 | 1156.0938 | 1314.8213 | -0.0024794
28 |  | 13.4371 | 48.6624 | 4187 | 0.00086494 | 6.0234 | 6.0242 | -2.8664 | 1156.1527 | 1363.4836 | -0.0024793
29 |  | 13.4371 | 48.6599 | 4187 | 0.00086489 | 6.0242 | 6.0251 | -2.8664 | 1156.2116 | 1412.1435 | -0.0024792
30 |  | 13.4371 | 48.6574 | 4187 | 0.00086485 | 6.0251 | 6.026 | -2.8664 | 1156.2705 | 1460.8009 | -0.002479
31 |  | 13.4371 | 48.6549 | 4187 | 0.00086481 | 6.026 | 6.0268 | -2.8664 | 1156.3294 | 1509.4558 | -0.0024789
32 |  | 13.4371 | 48.6524 | 4187 | 0.00086476 | 6.0268 | 6.0277 | -2.8664 | 1156.3883 | 1558.1083 | -0.0024788
33 |  | 13.4371 | 48.65 | 4187 | 0.00086472 | 6.0277 | 6.0286 | -2.8664 | 1156.4473 | 1606.7582 | -0.0024787
34 |  | 13.4371 | 48.6475 | 4187 | 0.00086467 | 6.0286 | 6.0294 | -2.8664 | 1156.5062 | 1655.4057 | -0.0024785
35 |  | 13.4371 | 48.645 | 4187 | 0.00086463 | 6.0294 | 6.0303 | -2.8664 | 1156.5651 | 1704.0507 | -0.0024784
36 |  | 13.4371 | 48.6425 | 4187 | 0.00086459 | 6.0303 | 6.0312 | -2.8664 | 1156.624 | 1752.6932 | -0.0024783
37 |  | 13.4371 | 48.64 | 4187 | 0.00086454 | 6.0312 | 6.032 | -2.8664 | 1156.683 | 1801.3333 | -0.0024781
38 |  | 13.4371 | 48.6376 | 4187 | 0.0008645 | 6.032 | 6.0329 | -2.8664 | 1156.7419 | 1849.9708 | -0.002478
39 |  | 13.4371 | 48.6351 | 4187 | 0.00086445 | 6.0329 | 6.0337 | -2.8664 | 1156.8008 | 1898.6059 | -0.0024779
40 |  | 13.4371 | 48.6326 | 4187 | 0.00086441 | 6.0337 | 6.0346 | -2.8664 | 1156.8598 | 1947.2386 | -0.0024778
41 |  | 13.4371 | 48.6301 | 4187 | 0.00086436 | 6.0346 | 6.0355 | -2.8664 | 1156.9187 | 1995.8687 | -0.0024776
42 |  | 13.4371 | 48.6277 | 4187 | 0.00086432 | 6.0355 | 6.0363 | -2.8664 | 1156.9777 | 2044.4963 | -0.0024775
43 |  | 13.4371 | 48.6252 | 4187 | 0.00086428 | 6.0363 | 6.0372 | -2.8664 | 1157.0366 | 2093.1215 | -0.0024774
44 |  | 13.4371 | 48.6227 | 4187 | 0.00086423 | 6.0372 | 6.0381 | -2.8664 | 1157.0956 | 2141.7442 | -0.0024773
45 |  | 13.4371 | 48.6202 | 4187 | 0.00086419 | 6.0381 | 6.0389 | -2.8664 | 1157.1545 | 2190.3645 | -0.0024771
46 |  | 13.4371 | 48.6177 | 4187 | 0.00086414 | 6.0389 | 6.0398 | -2.8664 | 1157.2135 | 2238.9822 | -0.002477
47 |  | 13.4371 | 48.6153 | 4187 | 0.0008641 | 6.0398 | 6.0407 | -2.8664 | 1157.2724 | 2287.5975 | -0.0024769
48 |  | 13.4371 | 48.6128 | 4187 | 0.00086406 | 6.0407 | 6.0415 | -2.8664 | 1157.3314 | 2336.2103 | -0.0024768
49 |  | 13.4371 | 48.6103 | 4187 | 0.00086401 | 6.0415 | 6.0424 | -2.8664 | 1157.3904 | 2384.8206 | -0.0024766
50 |  | 13.4371 | 48.6078 | 4187 | 0.00086397 | 6.0424 | 6.0433 | -2.8664 | 1157.4493 | 2433.4284 | -0.0024765
51 |  | 13.4371 | 48.6054 | 4187 | 0.00086392 | 6.0433 | 6.0441 | -2.8664 | 1157.5083 | 2482.0338 | -0.0024764
52 |  | 13.4371 | 48.6029 | 4187 | 0.00086388 | 6.0441 | 6.045 | -2.8664 | 1157.5673 | 2530.6367 | -0.0024763
53 |  | 13.4371 | 48.6004 | 4187 | 0.00086384 | 6.045 | 6.0458 | -2.8664 | 1157.6263 | 2579.2371 | -0.0024761
54 |  | 13.4371 | 48.5979 | 4187 | 0.00086379 | 6.0458 | 6.0467 | -2.8664 | 1157.6853 | 2627.835 | -0.002476
55 |  | 13.4371 | 48.5955 | 4187 | 0.00086375 | 6.0467 | 6.0476 | -2.8664 | 1157.7442 | 2676.4305 | -0.0024759
56 |  | 13.4371 | 48.593 | 4187 | 0.0008637 | 6.0476 | 6.0484 | -2.8664 | 1157.8032 | 2725.0235 | -0.0024758
57 |  | 13.4371 | 48.5905 | 4187 | 0.00086366 | 6.0484 | 6.0493 | -2.8664 | 1157.8622 | 2773.614 | -0.0024756
58 |  | 13.4371 | 48.588 | 4187 | 0.00086362 | 6.0493 | 6.0502 | -2.8664 | 1157.9212 | 2822.202 | -0.0024755
59 |  | 13.4371 | 48.5856 | 4187 | 0.00086357 | 6.0502 | 6.051 | -2.8664 | 1157.9802 | 2870.7876 | -0.0024754
60 |  | 13.4371 | 48.5831 | 4187 | 0.00086353 | 6.051 | 6.0519 | -2.8664 | 1158.0392 | 2919.3707 | -0.0024752
61 |  | 13.4371 | 48.5806 | 4187 | 0.00086348 | 6.0519 | 6.0528 | -2.8664 | 1158.0982 | 2967.9513 | -0.0024751
62 |  | 13.4371 | 48.5781 | 4187 | 0.00086344 | 6.0528 | 6.0536 | -2.8664 | 1158.1572 | 3016.5294 | -0.002475
63 |  | 13.4371 | 48.5757 | 4187 | 0.0008634 | 6.0536 | 6.0545 | -2.8664 | 1158.2162 | 3065.1051 | -0.0024749
64 |  | 13.4371 | 48.5732 | 4187 | 0.00086335 | 6.0545 | 6.0553 | -2.8664 | 1158.2752 | 3113.6782 | -0.0024747
65 |  | 13.4371 | 48.5707 | 4187 | 0.00086331 | 6.0553 | 6.0562 | -2.8664 | 1158.3343 | 3162.2489 | -0.0024746
66 |  | 13.4371 | 48.5682 | 4187 | 0.00086326 | 6.0562 | 6.0571 | -2.8664 | 1158.3933 | 3210.8172 | -0.0024745
67 |  | 13.4371 | 48.5658 | 4187 | 0.00086322 | 6.0571 | 6.0579 | -2.8664 | 1158.4523 | 3259.3829 | -0.0024744
68 |  | 13.4371 | 48.5633 | 4187 | 0.00086318 | 6.0579 | 6.0588 | -2.8664 | 1158.5113 | 3307.9462 | -0.0024742
69 |  | 13.4371 | 48.5608 | 4187 | 0.00086313 | 6.0588 | 6.0597 | -2.8664 | 1158.5704 | 3356.507 | -0.0024741
70 |  | 13.4371 | 48.5583 | 4187 | 0.00086309 | 6.0597 | 6.0605 | -2.8664 | 1158.6294 | 3405.0654 | -0.002474
71 |  | 13.4371 | 48.5559 | 4187 | 0.00086304 | 6.0605 | 6.0614 | -2.8664 | 1158.6884 | 3453.6212 | -0.0024739
72 |  | 13.4371 | 48.5534 | 4187 | 0.000863 | 6.0614 | 6.0622 | -2.8664 | 1158.7475 | 3502.1746 | -0.0024737
73 |  | 13.4371 | 48.5509 | 4187 | 0.00086296 | 6.0622 | 6.0631 | -2.8664 | 1158.8065 | 3550.7255 | -0.0024736
74 |  | 13.4371 | 48.5484 | 4187 | 0.00086291 | 6.0631 | 6.064 | -2.8664 | 1158.8655 | 3599.274 | -0.0024735
75 |  | 13.4371 | 48.546 | 4187 | 0.00086287 | 6.064 | 6.0648 | -2.8664 | 1158.9246 | 3647.8199 | -0.0024734
76 |  | 13.4371 | 48.5435 | 4187 | 0.00086282 | 6.0648 | 6.0657 | -2.8664 | 1158.9836 | 3696.3634 | -0.0024732
77 |  | 13.4371 | 48.541 | 4187 | 0.00086278 | 6.0657 | 6.0666 | -2.8664 | 1159.0427 | 3744.9044 | -0.0024731
78 |  | 13.4371 | 48.5385 | 4187 | 0.00086274 | 6.0666 | 6.0674 | -2.8664 | 1159.1017 | 3793.443 | -0.002473
79 |  | 13.4371 | 48.5361 | 4187 | 0.00086269 | 6.0674 | 6.0683 | -2.8664 | 1159.1608 | 3841.9791 | -0.0024729
80 |  | 13.4371 | 48.5336 | 4187 | 0.00086265 | 6.0683 | 6.0692 | -2.8664 | 1159.2199 | 3890.5127 | -0.0024727
81 |  | 13.4371 | 48.5311 | 4187 | 0.00086261 | 6.0692 | 6.07 | -2.8664 | 1159.2789 | 3939.0438 | -0.0024726
82 |  | 13.4371 | 48.5287 | 4187 | 0.00086256 | 6.07 | 6.0709 | -2.8664 | 1159.338 | 3987.5725 | -0.0024725
83 |  | 13.4371 | 48.5262 | 4187 | 0.00086252 | 6.0709 | 6.0717 | -2.8664 | 1159.3971 | 4036.0986 | -0.0024723
84 |  | 13.4371 | 48.5237 | 4187 | 0.00086247 | 6.0717 | 6.0726 | -2.8664 | 1159.4561 | 4084.6223 | -0.0024722
85 |  | 13.4371 | 48.5212 | 4187 | 0.00086243 | 6.0726 | 6.0735 | -2.8664 | 1159.5152 | 4133.1436 | -0.0024721
86 |  | 13.4371 | 48.5188 | 4187 | 0.00086239 | 6.0735 | 6.0743 | -2.8664 | 1159.5743 | 4181.6624 | -0.002472
87 |  | 13.4371 | 48.5163 | 4187 | 0.00086234 | 6.0743 | 6.0752 | -2.8664 | 1159.6334 | 4230.1786 | -0.0024718
88 |  | 13.4371 | 48.5138 | 4187 | 0.0008623 | 6.0752 | 6.0761 | -2.8664 | 1159.6925 | 4278.6925 | -0.0024717
89 |  | 13.4371 | 48.5114 | 4187 | 0.00086225 | 6.0761 | 6.0769 | -2.8664 | 1159.7515 | 4327.2038 | -0.0024716
90 |  | 13.4371 | 48.5089 | 4187 | 0.00086221 | 6.0769 | 6.0778 | -2.8664 | 1159.8106 | 4375.7127 | -0.0024715
91 |  | 13.4371 | 48.5064 | 4187 | 0.00086217 | 6.0778 | 6.0786 | -2.8664 | 1159.8697 | 4424.2191 | -0.0024713
92 |  | 13.4371 | 48.5039 | 4187 | 0.00086212 | 6.0786 | 6.0795 | -2.8664 | 1159.9288 | 4472.723 | -0.0024712
93 |  | 13.4371 | 48.5015 | 4187 | 0.00086208 | 6.0795 | 6.0804 | -2.8664 | 1159.9879 | 4521.2245 | -0.0024711
94 |  | 13.4371 | 48.499 | 4187 | 0.00086203 | 6.0804 | 6.0812 | -2.8664 | 1160.047 | 4569.7235 | -0.002471
95 |  | 13.4371 | 48.4965 | 4187 | 0.00086199 | 6.0812 | 6.0821 | -2.8664 | 1160.1061 | 4618.22 | -0.0024708
96 |  | 13.4371 | 48.4941 | 4187 | 0.00086195 | 6.0821 | 6.0829 | -2.8664 | 1160.1652 | 4666.7141 | -0.0024707
97 |  | 13.4371 | 48.4916 | 4187 | 0.0008619 | 6.0829 | 6.0838 | -2.8664 | 1160.2244 | 4715.2057 | -0.0024706
98 |  | 13.4371 | 48.4891 | 4187 | 0.00086186 | 6.0838 | 6.0847 | -2.8664 | 1160.2835 | 4763.6948 | -0.0024705
99 |  | 13.4371 | 48.4866 | 4187 | 0.00086181 | 6.0847 | 6.0855 | -2.8664 | 1160.3426 | 4812.1814 | -0.0024703
100 |  | 13.4371 | 48.4842 | 4187 | 0.00086177 | 6.0855 | 6.0864 | -2.8664 | 1160.4017 | 4860.6656 | -0.0024702
101 |  | 13.4371 | 48.4817 | 4187 | 0.00086173 | 6.0864 | 6.0873 | -2.8664 | 1160.4608 | 4909.1473 | -0.0024701
102 |  | 13.4371 | 48.4792 | 4187 | 0.00086168 | 6.0873 | 6.0881 | -2.8664 | 1160.52 | 4957.6265 | -0.00247
103 |  | 13.4371 | 48.4768 | 4187 | 0.00086164 | 6.0881 | 6.089 | -2.8664 | 1160.5791 | 5006.1033 | -0.0024698
104 |  | 13.4371 | 48.4743 | 4187 | 0.00086159 | 6.089 | 6.0898 | -2.8664 | 1160.6382 | 5054.5776 | -0.0024697
105 |  | 13.4371 | 48.4718 | 4187 | 0.00086155 | 6.0898 | 6.0907 | -2.8664 | 1160.6974 | 5103.0494 | -0.0024696
106 |  | 13.4371 | 48.4694 | 4187 | 0.00086151 | 6.0907 | 6.0916 | -2.8664 | 1160.7565 | 5151.5187 | -0.0024695
107 |  | 13.4371 | 48.4669 | 4187 | 0.00086146 | 6.0916 | 6.0924 | -2.8664 | 1160.8156 | 5199.9856 | -0.0024693
108 |  | 13.4371 | 48.4644 | 4187 | 0.00086142 | 6.0924 | 6.0933 | -2.8664 | 1160.8748 | 5248.45 | -0.0024692
109 |  | 13.4371 | 48.4619 | 4187 | 0.00086138 | 6.0933 | 6.0941 | -2.8664 | 1160.9339 | 5296.912 | -0.0024691
110 |  | 13.4371 | 48.4595 | 4187 | 0.00086133 | 6.0941 | 6.095 | -2.8664 | 1160.9931 | 5345.3715 | -0.0024689
111 |  | 13.4371 | 48.457 | 4187 | 0.00086129 | 6.095 | 6.0959 | -2.8664 | 1161.0522 | 5393.8285 | -0.0024688
112 |  | 13.4371 | 48.4545 | 4187 | 0.00086124 | 6.0959 | 6.0967 | -2.8664 | 1161.1114 | 5442.283 | -0.0024687
113 |  | 13.4371 | 48.4521 | 4187 | 0.0008612 | 6.0967 | 6.0976 | -2.8664 | 1161.1706 | 5490.7351 | -0.0024686
114 |  | 13.4371 | 48.4496 | 4187 | 0.00086116 | 6.0976 | 6.0985 | -2.8664 | 1161.2297 | 5539.1847 | -0.0024684
115 |  | 13.4371 | 48.4471 | 4187 | 0.00086111 | 6.0985 | 6.0993 | -2.8664 | 1161.2889 | 5587.6318 | -0.0024683
116 |  | 13.4371 | 48.4447 | 4187 | 0.00086107 | 6.0993 | 6.1002 | -2.8664 | 1161.3481 | 5636.0765 | -0.0024682
117 |  | 13.4371 | 48.4422 | 4187 | 0.00086102 | 6.1002 | 6.101 | -2.8664 | 1161.4072 | 5684.5187 | -0.0024681
118 |  | 13.4371 | 48.4397 | 4187 | 0.00086098 | 6.101 | 6.1019 | -2.8664 | 1161.4664 | 5732.9584 | -0.0024679
119 |  | 13.4371 | 48.4373 | 4187 | 0.00086094 | 6.1019 | 6.1028 | -2.8664 | 1161.5256 | 5781.3956 | -0.0024678
120 |  | 13.4371 | 48.4348 | 4187 | 0.00086089 | 6.1028 | 6.1036 | -2.8664 | 1161.5848 | 5829.8304 | -0.0024677
121 |  | 13.4371 | 48.4323 | 4187 | 0.00086085 | 6.1036 | 6.1045 | -2.8664 | 1161.6439 | 5878.2627 | -0.0024676
122 |  | 13.4371 | 48.4299 | 4187 | 0.00086081 | 6.1045 | 6.1053 | -2.8664 | 1161.7031 | 5926.6926 | -0.0024674
123 |  | 13.4371 | 48.4274 | 4187 | 0.00086076 | 6.1053 | 6.1062 | -2.8664 | 1161.7623 | 5975.12 | -0.0024673
124 |  | 13.4371 | 48.4249 | 4187 | 0.00086072 | 6.1062 | 6.1071 | -2.8664 | 1161.8215 | 6023.5449 | -0.0024672
125 |  | 13.4371 | 48.4225 | 4187 | 0.00086067 | 6.1071 | 6.1079 | -2.8664 | 1161.8807 | 6071.9674 | -0.0024671
126 |  | 13.4371 | 48.42 | 4187 | 0.00086063 | 6.1079 | 6.1088 | -2.8664 | 1161.9399 | 6120.3874 | -0.0024669
127 |  | 13.4371 | 48.4175 | 4187 | 0.00086059 | 6.1088 | 6.1096 | -2.8664 | 1161.9991 | 6168.8049 | -0.0024668
128 |  | 13.4371 | 48.4151 | 4187 | 0.00086054 | 6.1096 | 6.1105 | -2.8664 | 1162.0583 | 6217.2199 | -0.0024667
129 |  | 13.4371 | 48.4126 | 4187 | 0.0008605 | 6.1105 | 6.1114 | -2.8664 | 1162.1175 | 6265.6325 | -0.0024666
130 |  | 13.4371 | 48.4101 | 4187 | 0.00086045 | 6.1114 | 6.1122 | -2.8664 | 1162.1767 | 6314.0426 | -0.0024664
131 |  | 13.4371 | 48.4077 | 4187 | 0.00086041 | 6.1122 | 6.1131 | -2.8664 | 1162.236 | 6362.4503 | -0.0024663
132 |  | 13.4371 | 48.4052 | 4187 | 0.00086037 | 6.1131 | 6.1139 | -2.8664 | 1162.2952 | 6410.8555 | -0.0024662
133 |  | 13.4371 | 48.4027 | 4187 | 0.00086032 | 6.1139 | 6.1148 | -2.8664 | 1162.3544 | 6459.2582 | -0.0024661
134 |  | 13.4371 | 48.4003 | 4187 | 0.00086028 | 6.1148 | 6.1157 | -2.8664 | 1162.4136 | 6507.6584 | -0.0024659
135 |  | 13.4371 | 48.3978 | 4187 | 0.00086024 | 6.1157 | 6.1165 | -2.8664 | 1162.4728 | 6556.0562 | -0.0024658
136 |  | 13.4371 | 48.3953 | 4187 | 0.00086019 | 6.1165 | 6.1174 | -2.8664 | 1162.5321 | 6604.4516 | -0.0024657
137 |  | 13.4371 | 48.3929 | 4187 | 0.00086015 | 6.1174 | 6.1182 | -2.8664 | 1162.5913 | 6652.8444 | -0.0024656
138 |  | 13.4371 | 48.3904 | 4187 | 0.0008601 | 6.1182 | 6.1191 | -2.8664 | 1162.6505 | 6701.2348 | -0.0024654
139 |  | 13.4371 | 48.3879 | 4187 | 0.00086006 | 6.1191 | 6.12 | -2.8664 | 1162.7098 | 6749.6227 | -0.0024653
140 |  | 13.4371 | 48.3855 | 4187 | 0.00086002 | 6.12 | 6.1208 | -2.8664 | 1162.769 | 6798.0082 | -0.0024652
141 |  | 13.4371 | 48.383 | 4187 | 0.00085997 | 6.1208 | 6.1217 | -2.8664 | 1162.8283 | 6846.3912 | -0.0024651
142 |  | 13.4371 | 48.3805 | 4187 | 0.00085993 | 6.1217 | 6.1225 | -2.8664 | 1162.8875 | 6894.7717 | -0.0024649
143 |  | 13.4371 | 48.3781 | 4187 | 0.00085988 | 6.1225 | 6.1234 | -2.8664 | 1162.9468 | 6943.1498 | -0.0024648
144 |  | 13.4371 | 48.3756 | 4187 | 0.00085984 | 6.1234 | 6.1243 | -2.8664 | 1163.006 | 6991.5254 | -0.0024647
145 |  | 13.4371 | 48.3731 | 4187 | 0.0008598 | 6.1243 | 6.1251 | -2.8664 | 1163.0653 | 7039.8985 | -0.0024645
146 |  | 13.4371 | 48.3707 | 4187 | 0.00085975 | 6.1251 | 6.126 | -2.8664 | 1163.1245 | 7088.2692 | -0.0024644
147 |  | 13.4371 | 48.3682 | 4187 | 0.00085971 | 6.126 | 6.1268 | -2.8664 | 1163.1838 | 7136.6374 | -0.0024643
148 |  | 13.4371 | 48.3657 | 4187 | 0.00085967 | 6.1268 | 6.1277 | -2.8664 | 1163.2431 | 7185.0031 | -0.0024642
149 |  | 13.4371 | 48.3633 | 4187 | 0.00085962 | 6.1277 | 6.1286 | -2.8664 | 1163.3023 | 7233.3664 | -0.002464
150 |  | 13.4371 | 48.3608 | 4187 | 0.00085958 | 6.1286 | 6.1294 | -2.8664 | 1163.3616 | 7281.7272 | -0.0024639
151 |  | 13.4371 | 48.3584 | 4187 | 0.00085953 | 6.1294 | 6.1303 | -2.8664 | 1163.4209 | 7330.0856 | -0.0024638
152 |  | 13.4371 | 48.3559 | 4187 | 0.00085949 | 6.1303 | 6.1311 | -2.8664 | 1163.4802 | 7378.4415 | -0.0024637
153 |  | 13.4371 | 48.3534 | 4187 | 0.00085945 | 6.1311 | 6.132 | -2.8664 | 1163.5394 | 7426.7949 | -0.0024635
154 |  | 13.4371 | 48.351 | 4187 | 0.0008594 | 6.132 | 6.1329 | -2.8664 | 1163.5987 | 7475.1458 | -0.0024634
155 |  | 13.4371 | 48.3485 | 4187 | 0.00085936 | 6.1329 | 6.1337 | -2.8664 | 1163.658 | 7523.4943 | -0.0024633
156 |  | 13.4371 | 48.346 | 4187 | 0.00085932 | 6.1337 | 6.1346 | -2.8664 | 1163.7173 | 7571.8404 | -0.0024632
157 |  | 13.4371 | 48.3436 | 4187 | 0.00085927 | 6.1346 | 6.1354 | -2.8664 | 1163.7766 | 7620.1839 | -0.002463
158 |  | 13.4371 | 48.3411 | 4187 | 0.00085923 | 6.1354 | 6.1363 | -2.8664 | 1163.8359 | 7668.5251 | -0.0024629
159 |  | 13.4371 | 48.3386 | 4187 | 0.00085918 | 6.1363 | 6.1372 | -2.8664 | 1163.8952 | 7716.8637 | -0.0024628
160 |  | 13.4371 | 48.3362 | 4187 | 0.00085914 | 6.1372 | 6.138 | -2.8664 | 1163.9545 | 7765.1999 | -0.0024627
161 |  | 13.4371 | 48.3337 | 4187 | 0.0008591 | 6.138 | 6.1389 | -2.8664 | 1164.0138 | 7813.5336 | -0.0024625
162 |  | 13.4371 | 48.3313 | 4187 | 0.00085905 | 6.1389 | 6.1397 | -2.8664 | 1164.0731 | 7861.8649 | -0.0024624
163 |  | 13.4371 | 48.3288 | 4187 | 0.00085901 | 6.1397 | 6.1406 | -2.8664 | 1164.1324 | 7910.1936 | -0.0024623
164 |  | 13.4371 | 48.3263 | 4187 | 0.00085897 | 6.1406 | 6.1415 | -2.8664 | 1164.1917 | 7958.52 | -0.0024622
165 |  | 13.4371 | 48.3239 | 4187 | 0.00085892 | 6.1415 | 6.1423 | -2.8664 | 1164.251 | 8006.8438 | -0.002462
166 |  | 13.4371 | 48.3214 | 4187 | 0.00085888 | 6.1423 | 6.1432 | -2.8664 | 1164.3104 | 8055.1653 | -0.0024619
167 |  | 13.4371 | 48.3189 | 4187 | 0.00085883 | 6.1432 | 6.144 | -2.8664 | 1164.3697 | 8103.4842 | -0.0024618
168 |  | 13.4371 | 48.3165 | 4187 | 0.00085879 | 6.144 | 6.1449 | -2.8664 | 1164.429 | 8151.8007 | -0.0024617
169 |  | 13.4371 | 48.314 | 4187 | 0.00085875 | 6.1449 | 6.1458 | -2.8664 | 1164.4883 | 8200.1147 | -0.0024615
170 |  | 13.4371 | 48.3116 | 4187 | 0.0008587 | 6.1458 | 6.1466 | -2.8664 | 1164.5477 | 8248.4263 | -0.0024614
171 |  | 13.4371 | 48.3091 | 4187 | 0.00085866 | 6.1466 | 6.1475 | -2.8664 | 1164.607 | 8296.7354 | -0.0024613
172 |  | 13.4371 | 48.3066 | 4187 | 0.00085862 | 6.1475 | 6.1483 | -2.8664 | 1164.6663 | 8345.042 | -0.0024612
173 |  | 13.4371 | 48.3042 | 4187 | 0.00085857 | 6.1483 | 6.1492 | -2.8664 | 1164.7257 | 8393.3462 | -0.002461
174 |  | 13.4371 | 48.3017 | 4187 | 0.00085853 | 6.1492 | 6.15 | -2.8664 | 1164.785 | 8441.6479 | -0.0024609
175 |  | 13.4371 | 48.2993 | 4187 | 0.00085848 | 6.15 | 6.1509 | -2.8664 | 1164.8444 | 8489.9471 | -0.0024608
176 |  | 13.4371 | 48.2968 | 4187 | 0.00085844 | 6.1509 | 6.1518 | -2.8664 | 1164.9037 | 8538.2439 | -0.0024607
177 |  | 13.4371 | 48.2943 | 4187 | 0.0008584 | 6.1518 | 6.1526 | -2.8664 | 1164.9631 | 8586.5383 | -0.0024605
178 |  | 13.4371 | 48.2919 | 4187 | 0.00085835 | 6.1526 | 6.1535 | -2.8664 | 1165.0224 | 8634.8301 | -0.0024604
179 |  | 13.4371 | 48.2894 | 4187 | 0.00085831 | 6.1535 | 6.1543 | -2.8664 | 1165.0818 | 8683.1195 | -0.0024603
180 |  | 13.4371 | 48.287 | 4187 | 0.00085827 | 6.1543 | 6.1552 | -2.8664 | 1165.1412 | 8731.4065 | -0.0024602
181 |  | 13.4371 | 48.2845 | 4187 | 0.00085822 | 6.1552 | 6.1561 | -2.8664 | 1165.2005 | 8779.691 | -0.00246
182 |  | 13.4371 | 48.282 | 4187 | 0.00085818 | 6.1561 | 6.1569 | -2.8664 | 1165.2599 | 8827.973 | -0.0024599
183 |  | 13.4371 | 48.2796 | 4187 | 0.00085813 | 6.1569 | 6.1578 | -2.8664 | 1165.3193 | 8876.2526 | -0.0024598
184 |  | 13.4371 | 48.2771 | 4187 | 0.00085809 | 6.1578 | 6.1586 | -2.8664 | 1165.3786 | 8924.5297 | -0.0024597
185 |  | 13.4371 | 48.2747 | 4187 | 0.00085805 | 6.1586 | 6.1595 | -2.8664 | 1165.438 | 8972.8044 | -0.0024595
186 |  | 13.4371 | 48.2722 | 4187 | 0.000858 | 6.1595 | 6.1603 | -2.8664 | 1165.4974 | 9021.0765 | -0.0024594
187 |  | 13.4371 | 48.2697 | 4187 | 0.00085796 | 6.1603 | 6.1612 | -2.8664 | 1165.5568 | 9069.3463 | -0.0024593
188 |  | 13.4371 | 48.2673 | 4187 | 0.00085792 | 6.1612 | 6.1621 | -2.8664 | 1165.6162 | 9117.6136 | -0.0024592
189 |  | 13.4371 | 48.2648 | 4187 | 0.00085787 | 6.1621 | 6.1629 | -2.8664 | 1165.6756 | 9165.8784 | -0.002459
190 |  | 13.4371 | 48.2624 | 4187 | 0.00085783 | 6.1629 | 6.1638 | -2.8664 | 1165.7349 | 9214.1407 | -0.0024589
191 |  | 13.4371 | 48.2599 | 4187 | 0.00085778 | 6.1638 | 6.1646 | -2.8664 | 1165.7943 | 9262.4006 | -0.0024588
192 |  | 13.4371 | 48.2574 | 4187 | 0.00085774 | 6.1646 | 6.1655 | -2.8664 | 1165.8537 | 9310.6581 | -0.0024587
193 |  | 13.4371 | 48.255 | 4187 | 0.0008577 | 6.1655 | 6.1663 | -2.8664 | 1165.9131 | 9358.913 | -0.0024585
194 |  | 13.4371 | 48.2525 | 4187 | 0.00085765 | 6.1663 | 6.1672 | -2.8664 | 1165.9726 | 9407.1656 | -0.0024584
195 |  | 13.4371 | 48.2501 | 4187 | 0.00085761 | 6.1672 | 6.1681 | -2.8664 | 1166.032 | 9455.4156 | -0.0024583
196 |  | 13.4371 | 48.2476 | 4187 | 0.00085757 | 6.1681 | 6.1689 | -2.8664 | 1166.0914 | 9503.6632 | -0.0024582
197 |  | 13.4371 | 48.2451 | 4187 | 0.00085752 | 6.1689 | 6.1698 | -2.8664 | 1166.1508 | 9551.9084 | -0.002458
198 |  | 13.4371 | 48.2427 | 4187 | 0.00085748 | 6.1698 | 6.1706 | -2.8664 | 1166.2102 | 9600.1511 | -0.0024579
199 |  | 13.4371 | 48.2402 | 4187 | 0.00085743 | 6.1706 | 6.1715 | -2.8664 | 1166.2696 | 9648.3913 | -0.0024578
200 |  | 13.4371 | 48.2378 | 4187 | 0.00085739 | 6.1715 | 6.1724 | -2.8664 | 1166.329 | 9696.6291 | -0.0024577
201 |  | 13.4371 | 48.2353 | 4187 | 0.00085735 | 6.1724 | 6.1732 | -2.8664 | 1166.3885 | 9744.8644 | -0.0024575
202 |  | 13.4371 | 48.2329 | 4187 | 0.0008573 | 6.1732 | 6.1741 | -2.8664 | 1166.4479 | 9793.0972 | -0.0024574
203 |  | 13.4371 | 48.2304 | 4187 | 0.00085726 | 6.1741 | 6.1749 | -2.8664 | 1166.5073 | 9841.3276 | -0.0024573
204 |  | 13.4371 | 48.2279 | 4187 | 0.00085722 | 6.1749 | 6.1758 | -2.8664 | 1166.5668 | 9889.5556 | -0.0024572
205 |  | 13.4371 | 48.2255 | 4187 | 0.00085717 | 6.1758 | 6.1766 | -2.8664 | 1166.6262 | 9937.7811 | -0.002457
206 |  | 13.4371 | 48.223 | 4187 | 0.00085713 | 6.1766 | 6.1775 | -2.8664 | 1166.6856 | 9986.0041 | -0.0024569
207 |  | 13.4371 | 48.2206 | 4187 | 0.00085709 | 6.1775 | 6.1784 | -2.8664 | 1166.7451 | 10034.2247 | -0.0024568
208 |  | 13.4371 | 48.2181 | 4187 | 0.00085704 | 6.1784 | 6.1792 | -2.8664 | 1166.8045 | 10082.4428 | -0.0024567
209 |  | 13.4371 | 48.2157 | 4187 | 0.000857 | 6.1792 | 6.1801 | -2.8664 | 1166.864 | 10130.6584 | -0.0024565
210 |  | 13.4371 | 48.2132 | 4187 | 0.00085695 | 6.1801 | 6.1809 | -2.8664 | 1166.9234 | 10178.8716 | -0.0024564
211 |  | 13.4371 | 48.2107 | 4187 | 0.00085691 | 6.1809 | 6.1818 | -2.8664 | 1166.9829 | 10227.0824 | -0.0024563
212 |  | 13.4371 | 48.2083 | 4187 | 0.00085687 | 6.1818 | 6.1826 | -2.8664 | 1167.0424 | 10275.2907 | -0.0024562
213 |  | 13.4371 | 48.2058 | 4187 | 0.00085682 | 6.1826 | 6.1835 | -2.8664 | 1167.1018 | 10323.4965 | -0.002456
214 |  | 13.4371 | 48.2034 | 4187 | 0.00085678 | 6.1835 | 6.1843 | -2.8664 | 1167.1613 | 10371.6999 | -0.0024559
215 |  | 13.4371 | 48.2009 | 4187 | 0.00085674 | 6.1843 | 6.1852 | -2.8664 | 1167.2208 | 10419.9008 | -0.0024558
216 |  | 13.4371 | 48.1985 | 4187 | 0.00085669 | 6.1852 | 6.1861 | -2.8664 | 1167.2802 | 10468.0993 | -0.0024557
217 |  | 13.4371 | 48.196 | 4187 | 0.00085665 | 6.1861 | 6.1869 | -2.8664 | 1167.3397 | 10516.2953 | -0.0024555
218 |  | 13.4371 | 48.1936 | 4187 | 0.00085661 | 6.1869 | 6.1878 | -2.8664 | 1167.3992 | 10564.4888 | -0.0024554
219 |  | 13.4371 | 48.1911 | 4187 | 0.00085656 | 6.1878 | 6.1886 | -2.8664 | 1167.4587 | 10612.6799 | -0.0024553
220 |  | 13.4371 | 48.1886 | 4187 | 0.00085652 | 6.1886 | 6.1895 | -2.8664 | 1167.5181 | 10660.8686 | -0.0024551
221 |  | 13.4371 | 48.1862 | 4187 | 0.00085647 | 6.1895 | 6.1903 | -2.8664 | 1167.5776 | 10709.0547 | -0.002455
222 |  | 13.4371 | 48.1837 | 4187 | 0.00085643 | 6.1903 | 6.1912 | -2.8664 | 1167.6371 | 10757.2385 | -0.0024549
223 |  | 13.4371 | 48.1813 | 4187 | 0.00085639 | 6.1912 | 6.1921 | -2.8664 | 1167.6966 | 10805.4198 | -0.0024548
224 |  | 13.4371 | 48.1788 | 4187 | 0.00085634 | 6.1921 | 6.1929 | -2.8664 | 1167.7561 | 10853.5986 | -0.0024546
225 |  | 13.4371 | 48.1764 | 4187 | 0.0008563 | 6.1929 | 6.1938 | -2.8664 | 1167.8156 | 10901.7749 | -0.0024545
226 |  | 13.4371 | 48.1739 | 4187 | 0.00085626 | 6.1938 | 6.1946 | -2.8664 | 1167.8751 | 10949.9489 | -0.0024544
227 |  | 13.4371 | 48.1715 | 4187 | 0.00085621 | 6.1946 | 6.1955 | -2.8664 | 1167.9346 | 10998.1203 | -0.0024543
228 |  | 13.4371 | 48.169 | 4187 | 0.00085617 | 6.1955 | 6.1963 | -2.8664 | 1167.9941 | 11046.2893 | -0.0024541
229 |  | 13.4371 | 48.1666 | 4187 | 0.00085613 | 6.1963 | 6.1972 | -2.8664 | 1168.0536 | 11094.4559 | -0.002454
230 |  | 13.4371 | 48.1641 | 4187 | 0.00085608 | 6.1972 | 6.1981 | -2.8664 | 1168.1131 | 11142.62 | -0.0024539
231 |  | 13.4371 | 48.1616 | 4187 | 0.00085604 | 6.1981 | 6.1989 | -2.8664 | 1168.1727 | 11190.7816 | -0.0024538
232 |  | 13.4371 | 48.1592 | 4187 | 0.00085599 | 6.1989 | 6.1998 | -2.8664 | 1168.2322 | 11238.9408 | -0.0024536
233 |  | 13.4371 | 48.1567 | 4187 | 0.00085595 | 6.1998 | 6.2006 | -2.8664 | 1168.2917 | 11287.0975 | -0.0024535
234 |  | 13.4371 | 48.1543 | 4187 | 0.00085591 | 6.2006 | 6.2015 | -2.8664 | 1168.3512 | 11335.2518 | -0.0024534
235 |  | 13.4371 | 48.1518 | 4187 | 0.00085586 | 6.2015 | 6.2023 | -2.8664 | 1168.4108 | 11383.4036 | -0.0024533
236 |  | 13.4371 | 48.1494 | 4187 | 0.00085582 | 6.2023 | 6.2032 | -2.8664 | 1168.4703 | 11431.553 | -0.0024531

## 200
|  |  | buis | verlies W/M | L /°C/sec
diam | wandikte |  | inhoud l/m |  | W/M
200 | 18.2 | 3.1416 | 21.0212 | 52.926 | 4187
[8 empty] | J/sec/mtr | aantal mtr. | verlies
|  | buis | verlies W/M | L /°C/sec | verlies temp | begintemp | eindtemp | verlies | bij 1°C | totaal J/sec
|  | inhoud L |  | W/M | °C per M | °C | °C | per m°C | daling | aantal mtr
1 | 200 | 21.0212 | 52.926 | 4187 | 0.00060133 | 6 | 6.0006 | -3.1133 | 1662.9932 | 52.926 | -0.0018721
2 |  | 21.0212 | 52.9241 | 4187 | 0.0006013 | 6.0006 | 6.0012 | -3.1133 | 1663.052 | 105.8501 | -0.001872
3 |  | 21.0212 | 52.9222 | 4187 | 0.00060128 | 6.0012 | 6.0018 | -3.1133 | 1663.1108 | 158.7723 | -0.001872
4 |  | 21.0212 | 52.9204 | 4187 | 0.00060126 | 6.0018 | 6.0024 | -3.1133 | 1663.1696 | 211.6927 | -0.0018719
5 |  | 21.0212 | 52.9185 | 4187 | 0.00060124 | 6.0024 | 6.003 | -3.1133 | 1663.2285 | 264.6112 | -0.0018718
6 |  | 21.0212 | 52.9166 | 4187 | 0.00060122 | 6.003 | 6.0036 | -3.1133 | 1663.2873 | 317.5279 | -0.0018718
7 |  | 21.0212 | 52.9148 | 4187 | 0.0006012 | 6.0036 | 6.0042 | -3.1133 | 1663.3461 | 370.4426 | -0.0018717
8 |  | 21.0212 | 52.9129 | 4187 | 0.00060118 | 6.0042 | 6.0048 | -3.1133 | 1663.405 | 423.3555 | -0.0018716
9 |  | 21.0212 | 52.911 | 4187 | 0.00060116 | 6.0048 | 6.0054 | -3.1133 | 1663.4638 | 476.2665 | -0.0018716
10 |  | 21.0212 | 52.9091 | 4187 | 0.00060113 | 6.0054 | 6.006 | -3.1133 | 1663.5227 | 529.1756 | -0.0018715
11 |  | 21.0212 | 52.9073 | 4187 | 0.00060111 | 6.006 | 6.0066 | -3.1133 | 1663.5815 | 582.0829 | -0.0018714
12 |  | 21.0212 | 52.9054 | 4187 | 0.00060109 | 6.0066 | 6.0072 | -3.1133 | 1663.6404 | 634.9883 | -0.0018714
13 |  | 21.0212 | 52.9035 | 4187 | 0.00060107 | 6.0072 | 6.0078 | -3.1133 | 1663.6992 | 687.8918 | -0.0018713
14 |  | 21.0212 | 52.9017 | 4187 | 0.00060105 | 6.0078 | 6.0084 | -3.1133 | 1663.7581 | 740.7935 | -0.0018712
15 |  | 21.0212 | 52.8998 | 4187 | 0.00060103 | 6.0084 | 6.009 | -3.1133 | 1663.8169 | 793.6933 | -0.0018712
16 |  | 21.0212 | 52.8979 | 4187 | 0.00060101 | 6.009 | 6.0096 | -3.1133 | 1663.8758 | 846.5912 | -0.0018711
17 |  | 21.0212 | 52.896 | 4187 | 0.00060099 | 6.0096 | 6.0102 | -3.1133 | 1663.9346 | 899.4872 | -0.001871
18 |  | 21.0212 | 52.8942 | 4187 | 0.00060096 | 6.0102 | 6.0108 | -3.1133 | 1663.9935 | 952.3814 | -0.001871
19 |  | 21.0212 | 52.8923 | 4187 | 0.00060094 | 6.0108 | 6.0114 | -3.1133 | 1664.0523 | 1005.2737 | -0.0018709
20 |  | 21.0212 | 52.8904 | 4187 | 0.00060092 | 6.0114 | 6.012 | -3.1133 | 1664.1112 | 1058.1641 | -0.0018708
21 |  | 21.0212 | 52.8886 | 4187 | 0.0006009 | 6.012 | 6.0126 | -3.1133 | 1664.1701 | 1111.0527 | -0.0018708
22 |  | 21.0212 | 52.8867 | 4187 | 0.00060088 | 6.0126 | 6.0132 | -3.1133 | 1664.2289 | 1163.9394 | -0.0018707
23 |  | 21.0212 | 52.8848 | 4187 | 0.00060086 | 6.0132 | 6.0138 | -3.1133 | 1664.2878 | 1216.8242 | -0.0018706
24 |  | 21.0212 | 52.8829 | 4187 | 0.00060084 | 6.0138 | 6.0144 | -3.1133 | 1664.3467 | 1269.7072 | -0.0018706
25 |  | 21.0212 | 52.8811 | 4187 | 0.00060082 | 6.0144 | 6.015 | -3.1133 | 1664.4055 | 1322.5882 | -0.0018705
26 |  | 21.0212 | 52.8792 | 4187 | 0.00060079 | 6.015 | 6.0156 | -3.1133 | 1664.4644 | 1375.4674 | -0.0018704
27 |  | 21.0212 | 52.8773 | 4187 | 0.00060077 | 6.0156 | 6.0162 | -3.1133 | 1664.5233 | 1428.3448 | -0.0018704
28 |  | 21.0212 | 52.8755 | 4187 | 0.00060075 | 6.0162 | 6.0168 | -3.1133 | 1664.5822 | 1481.2202 | -0.0018703
29 |  | 21.0212 | 52.8736 | 4187 | 0.00060073 | 6.0168 | 6.0174 | -3.1133 | 1664.6411 | 1534.0938 | -0.0018702
30 |  | 21.0212 | 52.8717 | 4187 | 0.00060071 | 6.0174 | 6.018 | -3.1133 | 1664.6999 | 1586.9656 | -0.0018702
31 |  | 21.0212 | 52.8699 | 4187 | 0.00060069 | 6.018 | 6.0186 | -3.1133 | 1664.7588 | 1639.8354 | -0.0018701
32 |  | 21.0212 | 52.868 | 4187 | 0.00060067 | 6.0186 | 6.0192 | -3.1133 | 1664.8177 | 1692.7034 | -0.0018701
33 |  | 21.0212 | 52.8661 | 4187 | 0.00060065 | 6.0192 | 6.0198 | -3.1133 | 1664.8766 | 1745.5695 | -0.00187
34 |  | 21.0212 | 52.8642 | 4187 | 0.00060062 | 6.0198 | 6.0204 | -3.1133 | 1664.9355 | 1798.4338 | -0.0018699
35 |  | 21.0212 | 52.8624 | 4187 | 0.0006006 | 6.0204 | 6.021 | -3.1133 | 1664.9944 | 1851.2961 | -0.0018699
36 |  | 21.0212 | 52.8605 | 4187 | 0.00060058 | 6.021 | 6.0216 | -3.1133 | 1665.0533 | 1904.1566 | -0.0018698
37 |  | 21.0212 | 52.8586 | 4187 | 0.00060056 | 6.0216 | 6.0222 | -3.1133 | 1665.1122 | 1957.0153 | -0.0018697
38 |  | 21.0212 | 52.8568 | 4187 | 0.00060054 | 6.0222 | 6.0228 | -3.1133 | 1665.1711 | 2009.872 | -0.0018697
39 |  | 21.0212 | 52.8549 | 4187 | 0.00060052 | 6.0228 | 6.0234 | -3.1133 | 1665.23 | 2062.7269 | -0.0018696
40 |  | 21.0212 | 52.853 | 4187 | 0.0006005 | 6.0234 | 6.024 | -3.1133 | 1665.2889 | 2115.58 | -0.0018695
41 |  | 21.0212 | 52.8512 | 4187 | 0.00060048 | 6.024 | 6.0246 | -3.1133 | 1665.3478 | 2168.4311 | -0.0018695
42 |  | 21.0212 | 52.8493 | 4187 | 0.00060045 | 6.0246 | 6.0252 | -3.1133 | 1665.4067 | 2221.2804 | -0.0018694
43 |  | 21.0212 | 52.8474 | 4187 | 0.00060043 | 6.0252 | 6.0258 | -3.1133 | 1665.4656 | 2274.1278 | -0.0018693
44 |  | 21.0212 | 52.8455 | 4187 | 0.00060041 | 6.0258 | 6.0264 | -3.1133 | 1665.5245 | 2326.9734 | -0.0018693
45 |  | 21.0212 | 52.8437 | 4187 | 0.00060039 | 6.0264 | 6.027 | -3.1133 | 1665.5835 | 2379.817 | -0.0018692
46 |  | 21.0212 | 52.8418 | 4187 | 0.00060037 | 6.027 | 6.0276 | -3.1133 | 1665.6424 | 2432.6589 | -0.0018691
47 |  | 21.0212 | 52.8399 | 4187 | 0.00060035 | 6.0276 | 6.0282 | -3.1133 | 1665.7013 | 2485.4988 | -0.0018691
48 |  | 21.0212 | 52.8381 | 4187 | 0.00060033 | 6.0282 | 6.0288 | -3.1133 | 1665.7602 | 2538.3369 | -0.001869
49 |  | 21.0212 | 52.8362 | 4187 | 0.00060031 | 6.0288 | 6.0294 | -3.1133 | 1665.8191 | 2591.1731 | -0.0018689
50 |  | 21.0212 | 52.8343 | 4187 | 0.00060028 | 6.0294 | 6.03 | -3.1133 | 1665.8781 | 2644.0074 | -0.0018689
51 |  | 21.0212 | 52.8325 | 4187 | 0.00060026 | 6.03 | 6.0306 | -3.1133 | 1665.937 | 2696.8399 | -0.0018688
52 |  | 21.0212 | 52.8306 | 4187 | 0.00060024 | 6.0306 | 6.0312 | -3.1133 | 1665.9959 | 2749.6705 | -0.0018687
53 |  | 21.0212 | 52.8287 | 4187 | 0.00060022 | 6.0312 | 6.0318 | -3.1133 | 1666.0548 | 2802.4992 | -0.0018687
54 |  | 21.0212 | 52.8269 | 4187 | 0.0006002 | 6.0318 | 6.0324 | -3.1133 | 1666.1138 | 2855.3261 | -0.0018686
55 |  | 21.0212 | 52.825 | 4187 | 0.00060018 | 6.0324 | 6.033 | -3.1133 | 1666.1727 | 2908.151 | -0.0018685
56 |  | 21.0212 | 52.8231 | 4187 | 0.00060016 | 6.033 | 6.0336 | -3.1133 | 1666.2317 | 2960.9742 | -0.0018685
57 |  | 21.0212 | 52.8213 | 4187 | 0.00060014 | 6.0336 | 6.0342 | -3.1133 | 1666.2906 | 3013.7954 | -0.0018684
58 |  | 21.0212 | 52.8194 | 4187 | 0.00060011 | 6.0342 | 6.0348 | -3.1133 | 1666.3495 | 3066.6148 | -0.0018683
59 |  | 21.0212 | 52.8175 | 4187 | 0.00060009 | 6.0348 | 6.0354 | -3.1133 | 1666.4085 | 3119.4323 | -0.0018683
60 |  | 21.0212 | 52.8156 | 4187 | 0.00060007 | 6.0354 | 6.036 | -3.1133 | 1666.4674 | 3172.248 | -0.0018682
61 |  | 21.0212 | 52.8138 | 4187 | 0.00060005 | 6.036 | 6.0366 | -3.1133 | 1666.5264 | 3225.0617 | -0.0018681
62 |  | 21.0212 | 52.8119 | 4187 | 0.00060003 | 6.0366 | 6.0372 | -3.1133 | 1666.5853 | 3277.8737 | -0.0018681
63 |  | 21.0212 | 52.81 | 4187 | 0.00060001 | 6.0372 | 6.0378 | -3.1133 | 1666.6443 | 3330.6837 | -0.001868
64 |  | 21.0212 | 52.8082 | 4187 | 0.00059999 | 6.0378 | 6.0384 | -3.1133 | 1666.7032 | 3383.4919 | -0.0018679
65 |  | 21.0212 | 52.8063 | 4187 | 0.00059997 | 6.0384 | 6.039 | -3.1133 | 1666.7622 | 3436.2982 | -0.0018679
66 |  | 21.0212 | 52.8044 | 4187 | 0.00059994 | 6.039 | 6.0396 | -3.1133 | 1666.8212 | 3489.1026 | -0.0018678
67 |  | 21.0212 | 52.8026 | 4187 | 0.00059992 | 6.0396 | 6.0402 | -3.1133 | 1666.8801 | 3541.9052 | -0.0018677
68 |  | 21.0212 | 52.8007 | 4187 | 0.0005999 | 6.0402 | 6.0408 | -3.1133 | 1666.9391 | 3594.7059 | -0.0018677
69 |  | 21.0212 | 52.7988 | 4187 | 0.00059988 | 6.0408 | 6.0414 | -3.1133 | 1666.998 | 3647.5047 | -0.0018676
70 |  | 21.0212 | 52.797 | 4187 | 0.00059986 | 6.0414 | 6.042 | -3.1133 | 1667.057 | 3700.3017 | -0.0018675
71 |  | 21.0212 | 52.7951 | 4187 | 0.00059984 | 6.042 | 6.0426 | -3.1133 | 1667.116 | 3753.0968 | -0.0018675
72 |  | 21.0212 | 52.7932 | 4187 | 0.00059982 | 6.0426 | 6.0432 | -3.1133 | 1667.1749 | 3805.89 | -0.0018674
73 |  | 21.0212 | 52.7914 | 4187 | 0.0005998 | 6.0432 | 6.0438 | -3.1133 | 1667.2339 | 3858.6814 | -0.0018673
74 |  | 21.0212 | 52.7895 | 4187 | 0.00059977 | 6.0438 | 6.0444 | -3.1133 | 1667.2929 | 3911.4709 | -0.0018673
75 |  | 21.0212 | 52.7876 | 4187 | 0.00059975 | 6.0444 | 6.045 | -3.1133 | 1667.3519 | 3964.2585 | -0.0018672
76 |  | 21.0212 | 52.7858 | 4187 | 0.00059973 | 6.045 | 6.0456 | -3.1133 | 1667.4109 | 4017.0443 | -0.0018671
77 |  | 21.0212 | 52.7839 | 4187 | 0.00059971 | 6.0456 | 6.0462 | -3.1133 | 1667.4698 | 4069.8282 | -0.0018671
78 |  | 21.0212 | 52.782 | 4187 | 0.00059969 | 6.0462 | 6.0468 | -3.1133 | 1667.5288 | 4122.6102 | -0.001867
79 |  | 21.0212 | 52.7802 | 4187 | 0.00059967 | 6.0468 | 6.0474 | -3.1133 | 1667.5878 | 4175.3904 | -0.0018669
80 |  | 21.0212 | 52.7783 | 4187 | 0.00059965 | 6.0474 | 6.048 | -3.1133 | 1667.6468 | 4228.1687 | -0.0018669
81 |  | 21.0212 | 52.7764 | 4187 | 0.00059963 | 6.048 | 6.0486 | -3.1133 | 1667.7058 | 4280.9451 | -0.0018668
82 |  | 21.0212 | 52.7746 | 4187 | 0.0005996 | 6.0486 | 6.0492 | -3.1133 | 1667.7648 | 4333.7197 | -0.0018667
83 |  | 21.0212 | 52.7727 | 4187 | 0.00059958 | 6.0492 | 6.0498 | -3.1133 | 1667.8238 | 4386.4924 | -0.0018667
84 |  | 21.0212 | 52.7708 | 4187 | 0.00059956 | 6.0498 | 6.0504 | -3.1133 | 1667.8828 | 4439.2632 | -0.0018666
85 |  | 21.0212 | 52.769 | 4187 | 0.00059954 | 6.0504 | 6.051 | -3.1133 | 1667.9418 | 4492.0322 | -0.0018665
86 |  | 21.0212 | 52.7671 | 4187 | 0.00059952 | 6.051 | 6.0516 | -3.1133 | 1668.0008 | 4544.7993 | -0.0018665
87 |  | 21.0212 | 52.7652 | 4187 | 0.0005995 | 6.0516 | 6.0522 | -3.1133 | 1668.0598 | 4597.5645 | -0.0018664
88 |  | 21.0212 | 52.7634 | 4187 | 0.00059948 | 6.0522 | 6.0528 | -3.1133 | 1668.1188 | 4650.3279 | -0.0018663
89 |  | 21.0212 | 52.7615 | 4187 | 0.00059946 | 6.0528 | 6.0534 | -3.1133 | 1668.1778 | 4703.0894 | -0.0018663
90 |  | 21.0212 | 52.7596 | 4187 | 0.00059944 | 6.0534 | 6.054 | -3.1133 | 1668.2368 | 4755.849 | -0.0018662
91 |  | 21.0212 | 52.7578 | 4187 | 0.00059941 | 6.054 | 6.0546 | -3.1133 | 1668.2958 | 4808.6067 | -0.0018662
92 |  | 21.0212 | 52.7559 | 4187 | 0.00059939 | 6.0546 | 6.0552 | -3.1133 | 1668.3548 | 4861.3626 | -0.0018661
93 |  | 21.0212 | 52.754 | 4187 | 0.00059937 | 6.0552 | 6.0558 | -3.1133 | 1668.4138 | 4914.1167 | -0.001866
94 |  | 21.0212 | 52.7522 | 4187 | 0.00059935 | 6.0558 | 6.0564 | -3.1133 | 1668.4728 | 4966.8688 | -0.001866
95 |  | 21.0212 | 52.7503 | 4187 | 0.00059933 | 6.0564 | 6.057 | -3.1133 | 1668.5319 | 5019.6191 | -0.0018659
96 |  | 21.0212 | 52.7484 | 4187 | 0.00059931 | 6.057 | 6.0576 | -3.1133 | 1668.5909 | 5072.3676 | -0.0018658
97 |  | 21.0212 | 52.7466 | 4187 | 0.00059929 | 6.0576 | 6.0582 | -3.1133 | 1668.6499 | 5125.1141 | -0.0018658
98 |  | 21.0212 | 52.7447 | 4187 | 0.00059927 | 6.0582 | 6.0588 | -3.1133 | 1668.7089 | 5177.8588 | -0.0018657
99 |  | 21.0212 | 52.7428 | 4187 | 0.00059924 | 6.0588 | 6.0594 | -3.1133 | 1668.768 | 5230.6017 | -0.0018656
100 |  | 21.0212 | 52.741 | 4187 | 0.00059922 | 6.0594 | 6.06 | -3.1133 | 1668.827 | 5283.3427 | -0.0018656
101 |  | 21.0212 | 52.7391 | 4187 | 0.0005992 | 6.06 | 6.0606 | -3.1133 | 1668.886 | 5336.0818 | -0.0018655
102 |  | 21.0212 | 52.7372 | 4187 | 0.00059918 | 6.0606 | 6.0612 | -3.1133 | 1668.9451 | 5388.819 | -0.0018654
103 |  | 21.0212 | 52.7354 | 4187 | 0.00059916 | 6.0612 | 6.0618 | -3.1133 | 1669.0041 | 5441.5544 | -0.0018654
104 |  | 21.0212 | 52.7335 | 4187 | 0.00059914 | 6.0618 | 6.0624 | -3.1133 | 1669.0631 | 5494.2879 | -0.0018653
105 |  | 21.0212 | 52.7316 | 4187 | 0.00059912 | 6.0624 | 6.063 | -3.1133 | 1669.1222 | 5547.0195 | -0.0018652
106 |  | 21.0212 | 52.7298 | 4187 | 0.0005991 | 6.063 | 6.0636 | -3.1133 | 1669.1812 | 5599.7493 | -0.0018652
107 |  | 21.0212 | 52.7279 | 4187 | 0.00059907 | 6.0636 | 6.0642 | -3.1133 | 1669.2403 | 5652.4772 | -0.0018651
108 |  | 21.0212 | 52.726 | 4187 | 0.00059905 | 6.0642 | 6.0648 | -3.1133 | 1669.2993 | 5705.2033 | -0.001865
109 |  | 21.0212 | 52.7242 | 4187 | 0.00059903 | 6.0648 | 6.0654 | -3.1133 | 1669.3584 | 5757.9275 | -0.001865
110 |  | 21.0212 | 52.7223 | 4187 | 0.00059901 | 6.0654 | 6.066 | -3.1133 | 1669.4174 | 5810.6498 | -0.0018649
111 |  | 21.0212 | 52.7205 | 4187 | 0.00059899 | 6.066 | 6.0666 | -3.1133 | 1669.4765 | 5863.3702 | -0.0018648
112 |  | 21.0212 | 52.7186 | 4187 | 0.00059897 | 6.0666 | 6.0672 | -3.1133 | 1669.5355 | 5916.0888 | -0.0018648
113 |  | 21.0212 | 52.7167 | 4187 | 0.00059895 | 6.0672 | 6.0678 | -3.1133 | 1669.5946 | 5968.8055 | -0.0018647
114 |  | 21.0212 | 52.7149 | 4187 | 0.00059893 | 6.0678 | 6.0684 | -3.1133 | 1669.6536 | 6021.5204 | -0.0018646
115 |  | 21.0212 | 52.713 | 4187 | 0.00059891 | 6.0684 | 6.069 | -3.1133 | 1669.7127 | 6074.2334 | -0.0018646
116 |  | 21.0212 | 52.7111 | 4187 | 0.00059888 | 6.069 | 6.0696 | -3.1133 | 1669.7718 | 6126.9445 | -0.0018645
117 |  | 21.0212 | 52.7093 | 4187 | 0.00059886 | 6.0696 | 6.0702 | -3.1133 | 1669.8308 | 6179.6538 | -0.0018644
118 |  | 21.0212 | 52.7074 | 4187 | 0.00059884 | 6.0702 | 6.0708 | -3.1133 | 1669.8899 | 6232.3612 | -0.0018644
119 |  | 21.0212 | 52.7055 | 4187 | 0.00059882 | 6.0708 | 6.0714 | -3.1133 | 1669.949 | 6285.0667 | -0.0018643
120 |  | 21.0212 | 52.7037 | 4187 | 0.0005988 | 6.0714 | 6.072 | -3.1133 | 1670.008 | 6337.7704 | -0.0018642
121 |  | 21.0212 | 52.7018 | 4187 | 0.00059878 | 6.072 | 6.0726 | -3.1133 | 1670.0671 | 6390.4722 | -0.0018642
122 |  | 21.0212 | 52.6999 | 4187 | 0.00059876 | 6.0726 | 6.0732 | -3.1133 | 1670.1262 | 6443.1722 | -0.0018641
123 |  | 21.0212 | 52.6981 | 4187 | 0.00059874 | 6.0732 | 6.0738 | -3.1133 | 1670.1853 | 6495.8702 | -0.001864
124 |  | 21.0212 | 52.6962 | 4187 | 0.00059871 | 6.0738 | 6.0744 | -3.1133 | 1670.2443 | 6548.5665 | -0.001864
125 |  | 21.0212 | 52.6944 | 4187 | 0.00059869 | 6.0744 | 6.075 | -3.1133 | 1670.3034 | 6601.2608 | -0.0018639
126 |  | 21.0212 | 52.6925 | 4187 | 0.00059867 | 6.075 | 6.0756 | -3.1133 | 1670.3625 | 6653.9533 | -0.0018638
127 |  | 21.0212 | 52.6906 | 4187 | 0.00059865 | 6.0756 | 6.0762 | -3.1133 | 1670.4216 | 6706.6439 | -0.0018638
128 |  | 21.0212 | 52.6888 | 4187 | 0.00059863 | 6.0762 | 6.0768 | -3.1133 | 1670.4807 | 6759.3327 | -0.0018637
129 |  | 21.0212 | 52.6869 | 4187 | 0.00059861 | 6.0768 | 6.0774 | -3.1133 | 1670.5398 | 6812.0196 | -0.0018636
130 |  | 21.0212 | 52.685 | 4187 | 0.00059859 | 6.0774 | 6.078 | -3.1133 | 1670.5989 | 6864.7046 | -0.0018636
131 |  | 21.0212 | 52.6832 | 4187 | 0.00059857 | 6.078 | 6.0786 | -3.1133 | 1670.658 | 6917.3878 | -0.0018635
132 |  | 21.0212 | 52.6813 | 4187 | 0.00059855 | 6.0786 | 6.0792 | -3.1133 | 1670.7171 | 6970.0691 | -0.0018634
133 |  | 21.0212 | 52.6794 | 4187 | 0.00059852 | 6.0792 | 6.0798 | -3.1133 | 1670.7762 | 7022.7485 | -0.0018634
134 |  | 21.0212 | 52.6776 | 4187 | 0.0005985 | 6.0798 | 6.0804 | -3.1133 | 1670.8353 | 7075.4261 | -0.0018633
135 |  | 21.0212 | 52.6757 | 4187 | 0.00059848 | 6.0804 | 6.081 | -3.1133 | 1670.8944 | 7128.1018 | -0.0018632
136 |  | 21.0212 | 52.6739 | 4187 | 0.00059846 | 6.081 | 6.0816 | -3.1133 | 1670.9535 | 7180.7757 | -0.0018632
137 |  | 21.0212 | 52.672 | 4187 | 0.00059844 | 6.0816 | 6.0822 | -3.1133 | 1671.0126 | 7233.4477 | -0.0018631
138 |  | 21.0212 | 52.6701 | 4187 | 0.00059842 | 6.0822 | 6.0828 | -3.1133 | 1671.0717 | 7286.1178 | -0.0018631
139 |  | 21.0212 | 52.6683 | 4187 | 0.0005984 | 6.0828 | 6.0834 | -3.1133 | 1671.1308 | 7338.7861 | -0.001863
140 |  | 21.0212 | 52.6664 | 4187 | 0.00059838 | 6.0834 | 6.084 | -3.1133 | 1671.1899 | 7391.4525 | -0.0018629
141 |  | 21.0212 | 52.6645 | 4187 | 0.00059835 | 6.084 | 6.0846 | -3.1133 | 1671.249 | 7444.117 | -0.0018629
142 |  | 21.0212 | 52.6627 | 4187 | 0.00059833 | 6.0846 | 6.0852 | -3.1133 | 1671.3081 | 7496.7797 | -0.0018628
143 |  | 21.0212 | 52.6608 | 4187 | 0.00059831 | 6.0852 | 6.0858 | -3.1133 | 1671.3673 | 7549.4405 | -0.0018627
144 |  | 21.0212 | 52.6589 | 4187 | 0.00059829 | 6.0858 | 6.0864 | -3.1133 | 1671.4264 | 7602.0994 | -0.0018627
145 |  | 21.0212 | 52.6571 | 4187 | 0.00059827 | 6.0864 | 6.087 | -3.1133 | 1671.4855 | 7654.7565 | -0.0018626
146 |  | 21.0212 | 52.6552 | 4187 | 0.00059825 | 6.087 | 6.0876 | -3.1133 | 1671.5446 | 7707.4117 | -0.0018625
147 |  | 21.0212 | 52.6534 | 4187 | 0.00059823 | 6.0876 | 6.0882 | -3.1133 | 1671.6038 | 7760.0651 | -0.0018625
148 |  | 21.0212 | 52.6515 | 4187 | 0.00059821 | 6.0882 | 6.0888 | -3.1133 | 1671.6629 | 7812.7166 | -0.0018624
149 |  | 21.0212 | 52.6496 | 4187 | 0.00059819 | 6.0888 | 6.0894 | -3.1133 | 1671.722 | 7865.3662 | -0.0018623
150 |  | 21.0212 | 52.6478 | 4187 | 0.00059816 | 6.0894 | 6.09 | -3.1133 | 1671.7812 | 7918.014 | -0.0018623
151 |  | 21.0212 | 52.6459 | 4187 | 0.00059814 | 6.09 | 6.0906 | -3.1133 | 1671.8403 | 7970.6599 | -0.0018622
152 |  | 21.0212 | 52.644 | 4187 | 0.00059812 | 6.0906 | 6.0912 | -3.1133 | 1671.8994 | 8023.304 | -0.0018621
153 |  | 21.0212 | 52.6422 | 4187 | 0.0005981 | 6.0912 | 6.0918 | -3.1133 | 1671.9586 | 8075.9462 | -0.0018621
154 |  | 21.0212 | 52.6403 | 4187 | 0.00059808 | 6.0918 | 6.0924 | -3.1133 | 1672.0177 | 8128.5865 | -0.001862
155 |  | 21.0212 | 52.6385 | 4187 | 0.00059806 | 6.0924 | 6.093 | -3.1133 | 1672.0769 | 8181.225 | -0.0018619
156 |  | 21.0212 | 52.6366 | 4187 | 0.00059804 | 6.093 | 6.0936 | -3.1133 | 1672.136 | 8233.8616 | -0.0018619
157 |  | 21.0212 | 52.6347 | 4187 | 0.00059802 | 6.0936 | 6.0941 | -3.1133 | 1672.1952 | 8286.4963 | -0.0018618
158 |  | 21.0212 | 52.6329 | 4187 | 0.000598 | 6.0941 | 6.0947 | -3.1133 | 1672.2543 | 8339.1292 | -0.0018617
159 |  | 21.0212 | 52.631 | 4187 | 0.00059797 | 6.0947 | 6.0953 | -3.1133 | 1672.3135 | 8391.7602 | -0.0018617
160 |  | 21.0212 | 52.6292 | 4187 | 0.00059795 | 6.0953 | 6.0959 | -3.1133 | 1672.3726 | 8444.3893 | -0.0018616
161 |  | 21.0212 | 52.6273 | 4187 | 0.00059793 | 6.0959 | 6.0965 | -3.1133 | 1672.4318 | 8497.0166 | -0.0018615
162 |  | 21.0212 | 52.6254 | 4187 | 0.00059791 | 6.0965 | 6.0971 | -3.1133 | 1672.4909 | 8549.6421 | -0.0018615
163 |  | 21.0212 | 52.6236 | 4187 | 0.00059789 | 6.0971 | 6.0977 | -3.1133 | 1672.5501 | 8602.2656 | -0.0018614
164 |  | 21.0212 | 52.6217 | 4187 | 0.00059787 | 6.0977 | 6.0983 | -3.1133 | 1672.6093 | 8654.8873 | -0.0018613
165 |  | 21.0212 | 52.6198 | 4187 | 0.00059785 | 6.0983 | 6.0989 | -3.1133 | 1672.6684 | 8707.5072 | -0.0018613
166 |  | 21.0212 | 52.618 | 4187 | 0.00059783 | 6.0989 | 6.0995 | -3.1133 | 1672.7276 | 8760.1252 | -0.0018612
167 |  | 21.0212 | 52.6161 | 4187 | 0.0005978 | 6.0995 | 6.1001 | -3.1133 | 1672.7868 | 8812.7413 | -0.0018611
168 |  | 21.0212 | 52.6143 | 4187 | 0.00059778 | 6.1001 | 6.1007 | -3.1133 | 1672.8459 | 8865.3556 | -0.0018611
169 |  | 21.0212 | 52.6124 | 4187 | 0.00059776 | 6.1007 | 6.1013 | -3.1133 | 1672.9051 | 8917.968 | -0.001861
170 |  | 21.0212 | 52.6105 | 4187 | 0.00059774 | 6.1013 | 6.1019 | -3.1133 | 1672.9643 | 8970.5785 | -0.0018609
171 |  | 21.0212 | 52.6087 | 4187 | 0.00059772 | 6.1019 | 6.1025 | -3.1133 | 1673.0235 | 9023.1872 | -0.0018609
172 |  | 21.0212 | 52.6068 | 4187 | 0.0005977 | 6.1025 | 6.1031 | -3.1133 | 1673.0826 | 9075.794 | -0.0018608
173 |  | 21.0212 | 52.605 | 4187 | 0.00059768 | 6.1031 | 6.1037 | -3.1133 | 1673.1418 | 9128.399 | -0.0018607
174 |  | 21.0212 | 52.6031 | 4187 | 0.00059766 | 6.1037 | 6.1043 | -3.1133 | 1673.201 | 9181.0021 | -0.0018607
175 |  | 21.0212 | 52.6012 | 4187 | 0.00059764 | 6.1043 | 6.1049 | -3.1133 | 1673.2602 | 9233.6033 | -0.0018606
176 |  | 21.0212 | 52.5994 | 4187 | 0.00059761 | 6.1049 | 6.1055 | -3.1133 | 1673.3194 | 9286.2027 | -0.0018605
177 |  | 21.0212 | 52.5975 | 4187 | 0.00059759 | 6.1055 | 6.1061 | -3.1133 | 1673.3786 | 9338.8002 | -0.0018605
178 |  | 21.0212 | 52.5957 | 4187 | 0.00059757 | 6.1061 | 6.1067 | -3.1133 | 1673.4378 | 9391.3959 | -0.0018604
179 |  | 21.0212 | 52.5938 | 4187 | 0.00059755 | 6.1067 | 6.1073 | -3.1133 | 1673.497 | 9443.9897 | -0.0018604
180 |  | 21.0212 | 52.5919 | 4187 | 0.00059753 | 6.1073 | 6.1079 | -3.1133 | 1673.5562 | 9496.5816 | -0.0018603
181 |  | 21.0212 | 52.5901 | 4187 | 0.00059751 | 6.1079 | 6.1085 | -3.1133 | 1673.6154 | 9549.1717 | -0.0018602
182 |  | 21.0212 | 52.5882 | 4187 | 0.00059749 | 6.1085 | 6.1091 | -3.1133 | 1673.6746 | 9601.7599 | -0.0018602
183 |  | 21.0212 | 52.5864 | 4187 | 0.00059747 | 6.1091 | 6.1097 | -3.1133 | 1673.7338 | 9654.3462 | -0.0018601
184 |  | 21.0212 | 52.5845 | 4187 | 0.00059745 | 6.1097 | 6.1103 | -3.1133 | 1673.793 | 9706.9307 | -0.00186
185 |  | 21.0212 | 52.5826 | 4187 | 0.00059742 | 6.1103 | 6.1109 | -3.1133 | 1673.8522 | 9759.5134 | -0.00186
186 |  | 21.0212 | 52.5808 | 4187 | 0.0005974 | 6.1109 | 6.1115 | -3.1133 | 1673.9114 | 9812.0941 | -0.0018599
187 |  | 21.0212 | 52.5789 | 4187 | 0.00059738 | 6.1115 | 6.1121 | -3.1133 | 1673.9706 | 9864.673 | -0.0018598
188 |  | 21.0212 | 52.5771 | 4187 | 0.00059736 | 6.1121 | 6.1127 | -3.1133 | 1674.0298 | 9917.2501 | -0.0018598
189 |  | 21.0212 | 52.5752 | 4187 | 0.00059734 | 6.1127 | 6.1133 | -3.1133 | 1674.089 | 9969.8253 | -0.0018597
190 |  | 21.0212 | 52.5733 | 4187 | 0.00059732 | 6.1133 | 6.1139 | -3.1133 | 1674.1482 | 10022.3986 | -0.0018596
191 |  | 21.0212 | 52.5715 | 4187 | 0.0005973 | 6.1139 | 6.1145 | -3.1133 | 1674.2075 | 10074.9701 | -0.0018596
192 |  | 21.0212 | 52.5696 | 4187 | 0.00059728 | 6.1145 | 6.1151 | -3.1133 | 1674.2667 | 10127.5397 | -0.0018595
193 |  | 21.0212 | 52.5678 | 4187 | 0.00059726 | 6.1151 | 6.1157 | -3.1133 | 1674.3259 | 10180.1075 | -0.0018594
194 |  | 21.0212 | 52.5659 | 4187 | 0.00059723 | 6.1157 | 6.1163 | -3.1133 | 1674.3851 | 10232.6734 | -0.0018594
195 |  | 21.0212 | 52.564 | 4187 | 0.00059721 | 6.1163 | 6.1169 | -3.1133 | 1674.4444 | 10285.2374 | -0.0018593
196 |  | 21.0212 | 52.5622 | 4187 | 0.00059719 | 6.1169 | 6.1175 | -3.1133 | 1674.5036 | 10337.7996 | -0.0018592
197 |  | 21.0212 | 52.5603 | 4187 | 0.00059717 | 6.1175 | 6.1181 | -3.1133 | 1674.5628 | 10390.3599 | -0.0018592
198 |  | 21.0212 | 52.5585 | 4187 | 0.00059715 | 6.1181 | 6.1186 | -3.1133 | 1674.6221 | 10442.9184 | -0.0018591
199 |  | 21.0212 | 52.5566 | 4187 | 0.00059713 | 6.1186 | 6.1192 | -3.1133 | 1674.6813 | 10495.475 | -0.001859
200 |  | 21.0212 | 52.5547 | 4187 | 0.00059711 | 6.1192 | 6.1198 | -3.1133 | 1674.7405 | 10548.0297 | -0.001859
201 |  | 21.0212 | 52.5529 | 4187 | 0.00059709 | 6.1198 | 6.1204 | -3.1133 | 1674.7998 | 10600.5826 | -0.0018589
202 |  | 21.0212 | 52.551 | 4187 | 0.00059707 | 6.1204 | 6.121 | -3.1133 | 1674.859 | 10653.1336 | -0.0018588
203 |  | 21.0212 | 52.5492 | 4187 | 0.00059704 | 6.121 | 6.1216 | -3.1133 | 1674.9183 | 10705.6828 | -0.0018588
204 |  | 21.0212 | 52.5473 | 4187 | 0.00059702 | 6.1216 | 6.1222 | -3.1133 | 1674.9775 | 10758.2301 | -0.0018587
205 |  | 21.0212 | 52.5454 | 4187 | 0.000597 | 6.1222 | 6.1228 | -3.1133 | 1675.0368 | 10810.7755 | -0.0018586
206 |  | 21.0212 | 52.5436 | 4187 | 0.00059698 | 6.1228 | 6.1234 | -3.1133 | 1675.096 | 10863.3191 | -0.0018586
207 |  | 21.0212 | 52.5417 | 4187 | 0.00059696 | 6.1234 | 6.124 | -3.1133 | 1675.1553 | 10915.8609 | -0.0018585
208 |  | 21.0212 | 52.5399 | 4187 | 0.00059694 | 6.124 | 6.1246 | -3.1133 | 1675.2145 | 10968.4007 | -0.0018584
209 |  | 21.0212 | 52.538 | 4187 | 0.00059692 | 6.1246 | 6.1252 | -3.1133 | 1675.2738 | 11020.9387 | -0.0018584
210 |  | 21.0212 | 52.5362 | 4187 | 0.0005969 | 6.1252 | 6.1258 | -3.1133 | 1675.333 | 11073.4749 | -0.0018583
211 |  | 21.0212 | 52.5343 | 4187 | 0.00059688 | 6.1258 | 6.1264 | -3.1133 | 1675.3923 | 11126.0092 | -0.0018582
212 |  | 21.0212 | 52.5324 | 4187 | 0.00059685 | 6.1264 | 6.127 | -3.1133 | 1675.4516 | 11178.5416 | -0.0018582
213 |  | 21.0212 | 52.5306 | 4187 | 0.00059683 | 6.127 | 6.1276 | -3.1133 | 1675.5108 | 11231.0722 | -0.0018581
214 |  | 21.0212 | 52.5287 | 4187 | 0.00059681 | 6.1276 | 6.1282 | -3.1133 | 1675.5701 | 11283.6009 | -0.0018581
215 |  | 21.0212 | 52.5269 | 4187 | 0.00059679 | 6.1282 | 6.1288 | -3.1133 | 1675.6294 | 11336.1278 | -0.001858
216 |  | 21.0212 | 52.525 | 4187 | 0.00059677 | 6.1288 | 6.1294 | -3.1133 | 1675.6887 | 11388.6528 | -0.0018579
217 |  | 21.0212 | 52.5231 | 4187 | 0.00059675 | 6.1294 | 6.13 | -3.1133 | 1675.7479 | 11441.176 | -0.0018579
218 |  | 21.0212 | 52.5213 | 4187 | 0.00059673 | 6.13 | 6.1306 | -3.1133 | 1675.8072 | 11493.6972 | -0.0018578
219 |  | 21.0212 | 52.5194 | 4187 | 0.00059671 | 6.1306 | 6.1312 | -3.1133 | 1675.8665 | 11546.2167 | -0.0018577
220 |  | 21.0212 | 52.5176 | 4187 | 0.00059669 | 6.1312 | 6.1318 | -3.1133 | 1675.9258 | 11598.7343 | -0.0018577
221 |  | 21.0212 | 52.5157 | 4187 | 0.00059666 | 6.1318 | 6.1324 | -3.1133 | 1675.985 | 11651.25 | -0.0018576
222 |  | 21.0212 | 52.5139 | 4187 | 0.00059664 | 6.1324 | 6.133 | -3.1133 | 1676.0443 | 11703.7638 | -0.0018575
223 |  | 21.0212 | 52.512 | 4187 | 0.00059662 | 6.133 | 6.1336 | -3.1133 | 1676.1036 | 11756.2758 | -0.0018575
224 |  | 21.0212 | 52.5101 | 4187 | 0.0005966 | 6.1336 | 6.1342 | -3.1133 | 1676.1629 | 11808.786 | -0.0018574
225 |  | 21.0212 | 52.5083 | 4187 | 0.00059658 | 6.1342 | 6.1348 | -3.1133 | 1676.2222 | 11861.2943 | -0.0018573
226 |  | 21.0212 | 52.5064 | 4187 | 0.00059656 | 6.1348 | 6.1354 | -3.1133 | 1676.2815 | 11913.8007 | -0.0018573
227 |  | 21.0212 | 52.5046 | 4187 | 0.00059654 | 6.1354 | 6.136 | -3.1133 | 1676.3408 | 11966.3053 | -0.0018572
228 |  | 21.0212 | 52.5027 | 4187 | 0.00059652 | 6.136 | 6.1366 | -3.1133 | 1676.4001 | 12018.808 | -0.0018571
229 |  | 21.0212 | 52.5009 | 4187 | 0.0005965 | 6.1366 | 6.1371 | -3.1133 | 1676.4594 | 12071.3088 | -0.0018571
230 |  | 21.0212 | 52.499 | 4187 | 0.00059647 | 6.1371 | 6.1377 | -3.1133 | 1676.5187 | 12123.8078 | -0.001857
231 |  | 21.0212 | 52.4971 | 4187 | 0.00059645 | 6.1377 | 6.1383 | -3.1133 | 1676.578 | 12176.305 | -0.0018569
232 |  | 21.0212 | 52.4953 | 4187 | 0.00059643 | 6.1383 | 6.1389 | -3.1133 | 1676.6373 | 12228.8003 | -0.0018569
233 |  | 21.0212 | 52.4934 | 4187 | 0.00059641 | 6.1389 | 6.1395 | -3.1133 | 1676.6966 | 12281.2937 | -0.0018568
234 |  | 21.0212 | 52.4916 | 4187 | 0.00059639 | 6.1395 | 6.1401 | -3.1133 | 1676.7559 | 12333.7853 | -0.0018567
235 |  | 21.0212 | 52.4897 | 4187 | 0.00059637 | 6.1401 | 6.1407 | -3.1133 | 1676.8152 | 12386.275 | -0.0018567
236 |  | 21.0212 | 52.4879 | 4187 | 0.00059635 | 6.1407 | 6.1413 | -3.1133 | 1676.8745 | 12438.7629 | -0.0018566

## 250
|  |  | buis | verlies W/M | L /°C/sec
diam | wandikte |  | inhoud l/m |  | W/M
250 | 22.7 | 3.1416 | 32.8777 | 56.8421 | 4187
[8 empty] | J/sec/mtr | aantal mtr. | verlies
|  | buis | verlies W/M | L /°C/sec | verlies temp | begintemp | eindtemp | verlies | bij 1°C | totaal J/sec
|  | inhoud L |  | W/M | °C per M | °C | °C | per m°C | daling | aantal mtr
1 | 250 | 32.8777 | 56.8421 | 4187 | 0.00041292 | 6 | 6.0004 | -3.3437 | 2421.775 | 56.8421 | -0.0013807
2 |  | 32.8777 | 56.8407 | 4187 | 0.00041291 | 6.0004 | 6.0008 | -3.3437 | 2421.8339 | 113.6829 | -0.0013806
3 |  | 32.8777 | 56.8394 | 4187 | 0.0004129 | 6.0008 | 6.0012 | -3.3437 | 2421.8927 | 170.5222 | -0.0013806
4 |  | 32.8777 | 56.838 | 4187 | 0.00041289 | 6.0012 | 6.0017 | -3.3437 | 2421.9515 | 227.3602 | -0.0013806
5 |  | 32.8777 | 56.8366 | 4187 | 0.00041288 | 6.0017 | 6.0021 | -3.3437 | 2422.0103 | 284.1968 | -0.0013805
6 |  | 32.8777 | 56.8352 | 4187 | 0.00041287 | 6.0021 | 6.0025 | -3.3437 | 2422.0692 | 341.032 | -0.0013805
7 |  | 32.8777 | 56.8338 | 4187 | 0.00041286 | 6.0025 | 6.0029 | -3.3437 | 2422.128 | 397.8659 | -0.0013805
8 |  | 32.8777 | 56.8325 | 4187 | 0.00041285 | 6.0029 | 6.0033 | -3.3437 | 2422.1868 | 454.6983 | -0.0013804
9 |  | 32.8777 | 56.8311 | 4187 | 0.00041284 | 6.0033 | 6.0037 | -3.3437 | 2422.2457 | 511.5294 | -0.0013804
10 |  | 32.8777 | 56.8297 | 4187 | 0.00041283 | 6.0037 | 6.0041 | -3.3437 | 2422.3045 | 568.3591 | -0.0013804
11 |  | 32.8777 | 56.8283 | 4187 | 0.00041282 | 6.0041 | 6.0045 | -3.3437 | 2422.3634 | 625.1874 | -0.0013803
12 |  | 32.8777 | 56.8269 | 4187 | 0.00041281 | 6.0045 | 6.005 | -3.3437 | 2422.4222 | 682.0144 | -0.0013803
13 |  | 32.8777 | 56.8256 | 4187 | 0.0004128 | 6.005 | 6.0054 | -3.3437 | 2422.481 | 738.8399 | -0.0013803
14 |  | 32.8777 | 56.8242 | 4187 | 0.00041279 | 6.0054 | 6.0058 | -3.3437 | 2422.5399 | 795.6641 | -0.0013802
15 |  | 32.8777 | 56.8228 | 4187 | 0.00041278 | 6.0058 | 6.0062 | -3.3437 | 2422.5987 | 852.4869 | -0.0013802
16 |  | 32.8777 | 56.8214 | 4187 | 0.00041277 | 6.0062 | 6.0066 | -3.3437 | 2422.6576 | 909.3083 | -0.0013802
17 |  | 32.8777 | 56.82 | 4187 | 0.00041276 | 6.0066 | 6.007 | -3.3437 | 2422.7164 | 966.1284 | -0.0013801
18 |  | 32.8777 | 56.8187 | 4187 | 0.00041275 | 6.007 | 6.0074 | -3.3437 | 2422.7753 | 1022.947 | -0.0013801
19 |  | 32.8777 | 56.8173 | 4187 | 0.00041274 | 6.0074 | 6.0078 | -3.3437 | 2422.8341 | 1079.7643 | -0.0013801
20 |  | 32.8777 | 56.8159 | 4187 | 0.00041273 | 6.0078 | 6.0083 | -3.3437 | 2422.893 | 1136.5802 | -0.00138
21 |  | 32.8777 | 56.8145 | 4187 | 0.00041272 | 6.0083 | 6.0087 | -3.3437 | 2422.9518 | 1193.3947 | -0.00138
22 |  | 32.8777 | 56.8131 | 4187 | 0.00041271 | 6.0087 | 6.0091 | -3.3437 | 2423.0107 | 1250.2079 | -0.00138
23 |  | 32.8777 | 56.8118 | 4187 | 0.0004127 | 6.0091 | 6.0095 | -3.3437 | 2423.0695 | 1307.0196 | -0.0013799
24 |  | 32.8777 | 56.8104 | 4187 | 0.00041269 | 6.0095 | 6.0099 | -3.3437 | 2423.1284 | 1363.83 | -0.0013799
25 |  | 32.8777 | 56.809 | 4187 | 0.00041268 | 6.0099 | 6.0103 | -3.3437 | 2423.1872 | 1420.639 | -0.0013799
26 |  | 32.8777 | 56.8076 | 4187 | 0.00041267 | 6.0103 | 6.0107 | -3.3437 | 2423.2461 | 1477.4466 | -0.0013798
27 |  | 32.8777 | 56.8062 | 4187 | 0.00041266 | 6.0107 | 6.0111 | -3.3437 | 2423.305 | 1534.2529 | -0.0013798
28 |  | 32.8777 | 56.8049 | 4187 | 0.00041265 | 6.0111 | 6.0116 | -3.3437 | 2423.3638 | 1591.0577 | -0.0013798
29 |  | 32.8777 | 56.8035 | 4187 | 0.00041264 | 6.0116 | 6.012 | -3.3437 | 2423.4227 | 1647.8612 | -0.0013797
30 |  | 32.8777 | 56.8021 | 4187 | 0.00041263 | 6.012 | 6.0124 | -3.3437 | 2423.4815 | 1704.6633 | -0.0013797
31 |  | 32.8777 | 56.8007 | 4187 | 0.00041262 | 6.0124 | 6.0128 | -3.3437 | 2423.5404 | 1761.464 | -0.0013797
32 |  | 32.8777 | 56.7993 | 4187 | 0.00041261 | 6.0128 | 6.0132 | -3.3437 | 2423.5993 | 1818.2633 | -0.0013796
33 |  | 32.8777 | 56.798 | 4187 | 0.0004126 | 6.0132 | 6.0136 | -3.3437 | 2423.6581 | 1875.0613 | -0.0013796
34 |  | 32.8777 | 56.7966 | 4187 | 0.00041259 | 6.0136 | 6.014 | -3.3437 | 2423.717 | 1931.8579 | -0.0013796
35 |  | 32.8777 | 56.7952 | 4187 | 0.00041258 | 6.014 | 6.0144 | -3.3437 | 2423.7759 | 1988.6531 | -0.0013795
36 |  | 32.8777 | 56.7938 | 4187 | 0.00041257 | 6.0144 | 6.0149 | -3.3437 | 2423.8348 | 2045.4469 | -0.0013795
37 |  | 32.8777 | 56.7924 | 4187 | 0.00041256 | 6.0149 | 6.0153 | -3.3437 | 2423.8936 | 2102.2394 | -0.0013795
38 |  | 32.8777 | 56.7911 | 4187 | 0.00041255 | 6.0153 | 6.0157 | -3.3437 | 2423.9525 | 2159.0304 | -0.0013794
39 |  | 32.8777 | 56.7897 | 4187 | 0.00041254 | 6.0157 | 6.0161 | -3.3437 | 2424.0114 | 2215.8201 | -0.0013794
40 |  | 32.8777 | 56.7883 | 4187 | 0.00041253 | 6.0161 | 6.0165 | -3.3437 | 2424.0703 | 2272.6084 | -0.0013794
41 |  | 32.8777 | 56.7869 | 4187 | 0.00041252 | 6.0165 | 6.0169 | -3.3437 | 2424.1292 | 2329.3953 | -0.0013793
42 |  | 32.8777 | 56.7855 | 4187 | 0.00041251 | 6.0169 | 6.0173 | -3.3437 | 2424.188 | 2386.1809 | -0.0013793
43 |  | 32.8777 | 56.7842 | 4187 | 0.0004125 | 6.0173 | 6.0177 | -3.3437 | 2424.2469 | 2442.965 | -0.0013793
44 |  | 32.8777 | 56.7828 | 4187 | 0.00041249 | 6.0177 | 6.0182 | -3.3437 | 2424.3058 | 2499.7478 | -0.0013792
45 |  | 32.8777 | 56.7814 | 4187 | 0.00041248 | 6.0182 | 6.0186 | -3.3437 | 2424.3647 | 2556.5292 | -0.0013792
46 |  | 32.8777 | 56.78 | 4187 | 0.00041247 | 6.0186 | 6.019 | -3.3437 | 2424.4236 | 2613.3093 | -0.0013792
47 |  | 32.8777 | 56.7786 | 4187 | 0.00041246 | 6.019 | 6.0194 | -3.3437 | 2424.4825 | 2670.0879 | -0.0013791
48 |  | 32.8777 | 56.7773 | 4187 | 0.00041245 | 6.0194 | 6.0198 | -3.3437 | 2424.5414 | 2726.8652 | -0.0013791
49 |  | 32.8777 | 56.7759 | 4187 | 0.00041244 | 6.0198 | 6.0202 | -3.3437 | 2424.6002 | 2783.6411 | -0.0013791
50 |  | 32.8777 | 56.7745 | 4187 | 0.00041243 | 6.0202 | 6.0206 | -3.3437 | 2424.6591 | 2840.4156 | -0.001379
51 |  | 32.8777 | 56.7731 | 4187 | 0.00041242 | 6.0206 | 6.021 | -3.3437 | 2424.718 | 2897.1887 | -0.001379
52 |  | 32.8777 | 56.7718 | 4187 | 0.00041241 | 6.021 | 6.0215 | -3.3437 | 2424.7769 | 2953.9605 | -0.001379
53 |  | 32.8777 | 56.7704 | 4187 | 0.0004124 | 6.0215 | 6.0219 | -3.3437 | 2424.8358 | 3010.7308 | -0.0013789
54 |  | 32.8777 | 56.769 | 4187 | 0.00041239 | 6.0219 | 6.0223 | -3.3437 | 2424.8947 | 3067.4998 | -0.0013789
55 |  | 32.8777 | 56.7676 | 4187 | 0.00041238 | 6.0223 | 6.0227 | -3.3437 | 2424.9536 | 3124.2675 | -0.0013789
56 |  | 32.8777 | 56.7662 | 4187 | 0.00041237 | 6.0227 | 6.0231 | -3.3437 | 2425.0125 | 3181.0337 | -0.0013788
57 |  | 32.8777 | 56.7649 | 4187 | 0.00041236 | 6.0231 | 6.0235 | -3.3437 | 2425.0714 | 3237.7985 | -0.0013788
58 |  | 32.8777 | 56.7635 | 4187 | 0.00041235 | 6.0235 | 6.0239 | -3.3437 | 2425.1303 | 3294.562 | -0.0013788
59 |  | 32.8777 | 56.7621 | 4187 | 0.00041234 | 6.0239 | 6.0243 | -3.3437 | 2425.1892 | 3351.3241 | -0.0013787
60 |  | 32.8777 | 56.7607 | 4187 | 0.00041233 | 6.0243 | 6.0248 | -3.3437 | 2425.2482 | 3408.0849 | -0.0013787
61 |  | 32.8777 | 56.7593 | 4187 | 0.00041232 | 6.0248 | 6.0252 | -3.3437 | 2425.3071 | 3464.8442 | -0.0013787
62 |  | 32.8777 | 56.758 | 4187 | 0.00041231 | 6.0252 | 6.0256 | -3.3437 | 2425.366 | 3521.6022 | -0.0013786
63 |  | 32.8777 | 56.7566 | 4187 | 0.0004123 | 6.0256 | 6.026 | -3.3437 | 2425.4249 | 3578.3587 | -0.0013786
64 |  | 32.8777 | 56.7552 | 4187 | 0.00041229 | 6.026 | 6.0264 | -3.3437 | 2425.4838 | 3635.114 | -0.0013786
65 |  | 32.8777 | 56.7538 | 4187 | 0.00041228 | 6.0264 | 6.0268 | -3.3437 | 2425.5427 | 3691.8678 | -0.0013785
66 |  | 32.8777 | 56.7525 | 4187 | 0.00041227 | 6.0268 | 6.0272 | -3.3437 | 2425.6016 | 3748.6202 | -0.0013785
67 |  | 32.8777 | 56.7511 | 4187 | 0.00041226 | 6.0272 | 6.0276 | -3.3437 | 2425.6606 | 3805.3713 | -0.0013785
68 |  | 32.8777 | 56.7497 | 4187 | 0.00041225 | 6.0276 | 6.0281 | -3.3437 | 2425.7195 | 3862.121 | -0.0013784
69 |  | 32.8777 | 56.7483 | 4187 | 0.00041224 | 6.0281 | 6.0285 | -3.3437 | 2425.7784 | 3918.8693 | -0.0013784
70 |  | 32.8777 | 56.7469 | 4187 | 0.00041223 | 6.0285 | 6.0289 | -3.3437 | 2425.8373 | 3975.6163 | -0.0013784
71 |  | 32.8777 | 56.7456 | 4187 | 0.00041222 | 6.0289 | 6.0293 | -3.3437 | 2425.8962 | 4032.3618 | -0.0013783
72 |  | 32.8777 | 56.7442 | 4187 | 0.00041221 | 6.0293 | 6.0297 | -3.3437 | 2425.9552 | 4089.106 | -0.0013783
73 |  | 32.8777 | 56.7428 | 4187 | 0.0004122 | 6.0297 | 6.0301 | -3.3437 | 2426.0141 | 4145.8488 | -0.0013783
74 |  | 32.8777 | 56.7414 | 4187 | 0.00041219 | 6.0301 | 6.0305 | -3.3437 | 2426.073 | 4202.5902 | -0.0013782
75 |  | 32.8777 | 56.74 | 4187 | 0.00041218 | 6.0305 | 6.0309 | -3.3437 | 2426.1319 | 4259.3303 | -0.0013782
76 |  | 32.8777 | 56.7387 | 4187 | 0.00041217 | 6.0309 | 6.0314 | -3.3437 | 2426.1909 | 4316.0689 | -0.0013781
77 |  | 32.8777 | 56.7373 | 4187 | 0.00041216 | 6.0314 | 6.0318 | -3.3437 | 2426.2498 | 4372.8062 | -0.0013781
78 |  | 32.8777 | 56.7359 | 4187 | 0.00041215 | 6.0318 | 6.0322 | -3.3437 | 2426.3087 | 4429.5421 | -0.0013781
79 |  | 32.8777 | 56.7345 | 4187 | 0.00041214 | 6.0322 | 6.0326 | -3.3437 | 2426.3677 | 4486.2767 | -0.001378
80 |  | 32.8777 | 56.7332 | 4187 | 0.00041213 | 6.0326 | 6.033 | -3.3437 | 2426.4266 | 4543.0098 | -0.001378
81 |  | 32.8777 | 56.7318 | 4187 | 0.00041212 | 6.033 | 6.0334 | -3.3437 | 2426.4856 | 4599.7416 | -0.001378
82 |  | 32.8777 | 56.7304 | 4187 | 0.00041211 | 6.0334 | 6.0338 | -3.3437 | 2426.5445 | 4656.472 | -0.0013779
83 |  | 32.8777 | 56.729 | 4187 | 0.0004121 | 6.0338 | 6.0342 | -3.3437 | 2426.6034 | 4713.201 | -0.0013779
84 |  | 32.8777 | 56.7276 | 4187 | 0.00041209 | 6.0342 | 6.0347 | -3.3437 | 2426.6624 | 4769.9287 | -0.0013779
85 |  | 32.8777 | 56.7263 | 4187 | 0.00041208 | 6.0347 | 6.0351 | -3.3437 | 2426.7213 | 4826.6549 | -0.0013778
86 |  | 32.8777 | 56.7249 | 4187 | 0.00041207 | 6.0351 | 6.0355 | -3.3437 | 2426.7803 | 4883.3798 | -0.0013778
87 |  | 32.8777 | 56.7235 | 4187 | 0.00041206 | 6.0355 | 6.0359 | -3.3437 | 2426.8392 | 4940.1033 | -0.0013778
88 |  | 32.8777 | 56.7221 | 4187 | 0.00041205 | 6.0359 | 6.0363 | -3.3437 | 2426.8982 | 4996.8255 | -0.0013777
89 |  | 32.8777 | 56.7208 | 4187 | 0.00041204 | 6.0363 | 6.0367 | -3.3437 | 2426.9571 | 5053.5462 | -0.0013777
90 |  | 32.8777 | 56.7194 | 4187 | 0.00041203 | 6.0367 | 6.0371 | -3.3437 | 2427.0161 | 5110.2656 | -0.0013777
91 |  | 32.8777 | 56.718 | 4187 | 0.00041202 | 6.0371 | 6.0375 | -3.3437 | 2427.075 | 5166.9836 | -0.0013776
92 |  | 32.8777 | 56.7166 | 4187 | 0.00041201 | 6.0375 | 6.0379 | -3.3437 | 2427.134 | 5223.7002 | -0.0013776
93 |  | 32.8777 | 56.7152 | 4187 | 0.000412 | 6.0379 | 6.0384 | -3.3437 | 2427.1929 | 5280.4155 | -0.0013776
94 |  | 32.8777 | 56.7139 | 4187 | 0.00041199 | 6.0384 | 6.0388 | -3.3437 | 2427.2519 | 5337.1293 | -0.0013775
95 |  | 32.8777 | 56.7125 | 4187 | 0.00041198 | 6.0388 | 6.0392 | -3.3437 | 2427.3108 | 5393.8418 | -0.0013775
96 |  | 32.8777 | 56.7111 | 4187 | 0.00041197 | 6.0392 | 6.0396 | -3.3437 | 2427.3698 | 5450.5529 | -0.0013775
97 |  | 32.8777 | 56.7097 | 4187 | 0.00041196 | 6.0396 | 6.04 | -3.3437 | 2427.4288 | 5507.2627 | -0.0013774
98 |  | 32.8777 | 56.7084 | 4187 | 0.00041195 | 6.04 | 6.0404 | -3.3437 | 2427.4877 | 5563.971 | -0.0013774
99 |  | 32.8777 | 56.707 | 4187 | 0.00041194 | 6.0404 | 6.0408 | -3.3437 | 2427.5467 | 5620.678 | -0.0013774
100 |  | 32.8777 | 56.7056 | 4187 | 0.00041193 | 6.0408 | 6.0412 | -3.3437 | 2427.6056 | 5677.3836 | -0.0013773
101 |  | 32.8777 | 56.7042 | 4187 | 0.00041192 | 6.0412 | 6.0417 | -3.3437 | 2427.6646 | 5734.0878 | -0.0013773
102 |  | 32.8777 | 56.7028 | 4187 | 0.00041191 | 6.0417 | 6.0421 | -3.3437 | 2427.7236 | 5790.7907 | -0.0013773
103 |  | 32.8777 | 56.7015 | 4187 | 0.0004119 | 6.0421 | 6.0425 | -3.3437 | 2427.7825 | 5847.4921 | -0.0013772
104 |  | 32.8777 | 56.7001 | 4187 | 0.00041189 | 6.0425 | 6.0429 | -3.3437 | 2427.8415 | 5904.1922 | -0.0013772
105 |  | 32.8777 | 56.6987 | 4187 | 0.00041188 | 6.0429 | 6.0433 | -3.3437 | 2427.9005 | 5960.891 | -0.0013772
106 |  | 32.8777 | 56.6973 | 4187 | 0.00041187 | 6.0433 | 6.0437 | -3.3437 | 2427.9595 | 6017.5883 | -0.0013771
107 |  | 32.8777 | 56.696 | 4187 | 0.00041186 | 6.0437 | 6.0441 | -3.3437 | 2428.0184 | 6074.2843 | -0.0013771
108 |  | 32.8777 | 56.6946 | 4187 | 0.00041185 | 6.0441 | 6.0445 | -3.3437 | 2428.0774 | 6130.9788 | -0.0013771
109 |  | 32.8777 | 56.6932 | 4187 | 0.00041184 | 6.0445 | 6.0449 | -3.3437 | 2428.1364 | 6187.672 | -0.001377
110 |  | 32.8777 | 56.6918 | 4187 | 0.00041183 | 6.0449 | 6.0454 | -3.3437 | 2428.1954 | 6244.3639 | -0.001377
111 |  | 32.8777 | 56.6905 | 4187 | 0.00041182 | 6.0454 | 6.0458 | -3.3437 | 2428.2544 | 6301.0543 | -0.001377
112 |  | 32.8777 | 56.6891 | 4187 | 0.00041181 | 6.0458 | 6.0462 | -3.3437 | 2428.3133 | 6357.7434 | -0.0013769
113 |  | 32.8777 | 56.6877 | 4187 | 0.0004118 | 6.0462 | 6.0466 | -3.3437 | 2428.3723 | 6414.4311 | -0.0013769
114 |  | 32.8777 | 56.6863 | 4187 | 0.00041179 | 6.0466 | 6.047 | -3.3437 | 2428.4313 | 6471.1174 | -0.0013769
115 |  | 32.8777 | 56.6849 | 4187 | 0.00041178 | 6.047 | 6.0474 | -3.3437 | 2428.4903 | 6527.8024 | -0.0013768
116 |  | 32.8777 | 56.6836 | 4187 | 0.00041177 | 6.0474 | 6.0478 | -3.3437 | 2428.5493 | 6584.4859 | -0.0013768
117 |  | 32.8777 | 56.6822 | 4187 | 0.00041176 | 6.0478 | 6.0482 | -3.3437 | 2428.6083 | 6641.1681 | -0.0013768
118 |  | 32.8777 | 56.6808 | 4187 | 0.00041175 | 6.0482 | 6.0487 | -3.3437 | 2428.6673 | 6697.8489 | -0.0013767
119 |  | 32.8777 | 56.6794 | 4187 | 0.00041174 | 6.0487 | 6.0491 | -3.3437 | 2428.7263 | 6754.5284 | -0.0013767
120 |  | 32.8777 | 56.6781 | 4187 | 0.00041173 | 6.0491 | 6.0495 | -3.3437 | 2428.7852 | 6811.2064 | -0.0013767
121 |  | 32.8777 | 56.6767 | 4187 | 0.00041172 | 6.0495 | 6.0499 | -3.3437 | 2428.8442 | 6867.8831 | -0.0013766
122 |  | 32.8777 | 56.6753 | 4187 | 0.00041171 | 6.0499 | 6.0503 | -3.3437 | 2428.9032 | 6924.5584 | -0.0013766
123 |  | 32.8777 | 56.6739 | 4187 | 0.0004117 | 6.0503 | 6.0507 | -3.3437 | 2428.9622 | 6981.2324 | -0.0013766
124 |  | 32.8777 | 56.6726 | 4187 | 0.00041169 | 6.0507 | 6.0511 | -3.3437 | 2429.0212 | 7037.9049 | -0.0013765
125 |  | 32.8777 | 56.6712 | 4187 | 0.00041168 | 6.0511 | 6.0515 | -3.3437 | 2429.0802 | 7094.5761 | -0.0013765
126 |  | 32.8777 | 56.6698 | 4187 | 0.00041167 | 6.0515 | 6.0519 | -3.3437 | 2429.1392 | 7151.2459 | -0.0013765
127 |  | 32.8777 | 56.6684 | 4187 | 0.00041166 | 6.0519 | 6.0524 | -3.3437 | 2429.1982 | 7207.9143 | -0.0013764
128 |  | 32.8777 | 56.667 | 4187 | 0.00041165 | 6.0524 | 6.0528 | -3.3437 | 2429.2573 | 7264.5814 | -0.0013764
129 |  | 32.8777 | 56.6657 | 4187 | 0.00041164 | 6.0528 | 6.0532 | -3.3437 | 2429.3163 | 7321.247 | -0.0013764
130 |  | 32.8777 | 56.6643 | 4187 | 0.00041163 | 6.0532 | 6.0536 | -3.3437 | 2429.3753 | 7377.9113 | -0.0013763
131 |  | 32.8777 | 56.6629 | 4187 | 0.00041162 | 6.0536 | 6.054 | -3.3437 | 2429.4343 | 7434.5743 | -0.0013763
132 |  | 32.8777 | 56.6615 | 4187 | 0.00041161 | 6.054 | 6.0544 | -3.3437 | 2429.4933 | 7491.2358 | -0.0013763
133 |  | 32.8777 | 56.6602 | 4187 | 0.0004116 | 6.0544 | 6.0548 | -3.3437 | 2429.5523 | 7547.896 | -0.0013762
134 |  | 32.8777 | 56.6588 | 4187 | 0.00041159 | 6.0548 | 6.0552 | -3.3437 | 2429.6113 | 7604.5548 | -0.0013762
135 |  | 32.8777 | 56.6574 | 4187 | 0.00041158 | 6.0552 | 6.0557 | -3.3437 | 2429.6703 | 7661.2122 | -0.0013762
136 |  | 32.8777 | 56.656 | 4187 | 0.00041157 | 6.0557 | 6.0561 | -3.3437 | 2429.7293 | 7717.8682 | -0.0013761
137 |  | 32.8777 | 56.6547 | 4187 | 0.00041156 | 6.0561 | 6.0565 | -3.3437 | 2429.7884 | 7774.5229 | -0.0013761
138 |  | 32.8777 | 56.6533 | 4187 | 0.00041155 | 6.0565 | 6.0569 | -3.3437 | 2429.8474 | 7831.1762 | -0.0013761
139 |  | 32.8777 | 56.6519 | 4187 | 0.00041154 | 6.0569 | 6.0573 | -3.3437 | 2429.9064 | 7887.8281 | -0.001376
140 |  | 32.8777 | 56.6505 | 4187 | 0.00041153 | 6.0573 | 6.0577 | -3.3437 | 2429.9654 | 7944.4786 | -0.001376
141 |  | 32.8777 | 56.6492 | 4187 | 0.00041152 | 6.0577 | 6.0581 | -3.3437 | 2430.0245 | 8001.1278 | -0.001376
142 |  | 32.8777 | 56.6478 | 4187 | 0.00041151 | 6.0581 | 6.0585 | -3.3437 | 2430.0835 | 8057.7755 | -0.0013759
143 |  | 32.8777 | 56.6464 | 4187 | 0.0004115 | 6.0585 | 6.0589 | -3.3437 | 2430.1425 | 8114.4219 | -0.0013759
144 |  | 32.8777 | 56.645 | 4187 | 0.00041149 | 6.0589 | 6.0594 | -3.3437 | 2430.2015 | 8171.067 | -0.0013759
145 |  | 32.8777 | 56.6437 | 4187 | 0.00041148 | 6.0594 | 6.0598 | -3.3437 | 2430.2606 | 8227.7106 | -0.0013758
146 |  | 32.8777 | 56.6423 | 4187 | 0.00041147 | 6.0598 | 6.0602 | -3.3437 | 2430.3196 | 8284.3529 | -0.0013758
147 |  | 32.8777 | 56.6409 | 4187 | 0.00041146 | 6.0602 | 6.0606 | -3.3437 | 2430.3786 | 8340.9938 | -0.0013758
148 |  | 32.8777 | 56.6395 | 4187 | 0.00041145 | 6.0606 | 6.061 | -3.3437 | 2430.4377 | 8397.6333 | -0.0013757
149 |  | 32.8777 | 56.6382 | 4187 | 0.00041144 | 6.061 | 6.0614 | -3.3437 | 2430.4967 | 8454.2715 | -0.0013757
150 |  | 32.8777 | 56.6368 | 4187 | 0.00041143 | 6.0614 | 6.0618 | -3.3437 | 2430.5557 | 8510.9083 | -0.0013757
151 |  | 32.8777 | 56.6354 | 4187 | 0.00041142 | 6.0618 | 6.0622 | -3.3437 | 2430.6148 | 8567.5437 | -0.0013756
152 |  | 32.8777 | 56.634 | 4187 | 0.00041141 | 6.0622 | 6.0626 | -3.3437 | 2430.6738 | 8624.1777 | -0.0013756
153 |  | 32.8777 | 56.6326 | 4187 | 0.0004114 | 6.0626 | 6.0631 | -3.3437 | 2430.7328 | 8680.8103 | -0.0013756
154 |  | 32.8777 | 56.6313 | 4187 | 0.00041139 | 6.0631 | 6.0635 | -3.3437 | 2430.7919 | 8737.4416 | -0.0013755
155 |  | 32.8777 | 56.6299 | 4187 | 0.00041138 | 6.0635 | 6.0639 | -3.3437 | 2430.8509 | 8794.0715 | -0.0013755
156 |  | 32.8777 | 56.6285 | 4187 | 0.00041137 | 6.0639 | 6.0643 | -3.3437 | 2430.91 | 8850.7 | -0.0013755
157 |  | 32.8777 | 56.6271 | 4187 | 0.00041136 | 6.0643 | 6.0647 | -3.3437 | 2430.969 | 8907.3272 | -0.0013754
158 |  | 32.8777 | 56.6258 | 4187 | 0.00041135 | 6.0647 | 6.0651 | -3.3437 | 2431.0281 | 8963.9529 | -0.0013754
159 |  | 32.8777 | 56.6244 | 4187 | 0.00041134 | 6.0651 | 6.0655 | -3.3437 | 2431.0871 | 9020.5773 | -0.0013754
160 |  | 32.8777 | 56.623 | 4187 | 0.00041133 | 6.0655 | 6.0659 | -3.3437 | 2431.1462 | 9077.2004 | -0.0013753
161 |  | 32.8777 | 56.6216 | 4187 | 0.00041132 | 6.0659 | 6.0664 | -3.3437 | 2431.2052 | 9133.822 | -0.0013753
162 |  | 32.8777 | 56.6203 | 4187 | 0.00041131 | 6.0664 | 6.0668 | -3.3437 | 2431.2643 | 9190.4423 | -0.0013753
163 |  | 32.8777 | 56.6189 | 4187 | 0.0004113 | 6.0668 | 6.0672 | -3.3437 | 2431.3233 | 9247.0612 | -0.0013752
164 |  | 32.8777 | 56.6175 | 4187 | 0.00041129 | 6.0672 | 6.0676 | -3.3437 | 2431.3824 | 9303.6787 | -0.0013752
165 |  | 32.8777 | 56.6161 | 4187 | 0.00041128 | 6.0676 | 6.068 | -3.3437 | 2431.4415 | 9360.2948 | -0.0013752
166 |  | 32.8777 | 56.6148 | 4187 | 0.00041127 | 6.068 | 6.0684 | -3.3437 | 2431.5005 | 9416.9096 | -0.0013751
167 |  | 32.8777 | 56.6134 | 4187 | 0.00041126 | 6.0684 | 6.0688 | -3.3437 | 2431.5596 | 9473.523 | -0.0013751
168 |  | 32.8777 | 56.612 | 4187 | 0.00041125 | 6.0688 | 6.0692 | -3.3437 | 2431.6186 | 9530.135 | -0.0013751
169 |  | 32.8777 | 56.6106 | 4187 | 0.00041124 | 6.0692 | 6.0696 | -3.3437 | 2431.6777 | 9586.7457 | -0.001375
170 |  | 32.8777 | 56.6093 | 4187 | 0.00041123 | 6.0696 | 6.0701 | -3.3437 | 2431.7368 | 9643.3549 | -0.001375
171 |  | 32.8777 | 56.6079 | 4187 | 0.00041122 | 6.0701 | 6.0705 | -3.3437 | 2431.7958 | 9699.9628 | -0.001375
172 |  | 32.8777 | 56.6065 | 4187 | 0.00041121 | 6.0705 | 6.0709 | -3.3437 | 2431.8549 | 9756.5693 | -0.0013749
173 |  | 32.8777 | 56.6051 | 4187 | 0.0004112 | 6.0709 | 6.0713 | -3.3437 | 2431.914 | 9813.1745 | -0.0013749
174 |  | 32.8777 | 56.6038 | 4187 | 0.00041119 | 6.0713 | 6.0717 | -3.3437 | 2431.973 | 9869.7782 | -0.0013749
175 |  | 32.8777 | 56.6024 | 4187 | 0.00041118 | 6.0717 | 6.0721 | -3.3437 | 2432.0321 | 9926.3806 | -0.0013748
176 |  | 32.8777 | 56.601 | 4187 | 0.00041117 | 6.0721 | 6.0725 | -3.3437 | 2432.0912 | 9982.9817 | -0.0013748
177 |  | 32.8777 | 56.5996 | 4187 | 0.00041116 | 6.0725 | 6.0729 | -3.3437 | 2432.1503 | 10039.5813 | -0.0013748
178 |  | 32.8777 | 56.5983 | 4187 | 0.00041115 | 6.0729 | 6.0733 | -3.3437 | 2432.2093 | 10096.1796 | -0.0013747
179 |  | 32.8777 | 56.5969 | 4187 | 0.00041114 | 6.0733 | 6.0738 | -3.3437 | 2432.2684 | 10152.7765 | -0.0013747
180 |  | 32.8777 | 56.5955 | 4187 | 0.00041113 | 6.0738 | 6.0742 | -3.3437 | 2432.3275 | 10209.372 | -0.0013747
181 |  | 32.8777 | 56.5941 | 4187 | 0.00041112 | 6.0742 | 6.0746 | -3.3437 | 2432.3866 | 10265.9661 | -0.0013746
182 |  | 32.8777 | 56.5928 | 4187 | 0.00041111 | 6.0746 | 6.075 | -3.3437 | 2432.4457 | 10322.5589 | -0.0013746
183 |  | 32.8777 | 56.5914 | 4187 | 0.0004111 | 6.075 | 6.0754 | -3.3437 | 2432.5047 | 10379.1503 | -0.0013746
184 |  | 32.8777 | 56.59 | 4187 | 0.00041109 | 6.0754 | 6.0758 | -3.3437 | 2432.5638 | 10435.7403 | -0.0013745
185 |  | 32.8777 | 56.5886 | 4187 | 0.00041108 | 6.0758 | 6.0762 | -3.3437 | 2432.6229 | 10492.329 | -0.0013745
186 |  | 32.8777 | 56.5873 | 4187 | 0.00041107 | 6.0762 | 6.0766 | -3.3437 | 2432.682 | 10548.9162 | -0.0013745
187 |  | 32.8777 | 56.5859 | 4187 | 0.00041106 | 6.0766 | 6.077 | -3.3437 | 2432.7411 | 10605.5021 | -0.0013744
188 |  | 32.8777 | 56.5845 | 4187 | 0.00041105 | 6.077 | 6.0775 | -3.3437 | 2432.8002 | 10662.0867 | -0.0013744
189 |  | 32.8777 | 56.5831 | 4187 | 0.00041104 | 6.0775 | 6.0779 | -3.3437 | 2432.8593 | 10718.6698 | -0.0013744
190 |  | 32.8777 | 56.5818 | 4187 | 0.00041103 | 6.0779 | 6.0783 | -3.3437 | 2432.9184 | 10775.2516 | -0.0013743
191 |  | 32.8777 | 56.5804 | 4187 | 0.00041102 | 6.0783 | 6.0787 | -3.3437 | 2432.9775 | 10831.832 | -0.0013743
192 |  | 32.8777 | 56.579 | 4187 | 0.00041101 | 6.0787 | 6.0791 | -3.3437 | 2433.0366 | 10888.411 | -0.0013743
193 |  | 32.8777 | 56.5777 | 4187 | 0.000411 | 6.0791 | 6.0795 | -3.3437 | 2433.0957 | 10944.9887 | -0.0013742
194 |  | 32.8777 | 56.5763 | 4187 | 0.00041099 | 6.0795 | 6.0799 | -3.3437 | 2433.1548 | 11001.5649 | -0.0013742
195 |  | 32.8777 | 56.5749 | 4187 | 0.00041098 | 6.0799 | 6.0803 | -3.3437 | 2433.2139 | 11058.1398 | -0.0013742
196 |  | 32.8777 | 56.5735 | 4187 | 0.00041097 | 6.0803 | 6.0807 | -3.3437 | 2433.273 | 11114.7134 | -0.0013741
197 |  | 32.8777 | 56.5722 | 4187 | 0.00041096 | 6.0807 | 6.0812 | -3.3437 | 2433.3321 | 11171.2855 | -0.0013741
198 |  | 32.8777 | 56.5708 | 4187 | 0.00041095 | 6.0812 | 6.0816 | -3.3437 | 2433.3912 | 11227.8563 | -0.0013741
199 |  | 32.8777 | 56.5694 | 4187 | 0.00041094 | 6.0816 | 6.082 | -3.3437 | 2433.4503 | 11284.4257 | -0.001374
200 |  | 32.8777 | 56.568 | 4187 | 0.00041093 | 6.082 | 6.0824 | -3.3437 | 2433.5094 | 11340.9937 | -0.001374
201 |  | 32.8777 | 56.5667 | 4187 | 0.00041092 | 6.0824 | 6.0828 | -3.3437 | 2433.5685 | 11397.5604 | -0.001374
202 |  | 32.8777 | 56.5653 | 4187 | 0.00041091 | 6.0828 | 6.0832 | -3.3437 | 2433.6276 | 11454.1257 | -0.0013739
203 |  | 32.8777 | 56.5639 | 4187 | 0.0004109 | 6.0832 | 6.0836 | -3.3437 | 2433.6867 | 11510.6896 | -0.0013739
204 |  | 32.8777 | 56.5625 | 4187 | 0.00041089 | 6.0836 | 6.084 | -3.3437 | 2433.7458 | 11567.2521 | -0.0013739
205 |  | 32.8777 | 56.5612 | 4187 | 0.00041088 | 6.084 | 6.0844 | -3.3437 | 2433.805 | 11623.8133 | -0.0013738
206 |  | 32.8777 | 56.5598 | 4187 | 0.00041087 | 6.0844 | 6.0849 | -3.3437 | 2433.8641 | 11680.3731 | -0.0013738
207 |  | 32.8777 | 56.5584 | 4187 | 0.00041086 | 6.0849 | 6.0853 | -3.3437 | 2433.9232 | 11736.9315 | -0.0013738
208 |  | 32.8777 | 56.557 | 4187 | 0.00041085 | 6.0853 | 6.0857 | -3.3437 | 2433.9823 | 11793.4885 | -0.0013737
209 |  | 32.8777 | 56.5557 | 4187 | 0.00041084 | 6.0857 | 6.0861 | -3.3437 | 2434.0414 | 11850.0442 | -0.0013737
210 |  | 32.8777 | 56.5543 | 4187 | 0.00041083 | 6.0861 | 6.0865 | -3.3437 | 2434.1006 | 11906.5985 | -0.0013737
211 |  | 32.8777 | 56.5529 | 4187 | 0.00041082 | 6.0865 | 6.0869 | -3.3437 | 2434.1597 | 11963.1514 | -0.0013736
212 |  | 32.8777 | 56.5515 | 4187 | 0.00041081 | 6.0869 | 6.0873 | -3.3437 | 2434.2188 | 12019.703 | -0.0013736
213 |  | 32.8777 | 56.5502 | 4187 | 0.0004108 | 6.0873 | 6.0877 | -3.3437 | 2434.2779 | 12076.2531 | -0.0013736
214 |  | 32.8777 | 56.5488 | 4187 | 0.00041079 | 6.0877 | 6.0881 | -3.3437 | 2434.3371 | 12132.8019 | -0.0013735
215 |  | 32.8777 | 56.5474 | 4187 | 0.00041078 | 6.0881 | 6.0885 | -3.3437 | 2434.3962 | 12189.3494 | -0.0013735
216 |  | 32.8777 | 56.5461 | 4187 | 0.00041077 | 6.0885 | 6.089 | -3.3437 | 2434.4553 | 12245.8954 | -0.0013735
217 |  | 32.8777 | 56.5447 | 4187 | 0.00041076 | 6.089 | 6.0894 | -3.3437 | 2434.5145 | 12302.4401 | -0.0013734
218 |  | 32.8777 | 56.5433 | 4187 | 0.00041075 | 6.0894 | 6.0898 | -3.3437 | 2434.5736 | 12358.9834 | -0.0013734
219 |  | 32.8777 | 56.5419 | 4187 | 0.00041074 | 6.0898 | 6.0902 | -3.3437 | 2434.6327 | 12415.5253 | -0.0013734
220 |  | 32.8777 | 56.5406 | 4187 | 0.00041073 | 6.0902 | 6.0906 | -3.3437 | 2434.6919 | 12472.0659 | -0.0013733
221 |  | 32.8777 | 56.5392 | 4187 | 0.00041072 | 6.0906 | 6.091 | -3.3437 | 2434.751 | 12528.6051 | -0.0013733
222 |  | 32.8777 | 56.5378 | 4187 | 0.00041071 | 6.091 | 6.0914 | -3.3437 | 2434.8102 | 12585.1429 | -0.0013733
223 |  | 32.8777 | 56.5364 | 4187 | 0.0004107 | 6.0914 | 6.0918 | -3.3437 | 2434.8693 | 12641.6793 | -0.0013732
224 |  | 32.8777 | 56.5351 | 4187 | 0.00041069 | 6.0918 | 6.0922 | -3.3437 | 2434.9284 | 12698.2144 | -0.0013732
225 |  | 32.8777 | 56.5337 | 4187 | 0.00041068 | 6.0922 | 6.0927 | -3.3437 | 2434.9876 | 12754.7481 | -0.0013732
226 |  | 32.8777 | 56.5323 | 4187 | 0.00041067 | 6.0927 | 6.0931 | -3.3437 | 2435.0467 | 12811.2804 | -0.0013731
227 |  | 32.8777 | 56.5309 | 4187 | 0.00041066 | 6.0931 | 6.0935 | -3.3437 | 2435.1059 | 12867.8113 | -0.0013731
228 |  | 32.8777 | 56.5296 | 4187 | 0.00041065 | 6.0935 | 6.0939 | -3.3437 | 2435.165 | 12924.3409 | -0.0013731
229 |  | 32.8777 | 56.5282 | 4187 | 0.00041064 | 6.0939 | 6.0943 | -3.3437 | 2435.2242 | 12980.8691 | -0.001373
230 |  | 32.8777 | 56.5268 | 4187 | 0.00041063 | 6.0943 | 6.0947 | -3.3437 | 2435.2833 | 13037.3959 | -0.001373
231 |  | 32.8777 | 56.5255 | 4187 | 0.00041062 | 6.0947 | 6.0951 | -3.3437 | 2435.3425 | 13093.9214 | -0.001373
232 |  | 32.8777 | 56.5241 | 4187 | 0.00041061 | 6.0951 | 6.0955 | -3.3437 | 2435.4016 | 13150.4455 | -0.0013729
233 |  | 32.8777 | 56.5227 | 4187 | 0.0004106 | 6.0955 | 6.0959 | -3.3437 | 2435.4608 | 13206.9682 | -0.0013729
234 |  | 32.8777 | 56.5213 | 4187 | 0.00041059 | 6.0959 | 6.0964 | -3.3437 | 2435.5199 | 13263.4895 | -0.0013729
235 |  | 32.8777 | 56.52 | 4187 | 0.00041058 | 6.0964 | 6.0968 | -3.3437 | 2435.5791 | 13320.0095 | -0.0013728
236 |  | 32.8777 | 56.5186 | 4187 | 0.00041057 | 6.0968 | 6.0972 | -3.3437 | 2435.6383 | 13376.5281 | -0.0013728

## 315
|  |  | buis | verlies W/M | L /°C/sec
diam | wandikte |  | inhoud l/m |  | W/M
315 | 28.6 | 3.1416 | 52.1982 | 60.4509 | 4187
[8 empty] | J/sec/mtr | aantal mtr. | verlies
|  | buis | verlies W/M | L /°C/sec | verlies temp | begintemp | eindtemp | verlies | bij 1°C | totaal J/sec
|  | inhoud L |  | W/M | °C per M | °C | °C | per m°C | daling | aantal mtr
1 | 315 | 52.1982 | 60.4509 | 4187 | 0.0002766 | 6 | 6.0003 | -3.5559 | 3615.3934 | 60.4509 | -0.00098355
2 |  | 52.1982 | 60.45 | 4187 | 0.00027659 | 6.0003 | 6.0006 | -3.5559 | 3615.4522 | 120.9009 | -0.00098354
3 |  | 52.1982 | 60.449 | 4187 | 0.00027659 | 6.0006 | 6.0008 | -3.5559 | 3615.511 | 181.3499 | -0.00098352
4 |  | 52.1982 | 60.448 | 4187 | 0.00027658 | 6.0008 | 6.0011 | -3.5559 | 3615.5699 | 241.7979 | -0.00098351
5 |  | 52.1982 | 60.447 | 4187 | 0.00027658 | 6.0011 | 6.0014 | -3.5559 | 3615.6287 | 302.2449 | -0.00098349
6 |  | 52.1982 | 60.446 | 4187 | 0.00027657 | 6.0014 | 6.0017 | -3.5559 | 3615.6875 | 362.6909 | -0.00098347
7 |  | 52.1982 | 60.445 | 4187 | 0.00027657 | 6.0017 | 6.0019 | -3.5559 | 3615.7463 | 423.136 | -0.00098346
8 |  | 52.1982 | 60.4441 | 4187 | 0.00027656 | 6.0019 | 6.0022 | -3.5559 | 3615.8052 | 483.58 | -0.00098344
9 |  | 52.1982 | 60.4431 | 4187 | 0.00027656 | 6.0022 | 6.0025 | -3.5559 | 3615.864 | 544.0231 | -0.00098343
10 |  | 52.1982 | 60.4421 | 4187 | 0.00027655 | 6.0025 | 6.0028 | -3.5559 | 3615.9228 | 604.4652 | -0.00098341
11 |  | 52.1982 | 60.4411 | 4187 | 0.00027655 | 6.0028 | 6.003 | -3.5559 | 3615.9817 | 664.9063 | -0.00098339
12 |  | 52.1982 | 60.4401 | 4187 | 0.00027655 | 6.003 | 6.0033 | -3.5559 | 3616.0405 | 725.3465 | -0.00098338
13 |  | 52.1982 | 60.4391 | 4187 | 0.00027654 | 6.0033 | 6.0036 | -3.5559 | 3616.0993 | 785.7856 | -0.00098336
14 |  | 52.1982 | 60.4382 | 4187 | 0.00027654 | 6.0036 | 6.0039 | -3.5559 | 3616.1582 | 846.2238 | -0.00098335
15 |  | 52.1982 | 60.4372 | 4187 | 0.00027653 | 6.0039 | 6.0041 | -3.5559 | 3616.217 | 906.6609 | -0.00098333
16 |  | 52.1982 | 60.4362 | 4187 | 0.00027653 | 6.0041 | 6.0044 | -3.5559 | 3616.2758 | 967.0971 | -0.00098331
17 |  | 52.1982 | 60.4352 | 4187 | 0.00027652 | 6.0044 | 6.0047 | -3.5559 | 3616.3347 | 1027.5324 | -0.0009833
18 |  | 52.1982 | 60.4342 | 4187 | 0.00027652 | 6.0047 | 6.005 | -3.5559 | 3616.3935 | 1087.9666 | -0.00098328
19 |  | 52.1982 | 60.4332 | 4187 | 0.00027651 | 6.005 | 6.0053 | -3.5559 | 3616.4524 | 1148.3998 | -0.00098327
20 |  | 52.1982 | 60.4323 | 4187 | 0.00027651 | 6.0053 | 6.0055 | -3.5559 | 3616.5112 | 1208.8321 | -0.00098325
21 |  | 52.1982 | 60.4313 | 4187 | 0.00027651 | 6.0055 | 6.0058 | -3.5559 | 3616.57 | 1269.2634 | -0.00098323
22 |  | 52.1982 | 60.4303 | 4187 | 0.0002765 | 6.0058 | 6.0061 | -3.5559 | 3616.6289 | 1329.6937 | -0.00098322
23 |  | 52.1982 | 60.4293 | 4187 | 0.0002765 | 6.0061 | 6.0064 | -3.5559 | 3616.6877 | 1390.123 | -0.0009832
24 |  | 52.1982 | 60.4283 | 4187 | 0.00027649 | 6.0064 | 6.0066 | -3.5559 | 3616.7466 | 1450.5513 | -0.00098319
25 |  | 52.1982 | 60.4273 | 4187 | 0.00027649 | 6.0066 | 6.0069 | -3.5559 | 3616.8054 | 1510.9787 | -0.00098317
26 |  | 52.1982 | 60.4264 | 4187 | 0.00027648 | 6.0069 | 6.0072 | -3.5559 | 3616.8643 | 1571.405 | -0.00098315
27 |  | 52.1982 | 60.4254 | 4187 | 0.00027648 | 6.0072 | 6.0075 | -3.5559 | 3616.9231 | 1631.8304 | -0.00098314
28 |  | 52.1982 | 60.4244 | 4187 | 0.00027647 | 6.0075 | 6.0077 | -3.5559 | 3616.982 | 1692.2548 | -0.00098312
29 |  | 52.1982 | 60.4234 | 4187 | 0.00027647 | 6.0077 | 6.008 | -3.5559 | 3617.0408 | 1752.6782 | -0.00098311
30 |  | 52.1982 | 60.4224 | 4187 | 0.00027646 | 6.008 | 6.0083 | -3.5559 | 3617.0997 | 1813.1006 | -0.00098309
31 |  | 52.1982 | 60.4214 | 4187 | 0.00027646 | 6.0083 | 6.0086 | -3.5559 | 3617.1585 | 1873.5221 | -0.00098307
32 |  | 52.1982 | 60.4205 | 4187 | 0.00027646 | 6.0086 | 6.0088 | -3.5559 | 3617.2174 | 1933.9425 | -0.00098306
33 |  | 52.1982 | 60.4195 | 4187 | 0.00027645 | 6.0088 | 6.0091 | -3.5559 | 3617.2762 | 1994.362 | -0.00098304
34 |  | 52.1982 | 60.4185 | 4187 | 0.00027645 | 6.0091 | 6.0094 | -3.5559 | 3617.3351 | 2054.7805 | -0.00098303
35 |  | 52.1982 | 60.4175 | 4187 | 0.00027644 | 6.0094 | 6.0097 | -3.5559 | 3617.3939 | 2115.198 | -0.00098301
36 |  | 52.1982 | 60.4165 | 4187 | 0.00027644 | 6.0097 | 6.01 | -3.5559 | 3617.4528 | 2175.6146 | -0.000983
37 |  | 52.1982 | 60.4155 | 4187 | 0.00027643 | 6.01 | 6.0102 | -3.5559 | 3617.5117 | 2236.0301 | -0.00098298
38 |  | 52.1982 | 60.4146 | 4187 | 0.00027643 | 6.0102 | 6.0105 | -3.5559 | 3617.5705 | 2296.4447 | -0.00098296
39 |  | 52.1982 | 60.4136 | 4187 | 0.00027642 | 6.0105 | 6.0108 | -3.5559 | 3617.6294 | 2356.8583 | -0.00098295
40 |  | 52.1982 | 60.4126 | 4187 | 0.00027642 | 6.0108 | 6.0111 | -3.5559 | 3617.6882 | 2417.2709 | -0.00098293
41 |  | 52.1982 | 60.4116 | 4187 | 0.00027642 | 6.0111 | 6.0113 | -3.5559 | 3617.7471 | 2477.6825 | -0.00098292
42 |  | 52.1982 | 60.4106 | 4187 | 0.00027641 | 6.0113 | 6.0116 | -3.5559 | 3617.806 | 2538.0931 | -0.0009829
43 |  | 52.1982 | 60.4097 | 4187 | 0.00027641 | 6.0116 | 6.0119 | -3.5559 | 3617.8648 | 2598.5028 | -0.00098288
44 |  | 52.1982 | 60.4087 | 4187 | 0.0002764 | 6.0119 | 6.0122 | -3.5559 | 3617.9237 | 2658.9114 | -0.00098287
45 |  | 52.1982 | 60.4077 | 4187 | 0.0002764 | 6.0122 | 6.0124 | -3.5559 | 3617.9826 | 2719.3191 | -0.00098285
46 |  | 52.1982 | 60.4067 | 4187 | 0.00027639 | 6.0124 | 6.0127 | -3.5559 | 3618.0414 | 2779.7258 | -0.00098284
47 |  | 52.1982 | 60.4057 | 4187 | 0.00027639 | 6.0127 | 6.013 | -3.5559 | 3618.1003 | 2840.1316 | -0.00098282
48 |  | 52.1982 | 60.4047 | 4187 | 0.00027638 | 6.013 | 6.0133 | -3.5559 | 3618.1592 | 2900.5363 | -0.0009828
49 |  | 52.1982 | 60.4038 | 4187 | 0.00027638 | 6.0133 | 6.0135 | -3.5559 | 3618.218 | 2960.94 | -0.00098279
50 |  | 52.1982 | 60.4028 | 4187 | 0.00027637 | 6.0135 | 6.0138 | -3.5559 | 3618.2769 | 3021.3428 | -0.00098277
51 |  | 52.1982 | 60.4018 | 4187 | 0.00027637 | 6.0138 | 6.0141 | -3.5559 | 3618.3358 | 3081.7446 | -0.00098276
52 |  | 52.1982 | 60.4008 | 4187 | 0.00027637 | 6.0141 | 6.0144 | -3.5559 | 3618.3946 | 3142.1454 | -0.00098274
53 |  | 52.1982 | 60.3998 | 4187 | 0.00027636 | 6.0144 | 6.0147 | -3.5559 | 3618.4535 | 3202.5452 | -0.00098272
54 |  | 52.1982 | 60.3988 | 4187 | 0.00027636 | 6.0147 | 6.0149 | -3.5559 | 3618.5124 | 3262.9441 | -0.00098271
55 |  | 52.1982 | 60.3979 | 4187 | 0.00027635 | 6.0149 | 6.0152 | -3.5559 | 3618.5713 | 3323.3419 | -0.00098269
56 |  | 52.1982 | 60.3969 | 4187 | 0.00027635 | 6.0152 | 6.0155 | -3.5559 | 3618.6301 | 3383.7388 | -0.00098268
57 |  | 52.1982 | 60.3959 | 4187 | 0.00027634 | 6.0155 | 6.0158 | -3.5559 | 3618.689 | 3444.1347 | -0.00098266
58 |  | 52.1982 | 60.3949 | 4187 | 0.00027634 | 6.0158 | 6.016 | -3.5559 | 3618.7479 | 3504.5296 | -0.00098264
59 |  | 52.1982 | 60.3939 | 4187 | 0.00027633 | 6.016 | 6.0163 | -3.5559 | 3618.8068 | 3564.9235 | -0.00098263
60 |  | 52.1982 | 60.3929 | 4187 | 0.00027633 | 6.0163 | 6.0166 | -3.5559 | 3618.8657 | 3625.3165 | -0.00098261
61 |  | 52.1982 | 60.392 | 4187 | 0.00027633 | 6.0166 | 6.0169 | -3.5559 | 3618.9245 | 3685.7085 | -0.0009826
62 |  | 52.1982 | 60.391 | 4187 | 0.00027632 | 6.0169 | 6.0171 | -3.5559 | 3618.9834 | 3746.0994 | -0.00098258
63 |  | 52.1982 | 60.39 | 4187 | 0.00027632 | 6.0171 | 6.0174 | -3.5559 | 3619.0423 | 3806.4894 | -0.00098256
64 |  | 52.1982 | 60.389 | 4187 | 0.00027631 | 6.0174 | 6.0177 | -3.5559 | 3619.1012 | 3866.8784 | -0.00098255
65 |  | 52.1982 | 60.388 | 4187 | 0.00027631 | 6.0177 | 6.018 | -3.5559 | 3619.1601 | 3927.2665 | -0.00098253
66 |  | 52.1982 | 60.387 | 4187 | 0.0002763 | 6.018 | 6.0182 | -3.5559 | 3619.219 | 3987.6535 | -0.00098252
67 |  | 52.1982 | 60.3861 | 4187 | 0.0002763 | 6.0182 | 6.0185 | -3.5559 | 3619.2778 | 4048.0396 | -0.0009825
68 |  | 52.1982 | 60.3851 | 4187 | 0.00027629 | 6.0185 | 6.0188 | -3.5559 | 3619.3367 | 4108.4247 | -0.00098248
69 |  | 52.1982 | 60.3841 | 4187 | 0.00027629 | 6.0188 | 6.0191 | -3.5559 | 3619.3956 | 4168.8088 | -0.00098247
70 |  | 52.1982 | 60.3831 | 4187 | 0.00027628 | 6.0191 | 6.0194 | -3.5559 | 3619.4545 | 4229.1919 | -0.00098245
71 |  | 52.1982 | 60.3821 | 4187 | 0.00027628 | 6.0194 | 6.0196 | -3.5559 | 3619.5134 | 4289.574 | -0.00098244
72 |  | 52.1982 | 60.3812 | 4187 | 0.00027628 | 6.0196 | 6.0199 | -3.5559 | 3619.5723 | 4349.9552 | -0.00098242
73 |  | 52.1982 | 60.3802 | 4187 | 0.00027627 | 6.0199 | 6.0202 | -3.5559 | 3619.6312 | 4410.3354 | -0.0009824
74 |  | 52.1982 | 60.3792 | 4187 | 0.00027627 | 6.0202 | 6.0205 | -3.5559 | 3619.6901 | 4470.7146 | -0.00098239
75 |  | 52.1982 | 60.3782 | 4187 | 0.00027626 | 6.0205 | 6.0207 | -3.5559 | 3619.749 | 4531.0928 | -0.00098237
76 |  | 52.1982 | 60.3772 | 4187 | 0.00027626 | 6.0207 | 6.021 | -3.5559 | 3619.8079 | 4591.47 | -0.00098236
77 |  | 52.1982 | 60.3762 | 4187 | 0.00027625 | 6.021 | 6.0213 | -3.5559 | 3619.8668 | 4651.8462 | -0.00098234
78 |  | 52.1982 | 60.3753 | 4187 | 0.00027625 | 6.0213 | 6.0216 | -3.5559 | 3619.9257 | 4712.2215 | -0.00098232
79 |  | 52.1982 | 60.3743 | 4187 | 0.00027624 | 6.0216 | 6.0218 | -3.5559 | 3619.9846 | 4772.5958 | -0.00098231
80 |  | 52.1982 | 60.3733 | 4187 | 0.00027624 | 6.0218 | 6.0221 | -3.5559 | 3620.0435 | 4832.9691 | -0.00098229
81 |  | 52.1982 | 60.3723 | 4187 | 0.00027624 | 6.0221 | 6.0224 | -3.5559 | 3620.1024 | 4893.3414 | -0.00098228
82 |  | 52.1982 | 60.3713 | 4187 | 0.00027623 | 6.0224 | 6.0227 | -3.5559 | 3620.1613 | 4953.7127 | -0.00098226
83 |  | 52.1982 | 60.3703 | 4187 | 0.00027623 | 6.0227 | 6.0229 | -3.5559 | 3620.2202 | 5014.0831 | -0.00098224
84 |  | 52.1982 | 60.3694 | 4187 | 0.00027622 | 6.0229 | 6.0232 | -3.5559 | 3620.2791 | 5074.4524 | -0.00098223
85 |  | 52.1982 | 60.3684 | 4187 | 0.00027622 | 6.0232 | 6.0235 | -3.5559 | 3620.338 | 5134.8208 | -0.00098221
86 |  | 52.1982 | 60.3674 | 4187 | 0.00027621 | 6.0235 | 6.0238 | -3.5559 | 3620.3969 | 5195.1882 | -0.0009822
87 |  | 52.1982 | 60.3664 | 4187 | 0.00027621 | 6.0238 | 6.024 | -3.5559 | 3620.4558 | 5255.5546 | -0.00098218
88 |  | 52.1982 | 60.3654 | 4187 | 0.0002762 | 6.024 | 6.0243 | -3.5559 | 3620.5147 | 5315.9201 | -0.00098216
89 |  | 52.1982 | 60.3645 | 4187 | 0.0002762 | 6.0243 | 6.0246 | -3.5559 | 3620.5736 | 5376.2845 | -0.00098215
90 |  | 52.1982 | 60.3635 | 4187 | 0.00027619 | 6.0246 | 6.0249 | -3.5559 | 3620.6325 | 5436.648 | -0.00098213
91 |  | 52.1982 | 60.3625 | 4187 | 0.00027619 | 6.0249 | 6.0252 | -3.5559 | 3620.6914 | 5497.0105 | -0.00098212
92 |  | 52.1982 | 60.3615 | 4187 | 0.00027619 | 6.0252 | 6.0254 | -3.5559 | 3620.7503 | 5557.372 | -0.0009821
93 |  | 52.1982 | 60.3605 | 4187 | 0.00027618 | 6.0254 | 6.0257 | -3.5559 | 3620.8092 | 5617.7325 | -0.00098208
94 |  | 52.1982 | 60.3595 | 4187 | 0.00027618 | 6.0257 | 6.026 | -3.5559 | 3620.8681 | 5678.0921 | -0.00098207
95 |  | 52.1982 | 60.3586 | 4187 | 0.00027617 | 6.026 | 6.0263 | -3.5559 | 3620.9271 | 5738.4506 | -0.00098205
96 |  | 52.1982 | 60.3576 | 4187 | 0.00027617 | 6.0263 | 6.0265 | -3.5559 | 3620.986 | 5798.8082 | -0.00098204
97 |  | 52.1982 | 60.3566 | 4187 | 0.00027616 | 6.0265 | 6.0268 | -3.5559 | 3621.0449 | 5859.1648 | -0.00098202
98 |  | 52.1982 | 60.3556 | 4187 | 0.00027616 | 6.0268 | 6.0271 | -3.5559 | 3621.1038 | 5919.5204 | -0.000982
99 |  | 52.1982 | 60.3546 | 4187 | 0.00027615 | 6.0271 | 6.0274 | -3.5559 | 3621.1627 | 5979.8751 | -0.00098199
100 |  | 52.1982 | 60.3537 | 4187 | 0.00027615 | 6.0274 | 6.0276 | -3.5559 | 3621.2216 | 6040.2287 | -0.00098197
101 |  | 52.1982 | 60.3527 | 4187 | 0.00027615 | 6.0276 | 6.0279 | -3.5559 | 3621.2806 | 6100.5814 | -0.00098196
102 |  | 52.1982 | 60.3517 | 4187 | 0.00027614 | 6.0279 | 6.0282 | -3.5559 | 3621.3395 | 6160.9331 | -0.00098194
103 |  | 52.1982 | 60.3507 | 4187 | 0.00027614 | 6.0282 | 6.0285 | -3.5559 | 3621.3984 | 6221.2838 | -0.00098192
104 |  | 52.1982 | 60.3497 | 4187 | 0.00027613 | 6.0285 | 6.0287 | -3.5559 | 3621.4573 | 6281.6335 | -0.00098191
105 |  | 52.1982 | 60.3487 | 4187 | 0.00027613 | 6.0287 | 6.029 | -3.5559 | 3621.5162 | 6341.9822 | -0.00098189
106 |  | 52.1982 | 60.3478 | 4187 | 0.00027612 | 6.029 | 6.0293 | -3.5559 | 3621.5752 | 6402.33 | -0.00098188
107 |  | 52.1982 | 60.3468 | 4187 | 0.00027612 | 6.0293 | 6.0296 | -3.5559 | 3621.6341 | 6462.6768 | -0.00098186
108 |  | 52.1982 | 60.3458 | 4187 | 0.00027611 | 6.0296 | 6.0298 | -3.5559 | 3621.693 | 6523.0226 | -0.00098184
109 |  | 52.1982 | 60.3448 | 4187 | 0.00027611 | 6.0298 | 6.0301 | -3.5559 | 3621.752 | 6583.3674 | -0.00098183
110 |  | 52.1982 | 60.3438 | 4187 | 0.0002761 | 6.0301 | 6.0304 | -3.5559 | 3621.8109 | 6643.7112 | -0.00098181
111 |  | 52.1982 | 60.3429 | 4187 | 0.0002761 | 6.0304 | 6.0307 | -3.5559 | 3621.8698 | 6704.0541 | -0.0009818
112 |  | 52.1982 | 60.3419 | 4187 | 0.0002761 | 6.0307 | 6.031 | -3.5559 | 3621.9287 | 6764.396 | -0.00098178
113 |  | 52.1982 | 60.3409 | 4187 | 0.00027609 | 6.031 | 6.0312 | -3.5559 | 3621.9877 | 6824.7368 | -0.00098176
114 |  | 52.1982 | 60.3399 | 4187 | 0.00027609 | 6.0312 | 6.0315 | -3.5559 | 3622.0466 | 6885.0768 | -0.00098175
115 |  | 52.1982 | 60.3389 | 4187 | 0.00027608 | 6.0315 | 6.0318 | -3.5559 | 3622.1055 | 6945.4157 | -0.00098173
116 |  | 52.1982 | 60.3379 | 4187 | 0.00027608 | 6.0318 | 6.0321 | -3.5559 | 3622.1645 | 7005.7536 | -0.00098172
117 |  | 52.1982 | 60.337 | 4187 | 0.00027607 | 6.0321 | 6.0323 | -3.5559 | 3622.2234 | 7066.0906 | -0.0009817
118 |  | 52.1982 | 60.336 | 4187 | 0.00027607 | 6.0323 | 6.0326 | -3.5559 | 3622.2823 | 7126.4266 | -0.00098168
119 |  | 52.1982 | 60.335 | 4187 | 0.00027606 | 6.0326 | 6.0329 | -3.5559 | 3622.3413 | 7186.7616 | -0.00098167
120 |  | 52.1982 | 60.334 | 4187 | 0.00027606 | 6.0329 | 6.0332 | -3.5559 | 3622.4002 | 7247.0956 | -0.00098165
121 |  | 52.1982 | 60.333 | 4187 | 0.00027606 | 6.0332 | 6.0334 | -3.5559 | 3622.4592 | 7307.4286 | -0.00098164
122 |  | 52.1982 | 60.3321 | 4187 | 0.00027605 | 6.0334 | 6.0337 | -3.5559 | 3622.5181 | 7367.7607 | -0.00098162
123 |  | 52.1982 | 60.3311 | 4187 | 0.00027605 | 6.0337 | 6.034 | -3.5559 | 3622.577 | 7428.0917 | -0.0009816
124 |  | 52.1982 | 60.3301 | 4187 | 0.00027604 | 6.034 | 6.0343 | -3.5559 | 3622.636 | 7488.4218 | -0.00098159
125 |  | 52.1982 | 60.3291 | 4187 | 0.00027604 | 6.0343 | 6.0345 | -3.5559 | 3622.6949 | 7548.7509 | -0.00098157
126 |  | 52.1982 | 60.3281 | 4187 | 0.00027603 | 6.0345 | 6.0348 | -3.5559 | 3622.7539 | 7609.0791 | -0.00098156
127 |  | 52.1982 | 60.3271 | 4187 | 0.00027603 | 6.0348 | 6.0351 | -3.5559 | 3622.8128 | 7669.4062 | -0.00098154
128 |  | 52.1982 | 60.3262 | 4187 | 0.00027602 | 6.0351 | 6.0354 | -3.5559 | 3622.8717 | 7729.7324 | -0.00098152
129 |  | 52.1982 | 60.3252 | 4187 | 0.00027602 | 6.0354 | 6.0356 | -3.5559 | 3622.9307 | 7790.0576 | -0.00098151
130 |  | 52.1982 | 60.3242 | 4187 | 0.00027602 | 6.0356 | 6.0359 | -3.5559 | 3622.9896 | 7850.3818 | -0.00098149
131 |  | 52.1982 | 60.3232 | 4187 | 0.00027601 | 6.0359 | 6.0362 | -3.5559 | 3623.0486 | 7910.705 | -0.00098148
132 |  | 52.1982 | 60.3222 | 4187 | 0.00027601 | 6.0362 | 6.0365 | -3.5559 | 3623.1075 | 7971.0272 | -0.00098146
133 |  | 52.1982 | 60.3213 | 4187 | 0.000276 | 6.0365 | 6.0367 | -3.5559 | 3623.1665 | 8031.3485 | -0.00098144
134 |  | 52.1982 | 60.3203 | 4187 | 0.000276 | 6.0367 | 6.037 | -3.5559 | 3623.2254 | 8091.6687 | -0.00098143
135 |  | 52.1982 | 60.3193 | 4187 | 0.00027599 | 6.037 | 6.0373 | -3.5559 | 3623.2844 | 8151.988 | -0.00098141
136 |  | 52.1982 | 60.3183 | 4187 | 0.00027599 | 6.0373 | 6.0376 | -3.5559 | 3623.3433 | 8212.3063 | -0.0009814
137 |  | 52.1982 | 60.3173 | 4187 | 0.00027598 | 6.0376 | 6.0379 | -3.5559 | 3623.4023 | 8272.6237 | -0.00098138
138 |  | 52.1982 | 60.3163 | 4187 | 0.00027598 | 6.0379 | 6.0381 | -3.5559 | 3623.4613 | 8332.94 | -0.00098137
139 |  | 52.1982 | 60.3154 | 4187 | 0.00027597 | 6.0381 | 6.0384 | -3.5559 | 3623.5202 | 8393.2554 | -0.00098135
140 |  | 52.1982 | 60.3144 | 4187 | 0.00027597 | 6.0384 | 6.0387 | -3.5559 | 3623.5792 | 8453.5698 | -0.00098133
141 |  | 52.1982 | 60.3134 | 4187 | 0.00027597 | 6.0387 | 6.039 | -3.5559 | 3623.6381 | 8513.8832 | -0.00098132
142 |  | 52.1982 | 60.3124 | 4187 | 0.00027596 | 6.039 | 6.0392 | -3.5559 | 3623.6971 | 8574.1956 | -0.0009813
143 |  | 52.1982 | 60.3114 | 4187 | 0.00027596 | 6.0392 | 6.0395 | -3.5559 | 3623.756 | 8634.5071 | -0.00098129
144 |  | 52.1982 | 60.3105 | 4187 | 0.00027595 | 6.0395 | 6.0398 | -3.5559 | 3623.815 | 8694.8175 | -0.00098127
145 |  | 52.1982 | 60.3095 | 4187 | 0.00027595 | 6.0398 | 6.0401 | -3.5559 | 3623.874 | 8755.127 | -0.00098125
146 |  | 52.1982 | 60.3085 | 4187 | 0.00027594 | 6.0401 | 6.0403 | -3.5559 | 3623.9329 | 8815.4355 | -0.00098124
147 |  | 52.1982 | 60.3075 | 4187 | 0.00027594 | 6.0403 | 6.0406 | -3.5559 | 3623.9919 | 8875.743 | -0.00098122
148 |  | 52.1982 | 60.3065 | 4187 | 0.00027593 | 6.0406 | 6.0409 | -3.5559 | 3624.0509 | 8936.0495 | -0.00098121
149 |  | 52.1982 | 60.3056 | 4187 | 0.00027593 | 6.0409 | 6.0412 | -3.5559 | 3624.1098 | 8996.3551 | -0.00098119
150 |  | 52.1982 | 60.3046 | 4187 | 0.00027593 | 6.0412 | 6.0414 | -3.5559 | 3624.1688 | 9056.6597 | -0.00098117
151 |  | 52.1982 | 60.3036 | 4187 | 0.00027592 | 6.0414 | 6.0417 | -3.5559 | 3624.2278 | 9116.9633 | -0.00098116
152 |  | 52.1982 | 60.3026 | 4187 | 0.00027592 | 6.0417 | 6.042 | -3.5559 | 3624.2867 | 9177.2659 | -0.00098114
153 |  | 52.1982 | 60.3016 | 4187 | 0.00027591 | 6.042 | 6.0423 | -3.5559 | 3624.3457 | 9237.5675 | -0.00098113
154 |  | 52.1982 | 60.3006 | 4187 | 0.00027591 | 6.0423 | 6.0425 | -3.5559 | 3624.4047 | 9297.8682 | -0.00098111
155 |  | 52.1982 | 60.2997 | 4187 | 0.0002759 | 6.0425 | 6.0428 | -3.5559 | 3624.4636 | 9358.1678 | -0.00098109
156 |  | 52.1982 | 60.2987 | 4187 | 0.0002759 | 6.0428 | 6.0431 | -3.5559 | 3624.5226 | 9418.4665 | -0.00098108
157 |  | 52.1982 | 60.2977 | 4187 | 0.00027589 | 6.0431 | 6.0434 | -3.5559 | 3624.5816 | 9478.7642 | -0.00098106
158 |  | 52.1982 | 60.2967 | 4187 | 0.00027589 | 6.0434 | 6.0436 | -3.5559 | 3624.6405 | 9539.0609 | -0.00098105
159 |  | 52.1982 | 60.2957 | 4187 | 0.00027588 | 6.0436 | 6.0439 | -3.5559 | 3624.6995 | 9599.3567 | -0.00098103
160 |  | 52.1982 | 60.2948 | 4187 | 0.00027588 | 6.0439 | 6.0442 | -3.5559 | 3624.7585 | 9659.6515 | -0.00098101
161 |  | 52.1982 | 60.2938 | 4187 | 0.00027588 | 6.0442 | 6.0445 | -3.5559 | 3624.8175 | 9719.9452 | -0.000981
162 |  | 52.1982 | 60.2928 | 4187 | 0.00027587 | 6.0445 | 6.0447 | -3.5559 | 3624.8765 | 9780.238 | -0.00098098
163 |  | 52.1982 | 60.2918 | 4187 | 0.00027587 | 6.0447 | 6.045 | -3.5559 | 3624.9354 | 9840.5299 | -0.00098097
164 |  | 52.1982 | 60.2908 | 4187 | 0.00027586 | 6.045 | 6.0453 | -3.5559 | 3624.9944 | 9900.8207 | -0.00098095
165 |  | 52.1982 | 60.2899 | 4187 | 0.00027586 | 6.0453 | 6.0456 | -3.5559 | 3625.0534 | 9961.1106 | -0.00098093
166 |  | 52.1982 | 60.2889 | 4187 | 0.00027585 | 6.0456 | 6.0459 | -3.5559 | 3625.1124 | 10021.3994 | -0.00098092
167 |  | 52.1982 | 60.2879 | 4187 | 0.00027585 | 6.0459 | 6.0461 | -3.5559 | 3625.1714 | 10081.6873 | -0.0009809
168 |  | 52.1982 | 60.2869 | 4187 | 0.00027584 | 6.0461 | 6.0464 | -3.5559 | 3625.2303 | 10141.9742 | -0.00098089
169 |  | 52.1982 | 60.2859 | 4187 | 0.00027584 | 6.0464 | 6.0467 | -3.5559 | 3625.2893 | 10202.2602 | -0.00098087
170 |  | 52.1982 | 60.285 | 4187 | 0.00027584 | 6.0467 | 6.047 | -3.5559 | 3625.3483 | 10262.5451 | -0.00098085
171 |  | 52.1982 | 60.284 | 4187 | 0.00027583 | 6.047 | 6.0472 | -3.5559 | 3625.4073 | 10322.8291 | -0.00098084
172 |  | 52.1982 | 60.283 | 4187 | 0.00027583 | 6.0472 | 6.0475 | -3.5559 | 3625.4663 | 10383.1121 | -0.00098082
173 |  | 52.1982 | 60.282 | 4187 | 0.00027582 | 6.0475 | 6.0478 | -3.5559 | 3625.5253 | 10443.3941 | -0.00098081
174 |  | 52.1982 | 60.281 | 4187 | 0.00027582 | 6.0478 | 6.0481 | -3.5559 | 3625.5843 | 10503.6751 | -0.00098079
175 |  | 52.1982 | 60.28 | 4187 | 0.00027581 | 6.0481 | 6.0483 | -3.5559 | 3625.6433 | 10563.9552 | -0.00098077
176 |  | 52.1982 | 60.2791 | 4187 | 0.00027581 | 6.0483 | 6.0486 | -3.5559 | 3625.7022 | 10624.2343 | -0.00098076
177 |  | 52.1982 | 60.2781 | 4187 | 0.0002758 | 6.0486 | 6.0489 | -3.5559 | 3625.7612 | 10684.5123 | -0.00098074
178 |  | 52.1982 | 60.2771 | 4187 | 0.0002758 | 6.0489 | 6.0492 | -3.5559 | 3625.8202 | 10744.7894 | -0.00098073
179 |  | 52.1982 | 60.2761 | 4187 | 0.0002758 | 6.0492 | 6.0494 | -3.5559 | 3625.8792 | 10805.0656 | -0.00098071
180 |  | 52.1982 | 60.2751 | 4187 | 0.00027579 | 6.0494 | 6.0497 | -3.5559 | 3625.9382 | 10865.3407 | -0.00098069
181 |  | 52.1982 | 60.2742 | 4187 | 0.00027579 | 6.0497 | 6.05 | -3.5559 | 3625.9972 | 10925.6149 | -0.00098068
182 |  | 52.1982 | 60.2732 | 4187 | 0.00027578 | 6.05 | 6.0503 | -3.5559 | 3626.0562 | 10985.8881 | -0.00098066
183 |  | 52.1982 | 60.2722 | 4187 | 0.00027578 | 6.0503 | 6.0505 | -3.5559 | 3626.1152 | 11046.1603 | -0.00098065
184 |  | 52.1982 | 60.2712 | 4187 | 0.00027577 | 6.0505 | 6.0508 | -3.5559 | 3626.1742 | 11106.4315 | -0.00098063
185 |  | 52.1982 | 60.2702 | 4187 | 0.00027577 | 6.0508 | 6.0511 | -3.5559 | 3626.2332 | 11166.7017 | -0.00098061
186 |  | 52.1982 | 60.2693 | 4187 | 0.00027576 | 6.0511 | 6.0514 | -3.5559 | 3626.2922 | 11226.971 | -0.0009806
187 |  | 52.1982 | 60.2683 | 4187 | 0.00027576 | 6.0514 | 6.0516 | -3.5559 | 3626.3512 | 11287.2393 | -0.00098058
188 |  | 52.1982 | 60.2673 | 4187 | 0.00027575 | 6.0516 | 6.0519 | -3.5559 | 3626.4102 | 11347.5066 | -0.00098057
189 |  | 52.1982 | 60.2663 | 4187 | 0.00027575 | 6.0519 | 6.0522 | -3.5559 | 3626.4692 | 11407.7729 | -0.00098055
190 |  | 52.1982 | 60.2653 | 4187 | 0.00027575 | 6.0522 | 6.0525 | -3.5559 | 3626.5282 | 11468.0382 | -0.00098054
191 |  | 52.1982 | 60.2644 | 4187 | 0.00027574 | 6.0525 | 6.0527 | -3.5559 | 3626.5872 | 11528.3026 | -0.00098052
192 |  | 52.1982 | 60.2634 | 4187 | 0.00027574 | 6.0527 | 6.053 | -3.5559 | 3626.6462 | 11588.566 | -0.0009805
193 |  | 52.1982 | 60.2624 | 4187 | 0.00027573 | 6.053 | 6.0533 | -3.5559 | 3626.7052 | 11648.8284 | -0.00098049
194 |  | 52.1982 | 60.2614 | 4187 | 0.00027573 | 6.0533 | 6.0536 | -3.5559 | 3626.7643 | 11709.0898 | -0.00098047
195 |  | 52.1982 | 60.2604 | 4187 | 0.00027572 | 6.0536 | 6.0539 | -3.5559 | 3626.8233 | 11769.3502 | -0.00098046
196 |  | 52.1982 | 60.2595 | 4187 | 0.00027572 | 6.0539 | 6.0541 | -3.5559 | 3626.8823 | 11829.6097 | -0.00098044
197 |  | 52.1982 | 60.2585 | 4187 | 0.00027571 | 6.0541 | 6.0544 | -3.5559 | 3626.9413 | 11889.8682 | -0.00098042
198 |  | 52.1982 | 60.2575 | 4187 | 0.00027571 | 6.0544 | 6.0547 | -3.5559 | 3627.0003 | 11950.1257 | -0.00098041
199 |  | 52.1982 | 60.2565 | 4187 | 0.00027571 | 6.0547 | 6.055 | -3.5559 | 3627.0593 | 12010.3822 | -0.00098039
200 |  | 52.1982 | 60.2555 | 4187 | 0.0002757 | 6.055 | 6.0552 | -3.5559 | 3627.1183 | 12070.6377 | -0.00098038
201 |  | 52.1982 | 60.2546 | 4187 | 0.0002757 | 6.0552 | 6.0555 | -3.5559 | 3627.1773 | 12130.8923 | -0.00098036
202 |  | 52.1982 | 60.2536 | 4187 | 0.00027569 | 6.0555 | 6.0558 | -3.5559 | 3627.2364 | 12191.1458 | -0.00098034
203 |  | 52.1982 | 60.2526 | 4187 | 0.00027569 | 6.0558 | 6.0561 | -3.5559 | 3627.2954 | 12251.3984 | -0.00098033
204 |  | 52.1982 | 60.2516 | 4187 | 0.00027568 | 6.0561 | 6.0563 | -3.5559 | 3627.3544 | 12311.65 | -0.00098031
205 |  | 52.1982 | 60.2506 | 4187 | 0.00027568 | 6.0563 | 6.0566 | -3.5559 | 3627.4134 | 12371.9007 | -0.0009803
206 |  | 52.1982 | 60.2497 | 4187 | 0.00027567 | 6.0566 | 6.0569 | -3.5559 | 3627.4724 | 12432.1503 | -0.00098028
207 |  | 52.1982 | 60.2487 | 4187 | 0.00027567 | 6.0569 | 6.0572 | -3.5559 | 3627.5315 | 12492.399 | -0.00098026
208 |  | 52.1982 | 60.2477 | 4187 | 0.00027567 | 6.0572 | 6.0574 | -3.5559 | 3627.5905 | 12552.6467 | -0.00098025
209 |  | 52.1982 | 60.2467 | 4187 | 0.00027566 | 6.0574 | 6.0577 | -3.5559 | 3627.6495 | 12612.8934 | -0.00098023
210 |  | 52.1982 | 60.2457 | 4187 | 0.00027566 | 6.0577 | 6.058 | -3.5559 | 3627.7085 | 12673.1391 | -0.00098022
211 |  | 52.1982 | 60.2448 | 4187 | 0.00027565 | 6.058 | 6.0583 | -3.5559 | 3627.7675 | 12733.3839 | -0.0009802
212 |  | 52.1982 | 60.2438 | 4187 | 0.00027565 | 6.0583 | 6.0585 | -3.5559 | 3627.8266 | 12793.6277 | -0.00098018
213 |  | 52.1982 | 60.2428 | 4187 | 0.00027564 | 6.0585 | 6.0588 | -3.5559 | 3627.8856 | 12853.8705 | -0.00098017
214 |  | 52.1982 | 60.2418 | 4187 | 0.00027564 | 6.0588 | 6.0591 | -3.5559 | 3627.9446 | 12914.1123 | -0.00098015
215 |  | 52.1982 | 60.2408 | 4187 | 0.00027563 | 6.0591 | 6.0594 | -3.5559 | 3628.0037 | 12974.3531 | -0.00098014
216 |  | 52.1982 | 60.2399 | 4187 | 0.00027563 | 6.0594 | 6.0596 | -3.5559 | 3628.0627 | 13034.5929 | -0.00098012
217 |  | 52.1982 | 60.2389 | 4187 | 0.00027562 | 6.0596 | 6.0599 | -3.5559 | 3628.1217 | 13094.8318 | -0.0009801
218 |  | 52.1982 | 60.2379 | 4187 | 0.00027562 | 6.0599 | 6.0602 | -3.5559 | 3628.1807 | 13155.0697 | -0.00098009
219 |  | 52.1982 | 60.2369 | 4187 | 0.00027562 | 6.0602 | 6.0605 | -3.5559 | 3628.2398 | 13215.3066 | -0.00098007
220 |  | 52.1982 | 60.2359 | 4187 | 0.00027561 | 6.0605 | 6.0607 | -3.5559 | 3628.2988 | 13275.5425 | -0.00098006
221 |  | 52.1982 | 60.235 | 4187 | 0.00027561 | 6.0607 | 6.061 | -3.5559 | 3628.3578 | 13335.7775 | -0.00098004
222 |  | 52.1982 | 60.234 | 4187 | 0.0002756 | 6.061 | 6.0613 | -3.5559 | 3628.4169 | 13396.0115 | -0.00098002
223 |  | 52.1982 | 60.233 | 4187 | 0.0002756 | 6.0613 | 6.0616 | -3.5559 | 3628.4759 | 13456.2445 | -0.00098001
224 |  | 52.1982 | 60.232 | 4187 | 0.00027559 | 6.0616 | 6.0618 | -3.5559 | 3628.535 | 13516.4765 | -0.00097999
225 |  | 52.1982 | 60.231 | 4187 | 0.00027559 | 6.0618 | 6.0621 | -3.5559 | 3628.594 | 13576.7075 | -0.00097998
226 |  | 52.1982 | 60.2301 | 4187 | 0.00027558 | 6.0621 | 6.0624 | -3.5559 | 3628.653 | 13636.9375 | -0.00097996
227 |  | 52.1982 | 60.2291 | 4187 | 0.00027558 | 6.0624 | 6.0627 | -3.5559 | 3628.7121 | 13697.1666 | -0.00097994
228 |  | 52.1982 | 60.2281 | 4187 | 0.00027558 | 6.0627 | 6.0629 | -3.5559 | 3628.7711 | 13757.3947 | -0.00097993
229 |  | 52.1982 | 60.2271 | 4187 | 0.00027557 | 6.0629 | 6.0632 | -3.5559 | 3628.8302 | 13817.6218 | -0.00097991
230 |  | 52.1982 | 60.2261 | 4187 | 0.00027557 | 6.0632 | 6.0635 | -3.5559 | 3628.8892 | 13877.8479 | -0.0009799
231 |  | 52.1982 | 60.2252 | 4187 | 0.00027556 | 6.0635 | 6.0638 | -3.5559 | 3628.9482 | 13938.0731 | -0.00097988
232 |  | 52.1982 | 60.2242 | 4187 | 0.00027556 | 6.0638 | 6.064 | -3.5559 | 3629.0073 | 13998.2973 | -0.00097987
233 |  | 52.1982 | 60.2232 | 4187 | 0.00027555 | 6.064 | 6.0643 | -3.5559 | 3629.0663 | 14058.5205 | -0.00097985
234 |  | 52.1982 | 60.2222 | 4187 | 0.00027555 | 6.0643 | 6.0646 | -3.5559 | 3629.1254 | 14118.7427 | -0.00097983
235 |  | 52.1982 | 60.2212 | 4187 | 0.00027554 | 6.0646 | 6.0649 | -3.5559 | 3629.1844 | 14178.9639 | -0.00097982
236 |  | 52.1982 | 60.2203 | 4187 | 0.00027554 | 6.0649 | 6.0652 | -3.5559 | 3629.2435 | 14239.1842 | -0.0009798

## 355
|  |  | buis | verlies W/M | L /°C/sec
diam | wandikte |  | inhoud l/m |  | W/M
355 | 32.2 | 3.1416 | 66.3256 | 62.2125 | 4187
[8 empty] | J/sec/mtr | aantal mtr. | verlies
|  | buis | verlies W/M | L /°C/sec | verlies temp | begintemp | eindtemp | verlies | bij 1°C | totaal J/sec
|  | inhoud L |  | W/M | °C per M | °C | °C | per m°C | daling | aantal mtr
1 | 355 | 66.3256 | 62.2125 | 4187 | 0.00022402 | 6 | 6.0002 | -3.6596 | 4463.8161 | 62.2125 | -0.00081983
2 |  | 66.3256 | 62.2117 | 4187 | 0.00022402 | 6.0002 | 6.0004 | -3.6596 | 4463.8749 | 124.4242 | -0.00081982
3 |  | 66.3256 | 62.2109 | 4187 | 0.00022402 | 6.0004 | 6.0007 | -3.6596 | 4463.9337 | 186.6351 | -0.00081981
4 |  | 66.3256 | 62.2101 | 4187 | 0.00022401 | 6.0007 | 6.0009 | -3.6596 | 4463.9926 | 248.8451 | -0.0008198
5 |  | 66.3256 | 62.2092 | 4187 | 0.00022401 | 6.0009 | 6.0011 | -3.6596 | 4464.0514 | 311.0544 | -0.00081978
6 |  | 66.3256 | 62.2084 | 4187 | 0.00022401 | 6.0011 | 6.0013 | -3.6596 | 4464.1102 | 373.2628 | -0.00081977
7 |  | 66.3256 | 62.2076 | 4187 | 0.00022401 | 6.0013 | 6.0016 | -3.6596 | 4464.1691 | 435.4704 | -0.00081976
8 |  | 66.3256 | 62.2068 | 4187 | 0.000224 | 6.0016 | 6.0018 | -3.6596 | 4464.2279 | 497.6772 | -0.00081975
9 |  | 66.3256 | 62.206 | 4187 | 0.000224 | 6.0018 | 6.002 | -3.6596 | 4464.2867 | 559.8831 | -0.00081974
10 |  | 66.3256 | 62.2051 | 4187 | 0.000224 | 6.002 | 6.0022 | -3.6596 | 4464.3455 | 622.0883 | -0.00081973
11 |  | 66.3256 | 62.2043 | 4187 | 0.00022399 | 6.0022 | 6.0025 | -3.6596 | 4464.4044 | 684.2926 | -0.00081972
12 |  | 66.3256 | 62.2035 | 4187 | 0.00022399 | 6.0025 | 6.0027 | -3.6596 | 4464.4632 | 746.4961 | -0.00081971
13 |  | 66.3256 | 62.2027 | 4187 | 0.00022399 | 6.0027 | 6.0029 | -3.6596 | 4464.522 | 808.6988 | -0.0008197
14 |  | 66.3256 | 62.2019 | 4187 | 0.00022399 | 6.0029 | 6.0031 | -3.6596 | 4464.5809 | 870.9006 | -0.00081969
15 |  | 66.3256 | 62.201 | 4187 | 0.00022398 | 6.0031 | 6.0034 | -3.6596 | 4464.6397 | 933.1017 | -0.00081968
16 |  | 66.3256 | 62.2002 | 4187 | 0.00022398 | 6.0034 | 6.0036 | -3.6596 | 4464.6985 | 995.3019 | -0.00081967
17 |  | 66.3256 | 62.1994 | 4187 | 0.00022398 | 6.0036 | 6.0038 | -3.6596 | 4464.7574 | 1057.5013 | -0.00081965
18 |  | 66.3256 | 62.1986 | 4187 | 0.00022397 | 6.0038 | 6.004 | -3.6596 | 4464.8162 | 1119.6999 | -0.00081964
19 |  | 66.3256 | 62.1978 | 4187 | 0.00022397 | 6.004 | 6.0043 | -3.6596 | 4464.8751 | 1181.8976 | -0.00081963
20 |  | 66.3256 | 62.1969 | 4187 | 0.00022397 | 6.0043 | 6.0045 | -3.6596 | 4464.9339 | 1244.0946 | -0.00081962
21 |  | 66.3256 | 62.1961 | 4187 | 0.00022396 | 6.0045 | 6.0047 | -3.6596 | 4464.9927 | 1306.2907 | -0.00081961
22 |  | 66.3256 | 62.1953 | 4187 | 0.00022396 | 6.0047 | 6.0049 | -3.6596 | 4465.0516 | 1368.486 | -0.0008196
23 |  | 66.3256 | 62.1945 | 4187 | 0.00022396 | 6.0049 | 6.0052 | -3.6596 | 4465.1104 | 1430.6805 | -0.00081959
24 |  | 66.3256 | 62.1937 | 4187 | 0.00022396 | 6.0052 | 6.0054 | -3.6596 | 4465.1693 | 1492.8741 | -0.00081958
25 |  | 66.3256 | 62.1928 | 4187 | 0.00022395 | 6.0054 | 6.0056 | -3.6596 | 4465.2281 | 1555.067 | -0.00081957
26 |  | 66.3256 | 62.192 | 4187 | 0.00022395 | 6.0056 | 6.0058 | -3.6596 | 4465.2869 | 1617.259 | -0.00081956
27 |  | 66.3256 | 62.1912 | 4187 | 0.00022395 | 6.0058 | 6.006 | -3.6596 | 4465.3458 | 1679.4502 | -0.00081955
28 |  | 66.3256 | 62.1904 | 4187 | 0.00022394 | 6.006 | 6.0063 | -3.6596 | 4465.4046 | 1741.6406 | -0.00081954
29 |  | 66.3256 | 62.1896 | 4187 | 0.00022394 | 6.0063 | 6.0065 | -3.6596 | 4465.4635 | 1803.8302 | -0.00081953
30 |  | 66.3256 | 62.1887 | 4187 | 0.00022394 | 6.0065 | 6.0067 | -3.6596 | 4465.5223 | 1866.0189 | -0.00081951
31 |  | 66.3256 | 62.1879 | 4187 | 0.00022394 | 6.0067 | 6.0069 | -3.6596 | 4465.5812 | 1928.2068 | -0.0008195
32 |  | 66.3256 | 62.1871 | 4187 | 0.00022393 | 6.0069 | 6.0072 | -3.6596 | 4465.64 | 1990.3939 | -0.00081949
33 |  | 66.3256 | 62.1863 | 4187 | 0.00022393 | 6.0072 | 6.0074 | -3.6596 | 4465.6989 | 2052.5802 | -0.00081948
34 |  | 66.3256 | 62.1855 | 4187 | 0.00022393 | 6.0074 | 6.0076 | -3.6596 | 4465.7577 | 2114.7657 | -0.00081947
35 |  | 66.3256 | 62.1846 | 4187 | 0.00022392 | 6.0076 | 6.0078 | -3.6596 | 4465.8166 | 2176.9503 | -0.00081946
36 |  | 66.3256 | 62.1838 | 4187 | 0.00022392 | 6.0078 | 6.0081 | -3.6596 | 4465.8754 | 2239.1342 | -0.00081945
37 |  | 66.3256 | 62.183 | 4187 | 0.00022392 | 6.0081 | 6.0083 | -3.6596 | 4465.9343 | 2301.3172 | -0.00081944
38 |  | 66.3256 | 62.1822 | 4187 | 0.00022391 | 6.0083 | 6.0085 | -3.6596 | 4465.9931 | 2363.4994 | -0.00081943
39 |  | 66.3256 | 62.1814 | 4187 | 0.00022391 | 6.0085 | 6.0087 | -3.6596 | 4466.052 | 2425.6807 | -0.00081942
40 |  | 66.3256 | 62.1806 | 4187 | 0.00022391 | 6.0087 | 6.009 | -3.6596 | 4466.1108 | 2487.8613 | -0.00081941
41 |  | 66.3256 | 62.1797 | 4187 | 0.00022391 | 6.009 | 6.0092 | -3.6596 | 4466.1697 | 2550.041 | -0.0008194
42 |  | 66.3256 | 62.1789 | 4187 | 0.0002239 | 6.0092 | 6.0094 | -3.6596 | 4466.2285 | 2612.2199 | -0.00081938
43 |  | 66.3256 | 62.1781 | 4187 | 0.0002239 | 6.0094 | 6.0096 | -3.6596 | 4466.2874 | 2674.398 | -0.00081937
44 |  | 66.3256 | 62.1773 | 4187 | 0.0002239 | 6.0096 | 6.0099 | -3.6596 | 4466.3462 | 2736.5753 | -0.00081936
45 |  | 66.3256 | 62.1765 | 4187 | 0.00022389 | 6.0099 | 6.0101 | -3.6596 | 4466.4051 | 2798.7518 | -0.00081935
46 |  | 66.3256 | 62.1756 | 4187 | 0.00022389 | 6.0101 | 6.0103 | -3.6596 | 4466.464 | 2860.9274 | -0.00081934
47 |  | 66.3256 | 62.1748 | 4187 | 0.00022389 | 6.0103 | 6.0105 | -3.6596 | 4466.5228 | 2923.1022 | -0.00081933
48 |  | 66.3256 | 62.174 | 4187 | 0.00022388 | 6.0105 | 6.0107 | -3.6596 | 4466.5817 | 2985.2762 | -0.00081932
49 |  | 66.3256 | 62.1732 | 4187 | 0.00022388 | 6.0107 | 6.011 | -3.6596 | 4466.6405 | 3047.4494 | -0.00081931
50 |  | 66.3256 | 62.1724 | 4187 | 0.00022388 | 6.011 | 6.0112 | -3.6596 | 4466.6994 | 3109.6217 | -0.0008193
51 |  | 66.3256 | 62.1715 | 4187 | 0.00022388 | 6.0112 | 6.0114 | -3.6596 | 4466.7583 | 3171.7933 | -0.00081929
52 |  | 66.3256 | 62.1707 | 4187 | 0.00022387 | 6.0114 | 6.0116 | -3.6596 | 4466.8171 | 3233.964 | -0.00081928
53 |  | 66.3256 | 62.1699 | 4187 | 0.00022387 | 6.0116 | 6.0119 | -3.6596 | 4466.876 | 3296.1339 | -0.00081927
54 |  | 66.3256 | 62.1691 | 4187 | 0.00022387 | 6.0119 | 6.0121 | -3.6596 | 4466.9349 | 3358.303 | -0.00081926
55 |  | 66.3256 | 62.1683 | 4187 | 0.00022386 | 6.0121 | 6.0123 | -3.6596 | 4466.9937 | 3420.4712 | -0.00081924
56 |  | 66.3256 | 62.1674 | 4187 | 0.00022386 | 6.0123 | 6.0125 | -3.6596 | 4467.0526 | 3482.6387 | -0.00081923
57 |  | 66.3256 | 62.1666 | 4187 | 0.00022386 | 6.0125 | 6.0128 | -3.6596 | 4467.1115 | 3544.8053 | -0.00081922
58 |  | 66.3256 | 62.1658 | 4187 | 0.00022386 | 6.0128 | 6.013 | -3.6596 | 4467.1703 | 3606.9711 | -0.00081921
59 |  | 66.3256 | 62.165 | 4187 | 0.00022385 | 6.013 | 6.0132 | -3.6596 | 4467.2292 | 3669.1361 | -0.0008192
60 |  | 66.3256 | 62.1642 | 4187 | 0.00022385 | 6.0132 | 6.0134 | -3.6596 | 4467.2881 | 3731.3003 | -0.00081919
61 |  | 66.3256 | 62.1633 | 4187 | 0.00022385 | 6.0134 | 6.0137 | -3.6596 | 4467.3469 | 3793.4636 | -0.00081918
62 |  | 66.3256 | 62.1625 | 4187 | 0.00022384 | 6.0137 | 6.0139 | -3.6596 | 4467.4058 | 3855.6261 | -0.00081917
63 |  | 66.3256 | 62.1617 | 4187 | 0.00022384 | 6.0139 | 6.0141 | -3.6596 | 4467.4647 | 3917.7878 | -0.00081916
64 |  | 66.3256 | 62.1609 | 4187 | 0.00022384 | 6.0141 | 6.0143 | -3.6596 | 4467.5235 | 3979.9487 | -0.00081915
65 |  | 66.3256 | 62.1601 | 4187 | 0.00022383 | 6.0143 | 6.0146 | -3.6596 | 4467.5824 | 4042.1088 | -0.00081914
66 |  | 66.3256 | 62.1593 | 4187 | 0.00022383 | 6.0146 | 6.0148 | -3.6596 | 4467.6413 | 4104.268 | -0.00081913
67 |  | 66.3256 | 62.1584 | 4187 | 0.00022383 | 6.0148 | 6.015 | -3.6596 | 4467.7002 | 4166.4265 | -0.00081911
68 |  | 66.3256 | 62.1576 | 4187 | 0.00022383 | 6.015 | 6.0152 | -3.6596 | 4467.759 | 4228.5841 | -0.0008191
69 |  | 66.3256 | 62.1568 | 4187 | 0.00022382 | 6.0152 | 6.0155 | -3.6596 | 4467.8179 | 4290.7409 | -0.00081909
70 |  | 66.3256 | 62.156 | 4187 | 0.00022382 | 6.0155 | 6.0157 | -3.6596 | 4467.8768 | 4352.8969 | -0.00081908
71 |  | 66.3256 | 62.1552 | 4187 | 0.00022382 | 6.0157 | 6.0159 | -3.6596 | 4467.9357 | 4415.052 | -0.00081907
72 |  | 66.3256 | 62.1543 | 4187 | 0.00022381 | 6.0159 | 6.0161 | -3.6596 | 4467.9945 | 4477.2063 | -0.00081906
73 |  | 66.3256 | 62.1535 | 4187 | 0.00022381 | 6.0161 | 6.0163 | -3.6596 | 4468.0534 | 4539.3599 | -0.00081905
74 |  | 66.3256 | 62.1527 | 4187 | 0.00022381 | 6.0163 | 6.0166 | -3.6596 | 4468.1123 | 4601.5126 | -0.00081904
75 |  | 66.3256 | 62.1519 | 4187 | 0.00022381 | 6.0166 | 6.0168 | -3.6596 | 4468.1712 | 4663.6644 | -0.00081903
76 |  | 66.3256 | 62.1511 | 4187 | 0.0002238 | 6.0168 | 6.017 | -3.6596 | 4468.2301 | 4725.8155 | -0.00081902
77 |  | 66.3256 | 62.1502 | 4187 | 0.0002238 | 6.017 | 6.0172 | -3.6596 | 4468.289 | 4787.9657 | -0.00081901
78 |  | 66.3256 | 62.1494 | 4187 | 0.0002238 | 6.0172 | 6.0175 | -3.6596 | 4468.3478 | 4850.1152 | -0.000819
79 |  | 66.3256 | 62.1486 | 4187 | 0.00022379 | 6.0175 | 6.0177 | -3.6596 | 4468.4067 | 4912.2638 | -0.00081899
80 |  | 66.3256 | 62.1478 | 4187 | 0.00022379 | 6.0177 | 6.0179 | -3.6596 | 4468.4656 | 4974.4115 | -0.00081897
81 |  | 66.3256 | 62.147 | 4187 | 0.00022379 | 6.0179 | 6.0181 | -3.6596 | 4468.5245 | 5036.5585 | -0.00081896
82 |  | 66.3256 | 62.1461 | 4187 | 0.00022378 | 6.0181 | 6.0184 | -3.6596 | 4468.5834 | 5098.7047 | -0.00081895
83 |  | 66.3256 | 62.1453 | 4187 | 0.00022378 | 6.0184 | 6.0186 | -3.6596 | 4468.6423 | 5160.85 | -0.00081894
84 |  | 66.3256 | 62.1445 | 4187 | 0.00022378 | 6.0186 | 6.0188 | -3.6596 | 4468.7012 | 5222.9945 | -0.00081893
85 |  | 66.3256 | 62.1437 | 4187 | 0.00022378 | 6.0188 | 6.019 | -3.6596 | 4468.76 | 5285.1382 | -0.00081892
86 |  | 66.3256 | 62.1429 | 4187 | 0.00022377 | 6.019 | 6.0193 | -3.6596 | 4468.8189 | 5347.281 | -0.00081891
87 |  | 66.3256 | 62.1421 | 4187 | 0.00022377 | 6.0193 | 6.0195 | -3.6596 | 4468.8778 | 5409.4231 | -0.0008189
88 |  | 66.3256 | 62.1412 | 4187 | 0.00022377 | 6.0195 | 6.0197 | -3.6596 | 4468.9367 | 5471.5643 | -0.00081889
89 |  | 66.3256 | 62.1404 | 4187 | 0.00022376 | 6.0197 | 6.0199 | -3.6596 | 4468.9956 | 5533.7047 | -0.00081888
90 |  | 66.3256 | 62.1396 | 4187 | 0.00022376 | 6.0199 | 6.0202 | -3.6596 | 4469.0545 | 5595.8443 | -0.00081887
91 |  | 66.3256 | 62.1388 | 4187 | 0.00022376 | 6.0202 | 6.0204 | -3.6596 | 4469.1134 | 5657.9831 | -0.00081886
92 |  | 66.3256 | 62.138 | 4187 | 0.00022376 | 6.0204 | 6.0206 | -3.6596 | 4469.1723 | 5720.1211 | -0.00081885
93 |  | 66.3256 | 62.1371 | 4187 | 0.00022375 | 6.0206 | 6.0208 | -3.6596 | 4469.2312 | 5782.2582 | -0.00081883
94 |  | 66.3256 | 62.1363 | 4187 | 0.00022375 | 6.0208 | 6.021 | -3.6596 | 4469.2901 | 5844.3945 | -0.00081882
95 |  | 66.3256 | 62.1355 | 4187 | 0.00022375 | 6.021 | 6.0213 | -3.6596 | 4469.349 | 5906.53 | -0.00081881
96 |  | 66.3256 | 62.1347 | 4187 | 0.00022374 | 6.0213 | 6.0215 | -3.6596 | 4469.4079 | 5968.6647 | -0.0008188
97 |  | 66.3256 | 62.1339 | 4187 | 0.00022374 | 6.0215 | 6.0217 | -3.6596 | 4469.4668 | 6030.7986 | -0.00081879
98 |  | 66.3256 | 62.133 | 4187 | 0.00022374 | 6.0217 | 6.0219 | -3.6596 | 4469.5257 | 6092.9316 | -0.00081878
99 |  | 66.3256 | 62.1322 | 4187 | 0.00022373 | 6.0219 | 6.0222 | -3.6596 | 4469.5846 | 6155.0638 | -0.00081877
100 |  | 66.3256 | 62.1314 | 4187 | 0.00022373 | 6.0222 | 6.0224 | -3.6596 | 4469.6435 | 6217.1952 | -0.00081876
101 |  | 66.3256 | 62.1306 | 4187 | 0.00022373 | 6.0224 | 6.0226 | -3.6596 | 4469.7024 | 6279.3258 | -0.00081875
102 |  | 66.3256 | 62.1298 | 4187 | 0.00022373 | 6.0226 | 6.0228 | -3.6596 | 4469.7613 | 6341.4556 | -0.00081874
103 |  | 66.3256 | 62.1289 | 4187 | 0.00022372 | 6.0228 | 6.0231 | -3.6596 | 4469.8202 | 6403.5845 | -0.00081873
104 |  | 66.3256 | 62.1281 | 4187 | 0.00022372 | 6.0231 | 6.0233 | -3.6596 | 4469.8791 | 6465.7127 | -0.00081872
105 |  | 66.3256 | 62.1273 | 4187 | 0.00022372 | 6.0233 | 6.0235 | -3.6596 | 4469.938 | 6527.84 | -0.0008187
106 |  | 66.3256 | 62.1265 | 4187 | 0.00022371 | 6.0235 | 6.0237 | -3.6596 | 4469.9969 | 6589.9665 | -0.00081869
107 |  | 66.3256 | 62.1257 | 4187 | 0.00022371 | 6.0237 | 6.024 | -3.6596 | 4470.0558 | 6652.0922 | -0.00081868
108 |  | 66.3256 | 62.1249 | 4187 | 0.00022371 | 6.024 | 6.0242 | -3.6596 | 4470.1147 | 6714.217 | -0.00081867
109 |  | 66.3256 | 62.124 | 4187 | 0.0002237 | 6.0242 | 6.0244 | -3.6596 | 4470.1736 | 6776.3411 | -0.00081866
110 |  | 66.3256 | 62.1232 | 4187 | 0.0002237 | 6.0244 | 6.0246 | -3.6596 | 4470.2325 | 6838.4643 | -0.00081865
111 |  | 66.3256 | 62.1224 | 4187 | 0.0002237 | 6.0246 | 6.0248 | -3.6596 | 4470.2914 | 6900.5867 | -0.00081864
112 |  | 66.3256 | 62.1216 | 4187 | 0.0002237 | 6.0248 | 6.0251 | -3.6596 | 4470.3503 | 6962.7083 | -0.00081863
113 |  | 66.3256 | 62.1208 | 4187 | 0.00022369 | 6.0251 | 6.0253 | -3.6596 | 4470.4092 | 7024.829 | -0.00081862
114 |  | 66.3256 | 62.1199 | 4187 | 0.00022369 | 6.0253 | 6.0255 | -3.6596 | 4470.4682 | 7086.949 | -0.00081861
115 |  | 66.3256 | 62.1191 | 4187 | 0.00022369 | 6.0255 | 6.0257 | -3.6596 | 4470.5271 | 7149.0681 | -0.0008186
116 |  | 66.3256 | 62.1183 | 4187 | 0.00022368 | 6.0257 | 6.026 | -3.6596 | 4470.586 | 7211.1864 | -0.00081859
117 |  | 66.3256 | 62.1175 | 4187 | 0.00022368 | 6.026 | 6.0262 | -3.6596 | 4470.6449 | 7273.3039 | -0.00081858
118 |  | 66.3256 | 62.1167 | 4187 | 0.00022368 | 6.0262 | 6.0264 | -3.6596 | 4470.7038 | 7335.4205 | -0.00081856
119 |  | 66.3256 | 62.1159 | 4187 | 0.00022368 | 6.0264 | 6.0266 | -3.6596 | 4470.7627 | 7397.5364 | -0.00081855
120 |  | 66.3256 | 62.115 | 4187 | 0.00022367 | 6.0266 | 6.0269 | -3.6596 | 4470.8216 | 7459.6514 | -0.00081854
121 |  | 66.3256 | 62.1142 | 4187 | 0.00022367 | 6.0269 | 6.0271 | -3.6596 | 4470.8806 | 7521.7656 | -0.00081853
122 |  | 66.3256 | 62.1134 | 4187 | 0.00022367 | 6.0271 | 6.0273 | -3.6596 | 4470.9395 | 7583.879 | -0.00081852
123 |  | 66.3256 | 62.1126 | 4187 | 0.00022366 | 6.0273 | 6.0275 | -3.6596 | 4470.9984 | 7645.9916 | -0.00081851
124 |  | 66.3256 | 62.1118 | 4187 | 0.00022366 | 6.0275 | 6.0278 | -3.6596 | 4471.0573 | 7708.1034 | -0.0008185
125 |  | 66.3256 | 62.1109 | 4187 | 0.00022366 | 6.0278 | 6.028 | -3.6596 | 4471.1162 | 7770.2143 | -0.00081849
126 |  | 66.3256 | 62.1101 | 4187 | 0.00022365 | 6.028 | 6.0282 | -3.6596 | 4471.1751 | 7832.3244 | -0.00081848
127 |  | 66.3256 | 62.1093 | 4187 | 0.00022365 | 6.0282 | 6.0284 | -3.6596 | 4471.2341 | 7894.4337 | -0.00081847
128 |  | 66.3256 | 62.1085 | 4187 | 0.00022365 | 6.0284 | 6.0287 | -3.6596 | 4471.293 | 7956.5422 | -0.00081846
129 |  | 66.3256 | 62.1077 | 4187 | 0.00022365 | 6.0287 | 6.0289 | -3.6596 | 4471.3519 | 8018.6499 | -0.00081845
130 |  | 66.3256 | 62.1068 | 4187 | 0.00022364 | 6.0289 | 6.0291 | -3.6596 | 4471.4108 | 8080.7567 | -0.00081844
131 |  | 66.3256 | 62.106 | 4187 | 0.00022364 | 6.0291 | 6.0293 | -3.6596 | 4471.4698 | 8142.8628 | -0.00081842
132 |  | 66.3256 | 62.1052 | 4187 | 0.00022364 | 6.0293 | 6.0295 | -3.6596 | 4471.5287 | 8204.968 | -0.00081841
133 |  | 66.3256 | 62.1044 | 4187 | 0.00022363 | 6.0295 | 6.0298 | -3.6596 | 4471.5876 | 8267.0724 | -0.0008184
134 |  | 66.3256 | 62.1036 | 4187 | 0.00022363 | 6.0298 | 6.03 | -3.6596 | 4471.6465 | 8329.1759 | -0.00081839
135 |  | 66.3256 | 62.1028 | 4187 | 0.00022363 | 6.03 | 6.0302 | -3.6596 | 4471.7055 | 8391.2787 | -0.00081838
136 |  | 66.3256 | 62.1019 | 4187 | 0.00022363 | 6.0302 | 6.0304 | -3.6596 | 4471.7644 | 8453.3806 | -0.00081837
137 |  | 66.3256 | 62.1011 | 4187 | 0.00022362 | 6.0304 | 6.0307 | -3.6596 | 4471.8233 | 8515.4818 | -0.00081836
138 |  | 66.3256 | 62.1003 | 4187 | 0.00022362 | 6.0307 | 6.0309 | -3.6596 | 4471.8823 | 8577.5821 | -0.00081835
139 |  | 66.3256 | 62.0995 | 4187 | 0.00022362 | 6.0309 | 6.0311 | -3.6596 | 4471.9412 | 8639.6815 | -0.00081834
140 |  | 66.3256 | 62.0987 | 4187 | 0.00022361 | 6.0311 | 6.0313 | -3.6596 | 4472.0001 | 8701.7802 | -0.00081833
141 |  | 66.3256 | 62.0978 | 4187 | 0.00022361 | 6.0313 | 6.0316 | -3.6596 | 4472.059 | 8763.8781 | -0.00081832
142 |  | 66.3256 | 62.097 | 4187 | 0.00022361 | 6.0316 | 6.0318 | -3.6596 | 4472.118 | 8825.9751 | -0.00081831
143 |  | 66.3256 | 62.0962 | 4187 | 0.0002236 | 6.0318 | 6.032 | -3.6596 | 4472.1769 | 8888.0713 | -0.00081829
144 |  | 66.3256 | 62.0954 | 4187 | 0.0002236 | 6.032 | 6.0322 | -3.6596 | 4472.2358 | 8950.1667 | -0.00081828
145 |  | 66.3256 | 62.0946 | 4187 | 0.0002236 | 6.0322 | 6.0325 | -3.6596 | 4472.2948 | 9012.2613 | -0.00081827
146 |  | 66.3256 | 62.0938 | 4187 | 0.0002236 | 6.0325 | 6.0327 | -3.6596 | 4472.3537 | 9074.355 | -0.00081826
147 |  | 66.3256 | 62.0929 | 4187 | 0.00022359 | 6.0327 | 6.0329 | -3.6596 | 4472.4127 | 9136.4479 | -0.00081825
148 |  | 66.3256 | 62.0921 | 4187 | 0.00022359 | 6.0329 | 6.0331 | -3.6596 | 4472.4716 | 9198.5401 | -0.00081824
149 |  | 66.3256 | 62.0913 | 4187 | 0.00022359 | 6.0331 | 6.0333 | -3.6596 | 4472.5305 | 9260.6314 | -0.00081823
150 |  | 66.3256 | 62.0905 | 4187 | 0.00022358 | 6.0333 | 6.0336 | -3.6596 | 4472.5895 | 9322.7218 | -0.00081822
151 |  | 66.3256 | 62.0897 | 4187 | 0.00022358 | 6.0336 | 6.0338 | -3.6596 | 4472.6484 | 9384.8115 | -0.00081821
152 |  | 66.3256 | 62.0888 | 4187 | 0.00022358 | 6.0338 | 6.034 | -3.6596 | 4472.7074 | 9446.9003 | -0.0008182
153 |  | 66.3256 | 62.088 | 4187 | 0.00022358 | 6.034 | 6.0342 | -3.6596 | 4472.7663 | 9508.9884 | -0.00081819
154 |  | 66.3256 | 62.0872 | 4187 | 0.00022357 | 6.0342 | 6.0345 | -3.6596 | 4472.8252 | 9571.0756 | -0.00081818
155 |  | 66.3256 | 62.0864 | 4187 | 0.00022357 | 6.0345 | 6.0347 | -3.6596 | 4472.8842 | 9633.162 | -0.00081817
156 |  | 66.3256 | 62.0856 | 4187 | 0.00022357 | 6.0347 | 6.0349 | -3.6596 | 4472.9431 | 9695.2475 | -0.00081815
157 |  | 66.3256 | 62.0848 | 4187 | 0.00022356 | 6.0349 | 6.0351 | -3.6596 | 4473.0021 | 9757.3323 | -0.00081814
158 |  | 66.3256 | 62.0839 | 4187 | 0.00022356 | 6.0351 | 6.0354 | -3.6596 | 4473.061 | 9819.4162 | -0.00081813
159 |  | 66.3256 | 62.0831 | 4187 | 0.00022356 | 6.0354 | 6.0356 | -3.6596 | 4473.12 | 9881.4994 | -0.00081812
160 |  | 66.3256 | 62.0823 | 4187 | 0.00022355 | 6.0356 | 6.0358 | -3.6596 | 4473.1789 | 9943.5817 | -0.00081811
161 |  | 66.3256 | 62.0815 | 4187 | 0.00022355 | 6.0358 | 6.036 | -3.6596 | 4473.2379 | 10005.6631 | -0.0008181
162 |  | 66.3256 | 62.0807 | 4187 | 0.00022355 | 6.036 | 6.0363 | -3.6596 | 4473.2968 | 10067.7438 | -0.00081809
163 |  | 66.3256 | 62.0798 | 4187 | 0.00022355 | 6.0363 | 6.0365 | -3.6596 | 4473.3557 | 10129.8236 | -0.00081808
164 |  | 66.3256 | 62.079 | 4187 | 0.00022354 | 6.0365 | 6.0367 | -3.6596 | 4473.4147 | 10191.9027 | -0.00081807
165 |  | 66.3256 | 62.0782 | 4187 | 0.00022354 | 6.0367 | 6.0369 | -3.6596 | 4473.4737 | 10253.9809 | -0.00081806
166 |  | 66.3256 | 62.0774 | 4187 | 0.00022354 | 6.0369 | 6.0371 | -3.6596 | 4473.5326 | 10316.0583 | -0.00081805
167 |  | 66.3256 | 62.0766 | 4187 | 0.00022353 | 6.0371 | 6.0374 | -3.6596 | 4473.5916 | 10378.1348 | -0.00081804
168 |  | 66.3256 | 62.0758 | 4187 | 0.00022353 | 6.0374 | 6.0376 | -3.6596 | 4473.6505 | 10440.2106 | -0.00081803
169 |  | 66.3256 | 62.0749 | 4187 | 0.00022353 | 6.0376 | 6.0378 | -3.6596 | 4473.7095 | 10502.2855 | -0.00081801
170 |  | 66.3256 | 62.0741 | 4187 | 0.00022353 | 6.0378 | 6.038 | -3.6596 | 4473.7684 | 10564.3597 | -0.000818
171 |  | 66.3256 | 62.0733 | 4187 | 0.00022352 | 6.038 | 6.0383 | -3.6596 | 4473.8274 | 10626.433 | -0.00081799
172 |  | 66.3256 | 62.0725 | 4187 | 0.00022352 | 6.0383 | 6.0385 | -3.6596 | 4473.8863 | 10688.5054 | -0.00081798
173 |  | 66.3256 | 62.0717 | 4187 | 0.00022352 | 6.0385 | 6.0387 | -3.6596 | 4473.9453 | 10750.5771 | -0.00081797
174 |  | 66.3256 | 62.0708 | 4187 | 0.00022351 | 6.0387 | 6.0389 | -3.6596 | 4474.0042 | 10812.6479 | -0.00081796
175 |  | 66.3256 | 62.07 | 4187 | 0.00022351 | 6.0389 | 6.0392 | -3.6596 | 4474.0632 | 10874.718 | -0.00081795
176 |  | 66.3256 | 62.0692 | 4187 | 0.00022351 | 6.0392 | 6.0394 | -3.6596 | 4474.1222 | 10936.7872 | -0.00081794
177 |  | 66.3256 | 62.0684 | 4187 | 0.0002235 | 6.0394 | 6.0396 | -3.6596 | 4474.1811 | 10998.8556 | -0.00081793
178 |  | 66.3256 | 62.0676 | 4187 | 0.0002235 | 6.0396 | 6.0398 | -3.6596 | 4474.2401 | 11060.9232 | -0.00081792
179 |  | 66.3256 | 62.0668 | 4187 | 0.0002235 | 6.0398 | 6.0401 | -3.6596 | 4474.299 | 11122.9899 | -0.00081791
180 |  | 66.3256 | 62.0659 | 4187 | 0.0002235 | 6.0401 | 6.0403 | -3.6596 | 4474.358 | 11185.0559 | -0.0008179
181 |  | 66.3256 | 62.0651 | 4187 | 0.00022349 | 6.0403 | 6.0405 | -3.6596 | 4474.417 | 11247.121 | -0.00081789
182 |  | 66.3256 | 62.0643 | 4187 | 0.00022349 | 6.0405 | 6.0407 | -3.6596 | 4474.4759 | 11309.1853 | -0.00081787
183 |  | 66.3256 | 62.0635 | 4187 | 0.00022349 | 6.0407 | 6.0409 | -3.6596 | 4474.5349 | 11371.2488 | -0.00081786
184 |  | 66.3256 | 62.0627 | 4187 | 0.00022348 | 6.0409 | 6.0412 | -3.6596 | 4474.5939 | 11433.3114 | -0.00081785
185 |  | 66.3256 | 62.0618 | 4187 | 0.00022348 | 6.0412 | 6.0414 | -3.6596 | 4474.6528 | 11495.3733 | -0.00081784
186 |  | 66.3256 | 62.061 | 4187 | 0.00022348 | 6.0414 | 6.0416 | -3.6596 | 4474.7118 | 11557.4343 | -0.00081783
187 |  | 66.3256 | 62.0602 | 4187 | 0.00022348 | 6.0416 | 6.0418 | -3.6596 | 4474.7708 | 11619.4945 | -0.00081782
188 |  | 66.3256 | 62.0594 | 4187 | 0.00022347 | 6.0418 | 6.0421 | -3.6596 | 4474.8297 | 11681.5539 | -0.00081781
189 |  | 66.3256 | 62.0586 | 4187 | 0.00022347 | 6.0421 | 6.0423 | -3.6596 | 4474.8887 | 11743.6125 | -0.0008178
190 |  | 66.3256 | 62.0578 | 4187 | 0.00022347 | 6.0423 | 6.0425 | -3.6596 | 4474.9477 | 11805.6703 | -0.00081779
191 |  | 66.3256 | 62.0569 | 4187 | 0.00022346 | 6.0425 | 6.0427 | -3.6596 | 4475.0066 | 11867.7272 | -0.00081778
192 |  | 66.3256 | 62.0561 | 4187 | 0.00022346 | 6.0427 | 6.043 | -3.6596 | 4475.0656 | 11929.7833 | -0.00081777
193 |  | 66.3256 | 62.0553 | 4187 | 0.00022346 | 6.043 | 6.0432 | -3.6596 | 4475.1246 | 11991.8386 | -0.00081776
194 |  | 66.3256 | 62.0545 | 4187 | 0.00022345 | 6.0432 | 6.0434 | -3.6596 | 4475.1836 | 12053.8931 | -0.00081775
195 |  | 66.3256 | 62.0537 | 4187 | 0.00022345 | 6.0434 | 6.0436 | -3.6596 | 4475.2425 | 12115.9468 | -0.00081773
196 |  | 66.3256 | 62.0529 | 4187 | 0.00022345 | 6.0436 | 6.0439 | -3.6596 | 4475.3015 | 12177.9997 | -0.00081772
197 |  | 66.3256 | 62.052 | 4187 | 0.00022345 | 6.0439 | 6.0441 | -3.6596 | 4475.3605 | 12240.0517 | -0.00081771
198 |  | 66.3256 | 62.0512 | 4187 | 0.00022344 | 6.0441 | 6.0443 | -3.6596 | 4475.4195 | 12302.1029 | -0.0008177
199 |  | 66.3256 | 62.0504 | 4187 | 0.00022344 | 6.0443 | 6.0445 | -3.6596 | 4475.4784 | 12364.1533 | -0.00081769
200 |  | 66.3256 | 62.0496 | 4187 | 0.00022344 | 6.0445 | 6.0447 | -3.6596 | 4475.5374 | 12426.2029 | -0.00081768
201 |  | 66.3256 | 62.0488 | 4187 | 0.00022343 | 6.0447 | 6.045 | -3.6596 | 4475.5964 | 12488.2517 | -0.00081767
202 |  | 66.3256 | 62.0479 | 4187 | 0.00022343 | 6.045 | 6.0452 | -3.6596 | 4475.6554 | 12550.2996 | -0.00081766
203 |  | 66.3256 | 62.0471 | 4187 | 0.00022343 | 6.0452 | 6.0454 | -3.6596 | 4475.7144 | 12612.3467 | -0.00081765
204 |  | 66.3256 | 62.0463 | 4187 | 0.00022343 | 6.0454 | 6.0456 | -3.6596 | 4475.7733 | 12674.393 | -0.00081764
205 |  | 66.3256 | 62.0455 | 4187 | 0.00022342 | 6.0456 | 6.0459 | -3.6596 | 4475.8323 | 12736.4385 | -0.00081763
206 |  | 66.3256 | 62.0447 | 4187 | 0.00022342 | 6.0459 | 6.0461 | -3.6596 | 4475.8913 | 12798.4832 | -0.00081762
207 |  | 66.3256 | 62.0439 | 4187 | 0.00022342 | 6.0461 | 6.0463 | -3.6596 | 4475.9503 | 12860.5271 | -0.00081761
208 |  | 66.3256 | 62.043 | 4187 | 0.00022341 | 6.0463 | 6.0465 | -3.6596 | 4476.0093 | 12922.5701 | -0.00081759
209 |  | 66.3256 | 62.0422 | 4187 | 0.00022341 | 6.0465 | 6.0468 | -3.6596 | 4476.0683 | 12984.6123 | -0.00081758
210 |  | 66.3256 | 62.0414 | 4187 | 0.00022341 | 6.0468 | 6.047 | -3.6596 | 4476.1272 | 13046.6538 | -0.00081757
211 |  | 66.3256 | 62.0406 | 4187 | 0.0002234 | 6.047 | 6.0472 | -3.6596 | 4476.1862 | 13108.6943 | -0.00081756
212 |  | 66.3256 | 62.0398 | 4187 | 0.0002234 | 6.0472 | 6.0474 | -3.6596 | 4476.2452 | 13170.7341 | -0.00081755
213 |  | 66.3256 | 62.039 | 4187 | 0.0002234 | 6.0474 | 6.0477 | -3.6596 | 4476.3042 | 13232.7731 | -0.00081754
214 |  | 66.3256 | 62.0381 | 4187 | 0.0002234 | 6.0477 | 6.0479 | -3.6596 | 4476.3632 | 13294.8112 | -0.00081753
215 |  | 66.3256 | 62.0373 | 4187 | 0.00022339 | 6.0479 | 6.0481 | -3.6596 | 4476.4222 | 13356.8485 | -0.00081752
216 |  | 66.3256 | 62.0365 | 4187 | 0.00022339 | 6.0481 | 6.0483 | -3.6596 | 4476.4812 | 13418.885 | -0.00081751
217 |  | 66.3256 | 62.0357 | 4187 | 0.00022339 | 6.0483 | 6.0485 | -3.6596 | 4476.5402 | 13480.9207 | -0.0008175
218 |  | 66.3256 | 62.0349 | 4187 | 0.00022338 | 6.0485 | 6.0488 | -3.6596 | 4476.5992 | 13542.9556 | -0.00081749
219 |  | 66.3256 | 62.034 | 4187 | 0.00022338 | 6.0488 | 6.049 | -3.6596 | 4476.6581 | 13604.9896 | -0.00081748
220 |  | 66.3256 | 62.0332 | 4187 | 0.00022338 | 6.049 | 6.0492 | -3.6596 | 4476.7171 | 13667.0229 | -0.00081747
221 |  | 66.3256 | 62.0324 | 4187 | 0.00022338 | 6.0492 | 6.0494 | -3.6596 | 4476.7761 | 13729.0553 | -0.00081745
222 |  | 66.3256 | 62.0316 | 4187 | 0.00022337 | 6.0494 | 6.0497 | -3.6596 | 4476.8351 | 13791.0869 | -0.00081744
223 |  | 66.3256 | 62.0308 | 4187 | 0.00022337 | 6.0497 | 6.0499 | -3.6596 | 4476.8941 | 13853.1177 | -0.00081743
224 |  | 66.3256 | 62.03 | 4187 | 0.00022337 | 6.0499 | 6.0501 | -3.6596 | 4476.9531 | 13915.1476 | -0.00081742
225 |  | 66.3256 | 62.0291 | 4187 | 0.00022336 | 6.0501 | 6.0503 | -3.6596 | 4477.0121 | 13977.1768 | -0.00081741
226 |  | 66.3256 | 62.0283 | 4187 | 0.00022336 | 6.0503 | 6.0506 | -3.6596 | 4477.0711 | 14039.2051 | -0.0008174
227 |  | 66.3256 | 62.0275 | 4187 | 0.00022336 | 6.0506 | 6.0508 | -3.6596 | 4477.1301 | 14101.2326 | -0.00081739
228 |  | 66.3256 | 62.0267 | 4187 | 0.00022335 | 6.0508 | 6.051 | -3.6596 | 4477.1891 | 14163.2593 | -0.00081738
229 |  | 66.3256 | 62.0259 | 4187 | 0.00022335 | 6.051 | 6.0512 | -3.6596 | 4477.2481 | 14225.2852 | -0.00081737
230 |  | 66.3256 | 62.0251 | 4187 | 0.00022335 | 6.0512 | 6.0514 | -3.6596 | 4477.3071 | 14287.3102 | -0.00081736
231 |  | 66.3256 | 62.0242 | 4187 | 0.00022335 | 6.0514 | 6.0517 | -3.6596 | 4477.3661 | 14349.3345 | -0.00081735
232 |  | 66.3256 | 62.0234 | 4187 | 0.00022334 | 6.0517 | 6.0519 | -3.6596 | 4477.4251 | 14411.3579 | -0.00081734
233 |  | 66.3256 | 62.0226 | 4187 | 0.00022334 | 6.0519 | 6.0521 | -3.6596 | 4477.4841 | 14473.3805 | -0.00081733
234 |  | 66.3256 | 62.0218 | 4187 | 0.00022334 | 6.0521 | 6.0523 | -3.6596 | 4477.5431 | 14535.4023 | -0.00081731
235 |  | 66.3256 | 62.021 | 4187 | 0.00022333 | 6.0523 | 6.0526 | -3.6596 | 4477.6021 | 14597.4232 | -0.0008173
236 |  | 66.3256 | 62.0202 | 4187 | 0.00022333 | 6.0526 | 6.0528 | -3.6596 | 4477.6611 | 14659.4434 | -0.00081729

## 400
|  |  | buis | verlies W/M | L /°C/sec
diam | wandikte |  | inhoud l/m |  | W/M
400 | 36.3 | 3.1416 | 84.1874 | 63.7834 | 4187
[8 empty] | J/sec/mtr | aantal mtr. | verlies
|  | buis | verlies W/M | L /°C/sec | verlies temp | begintemp | eindtemp | verlies | bij 1°C | totaal J/sec
|  | inhoud L |  | W/M | °C per M | °C | °C | per m°C | daling | aantal mtr
1 | 400 | 84.1874 | 63.7834 | 4187 | 0.00018095 | 6 | 6.0002 | -3.752 | 5526.3996 | 63.7834 | -0.00067892
2 |  | 84.1874 | 63.7828 | 4187 | 0.00018095 | 6.0002 | 6.0004 | -3.752 | 5526.4584 | 127.5662 | -0.00067891
3 |  | 84.1874 | 63.7821 | 4187 | 0.00018095 | 6.0004 | 6.0005 | -3.752 | 5526.5172 | 191.3483 | -0.0006789
4 |  | 84.1874 | 63.7814 | 4187 | 0.00018094 | 6.0005 | 6.0007 | -3.752 | 5526.576 | 255.1297 | -0.0006789
5 |  | 84.1874 | 63.7807 | 4187 | 0.00018094 | 6.0007 | 6.0009 | -3.752 | 5526.6349 | 318.9104 | -0.00067889
6 |  | 84.1874 | 63.78 | 4187 | 0.00018094 | 6.0009 | 6.0011 | -3.752 | 5526.6937 | 382.6904 | -0.00067888
7 |  | 84.1874 | 63.7794 | 4187 | 0.00018094 | 6.0011 | 6.0013 | -3.752 | 5526.7525 | 446.4698 | -0.00067887
8 |  | 84.1874 | 63.7787 | 4187 | 0.00018094 | 6.0013 | 6.0014 | -3.752 | 5526.8114 | 510.2485 | -0.00067887
9 |  | 84.1874 | 63.778 | 4187 | 0.00018093 | 6.0014 | 6.0016 | -3.752 | 5526.8702 | 574.0265 | -0.00067886
10 |  | 84.1874 | 63.7773 | 4187 | 0.00018093 | 6.0016 | 6.0018 | -3.752 | 5526.929 | 637.8038 | -0.00067885
11 |  | 84.1874 | 63.7766 | 4187 | 0.00018093 | 6.0018 | 6.002 | -3.752 | 5526.9878 | 701.5805 | -0.00067884
12 |  | 84.1874 | 63.776 | 4187 | 0.00018093 | 6.002 | 6.0022 | -3.752 | 5527.0467 | 765.3564 | -0.00067884
13 |  | 84.1874 | 63.7753 | 4187 | 0.00018093 | 6.0022 | 6.0024 | -3.752 | 5527.1055 | 829.1317 | -0.00067883
14 |  | 84.1874 | 63.7746 | 4187 | 0.00018092 | 6.0024 | 6.0025 | -3.752 | 5527.1643 | 892.9063 | -0.00067882
15 |  | 84.1874 | 63.7739 | 4187 | 0.00018092 | 6.0025 | 6.0027 | -3.752 | 5527.2232 | 956.6803 | -0.00067882
16 |  | 84.1874 | 63.7733 | 4187 | 0.00018092 | 6.0027 | 6.0029 | -3.752 | 5527.282 | 1020.4535 | -0.00067881
17 |  | 84.1874 | 63.7726 | 4187 | 0.00018092 | 6.0029 | 6.0031 | -3.752 | 5527.3408 | 1084.2261 | -0.0006788
18 |  | 84.1874 | 63.7719 | 4187 | 0.00018092 | 6.0031 | 6.0033 | -3.752 | 5527.3997 | 1147.998 | -0.00067879
19 |  | 84.1874 | 63.7712 | 4187 | 0.00018091 | 6.0033 | 6.0034 | -3.752 | 5527.4585 | 1211.7692 | -0.00067879
20 |  | 84.1874 | 63.7705 | 4187 | 0.00018091 | 6.0034 | 6.0036 | -3.752 | 5527.5173 | 1275.5397 | -0.00067878
21 |  | 84.1874 | 63.7699 | 4187 | 0.00018091 | 6.0036 | 6.0038 | -3.752 | 5527.5762 | 1339.3096 | -0.00067877
22 |  | 84.1874 | 63.7692 | 4187 | 0.00018091 | 6.0038 | 6.004 | -3.752 | 5527.635 | 1403.0788 | -0.00067877
23 |  | 84.1874 | 63.7685 | 4187 | 0.00018091 | 6.004 | 6.0042 | -3.752 | 5527.6938 | 1466.8473 | -0.00067876
24 |  | 84.1874 | 63.7678 | 4187 | 0.00018091 | 6.0042 | 6.0043 | -3.752 | 5527.7527 | 1530.6151 | -0.00067875
25 |  | 84.1874 | 63.7671 | 4187 | 0.0001809 | 6.0043 | 6.0045 | -3.752 | 5527.8115 | 1594.3822 | -0.00067874
26 |  | 84.1874 | 63.7665 | 4187 | 0.0001809 | 6.0045 | 6.0047 | -3.752 | 5527.8704 | 1658.1487 | -0.00067874
27 |  | 84.1874 | 63.7658 | 4187 | 0.0001809 | 6.0047 | 6.0049 | -3.752 | 5527.9292 | 1721.9145 | -0.00067873
28 |  | 84.1874 | 63.7651 | 4187 | 0.0001809 | 6.0049 | 6.0051 | -3.752 | 5527.988 | 1785.6796 | -0.00067872
29 |  | 84.1874 | 63.7644 | 4187 | 0.0001809 | 6.0051 | 6.0052 | -3.752 | 5528.0469 | 1849.444 | -0.00067871
30 |  | 84.1874 | 63.7638 | 4187 | 0.00018089 | 6.0052 | 6.0054 | -3.752 | 5528.1057 | 1913.2078 | -0.00067871
31 |  | 84.1874 | 63.7631 | 4187 | 0.00018089 | 6.0054 | 6.0056 | -3.752 | 5528.1646 | 1976.9708 | -0.0006787
32 |  | 84.1874 | 63.7624 | 4187 | 0.00018089 | 6.0056 | 6.0058 | -3.752 | 5528.2234 | 2040.7332 | -0.00067869
33 |  | 84.1874 | 63.7617 | 4187 | 0.00018089 | 6.0058 | 6.006 | -3.752 | 5528.2823 | 2104.495 | -0.00067869
34 |  | 84.1874 | 63.761 | 4187 | 0.00018089 | 6.006 | 6.0062 | -3.752 | 5528.3411 | 2168.256 | -0.00067868
35 |  | 84.1874 | 63.7604 | 4187 | 0.00018088 | 6.0062 | 6.0063 | -3.752 | 5528.3999 | 2232.0163 | -0.00067867
36 |  | 84.1874 | 63.7597 | 4187 | 0.00018088 | 6.0063 | 6.0065 | -3.752 | 5528.4588 | 2295.776 | -0.00067866
37 |  | 84.1874 | 63.759 | 4187 | 0.00018088 | 6.0065 | 6.0067 | -3.752 | 5528.5176 | 2359.535 | -0.00067866
38 |  | 84.1874 | 63.7583 | 4187 | 0.00018088 | 6.0067 | 6.0069 | -3.752 | 5528.5765 | 2423.2933 | -0.00067865
39 |  | 84.1874 | 63.7576 | 4187 | 0.00018088 | 6.0069 | 6.0071 | -3.752 | 5528.6353 | 2487.051 | -0.00067864
40 |  | 84.1874 | 63.757 | 4187 | 0.00018087 | 6.0071 | 6.0072 | -3.752 | 5528.6942 | 2550.808 | -0.00067864
41 |  | 84.1874 | 63.7563 | 4187 | 0.00018087 | 6.0072 | 6.0074 | -3.752 | 5528.753 | 2614.5642 | -0.00067863
42 |  | 84.1874 | 63.7556 | 4187 | 0.00018087 | 6.0074 | 6.0076 | -3.752 | 5528.8119 | 2678.3198 | -0.00067862
43 |  | 84.1874 | 63.7549 | 4187 | 0.00018087 | 6.0076 | 6.0078 | -3.752 | 5528.8707 | 2742.0748 | -0.00067861
44 |  | 84.1874 | 63.7542 | 4187 | 0.00018087 | 6.0078 | 6.008 | -3.752 | 5528.9296 | 2805.829 | -0.00067861
45 |  | 84.1874 | 63.7536 | 4187 | 0.00018086 | 6.008 | 6.0081 | -3.752 | 5528.9884 | 2869.5826 | -0.0006786
46 |  | 84.1874 | 63.7529 | 4187 | 0.00018086 | 6.0081 | 6.0083 | -3.752 | 5529.0473 | 2933.3355 | -0.00067859
47 |  | 84.1874 | 63.7522 | 4187 | 0.00018086 | 6.0083 | 6.0085 | -3.752 | 5529.1061 | 2997.0877 | -0.00067858
48 |  | 84.1874 | 63.7515 | 4187 | 0.00018086 | 6.0085 | 6.0087 | -3.752 | 5529.165 | 3060.8392 | -0.00067858
49 |  | 84.1874 | 63.7509 | 4187 | 0.00018086 | 6.0087 | 6.0089 | -3.752 | 5529.2238 | 3124.5901 | -0.00067857
50 |  | 84.1874 | 63.7502 | 4187 | 0.00018086 | 6.0089 | 6.009 | -3.752 | 5529.2827 | 3188.3403 | -0.00067856
51 |  | 84.1874 | 63.7495 | 4187 | 0.00018085 | 6.009 | 6.0092 | -3.752 | 5529.3415 | 3252.0898 | -0.00067856
52 |  | 84.1874 | 63.7488 | 4187 | 0.00018085 | 6.0092 | 6.0094 | -3.752 | 5529.4004 | 3315.8386 | -0.00067855
53 |  | 84.1874 | 63.7481 | 4187 | 0.00018085 | 6.0094 | 6.0096 | -3.752 | 5529.4593 | 3379.5867 | -0.00067854
54 |  | 84.1874 | 63.7475 | 4187 | 0.00018085 | 6.0096 | 6.0098 | -3.752 | 5529.5181 | 3443.3342 | -0.00067853
55 |  | 84.1874 | 63.7468 | 4187 | 0.00018085 | 6.0098 | 6.0099 | -3.752 | 5529.577 | 3507.081 | -0.00067853
56 |  | 84.1874 | 63.7461 | 4187 | 0.00018084 | 6.0099 | 6.0101 | -3.752 | 5529.6358 | 3570.8271 | -0.00067852
57 |  | 84.1874 | 63.7454 | 4187 | 0.00018084 | 6.0101 | 6.0103 | -3.752 | 5529.6947 | 3634.5725 | -0.00067851
58 |  | 84.1874 | 63.7447 | 4187 | 0.00018084 | 6.0103 | 6.0105 | -3.752 | 5529.7535 | 3698.3173 | -0.00067851
59 |  | 84.1874 | 63.7441 | 4187 | 0.00018084 | 6.0105 | 6.0107 | -3.752 | 5529.8124 | 3762.0613 | -0.0006785
60 |  | 84.1874 | 63.7434 | 4187 | 0.00018084 | 6.0107 | 6.0109 | -3.752 | 5529.8713 | 3825.8047 | -0.00067849
61 |  | 84.1874 | 63.7427 | 4187 | 0.00018083 | 6.0109 | 6.011 | -3.752 | 5529.9301 | 3889.5474 | -0.00067848
62 |  | 84.1874 | 63.742 | 4187 | 0.00018083 | 6.011 | 6.0112 | -3.752 | 5529.989 | 3953.2895 | -0.00067848
63 |  | 84.1874 | 63.7414 | 4187 | 0.00018083 | 6.0112 | 6.0114 | -3.752 | 5530.0479 | 4017.0308 | -0.00067847
64 |  | 84.1874 | 63.7407 | 4187 | 0.00018083 | 6.0114 | 6.0116 | -3.752 | 5530.1067 | 4080.7715 | -0.00067846
65 |  | 84.1874 | 63.74 | 4187 | 0.00018083 | 6.0116 | 6.0118 | -3.752 | 5530.1656 | 4144.5115 | -0.00067845
66 |  | 84.1874 | 63.7393 | 4187 | 0.00018082 | 6.0118 | 6.0119 | -3.752 | 5530.2244 | 4208.2508 | -0.00067845
67 |  | 84.1874 | 63.7386 | 4187 | 0.00018082 | 6.0119 | 6.0121 | -3.752 | 5530.2833 | 4271.9895 | -0.00067844
68 |  | 84.1874 | 63.738 | 4187 | 0.00018082 | 6.0121 | 6.0123 | -3.752 | 5530.3422 | 4335.7274 | -0.00067843
69 |  | 84.1874 | 63.7373 | 4187 | 0.00018082 | 6.0123 | 6.0125 | -3.752 | 5530.401 | 4399.4647 | -0.00067843
70 |  | 84.1874 | 63.7366 | 4187 | 0.00018082 | 6.0125 | 6.0127 | -3.752 | 5530.4599 | 4463.2013 | -0.00067842
71 |  | 84.1874 | 63.7359 | 4187 | 0.00018081 | 6.0127 | 6.0128 | -3.752 | 5530.5188 | 4526.9373 | -0.00067841
72 |  | 84.1874 | 63.7353 | 4187 | 0.00018081 | 6.0128 | 6.013 | -3.752 | 5530.5776 | 4590.6725 | -0.0006784
73 |  | 84.1874 | 63.7346 | 4187 | 0.00018081 | 6.013 | 6.0132 | -3.752 | 5530.6365 | 4654.4071 | -0.0006784
74 |  | 84.1874 | 63.7339 | 4187 | 0.00018081 | 6.0132 | 6.0134 | -3.752 | 5530.6954 | 4718.141 | -0.00067839
75 |  | 84.1874 | 63.7332 | 4187 | 0.00018081 | 6.0134 | 6.0136 | -3.752 | 5530.7542 | 4781.8742 | -0.00067838
76 |  | 84.1874 | 63.7325 | 4187 | 0.00018081 | 6.0136 | 6.0137 | -3.752 | 5530.8131 | 4845.6067 | -0.00067838
77 |  | 84.1874 | 63.7319 | 4187 | 0.0001808 | 6.0137 | 6.0139 | -3.752 | 5530.872 | 4909.3386 | -0.00067837
78 |  | 84.1874 | 63.7312 | 4187 | 0.0001808 | 6.0139 | 6.0141 | -3.752 | 5530.9309 | 4973.0698 | -0.00067836
79 |  | 84.1874 | 63.7305 | 4187 | 0.0001808 | 6.0141 | 6.0143 | -3.752 | 5530.9897 | 5036.8003 | -0.00067835
80 |  | 84.1874 | 63.7298 | 4187 | 0.0001808 | 6.0143 | 6.0145 | -3.752 | 5531.0486 | 5100.5301 | -0.00067835
81 |  | 84.1874 | 63.7291 | 4187 | 0.0001808 | 6.0145 | 6.0147 | -3.752 | 5531.1075 | 5164.2592 | -0.00067834
82 |  | 84.1874 | 63.7285 | 4187 | 0.00018079 | 6.0147 | 6.0148 | -3.752 | 5531.1664 | 5227.9877 | -0.00067833
83 |  | 84.1874 | 63.7278 | 4187 | 0.00018079 | 6.0148 | 6.015 | -3.752 | 5531.2252 | 5291.7155 | -0.00067832
84 |  | 84.1874 | 63.7271 | 4187 | 0.00018079 | 6.015 | 6.0152 | -3.752 | 5531.2841 | 5355.4426 | -0.00067832
85 |  | 84.1874 | 63.7264 | 4187 | 0.00018079 | 6.0152 | 6.0154 | -3.752 | 5531.343 | 5419.169 | -0.00067831
86 |  | 84.1874 | 63.7258 | 4187 | 0.00018079 | 6.0154 | 6.0156 | -3.752 | 5531.4019 | 5482.8948 | -0.0006783
87 |  | 84.1874 | 63.7251 | 4187 | 0.00018078 | 6.0156 | 6.0157 | -3.752 | 5531.4607 | 5546.6199 | -0.0006783
88 |  | 84.1874 | 63.7244 | 4187 | 0.00018078 | 6.0157 | 6.0159 | -3.752 | 5531.5196 | 5610.3443 | -0.00067829
89 |  | 84.1874 | 63.7237 | 4187 | 0.00018078 | 6.0159 | 6.0161 | -3.752 | 5531.5785 | 5674.068 | -0.00067828
90 |  | 84.1874 | 63.723 | 4187 | 0.00018078 | 6.0161 | 6.0163 | -3.752 | 5531.6374 | 5737.791 | -0.00067827
91 |  | 84.1874 | 63.7224 | 4187 | 0.00018078 | 6.0163 | 6.0165 | -3.752 | 5531.6963 | 5801.5134 | -0.00067827
92 |  | 84.1874 | 63.7217 | 4187 | 0.00018077 | 6.0165 | 6.0166 | -3.752 | 5531.7551 | 5865.2351 | -0.00067826
93 |  | 84.1874 | 63.721 | 4187 | 0.00018077 | 6.0166 | 6.0168 | -3.752 | 5531.814 | 5928.9561 | -0.00067825
94 |  | 84.1874 | 63.7203 | 4187 | 0.00018077 | 6.0168 | 6.017 | -3.752 | 5531.8729 | 5992.6764 | -0.00067825
95 |  | 84.1874 | 63.7196 | 4187 | 0.00018077 | 6.017 | 6.0172 | -3.752 | 5531.9318 | 6056.396 | -0.00067824
96 |  | 84.1874 | 63.719 | 4187 | 0.00018077 | 6.0172 | 6.0174 | -3.752 | 5531.9907 | 6120.115 | -0.00067823
97 |  | 84.1874 | 63.7183 | 4187 | 0.00018076 | 6.0174 | 6.0175 | -3.752 | 5532.0495 | 6183.8333 | -0.00067822
98 |  | 84.1874 | 63.7176 | 4187 | 0.00018076 | 6.0175 | 6.0177 | -3.752 | 5532.1084 | 6247.5509 | -0.00067822
99 |  | 84.1874 | 63.7169 | 4187 | 0.00018076 | 6.0177 | 6.0179 | -3.752 | 5532.1673 | 6311.2679 | -0.00067821
100 |  | 84.1874 | 63.7163 | 4187 | 0.00018076 | 6.0179 | 6.0181 | -3.752 | 5532.2262 | 6374.9841 | -0.0006782
101 |  | 84.1874 | 63.7156 | 4187 | 0.00018076 | 6.0181 | 6.0183 | -3.752 | 5532.2851 | 6438.6997 | -0.00067819
102 |  | 84.1874 | 63.7149 | 4187 | 0.00018076 | 6.0183 | 6.0184 | -3.752 | 5532.344 | 6502.4146 | -0.00067819
103 |  | 84.1874 | 63.7142 | 4187 | 0.00018075 | 6.0184 | 6.0186 | -3.752 | 5532.4029 | 6566.1288 | -0.00067818
104 |  | 84.1874 | 63.7135 | 4187 | 0.00018075 | 6.0186 | 6.0188 | -3.752 | 5532.4617 | 6629.8424 | -0.00067817
105 |  | 84.1874 | 63.7129 | 4187 | 0.00018075 | 6.0188 | 6.019 | -3.752 | 5532.5206 | 6693.5552 | -0.00067817
106 |  | 84.1874 | 63.7122 | 4187 | 0.00018075 | 6.019 | 6.0192 | -3.752 | 5532.5795 | 6757.2674 | -0.00067816
107 |  | 84.1874 | 63.7115 | 4187 | 0.00018075 | 6.0192 | 6.0194 | -3.752 | 5532.6384 | 6820.9789 | -0.00067815
108 |  | 84.1874 | 63.7108 | 4187 | 0.00018074 | 6.0194 | 6.0195 | -3.752 | 5532.6973 | 6884.6898 | -0.00067814
109 |  | 84.1874 | 63.7102 | 4187 | 0.00018074 | 6.0195 | 6.0197 | -3.752 | 5532.7562 | 6948.3999 | -0.00067814
110 |  | 84.1874 | 63.7095 | 4187 | 0.00018074 | 6.0197 | 6.0199 | -3.752 | 5532.8151 | 7012.1094 | -0.00067813
111 |  | 84.1874 | 63.7088 | 4187 | 0.00018074 | 6.0199 | 6.0201 | -3.752 | 5532.874 | 7075.8182 | -0.00067812
112 |  | 84.1874 | 63.7081 | 4187 | 0.00018074 | 6.0201 | 6.0203 | -3.752 | 5532.9329 | 7139.5263 | -0.00067812
113 |  | 84.1874 | 63.7074 | 4187 | 0.00018073 | 6.0203 | 6.0204 | -3.752 | 5532.9918 | 7203.2338 | -0.00067811
114 |  | 84.1874 | 63.7068 | 4187 | 0.00018073 | 6.0204 | 6.0206 | -3.752 | 5533.0507 | 7266.9405 | -0.0006781
115 |  | 84.1874 | 63.7061 | 4187 | 0.00018073 | 6.0206 | 6.0208 | -3.752 | 5533.1096 | 7330.6466 | -0.00067809
116 |  | 84.1874 | 63.7054 | 4187 | 0.00018073 | 6.0208 | 6.021 | -3.752 | 5533.1685 | 7394.352 | -0.00067809
117 |  | 84.1874 | 63.7047 | 4187 | 0.00018073 | 6.021 | 6.0212 | -3.752 | 5533.2274 | 7458.0567 | -0.00067808
118 |  | 84.1874 | 63.7041 | 4187 | 0.00018072 | 6.0212 | 6.0213 | -3.752 | 5533.2862 | 7521.7608 | -0.00067807
119 |  | 84.1874 | 63.7034 | 4187 | 0.00018072 | 6.0213 | 6.0215 | -3.752 | 5533.3451 | 7585.4642 | -0.00067806
120 |  | 84.1874 | 63.7027 | 4187 | 0.00018072 | 6.0215 | 6.0217 | -3.752 | 5533.404 | 7649.1669 | -0.00067806
121 |  | 84.1874 | 63.702 | 4187 | 0.00018072 | 6.0217 | 6.0219 | -3.752 | 5533.4629 | 7712.8689 | -0.00067805
122 |  | 84.1874 | 63.7013 | 4187 | 0.00018072 | 6.0219 | 6.0221 | -3.752 | 5533.5218 | 7776.5702 | -0.00067804
123 |  | 84.1874 | 63.7007 | 4187 | 0.00018071 | 6.0221 | 6.0222 | -3.752 | 5533.5807 | 7840.2709 | -0.00067804
124 |  | 84.1874 | 63.7 | 4187 | 0.00018071 | 6.0222 | 6.0224 | -3.752 | 5533.6396 | 7903.9709 | -0.00067803
125 |  | 84.1874 | 63.6993 | 4187 | 0.00018071 | 6.0224 | 6.0226 | -3.752 | 5533.6985 | 7967.6702 | -0.00067802
126 |  | 84.1874 | 63.6986 | 4187 | 0.00018071 | 6.0226 | 6.0228 | -3.752 | 5533.7574 | 8031.3688 | -0.00067801
127 |  | 84.1874 | 63.6979 | 4187 | 0.00018071 | 6.0228 | 6.023 | -3.752 | 5533.8163 | 8095.0668 | -0.00067801
128 |  | 84.1874 | 63.6973 | 4187 | 0.00018071 | 6.023 | 6.0231 | -3.752 | 5533.8753 | 8158.764 | -0.000678
129 |  | 84.1874 | 63.6966 | 4187 | 0.0001807 | 6.0231 | 6.0233 | -3.752 | 5533.9342 | 8222.4606 | -0.00067799
130 |  | 84.1874 | 63.6959 | 4187 | 0.0001807 | 6.0233 | 6.0235 | -3.752 | 5533.9931 | 8286.1565 | -0.00067799
131 |  | 84.1874 | 63.6952 | 4187 | 0.0001807 | 6.0235 | 6.0237 | -3.752 | 5534.052 | 8349.8518 | -0.00067798
132 |  | 84.1874 | 63.6946 | 4187 | 0.0001807 | 6.0237 | 6.0239 | -3.752 | 5534.1109 | 8413.5463 | -0.00067797
133 |  | 84.1874 | 63.6939 | 4187 | 0.0001807 | 6.0239 | 6.024 | -3.752 | 5534.1698 | 8477.2402 | -0.00067796
134 |  | 84.1874 | 63.6932 | 4187 | 0.00018069 | 6.024 | 6.0242 | -3.752 | 5534.2287 | 8540.9334 | -0.00067796
135 |  | 84.1874 | 63.6925 | 4187 | 0.00018069 | 6.0242 | 6.0244 | -3.752 | 5534.2876 | 8604.6259 | -0.00067795
136 |  | 84.1874 | 63.6918 | 4187 | 0.00018069 | 6.0244 | 6.0246 | -3.752 | 5534.3465 | 8668.3178 | -0.00067794
137 |  | 84.1874 | 63.6912 | 4187 | 0.00018069 | 6.0246 | 6.0248 | -3.752 | 5534.4054 | 8732.009 | -0.00067793
138 |  | 84.1874 | 63.6905 | 4187 | 0.00018069 | 6.0248 | 6.025 | -3.752 | 5534.4643 | 8795.6994 | -0.00067793
139 |  | 84.1874 | 63.6898 | 4187 | 0.00018068 | 6.025 | 6.0251 | -3.752 | 5534.5232 | 8859.3893 | -0.00067792
140 |  | 84.1874 | 63.6891 | 4187 | 0.00018068 | 6.0251 | 6.0253 | -3.752 | 5534.5821 | 8923.0784 | -0.00067791
141 |  | 84.1874 | 63.6885 | 4187 | 0.00018068 | 6.0253 | 6.0255 | -3.752 | 5534.641 | 8986.7669 | -0.00067791
142 |  | 84.1874 | 63.6878 | 4187 | 0.00018068 | 6.0255 | 6.0257 | -3.752 | 5534.7 | 9050.4546 | -0.0006779
143 |  | 84.1874 | 63.6871 | 4187 | 0.00018068 | 6.0257 | 6.0259 | -3.752 | 5534.7589 | 9114.1417 | -0.00067789
144 |  | 84.1874 | 63.6864 | 4187 | 0.00018067 | 6.0259 | 6.026 | -3.752 | 5534.8178 | 9177.8282 | -0.00067788
145 |  | 84.1874 | 63.6857 | 4187 | 0.00018067 | 6.026 | 6.0262 | -3.752 | 5534.8767 | 9241.5139 | -0.00067788
146 |  | 84.1874 | 63.6851 | 4187 | 0.00018067 | 6.0262 | 6.0264 | -3.752 | 5534.9356 | 9305.199 | -0.00067787
147 |  | 84.1874 | 63.6844 | 4187 | 0.00018067 | 6.0264 | 6.0266 | -3.752 | 5534.9945 | 9368.8834 | -0.00067786
148 |  | 84.1874 | 63.6837 | 4187 | 0.00018067 | 6.0266 | 6.0268 | -3.752 | 5535.0534 | 9432.5671 | -0.00067786
149 |  | 84.1874 | 63.683 | 4187 | 0.00018066 | 6.0268 | 6.0269 | -3.752 | 5535.1124 | 9496.2501 | -0.00067785
150 |  | 84.1874 | 63.6824 | 4187 | 0.00018066 | 6.0269 | 6.0271 | -3.752 | 5535.1713 | 9559.9325 | -0.00067784
151 |  | 84.1874 | 63.6817 | 4187 | 0.00018066 | 6.0271 | 6.0273 | -3.752 | 5535.2302 | 9623.6142 | -0.00067783
152 |  | 84.1874 | 63.681 | 4187 | 0.00018066 | 6.0273 | 6.0275 | -3.752 | 5535.2891 | 9687.2952 | -0.00067783
153 |  | 84.1874 | 63.6803 | 4187 | 0.00018066 | 6.0275 | 6.0277 | -3.752 | 5535.348 | 9750.9755 | -0.00067782
154 |  | 84.1874 | 63.6796 | 4187 | 0.00018066 | 6.0277 | 6.0278 | -3.752 | 5535.407 | 9814.6551 | -0.00067781
155 |  | 84.1874 | 63.679 | 4187 | 0.00018065 | 6.0278 | 6.028 | -3.752 | 5535.4659 | 9878.3341 | -0.00067781
156 |  | 84.1874 | 63.6783 | 4187 | 0.00018065 | 6.028 | 6.0282 | -3.752 | 5535.5248 | 9942.0124 | -0.0006778
157 |  | 84.1874 | 63.6776 | 4187 | 0.00018065 | 6.0282 | 6.0284 | -3.752 | 5535.5837 | 10005.69 | -0.00067779
158 |  | 84.1874 | 63.6769 | 4187 | 0.00018065 | 6.0284 | 6.0286 | -3.752 | 5535.6426 | 10069.3669 | -0.00067778
159 |  | 84.1874 | 63.6763 | 4187 | 0.00018065 | 6.0286 | 6.0287 | -3.752 | 5535.7016 | 10133.0432 | -0.00067778
160 |  | 84.1874 | 63.6756 | 4187 | 0.00018064 | 6.0287 | 6.0289 | -3.752 | 5535.7605 | 10196.7188 | -0.00067777
161 |  | 84.1874 | 63.6749 | 4187 | 0.00018064 | 6.0289 | 6.0291 | -3.752 | 5535.8194 | 10260.3937 | -0.00067776
162 |  | 84.1874 | 63.6742 | 4187 | 0.00018064 | 6.0291 | 6.0293 | -3.752 | 5535.8783 | 10324.0679 | -0.00067775
163 |  | 84.1874 | 63.6735 | 4187 | 0.00018064 | 6.0293 | 6.0295 | -3.752 | 5535.9373 | 10387.7414 | -0.00067775
164 |  | 84.1874 | 63.6729 | 4187 | 0.00018064 | 6.0295 | 6.0297 | -3.752 | 5535.9962 | 10451.4143 | -0.00067774
165 |  | 84.1874 | 63.6722 | 4187 | 0.00018063 | 6.0297 | 6.0298 | -3.752 | 5536.0551 | 10515.0865 | -0.00067773
166 |  | 84.1874 | 63.6715 | 4187 | 0.00018063 | 6.0298 | 6.03 | -3.752 | 5536.114 | 10578.758 | -0.00067773
167 |  | 84.1874 | 63.6708 | 4187 | 0.00018063 | 6.03 | 6.0302 | -3.752 | 5536.173 | 10642.4288 | -0.00067772
168 |  | 84.1874 | 63.6702 | 4187 | 0.00018063 | 6.0302 | 6.0304 | -3.752 | 5536.2319 | 10706.099 | -0.00067771
169 |  | 84.1874 | 63.6695 | 4187 | 0.00018063 | 6.0304 | 6.0306 | -3.752 | 5536.2908 | 10769.7685 | -0.0006777
170 |  | 84.1874 | 63.6688 | 4187 | 0.00018062 | 6.0306 | 6.0307 | -3.752 | 5536.3497 | 10833.4373 | -0.0006777
171 |  | 84.1874 | 63.6681 | 4187 | 0.00018062 | 6.0307 | 6.0309 | -3.752 | 5536.4087 | 10897.1054 | -0.00067769
172 |  | 84.1874 | 63.6674 | 4187 | 0.00018062 | 6.0309 | 6.0311 | -3.752 | 5536.4676 | 10960.7728 | -0.00067768
173 |  | 84.1874 | 63.6668 | 4187 | 0.00018062 | 6.0311 | 6.0313 | -3.752 | 5536.5265 | 11024.4396 | -0.00067768
174 |  | 84.1874 | 63.6661 | 4187 | 0.00018062 | 6.0313 | 6.0315 | -3.752 | 5536.5855 | 11088.1057 | -0.00067767
175 |  | 84.1874 | 63.6654 | 4187 | 0.00018061 | 6.0315 | 6.0316 | -3.752 | 5536.6444 | 11151.7711 | -0.00067766
176 |  | 84.1874 | 63.6647 | 4187 | 0.00018061 | 6.0316 | 6.0318 | -3.752 | 5536.7033 | 11215.4358 | -0.00067765
177 |  | 84.1874 | 63.6641 | 4187 | 0.00018061 | 6.0318 | 6.032 | -3.752 | 5536.7623 | 11279.0999 | -0.00067765
178 |  | 84.1874 | 63.6634 | 4187 | 0.00018061 | 6.032 | 6.0322 | -3.752 | 5536.8212 | 11342.7633 | -0.00067764
179 |  | 84.1874 | 63.6627 | 4187 | 0.00018061 | 6.0322 | 6.0324 | -3.752 | 5536.8801 | 11406.426 | -0.00067763
180 |  | 84.1874 | 63.662 | 4187 | 0.00018061 | 6.0324 | 6.0325 | -3.752 | 5536.9391 | 11470.088 | -0.00067762
181 |  | 84.1874 | 63.6613 | 4187 | 0.0001806 | 6.0325 | 6.0327 | -3.752 | 5536.998 | 11533.7494 | -0.00067762
182 |  | 84.1874 | 63.6607 | 4187 | 0.0001806 | 6.0327 | 6.0329 | -3.752 | 5537.0569 | 11597.41 | -0.00067761
183 |  | 84.1874 | 63.66 | 4187 | 0.0001806 | 6.0329 | 6.0331 | -3.752 | 5537.1159 | 11661.07 | -0.0006776
184 |  | 84.1874 | 63.6593 | 4187 | 0.0001806 | 6.0331 | 6.0333 | -3.752 | 5537.1748 | 11724.7293 | -0.0006776
185 |  | 84.1874 | 63.6586 | 4187 | 0.0001806 | 6.0333 | 6.0334 | -3.752 | 5537.2338 | 11788.388 | -0.00067759
186 |  | 84.1874 | 63.658 | 4187 | 0.00018059 | 6.0334 | 6.0336 | -3.752 | 5537.2927 | 11852.0459 | -0.00067758
187 |  | 84.1874 | 63.6573 | 4187 | 0.00018059 | 6.0336 | 6.0338 | -3.752 | 5537.3516 | 11915.7032 | -0.00067757
188 |  | 84.1874 | 63.6566 | 4187 | 0.00018059 | 6.0338 | 6.034 | -3.752 | 5537.4106 | 11979.3598 | -0.00067757
189 |  | 84.1874 | 63.6559 | 4187 | 0.00018059 | 6.034 | 6.0342 | -3.752 | 5537.4695 | 12043.0157 | -0.00067756
190 |  | 84.1874 | 63.6552 | 4187 | 0.00018059 | 6.0342 | 6.0343 | -3.752 | 5537.5285 | 12106.671 | -0.00067755
191 |  | 84.1874 | 63.6546 | 4187 | 0.00018058 | 6.0343 | 6.0345 | -3.752 | 5537.5874 | 12170.3256 | -0.00067755
192 |  | 84.1874 | 63.6539 | 4187 | 0.00018058 | 6.0345 | 6.0347 | -3.752 | 5537.6464 | 12233.9795 | -0.00067754
193 |  | 84.1874 | 63.6532 | 4187 | 0.00018058 | 6.0347 | 6.0349 | -3.752 | 5537.7053 | 12297.6327 | -0.00067753
194 |  | 84.1874 | 63.6525 | 4187 | 0.00018058 | 6.0349 | 6.0351 | -3.752 | 5537.7642 | 12361.2852 | -0.00067752
195 |  | 84.1874 | 63.6519 | 4187 | 0.00018058 | 6.0351 | 6.0352 | -3.752 | 5537.8232 | 12424.9371 | -0.00067752
196 |  | 84.1874 | 63.6512 | 4187 | 0.00018057 | 6.0352 | 6.0354 | -3.752 | 5537.8821 | 12488.5883 | -0.00067751
197 |  | 84.1874 | 63.6505 | 4187 | 0.00018057 | 6.0354 | 6.0356 | -3.752 | 5537.9411 | 12552.2388 | -0.0006775
198 |  | 84.1874 | 63.6498 | 4187 | 0.00018057 | 6.0356 | 6.0358 | -3.752 | 5538 | 12615.8886 | -0.00067749
199 |  | 84.1874 | 63.6492 | 4187 | 0.00018057 | 6.0358 | 6.036 | -3.752 | 5538.059 | 12679.5377 | -0.00067749
200 |  | 84.1874 | 63.6485 | 4187 | 0.00018057 | 6.036 | 6.0362 | -3.752 | 5538.1179 | 12743.1862 | -0.00067748
201 |  | 84.1874 | 63.6478 | 4187 | 0.00018056 | 6.0362 | 6.0363 | -3.752 | 5538.1769 | 12806.834 | -0.00067747
202 |  | 84.1874 | 63.6471 | 4187 | 0.00018056 | 6.0363 | 6.0365 | -3.752 | 5538.2358 | 12870.4811 | -0.00067747
203 |  | 84.1874 | 63.6464 | 4187 | 0.00018056 | 6.0365 | 6.0367 | -3.752 | 5538.2948 | 12934.1276 | -0.00067746
204 |  | 84.1874 | 63.6458 | 4187 | 0.00018056 | 6.0367 | 6.0369 | -3.752 | 5538.3537 | 12997.7733 | -0.00067745
205 |  | 84.1874 | 63.6451 | 4187 | 0.00018056 | 6.0369 | 6.0371 | -3.752 | 5538.4127 | 13061.4184 | -0.00067744
206 |  | 84.1874 | 63.6444 | 4187 | 0.00018056 | 6.0371 | 6.0372 | -3.752 | 5538.4716 | 13125.0628 | -0.00067744
207 |  | 84.1874 | 63.6437 | 4187 | 0.00018055 | 6.0372 | 6.0374 | -3.752 | 5538.5306 | 13188.7066 | -0.00067743
208 |  | 84.1874 | 63.6431 | 4187 | 0.00018055 | 6.0374 | 6.0376 | -3.752 | 5538.5895 | 13252.3496 | -0.00067742
209 |  | 84.1874 | 63.6424 | 4187 | 0.00018055 | 6.0376 | 6.0378 | -3.752 | 5538.6485 | 13315.992 | -0.00067742
210 |  | 84.1874 | 63.6417 | 4187 | 0.00018055 | 6.0378 | 6.038 | -3.752 | 5538.7074 | 13379.6337 | -0.00067741
211 |  | 84.1874 | 63.641 | 4187 | 0.00018055 | 6.038 | 6.0381 | -3.752 | 5538.7664 | 13443.2747 | -0.0006774
212 |  | 84.1874 | 63.6403 | 4187 | 0.00018054 | 6.0381 | 6.0383 | -3.752 | 5538.8253 | 13506.9151 | -0.00067739
213 |  | 84.1874 | 63.6397 | 4187 | 0.00018054 | 6.0383 | 6.0385 | -3.752 | 5538.8843 | 13570.5547 | -0.00067739
214 |  | 84.1874 | 63.639 | 4187 | 0.00018054 | 6.0385 | 6.0387 | -3.752 | 5538.9433 | 13634.1937 | -0.00067738
215 |  | 84.1874 | 63.6383 | 4187 | 0.00018054 | 6.0387 | 6.0389 | -3.752 | 5539.0022 | 13697.832 | -0.00067737
216 |  | 84.1874 | 63.6376 | 4187 | 0.00018054 | 6.0389 | 6.039 | -3.752 | 5539.0612 | 13761.4697 | -0.00067737
217 |  | 84.1874 | 63.637 | 4187 | 0.00018053 | 6.039 | 6.0392 | -3.752 | 5539.1201 | 13825.1066 | -0.00067736
218 |  | 84.1874 | 63.6363 | 4187 | 0.00018053 | 6.0392 | 6.0394 | -3.752 | 5539.1791 | 13888.7429 | -0.00067735
219 |  | 84.1874 | 63.6356 | 4187 | 0.00018053 | 6.0394 | 6.0396 | -3.752 | 5539.2381 | 13952.3785 | -0.00067734
220 |  | 84.1874 | 63.6349 | 4187 | 0.00018053 | 6.0396 | 6.0398 | -3.752 | 5539.297 | 14016.0134 | -0.00067734
221 |  | 84.1874 | 63.6342 | 4187 | 0.00018053 | 6.0398 | 6.0399 | -3.752 | 5539.356 | 14079.6477 | -0.00067733
222 |  | 84.1874 | 63.6336 | 4187 | 0.00018052 | 6.0399 | 6.0401 | -3.752 | 5539.4149 | 14143.2813 | -0.00067732
223 |  | 84.1874 | 63.6329 | 4187 | 0.00018052 | 6.0401 | 6.0403 | -3.752 | 5539.4739 | 14206.9141 | -0.00067731
224 |  | 84.1874 | 63.6322 | 4187 | 0.00018052 | 6.0403 | 6.0405 | -3.752 | 5539.5329 | 14270.5464 | -0.00067731
225 |  | 84.1874 | 63.6315 | 4187 | 0.00018052 | 6.0405 | 6.0407 | -3.752 | 5539.5918 | 14334.1779 | -0.0006773
226 |  | 84.1874 | 63.6309 | 4187 | 0.00018052 | 6.0407 | 6.0408 | -3.752 | 5539.6508 | 14397.8088 | -0.00067729
227 |  | 84.1874 | 63.6302 | 4187 | 0.00018051 | 6.0408 | 6.041 | -3.752 | 5539.7098 | 14461.4389 | -0.00067729
228 |  | 84.1874 | 63.6295 | 4187 | 0.00018051 | 6.041 | 6.0412 | -3.752 | 5539.7687 | 14525.0685 | -0.00067728
229 |  | 84.1874 | 63.6288 | 4187 | 0.00018051 | 6.0412 | 6.0414 | -3.752 | 5539.8277 | 14588.6973 | -0.00067727
230 |  | 84.1874 | 63.6282 | 4187 | 0.00018051 | 6.0414 | 6.0416 | -3.752 | 5539.8867 | 14652.3254 | -0.00067726
231 |  | 84.1874 | 63.6275 | 4187 | 0.00018051 | 6.0416 | 6.0417 | -3.752 | 5539.9456 | 14715.9529 | -0.00067726
232 |  | 84.1874 | 63.6268 | 4187 | 0.00018051 | 6.0417 | 6.0419 | -3.752 | 5540.0046 | 14779.5797 | -0.00067725
233 |  | 84.1874 | 63.6261 | 4187 | 0.0001805 | 6.0419 | 6.0421 | -3.752 | 5540.0636 | 14843.2058 | -0.00067724
234 |  | 84.1874 | 63.6254 | 4187 | 0.0001805 | 6.0421 | 6.0423 | -3.752 | 5540.1225 | 14906.8313 | -0.00067724
235 |  | 84.1874 | 63.6248 | 4187 | 0.0001805 | 6.0423 | 6.0425 | -3.752 | 5540.1815 | 14970.456 | -0.00067723
236 |  | 84.1874 | 63.6241 | 4187 | 0.0001805 | 6.0425 | 6.0427 | -3.752 | 5540.2405 | 15034.0801 | -0.00067722

## 450
|  |  | buis | verlies W/M | L /°C/sec
diam | wandikte |  | inhoud l/m |  | W/M
450 | 40.9 | 3.1416 | 106.4774 | 65.163 | 4187
[8 empty] | J/sec/mtr | aantal mtr. | verlies
|  | buis | verlies W/M | L /°C/sec | verlies temp | begintemp | eindtemp | verlies | bij 1°C | totaal J/sec
|  | inhoud L |  | W/M | °C per M | °C | °C | per m°C | daling | aantal mtr
1 | 450 | 106.4774 | 65.163 | 4187 | 0.00014616 | 6 | 6.0001 | -3.8331 | 6841.623 | 65.163 | -0.00056026
2 |  | 106.4774 | 65.1625 | 4187 | 0.00014616 | 6.0001 | 6.0003 | -3.8331 | 6841.6819 | 130.3255 | -0.00056026
3 |  | 106.4774 | 65.1619 | 4187 | 0.00014616 | 6.0003 | 6.0004 | -3.8331 | 6841.7407 | 195.4874 | -0.00056025
4 |  | 106.4774 | 65.1613 | 4187 | 0.00014616 | 6.0004 | 6.0006 | -3.8331 | 6841.7995 | 260.6488 | -0.00056025
5 |  | 106.4774 | 65.1608 | 4187 | 0.00014616 | 6.0006 | 6.0007 | -3.8331 | 6841.8583 | 325.8095 | -0.00056025
6 |  | 106.4774 | 65.1602 | 4187 | 0.00014616 | 6.0007 | 6.0009 | -3.8331 | 6841.9172 | 390.9698 | -0.00056024
7 |  | 106.4774 | 65.1597 | 4187 | 0.00014616 | 6.0009 | 6.001 | -3.8331 | 6841.976 | 456.1294 | -0.00056024
8 |  | 106.4774 | 65.1591 | 4187 | 0.00014616 | 6.001 | 6.0012 | -3.8331 | 6842.0348 | 521.2886 | -0.00056023
9 |  | 106.4774 | 65.1585 | 4187 | 0.00014615 | 6.0012 | 6.0013 | -3.8331 | 6842.0936 | 586.4471 | -0.00056023
10 |  | 106.4774 | 65.158 | 4187 | 0.00014615 | 6.0013 | 6.0015 | -3.8331 | 6842.1525 | 651.6051 | -0.00056022
11 |  | 106.4774 | 65.1574 | 4187 | 0.00014615 | 6.0015 | 6.0016 | -3.8331 | 6842.2113 | 716.7625 | -0.00056022
12 |  | 106.4774 | 65.1569 | 4187 | 0.00014615 | 6.0016 | 6.0018 | -3.8331 | 6842.2701 | 781.9194 | -0.00056021
13 |  | 106.4774 | 65.1563 | 4187 | 0.00014615 | 6.0018 | 6.0019 | -3.8331 | 6842.3289 | 847.0757 | -0.00056021
14 |  | 106.4774 | 65.1557 | 4187 | 0.00014615 | 6.0019 | 6.002 | -3.8331 | 6842.3878 | 912.2314 | -0.0005602
15 |  | 106.4774 | 65.1552 | 4187 | 0.00014615 | 6.002 | 6.0022 | -3.8331 | 6842.4466 | 977.3866 | -0.0005602
16 |  | 106.4774 | 65.1546 | 4187 | 0.00014615 | 6.0022 | 6.0023 | -3.8331 | 6842.5054 | 1042.5412 | -0.00056019
17 |  | 106.4774 | 65.1541 | 4187 | 0.00014614 | 6.0023 | 6.0025 | -3.8331 | 6842.5643 | 1107.6953 | -0.00056019
18 |  | 106.4774 | 65.1535 | 4187 | 0.00014614 | 6.0025 | 6.0026 | -3.8331 | 6842.6231 | 1172.8488 | -0.00056018
19 |  | 106.4774 | 65.1529 | 4187 | 0.00014614 | 6.0026 | 6.0028 | -3.8331 | 6842.6819 | 1238.0018 | -0.00056018
20 |  | 106.4774 | 65.1524 | 4187 | 0.00014614 | 6.0028 | 6.0029 | -3.8331 | 6842.7408 | 1303.1542 | -0.00056017
21 |  | 106.4774 | 65.1518 | 4187 | 0.00014614 | 6.0029 | 6.0031 | -3.8331 | 6842.7996 | 1368.306 | -0.00056017
22 |  | 106.4774 | 65.1513 | 4187 | 0.00014614 | 6.0031 | 6.0032 | -3.8331 | 6842.8584 | 1433.4572 | -0.00056016
23 |  | 106.4774 | 65.1507 | 4187 | 0.00014614 | 6.0032 | 6.0034 | -3.8331 | 6842.9173 | 1498.6079 | -0.00056016
24 |  | 106.4774 | 65.1501 | 4187 | 0.00014614 | 6.0034 | 6.0035 | -3.8331 | 6842.9761 | 1563.7581 | -0.00056015
25 |  | 106.4774 | 65.1496 | 4187 | 0.00014613 | 6.0035 | 6.0037 | -3.8331 | 6843.0349 | 1628.9077 | -0.00056015
26 |  | 106.4774 | 65.149 | 4187 | 0.00014613 | 6.0037 | 6.0038 | -3.8331 | 6843.0938 | 1694.0567 | -0.00056014
27 |  | 106.4774 | 65.1485 | 4187 | 0.00014613 | 6.0038 | 6.0039 | -3.8331 | 6843.1526 | 1759.2052 | -0.00056014
28 |  | 106.4774 | 65.1479 | 4187 | 0.00014613 | 6.0039 | 6.0041 | -3.8331 | 6843.2115 | 1824.3531 | -0.00056013
29 |  | 106.4774 | 65.1473 | 4187 | 0.00014613 | 6.0041 | 6.0042 | -3.8331 | 6843.2703 | 1889.5004 | -0.00056013
30 |  | 106.4774 | 65.1468 | 4187 | 0.00014613 | 6.0042 | 6.0044 | -3.8331 | 6843.3291 | 1954.6472 | -0.00056012
31 |  | 106.4774 | 65.1462 | 4187 | 0.00014613 | 6.0044 | 6.0045 | -3.8331 | 6843.388 | 2019.7934 | -0.00056012
32 |  | 106.4774 | 65.1457 | 4187 | 0.00014613 | 6.0045 | 6.0047 | -3.8331 | 6843.4468 | 2084.9391 | -0.00056012
33 |  | 106.4774 | 65.1451 | 4187 | 0.00014612 | 6.0047 | 6.0048 | -3.8331 | 6843.5056 | 2150.0842 | -0.00056011
34 |  | 106.4774 | 65.1445 | 4187 | 0.00014612 | 6.0048 | 6.005 | -3.8331 | 6843.5645 | 2215.2287 | -0.00056011
35 |  | 106.4774 | 65.144 | 4187 | 0.00014612 | 6.005 | 6.0051 | -3.8331 | 6843.6233 | 2280.3727 | -0.0005601
36 |  | 106.4774 | 65.1434 | 4187 | 0.00014612 | 6.0051 | 6.0053 | -3.8331 | 6843.6822 | 2345.5161 | -0.0005601
37 |  | 106.4774 | 65.1429 | 4187 | 0.00014612 | 6.0053 | 6.0054 | -3.8331 | 6843.741 | 2410.659 | -0.00056009
38 |  | 106.4774 | 65.1423 | 4187 | 0.00014612 | 6.0054 | 6.0056 | -3.8331 | 6843.7999 | 2475.8013 | -0.00056009
39 |  | 106.4774 | 65.1417 | 4187 | 0.00014612 | 6.0056 | 6.0057 | -3.8331 | 6843.8587 | 2540.9431 | -0.00056008
40 |  | 106.4774 | 65.1412 | 4187 | 0.00014612 | 6.0057 | 6.0058 | -3.8331 | 6843.9175 | 2606.0842 | -0.00056008
41 |  | 106.4774 | 65.1406 | 4187 | 0.00014611 | 6.0058 | 6.006 | -3.8331 | 6843.9764 | 2671.2249 | -0.00056007
42 |  | 106.4774 | 65.1401 | 4187 | 0.00014611 | 6.006 | 6.0061 | -3.8331 | 6844.0352 | 2736.3649 | -0.00056007
43 |  | 106.4774 | 65.1395 | 4187 | 0.00014611 | 6.0061 | 6.0063 | -3.8331 | 6844.0941 | 2801.5044 | -0.00056006
44 |  | 106.4774 | 65.1389 | 4187 | 0.00014611 | 6.0063 | 6.0064 | -3.8331 | 6844.1529 | 2866.6434 | -0.00056006
45 |  | 106.4774 | 65.1384 | 4187 | 0.00014611 | 6.0064 | 6.0066 | -3.8331 | 6844.2118 | 2931.7818 | -0.00056005
46 |  | 106.4774 | 65.1378 | 4187 | 0.00014611 | 6.0066 | 6.0067 | -3.8331 | 6844.2706 | 2996.9196 | -0.00056005
47 |  | 106.4774 | 65.1373 | 4187 | 0.00014611 | 6.0067 | 6.0069 | -3.8331 | 6844.3295 | 3062.0568 | -0.00056004
48 |  | 106.4774 | 65.1367 | 4187 | 0.00014611 | 6.0069 | 6.007 | -3.8331 | 6844.3883 | 3127.1935 | -0.00056004
49 |  | 106.4774 | 65.1361 | 4187 | 0.0001461 | 6.007 | 6.0072 | -3.8331 | 6844.4472 | 3192.3297 | -0.00056003
50 |  | 106.4774 | 65.1356 | 4187 | 0.0001461 | 6.0072 | 6.0073 | -3.8331 | 6844.506 | 3257.4653 | -0.00056003
51 |  | 106.4774 | 65.135 | 4187 | 0.0001461 | 6.0073 | 6.0075 | -3.8331 | 6844.5648 | 3322.6003 | -0.00056002
52 |  | 106.4774 | 65.1345 | 4187 | 0.0001461 | 6.0075 | 6.0076 | -3.8331 | 6844.6237 | 3387.7348 | -0.00056002
53 |  | 106.4774 | 65.1339 | 4187 | 0.0001461 | 6.0076 | 6.0077 | -3.8331 | 6844.6825 | 3452.8687 | -0.00056001
54 |  | 106.4774 | 65.1333 | 4187 | 0.0001461 | 6.0077 | 6.0079 | -3.8331 | 6844.7414 | 3518.002 | -0.00056001
55 |  | 106.4774 | 65.1328 | 4187 | 0.0001461 | 6.0079 | 6.008 | -3.8331 | 6844.8002 | 3583.1348 | -0.00056
56 |  | 106.4774 | 65.1322 | 4187 | 0.0001461 | 6.008 | 6.0082 | -3.8331 | 6844.8591 | 3648.267 | -0.00056
57 |  | 106.4774 | 65.1317 | 4187 | 0.00014609 | 6.0082 | 6.0083 | -3.8331 | 6844.918 | 3713.3987 | -0.00055999
58 |  | 106.4774 | 65.1311 | 4187 | 0.00014609 | 6.0083 | 6.0085 | -3.8331 | 6844.9768 | 3778.5298 | -0.00055999
59 |  | 106.4774 | 65.1305 | 4187 | 0.00014609 | 6.0085 | 6.0086 | -3.8331 | 6845.0357 | 3843.6603 | -0.00055999
60 |  | 106.4774 | 65.13 | 4187 | 0.00014609 | 6.0086 | 6.0088 | -3.8331 | 6845.0945 | 3908.7903 | -0.00055998
61 |  | 106.4774 | 65.1294 | 4187 | 0.00014609 | 6.0088 | 6.0089 | -3.8331 | 6845.1534 | 3973.9197 | -0.00055998
62 |  | 106.4774 | 65.1289 | 4187 | 0.00014609 | 6.0089 | 6.0091 | -3.8331 | 6845.2122 | 4039.0486 | -0.00055997
63 |  | 106.4774 | 65.1283 | 4187 | 0.00014609 | 6.0091 | 6.0092 | -3.8331 | 6845.2711 | 4104.1769 | -0.00055997
64 |  | 106.4774 | 65.1277 | 4187 | 0.00014608 | 6.0092 | 6.0094 | -3.8331 | 6845.3299 | 4169.3046 | -0.00055996
65 |  | 106.4774 | 65.1272 | 4187 | 0.00014608 | 6.0094 | 6.0095 | -3.8331 | 6845.3888 | 4234.4318 | -0.00055996
66 |  | 106.4774 | 65.1266 | 4187 | 0.00014608 | 6.0095 | 6.0096 | -3.8331 | 6845.4476 | 4299.5584 | -0.00055995
67 |  | 106.4774 | 65.1261 | 4187 | 0.00014608 | 6.0096 | 6.0098 | -3.8331 | 6845.5065 | 4364.6845 | -0.00055995
68 |  | 106.4774 | 65.1255 | 4187 | 0.00014608 | 6.0098 | 6.0099 | -3.8331 | 6845.5654 | 4429.81 | -0.00055994
69 |  | 106.4774 | 65.1249 | 4187 | 0.00014608 | 6.0099 | 6.0101 | -3.8331 | 6845.6242 | 4494.9349 | -0.00055994
70 |  | 106.4774 | 65.1244 | 4187 | 0.00014608 | 6.0101 | 6.0102 | -3.8331 | 6845.6831 | 4560.0593 | -0.00055993
71 |  | 106.4774 | 65.1238 | 4187 | 0.00014608 | 6.0102 | 6.0104 | -3.8331 | 6845.7419 | 4625.1831 | -0.00055993
72 |  | 106.4774 | 65.1233 | 4187 | 0.00014607 | 6.0104 | 6.0105 | -3.8331 | 6845.8008 | 4690.3064 | -0.00055992
73 |  | 106.4774 | 65.1227 | 4187 | 0.00014607 | 6.0105 | 6.0107 | -3.8331 | 6845.8597 | 4755.4291 | -0.00055992
74 |  | 106.4774 | 65.1221 | 4187 | 0.00014607 | 6.0107 | 6.0108 | -3.8331 | 6845.9185 | 4820.5513 | -0.00055991
75 |  | 106.4774 | 65.1216 | 4187 | 0.00014607 | 6.0108 | 6.011 | -3.8331 | 6845.9774 | 4885.6728 | -0.00055991
76 |  | 106.4774 | 65.121 | 4187 | 0.00014607 | 6.011 | 6.0111 | -3.8331 | 6846.0362 | 4950.7939 | -0.0005599
77 |  | 106.4774 | 65.1205 | 4187 | 0.00014607 | 6.0111 | 6.0113 | -3.8331 | 6846.0951 | 5015.9143 | -0.0005599
78 |  | 106.4774 | 65.1199 | 4187 | 0.00014607 | 6.0113 | 6.0114 | -3.8331 | 6846.154 | 5081.0342 | -0.00055989
79 |  | 106.4774 | 65.1193 | 4187 | 0.00014607 | 6.0114 | 6.0115 | -3.8331 | 6846.2128 | 5146.1536 | -0.00055989
80 |  | 106.4774 | 65.1188 | 4187 | 0.00014606 | 6.0115 | 6.0117 | -3.8331 | 6846.2717 | 5211.2724 | -0.00055988
81 |  | 106.4774 | 65.1182 | 4187 | 0.00014606 | 6.0117 | 6.0118 | -3.8331 | 6846.3305 | 5276.3906 | -0.00055988
82 |  | 106.4774 | 65.1177 | 4187 | 0.00014606 | 6.0118 | 6.012 | -3.8331 | 6846.3894 | 5341.5082 | -0.00055987
83 |  | 106.4774 | 65.1171 | 4187 | 0.00014606 | 6.012 | 6.0121 | -3.8331 | 6846.4483 | 5406.6253 | -0.00055987
84 |  | 106.4774 | 65.1165 | 4187 | 0.00014606 | 6.0121 | 6.0123 | -3.8331 | 6846.5071 | 5471.7419 | -0.00055986
85 |  | 106.4774 | 65.116 | 4187 | 0.00014606 | 6.0123 | 6.0124 | -3.8331 | 6846.566 | 5536.8579 | -0.00055986
86 |  | 106.4774 | 65.1154 | 4187 | 0.00014606 | 6.0124 | 6.0126 | -3.8331 | 6846.6249 | 5601.9733 | -0.00055986
87 |  | 106.4774 | 65.1149 | 4187 | 0.00014606 | 6.0126 | 6.0127 | -3.8331 | 6846.6837 | 5667.0882 | -0.00055985
88 |  | 106.4774 | 65.1143 | 4187 | 0.00014605 | 6.0127 | 6.0129 | -3.8331 | 6846.7426 | 5732.2025 | -0.00055985
89 |  | 106.4774 | 65.1137 | 4187 | 0.00014605 | 6.0129 | 6.013 | -3.8331 | 6846.8015 | 5797.3162 | -0.00055984
90 |  | 106.4774 | 65.1132 | 4187 | 0.00014605 | 6.013 | 6.0131 | -3.8331 | 6846.8603 | 5862.4294 | -0.00055984
91 |  | 106.4774 | 65.1126 | 4187 | 0.00014605 | 6.0131 | 6.0133 | -3.8331 | 6846.9192 | 5927.542 | -0.00055983
92 |  | 106.4774 | 65.1121 | 4187 | 0.00014605 | 6.0133 | 6.0134 | -3.8331 | 6846.9781 | 5992.6541 | -0.00055983
93 |  | 106.4774 | 65.1115 | 4187 | 0.00014605 | 6.0134 | 6.0136 | -3.8331 | 6847.037 | 6057.7656 | -0.00055982
94 |  | 106.4774 | 65.1109 | 4187 | 0.00014605 | 6.0136 | 6.0137 | -3.8331 | 6847.0958 | 6122.8765 | -0.00055982
95 |  | 106.4774 | 65.1104 | 4187 | 0.00014605 | 6.0137 | 6.0139 | -3.8331 | 6847.1547 | 6187.9869 | -0.00055981
96 |  | 106.4774 | 65.1098 | 4187 | 0.00014604 | 6.0139 | 6.014 | -3.8331 | 6847.2136 | 6253.0968 | -0.00055981
97 |  | 106.4774 | 65.1093 | 4187 | 0.00014604 | 6.014 | 6.0142 | -3.8331 | 6847.2724 | 6318.206 | -0.0005598
98 |  | 106.4774 | 65.1087 | 4187 | 0.00014604 | 6.0142 | 6.0143 | -3.8331 | 6847.3313 | 6383.3147 | -0.0005598
99 |  | 106.4774 | 65.1081 | 4187 | 0.00014604 | 6.0143 | 6.0145 | -3.8331 | 6847.3902 | 6448.4229 | -0.00055979
100 |  | 106.4774 | 65.1076 | 4187 | 0.00014604 | 6.0145 | 6.0146 | -3.8331 | 6847.4491 | 6513.5305 | -0.00055979
101 |  | 106.4774 | 65.107 | 4187 | 0.00014604 | 6.0146 | 6.0148 | -3.8331 | 6847.5079 | 6578.6375 | -0.00055978
102 |  | 106.4774 | 65.1065 | 4187 | 0.00014604 | 6.0148 | 6.0149 | -3.8331 | 6847.5668 | 6643.744 | -0.00055978
103 |  | 106.4774 | 65.1059 | 4187 | 0.00014604 | 6.0149 | 6.015 | -3.8331 | 6847.6257 | 6708.8499 | -0.00055977
104 |  | 106.4774 | 65.1053 | 4187 | 0.00014603 | 6.015 | 6.0152 | -3.8331 | 6847.6846 | 6773.9552 | -0.00055977
105 |  | 106.4774 | 65.1048 | 4187 | 0.00014603 | 6.0152 | 6.0153 | -3.8331 | 6847.7434 | 6839.06 | -0.00055976
106 |  | 106.4774 | 65.1042 | 4187 | 0.00014603 | 6.0153 | 6.0155 | -3.8331 | 6847.8023 | 6904.1642 | -0.00055976
107 |  | 106.4774 | 65.1037 | 4187 | 0.00014603 | 6.0155 | 6.0156 | -3.8331 | 6847.8612 | 6969.2679 | -0.00055975
108 |  | 106.4774 | 65.1031 | 4187 | 0.00014603 | 6.0156 | 6.0158 | -3.8331 | 6847.9201 | 7034.371 | -0.00055975
109 |  | 106.4774 | 65.1025 | 4187 | 0.00014603 | 6.0158 | 6.0159 | -3.8331 | 6847.9789 | 7099.4736 | -0.00055974
110 |  | 106.4774 | 65.102 | 4187 | 0.00014603 | 6.0159 | 6.0161 | -3.8331 | 6848.0378 | 7164.5755 | -0.00055974
111 |  | 106.4774 | 65.1014 | 4187 | 0.00014603 | 6.0161 | 6.0162 | -3.8331 | 6848.0967 | 7229.677 | -0.00055973
112 |  | 106.4774 | 65.1009 | 4187 | 0.00014602 | 6.0162 | 6.0164 | -3.8331 | 6848.1556 | 7294.7778 | -0.00055973
113 |  | 106.4774 | 65.1003 | 4187 | 0.00014602 | 6.0164 | 6.0165 | -3.8331 | 6848.2145 | 7359.8782 | -0.00055973
114 |  | 106.4774 | 65.0998 | 4187 | 0.00014602 | 6.0165 | 6.0167 | -3.8331 | 6848.2733 | 7424.9779 | -0.00055972
115 |  | 106.4774 | 65.0992 | 4187 | 0.00014602 | 6.0167 | 6.0168 | -3.8331 | 6848.3322 | 7490.0771 | -0.00055972
116 |  | 106.4774 | 65.0986 | 4187 | 0.00014602 | 6.0168 | 6.0169 | -3.8331 | 6848.3911 | 7555.1757 | -0.00055971
117 |  | 106.4774 | 65.0981 | 4187 | 0.00014602 | 6.0169 | 6.0171 | -3.8331 | 6848.45 | 7620.2738 | -0.00055971
118 |  | 106.4774 | 65.0975 | 4187 | 0.00014602 | 6.0171 | 6.0172 | -3.8331 | 6848.5089 | 7685.3713 | -0.0005597
119 |  | 106.4774 | 65.097 | 4187 | 0.00014602 | 6.0172 | 6.0174 | -3.8331 | 6848.5678 | 7750.4683 | -0.0005597
120 |  | 106.4774 | 65.0964 | 4187 | 0.00014601 | 6.0174 | 6.0175 | -3.8331 | 6848.6266 | 7815.5647 | -0.00055969
121 |  | 106.4774 | 65.0958 | 4187 | 0.00014601 | 6.0175 | 6.0177 | -3.8331 | 6848.6855 | 7880.6605 | -0.00055969
122 |  | 106.4774 | 65.0953 | 4187 | 0.00014601 | 6.0177 | 6.0178 | -3.8331 | 6848.7444 | 7945.7558 | -0.00055968
123 |  | 106.4774 | 65.0947 | 4187 | 0.00014601 | 6.0178 | 6.018 | -3.8331 | 6848.8033 | 8010.8505 | -0.00055968
124 |  | 106.4774 | 65.0942 | 4187 | 0.00014601 | 6.018 | 6.0181 | -3.8331 | 6848.8622 | 8075.9446 | -0.00055967
125 |  | 106.4774 | 65.0936 | 4187 | 0.00014601 | 6.0181 | 6.0183 | -3.8331 | 6848.9211 | 8141.0382 | -0.00055967
126 |  | 106.4774 | 65.093 | 4187 | 0.00014601 | 6.0183 | 6.0184 | -3.8331 | 6848.98 | 8206.1313 | -0.00055966
127 |  | 106.4774 | 65.0925 | 4187 | 0.00014601 | 6.0184 | 6.0186 | -3.8331 | 6849.0388 | 8271.2237 | -0.00055966
128 |  | 106.4774 | 65.0919 | 4187 | 0.000146 | 6.0186 | 6.0187 | -3.8331 | 6849.0977 | 8336.3156 | -0.00055965
129 |  | 106.4774 | 65.0914 | 4187 | 0.000146 | 6.0187 | 6.0188 | -3.8331 | 6849.1566 | 8401.407 | -0.00055965
130 |  | 106.4774 | 65.0908 | 4187 | 0.000146 | 6.0188 | 6.019 | -3.8331 | 6849.2155 | 8466.4978 | -0.00055964
131 |  | 106.4774 | 65.0902 | 4187 | 0.000146 | 6.019 | 6.0191 | -3.8331 | 6849.2744 | 8531.588 | -0.00055964
132 |  | 106.4774 | 65.0897 | 4187 | 0.000146 | 6.0191 | 6.0193 | -3.8331 | 6849.3333 | 8596.6777 | -0.00055963
133 |  | 106.4774 | 65.0891 | 4187 | 0.000146 | 6.0193 | 6.0194 | -3.8331 | 6849.3922 | 8661.7668 | -0.00055963
134 |  | 106.4774 | 65.0886 | 4187 | 0.000146 | 6.0194 | 6.0196 | -3.8331 | 6849.4511 | 8726.8554 | -0.00055962
135 |  | 106.4774 | 65.088 | 4187 | 0.000146 | 6.0196 | 6.0197 | -3.8331 | 6849.51 | 8791.9434 | -0.00055962
136 |  | 106.4774 | 65.0874 | 4187 | 0.00014599 | 6.0197 | 6.0199 | -3.8331 | 6849.5688 | 8857.0308 | -0.00055961
137 |  | 106.4774 | 65.0869 | 4187 | 0.00014599 | 6.0199 | 6.02 | -3.8331 | 6849.6277 | 8922.1177 | -0.00055961
138 |  | 106.4774 | 65.0863 | 4187 | 0.00014599 | 6.02 | 6.0202 | -3.8331 | 6849.6866 | 8987.204 | -0.00055961
139 |  | 106.4774 | 65.0858 | 4187 | 0.00014599 | 6.0202 | 6.0203 | -3.8331 | 6849.7455 | 9052.2898 | -0.0005596
140 |  | 106.4774 | 65.0852 | 4187 | 0.00014599 | 6.0203 | 6.0205 | -3.8331 | 6849.8044 | 9117.375 | -0.0005596
141 |  | 106.4774 | 65.0846 | 4187 | 0.00014599 | 6.0205 | 6.0206 | -3.8331 | 6849.8633 | 9182.4596 | -0.00055959
142 |  | 106.4774 | 65.0841 | 4187 | 0.00014599 | 6.0206 | 6.0207 | -3.8331 | 6849.9222 | 9247.5437 | -0.00055959
143 |  | 106.4774 | 65.0835 | 4187 | 0.00014599 | 6.0207 | 6.0209 | -3.8331 | 6849.9811 | 9312.6272 | -0.00055958
144 |  | 106.4774 | 65.083 | 4187 | 0.00014598 | 6.0209 | 6.021 | -3.8331 | 6850.04 | 9377.7102 | -0.00055958
145 |  | 106.4774 | 65.0824 | 4187 | 0.00014598 | 6.021 | 6.0212 | -3.8331 | 6850.0989 | 9442.7926 | -0.00055957
146 |  | 106.4774 | 65.0818 | 4187 | 0.00014598 | 6.0212 | 6.0213 | -3.8331 | 6850.1578 | 9507.8744 | -0.00055957
147 |  | 106.4774 | 65.0813 | 4187 | 0.00014598 | 6.0213 | 6.0215 | -3.8331 | 6850.2167 | 9572.9557 | -0.00055956
148 |  | 106.4774 | 65.0807 | 4187 | 0.00014598 | 6.0215 | 6.0216 | -3.8331 | 6850.2756 | 9638.0364 | -0.00055956
149 |  | 106.4774 | 65.0802 | 4187 | 0.00014598 | 6.0216 | 6.0218 | -3.8331 | 6850.3345 | 9703.1166 | -0.00055955
150 |  | 106.4774 | 65.0796 | 4187 | 0.00014598 | 6.0218 | 6.0219 | -3.8331 | 6850.3934 | 9768.1962 | -0.00055955
151 |  | 106.4774 | 65.079 | 4187 | 0.00014598 | 6.0219 | 6.0221 | -3.8331 | 6850.4523 | 9833.2752 | -0.00055954
152 |  | 106.4774 | 65.0785 | 4187 | 0.00014597 | 6.0221 | 6.0222 | -3.8331 | 6850.5112 | 9898.3537 | -0.00055954
153 |  | 106.4774 | 65.0779 | 4187 | 0.00014597 | 6.0222 | 6.0223 | -3.8331 | 6850.5701 | 9963.4316 | -0.00055953
154 |  | 106.4774 | 65.0774 | 4187 | 0.00014597 | 6.0223 | 6.0225 | -3.8331 | 6850.629 | 10028.509 | -0.00055953
155 |  | 106.4774 | 65.0768 | 4187 | 0.00014597 | 6.0225 | 6.0226 | -3.8331 | 6850.6879 | 10093.5858 | -0.00055952
156 |  | 106.4774 | 65.0762 | 4187 | 0.00014597 | 6.0226 | 6.0228 | -3.8331 | 6850.7468 | 10158.6621 | -0.00055952
157 |  | 106.4774 | 65.0757 | 4187 | 0.00014597 | 6.0228 | 6.0229 | -3.8331 | 6850.8057 | 10223.7377 | -0.00055951
158 |  | 106.4774 | 65.0751 | 4187 | 0.00014597 | 6.0229 | 6.0231 | -3.8331 | 6850.8646 | 10288.8129 | -0.00055951
159 |  | 106.4774 | 65.0746 | 4187 | 0.00014597 | 6.0231 | 6.0232 | -3.8331 | 6850.9235 | 10353.8874 | -0.0005595
160 |  | 106.4774 | 65.074 | 4187 | 0.00014596 | 6.0232 | 6.0234 | -3.8331 | 6850.9824 | 10418.9614 | -0.0005595
161 |  | 106.4774 | 65.0734 | 4187 | 0.00014596 | 6.0234 | 6.0235 | -3.8331 | 6851.0413 | 10484.0349 | -0.00055949
162 |  | 106.4774 | 65.0729 | 4187 | 0.00014596 | 6.0235 | 6.0237 | -3.8331 | 6851.1002 | 10549.1078 | -0.00055949
163 |  | 106.4774 | 65.0723 | 4187 | 0.00014596 | 6.0237 | 6.0238 | -3.8331 | 6851.1591 | 10614.1801 | -0.00055948
164 |  | 106.4774 | 65.0718 | 4187 | 0.00014596 | 6.0238 | 6.024 | -3.8331 | 6851.218 | 10679.2519 | -0.00055948
165 |  | 106.4774 | 65.0712 | 4187 | 0.00014596 | 6.024 | 6.0241 | -3.8331 | 6851.2769 | 10744.3231 | -0.00055948
166 |  | 106.4774 | 65.0707 | 4187 | 0.00014596 | 6.0241 | 6.0242 | -3.8331 | 6851.3358 | 10809.3937 | -0.00055947
167 |  | 106.4774 | 65.0701 | 4187 | 0.00014596 | 6.0242 | 6.0244 | -3.8331 | 6851.3947 | 10874.4638 | -0.00055947
168 |  | 106.4774 | 65.0695 | 4187 | 0.00014595 | 6.0244 | 6.0245 | -3.8331 | 6851.4537 | 10939.5334 | -0.00055946
169 |  | 106.4774 | 65.069 | 4187 | 0.00014595 | 6.0245 | 6.0247 | -3.8331 | 6851.5126 | 11004.6023 | -0.00055946
170 |  | 106.4774 | 65.0684 | 4187 | 0.00014595 | 6.0247 | 6.0248 | -3.8331 | 6851.5715 | 11069.6708 | -0.00055945
171 |  | 106.4774 | 65.0679 | 4187 | 0.00014595 | 6.0248 | 6.025 | -3.8331 | 6851.6304 | 11134.7386 | -0.00055945
172 |  | 106.4774 | 65.0673 | 4187 | 0.00014595 | 6.025 | 6.0251 | -3.8331 | 6851.6893 | 11199.8059 | -0.00055944
173 |  | 106.4774 | 65.0667 | 4187 | 0.00014595 | 6.0251 | 6.0253 | -3.8331 | 6851.7482 | 11264.8726 | -0.00055944
174 |  | 106.4774 | 65.0662 | 4187 | 0.00014595 | 6.0253 | 6.0254 | -3.8331 | 6851.8071 | 11329.9388 | -0.00055943
175 |  | 106.4774 | 65.0656 | 4187 | 0.00014595 | 6.0254 | 6.0256 | -3.8331 | 6851.866 | 11395.0044 | -0.00055943
176 |  | 106.4774 | 65.0651 | 4187 | 0.00014594 | 6.0256 | 6.0257 | -3.8331 | 6851.9249 | 11460.0695 | -0.00055942
177 |  | 106.4774 | 65.0645 | 4187 | 0.00014594 | 6.0257 | 6.0259 | -3.8331 | 6851.9838 | 11525.134 | -0.00055942
178 |  | 106.4774 | 65.0639 | 4187 | 0.00014594 | 6.0259 | 6.026 | -3.8331 | 6852.0428 | 11590.1979 | -0.00055941
179 |  | 106.4774 | 65.0634 | 4187 | 0.00014594 | 6.026 | 6.0261 | -3.8331 | 6852.1017 | 11655.2613 | -0.00055941
180 |  | 106.4774 | 65.0628 | 4187 | 0.00014594 | 6.0261 | 6.0263 | -3.8331 | 6852.1606 | 11720.3241 | -0.0005594
181 |  | 106.4774 | 65.0623 | 4187 | 0.00014594 | 6.0263 | 6.0264 | -3.8331 | 6852.2195 | 11785.3864 | -0.0005594
182 |  | 106.4774 | 65.0617 | 4187 | 0.00014594 | 6.0264 | 6.0266 | -3.8331 | 6852.2784 | 11850.4481 | -0.00055939
183 |  | 106.4774 | 65.0611 | 4187 | 0.00014594 | 6.0266 | 6.0267 | -3.8331 | 6852.3373 | 11915.5092 | -0.00055939
184 |  | 106.4774 | 65.0606 | 4187 | 0.00014593 | 6.0267 | 6.0269 | -3.8331 | 6852.3963 | 11980.5698 | -0.00055938
185 |  | 106.4774 | 65.06 | 4187 | 0.00014593 | 6.0269 | 6.027 | -3.8331 | 6852.4552 | 12045.6298 | -0.00055938
186 |  | 106.4774 | 65.0595 | 4187 | 0.00014593 | 6.027 | 6.0272 | -3.8331 | 6852.5141 | 12110.6893 | -0.00055937
187 |  | 106.4774 | 65.0589 | 4187 | 0.00014593 | 6.0272 | 6.0273 | -3.8331 | 6852.573 | 12175.7482 | -0.00055937
188 |  | 106.4774 | 65.0583 | 4187 | 0.00014593 | 6.0273 | 6.0275 | -3.8331 | 6852.6319 | 12240.8065 | -0.00055936
189 |  | 106.4774 | 65.0578 | 4187 | 0.00014593 | 6.0275 | 6.0276 | -3.8331 | 6852.6908 | 12305.8643 | -0.00055936
190 |  | 106.4774 | 65.0572 | 4187 | 0.00014593 | 6.0276 | 6.0277 | -3.8331 | 6852.7498 | 12370.9216 | -0.00055935
191 |  | 106.4774 | 65.0567 | 4187 | 0.00014593 | 6.0277 | 6.0279 | -3.8331 | 6852.8087 | 12435.9782 | -0.00055935
192 |  | 106.4774 | 65.0561 | 4187 | 0.00014592 | 6.0279 | 6.028 | -3.8331 | 6852.8676 | 12501.0343 | -0.00055935
193 |  | 106.4774 | 65.0555 | 4187 | 0.00014592 | 6.028 | 6.0282 | -3.8331 | 6852.9265 | 12566.0899 | -0.00055934
194 |  | 106.4774 | 65.055 | 4187 | 0.00014592 | 6.0282 | 6.0283 | -3.8331 | 6852.9854 | 12631.1449 | -0.00055934
195 |  | 106.4774 | 65.0544 | 4187 | 0.00014592 | 6.0283 | 6.0285 | -3.8331 | 6853.0444 | 12696.1993 | -0.00055933
196 |  | 106.4774 | 65.0539 | 4187 | 0.00014592 | 6.0285 | 6.0286 | -3.8331 | 6853.1033 | 12761.2532 | -0.00055933
197 |  | 106.4774 | 65.0533 | 4187 | 0.00014592 | 6.0286 | 6.0288 | -3.8331 | 6853.1622 | 12826.3065 | -0.00055932
198 |  | 106.4774 | 65.0528 | 4187 | 0.00014592 | 6.0288 | 6.0289 | -3.8331 | 6853.2211 | 12891.3592 | -0.00055932
199 |  | 106.4774 | 65.0522 | 4187 | 0.00014592 | 6.0289 | 6.0291 | -3.8331 | 6853.2801 | 12956.4114 | -0.00055931
200 |  | 106.4774 | 65.0516 | 4187 | 0.00014591 | 6.0291 | 6.0292 | -3.8331 | 6853.339 | 13021.463 | -0.00055931
201 |  | 106.4774 | 65.0511 | 4187 | 0.00014591 | 6.0292 | 6.0294 | -3.8331 | 6853.3979 | 13086.5141 | -0.0005593
202 |  | 106.4774 | 65.0505 | 4187 | 0.00014591 | 6.0294 | 6.0295 | -3.8331 | 6853.4568 | 13151.5646 | -0.0005593
203 |  | 106.4774 | 65.05 | 4187 | 0.00014591 | 6.0295 | 6.0296 | -3.8331 | 6853.5158 | 13216.6146 | -0.00055929
204 |  | 106.4774 | 65.0494 | 4187 | 0.00014591 | 6.0296 | 6.0298 | -3.8331 | 6853.5747 | 13281.664 | -0.00055929
205 |  | 106.4774 | 65.0488 | 4187 | 0.00014591 | 6.0298 | 6.0299 | -3.8331 | 6853.6336 | 13346.7128 | -0.00055928
206 |  | 106.4774 | 65.0483 | 4187 | 0.00014591 | 6.0299 | 6.0301 | -3.8331 | 6853.6925 | 13411.7611 | -0.00055928
207 |  | 106.4774 | 65.0477 | 4187 | 0.00014591 | 6.0301 | 6.0302 | -3.8331 | 6853.7515 | 13476.8088 | -0.00055927
208 |  | 106.4774 | 65.0472 | 4187 | 0.0001459 | 6.0302 | 6.0304 | -3.8331 | 6853.8104 | 13541.856 | -0.00055927
209 |  | 106.4774 | 65.0466 | 4187 | 0.0001459 | 6.0304 | 6.0305 | -3.8331 | 6853.8693 | 13606.9026 | -0.00055926
210 |  | 106.4774 | 65.046 | 4187 | 0.0001459 | 6.0305 | 6.0307 | -3.8331 | 6853.9283 | 13671.9486 | -0.00055926
211 |  | 106.4774 | 65.0455 | 4187 | 0.0001459 | 6.0307 | 6.0308 | -3.8331 | 6853.9872 | 13736.9941 | -0.00055925
212 |  | 106.4774 | 65.0449 | 4187 | 0.0001459 | 6.0308 | 6.031 | -3.8331 | 6854.0461 | 13802.039 | -0.00055925
213 |  | 106.4774 | 65.0444 | 4187 | 0.0001459 | 6.031 | 6.0311 | -3.8331 | 6854.105 | 13867.0834 | -0.00055924
214 |  | 106.4774 | 65.0438 | 4187 | 0.0001459 | 6.0311 | 6.0313 | -3.8331 | 6854.164 | 13932.1272 | -0.00055924
215 |  | 106.4774 | 65.0432 | 4187 | 0.0001459 | 6.0313 | 6.0314 | -3.8331 | 6854.2229 | 13997.1704 | -0.00055923
216 |  | 106.4774 | 65.0427 | 4187 | 0.00014589 | 6.0314 | 6.0315 | -3.8331 | 6854.2818 | 14062.2131 | -0.00055923
217 |  | 106.4774 | 65.0421 | 4187 | 0.00014589 | 6.0315 | 6.0317 | -3.8331 | 6854.3408 | 14127.2552 | -0.00055923
218 |  | 106.4774 | 65.0416 | 4187 | 0.00014589 | 6.0317 | 6.0318 | -3.8331 | 6854.3997 | 14192.2968 | -0.00055922
219 |  | 106.4774 | 65.041 | 4187 | 0.00014589 | 6.0318 | 6.032 | -3.8331 | 6854.4586 | 14257.3378 | -0.00055922
220 |  | 106.4774 | 65.0404 | 4187 | 0.00014589 | 6.032 | 6.0321 | -3.8331 | 6854.5176 | 14322.3782 | -0.00055921
221 |  | 106.4774 | 65.0399 | 4187 | 0.00014589 | 6.0321 | 6.0323 | -3.8331 | 6854.5765 | 14387.4181 | -0.00055921
222 |  | 106.4774 | 65.0393 | 4187 | 0.00014589 | 6.0323 | 6.0324 | -3.8331 | 6854.6354 | 14452.4575 | -0.0005592
223 |  | 106.4774 | 65.0388 | 4187 | 0.00014589 | 6.0324 | 6.0326 | -3.8331 | 6854.6944 | 14517.4962 | -0.0005592
224 |  | 106.4774 | 65.0382 | 4187 | 0.00014588 | 6.0326 | 6.0327 | -3.8331 | 6854.7533 | 14582.5344 | -0.00055919
225 |  | 106.4774 | 65.0377 | 4187 | 0.00014588 | 6.0327 | 6.0329 | -3.8331 | 6854.8123 | 14647.5721 | -0.00055919
226 |  | 106.4774 | 65.0371 | 4187 | 0.00014588 | 6.0329 | 6.033 | -3.8331 | 6854.8712 | 14712.6092 | -0.00055918
227 |  | 106.4774 | 65.0365 | 4187 | 0.00014588 | 6.033 | 6.0331 | -3.8331 | 6854.9301 | 14777.6457 | -0.00055918
228 |  | 106.4774 | 65.036 | 4187 | 0.00014588 | 6.0331 | 6.0333 | -3.8331 | 6854.9891 | 14842.6817 | -0.00055917
229 |  | 106.4774 | 65.0354 | 4187 | 0.00014588 | 6.0333 | 6.0334 | -3.8331 | 6855.048 | 14907.7171 | -0.00055917
230 |  | 106.4774 | 65.0349 | 4187 | 0.00014588 | 6.0334 | 6.0336 | -3.8331 | 6855.1069 | 14972.7519 | -0.00055916
231 |  | 106.4774 | 65.0343 | 4187 | 0.00014588 | 6.0336 | 6.0337 | -3.8331 | 6855.1659 | 15037.7862 | -0.00055916
232 |  | 106.4774 | 65.0337 | 4187 | 0.00014587 | 6.0337 | 6.0339 | -3.8331 | 6855.2248 | 15102.82 | -0.00055915
233 |  | 106.4774 | 65.0332 | 4187 | 0.00014587 | 6.0339 | 6.034 | -3.8331 | 6855.2838 | 15167.8532 | -0.00055915
234 |  | 106.4774 | 65.0326 | 4187 | 0.00014587 | 6.034 | 6.0342 | -3.8331 | 6855.3427 | 15232.8858 | -0.00055914
235 |  | 106.4774 | 65.0321 | 4187 | 0.00014587 | 6.0342 | 6.0343 | -3.8331 | 6855.4016 | 15297.9178 | -0.00055914
236 |  | 106.4774 | 65.0315 | 4187 | 0.00014587 | 6.0343 | 6.0345 | -3.8331 | 6855.4606 | 15362.9493 | -0.00055913

## CLX160
|  |  | buis | verlies W/M | L /°C/sec
diam | wandikte |  | inhoud l/m |  | W/M
160 | 9.1 | 3.1416 | 15.7922 | 64.6387 | 4187
[8 empty] | J/sec/mtr | aantal mtr. | verlies
|  | buis | verlies W/M | L /°C/sec | verlies temp | begintemp | eindtemp | verlies | bij 1°C | totaal J/sec
|  | inhoud L |  | W/M | °C per M | °C | °C | per m°C | daling | aantal mtr
1 | 160 | 15.7922 | 64.6387 | 4187 | 0.00097757 | 6 | 6.001 | -3.8023 | 1022.9463 | 64.6387 | -0.003717
2 |  | 15.7922 | 64.635 | 4187 | 0.00097751 | 6.001 | 6.002 | -3.8023 | 1023.0051 | 129.2736 | -0.0037168
3 |  | 15.7922 | 64.6312 | 4187 | 0.00097746 | 6.002 | 6.0029 | -3.8023 | 1023.064 | 193.9049 | -0.0037166
4 |  | 15.7922 | 64.6275 | 4187 | 0.0009774 | 6.0029 | 6.0039 | -3.8023 | 1023.1228 | 258.5324 | -0.0037163
5 |  | 15.7922 | 64.6238 | 4187 | 0.00097734 | 6.0039 | 6.0049 | -3.8023 | 1023.1816 | 323.1562 | -0.0037161
6 |  | 15.7922 | 64.6201 | 4187 | 0.00097729 | 6.0049 | 6.0059 | -3.8023 | 1023.2405 | 387.7763 | -0.0037159
7 |  | 15.7922 | 64.6164 | 4187 | 0.00097723 | 6.0059 | 6.0068 | -3.8023 | 1023.2993 | 452.3927 | -0.0037157
8 |  | 15.7922 | 64.6127 | 4187 | 0.00097717 | 6.0068 | 6.0078 | -3.8023 | 1023.3582 | 517.0054 | -0.0037155
9 |  | 15.7922 | 64.6089 | 4187 | 0.00097712 | 6.0078 | 6.0088 | -3.8023 | 1023.417 | 581.6143 | -0.0037153
10 |  | 15.7922 | 64.6052 | 4187 | 0.00097706 | 6.0088 | 6.0098 | -3.8023 | 1023.4759 | 646.2195 | -0.0037151
11 |  | 15.7922 | 64.6015 | 4187 | 0.00097701 | 6.0098 | 6.0108 | -3.8023 | 1023.5347 | 710.8211 | -0.0037148
12 |  | 15.7922 | 64.5978 | 4187 | 0.00097695 | 6.0108 | 6.0117 | -3.8023 | 1023.5936 | 775.4189 | -0.0037146
13 |  | 15.7922 | 64.5941 | 4187 | 0.00097689 | 6.0117 | 6.0127 | -3.8023 | 1023.6525 | 840.0129 | -0.0037144
14 |  | 15.7922 | 64.5904 | 4187 | 0.00097684 | 6.0127 | 6.0137 | -3.8023 | 1023.7113 | 904.6033 | -0.0037142
15 |  | 15.7922 | 64.5867 | 4187 | 0.00097678 | 6.0137 | 6.0147 | -3.8023 | 1023.7702 | 969.19 | -0.003714
16 |  | 15.7922 | 64.5829 | 4187 | 0.00097673 | 6.0147 | 6.0156 | -3.8023 | 1023.8291 | 1033.7729 | -0.0037138
17 |  | 15.7922 | 64.5792 | 4187 | 0.00097667 | 6.0156 | 6.0166 | -3.8023 | 1023.888 | 1098.3522 | -0.0037136
18 |  | 15.7922 | 64.5755 | 4187 | 0.00097661 | 6.0166 | 6.0176 | -3.8023 | 1023.9468 | 1162.9277 | -0.0037134
19 |  | 15.7922 | 64.5718 | 4187 | 0.00097656 | 6.0176 | 6.0186 | -3.8023 | 1024.0057 | 1227.4995 | -0.0037131
20 |  | 15.7922 | 64.5681 | 4187 | 0.0009765 | 6.0186 | 6.0195 | -3.8023 | 1024.0646 | 1292.0676 | -0.0037129
21 |  | 15.7922 | 64.5644 | 4187 | 0.00097644 | 6.0195 | 6.0205 | -3.8023 | 1024.1235 | 1356.6319 | -0.0037127
22 |  | 15.7922 | 64.5607 | 4187 | 0.00097639 | 6.0205 | 6.0215 | -3.8023 | 1024.1824 | 1421.1926 | -0.0037125
23 |  | 15.7922 | 64.557 | 4187 | 0.00097633 | 6.0215 | 6.0225 | -3.8023 | 1024.2413 | 1485.7496 | -0.0037123
24 |  | 15.7922 | 64.5532 | 4187 | 0.00097628 | 6.0225 | 6.0234 | -3.8023 | 1024.3002 | 1550.3028 | -0.0037121
25 |  | 15.7922 | 64.5495 | 4187 | 0.00097622 | 6.0234 | 6.0244 | -3.8023 | 1024.3591 | 1614.8523 | -0.0037119
26 |  | 15.7922 | 64.5458 | 4187 | 0.00097616 | 6.0244 | 6.0254 | -3.8023 | 1024.418 | 1679.3981 | -0.0037116
27 |  | 15.7922 | 64.5421 | 4187 | 0.00097611 | 6.0254 | 6.0264 | -3.8023 | 1024.4769 | 1743.9403 | -0.0037114
28 |  | 15.7922 | 64.5384 | 4187 | 0.00097605 | 6.0264 | 6.0274 | -3.8023 | 1024.5358 | 1808.4786 | -0.0037112
29 |  | 15.7922 | 64.5347 | 4187 | 0.000976 | 6.0274 | 6.0283 | -3.8023 | 1024.5947 | 1873.0133 | -0.003711
30 |  | 15.7922 | 64.531 | 4187 | 0.00097594 | 6.0283 | 6.0293 | -3.8023 | 1024.6537 | 1937.5443 | -0.0037108
31 |  | 15.7922 | 64.5273 | 4187 | 0.00097588 | 6.0293 | 6.0303 | -3.8023 | 1024.7126 | 2002.0716 | -0.0037106
32 |  | 15.7922 | 64.5236 | 4187 | 0.00097583 | 6.0303 | 6.0313 | -3.8023 | 1024.7715 | 2066.5951 | -0.0037104
33 |  | 15.7922 | 64.5198 | 4187 | 0.00097577 | 6.0313 | 6.0322 | -3.8023 | 1024.8305 | 2131.115 | -0.0037102
34 |  | 15.7922 | 64.5161 | 4187 | 0.00097572 | 6.0322 | 6.0332 | -3.8023 | 1024.8894 | 2195.6311 | -0.0037099
35 |  | 15.7922 | 64.5124 | 4187 | 0.00097566 | 6.0332 | 6.0342 | -3.8023 | 1024.9483 | 2260.1435 | -0.0037097
36 |  | 15.7922 | 64.5087 | 4187 | 0.0009756 | 6.0342 | 6.0352 | -3.8023 | 1025.0073 | 2324.6522 | -0.0037095
37 |  | 15.7922 | 64.505 | 4187 | 0.00097555 | 6.0352 | 6.0361 | -3.8023 | 1025.0662 | 2389.1572 | -0.0037093
38 |  | 15.7922 | 64.5013 | 4187 | 0.00097549 | 6.0361 | 6.0371 | -3.8023 | 1025.1252 | 2453.6585 | -0.0037091
39 |  | 15.7922 | 64.4976 | 4187 | 0.00097543 | 6.0371 | 6.0381 | -3.8023 | 1025.1841 | 2518.1561 | -0.0037089
40 |  | 15.7922 | 64.4939 | 4187 | 0.00097538 | 6.0381 | 6.0391 | -3.8023 | 1025.2431 | 2582.65 | -0.0037087
41 |  | 15.7922 | 64.4902 | 4187 | 0.00097532 | 6.0391 | 6.04 | -3.8023 | 1025.302 | 2647.1401 | -0.0037084
42 |  | 15.7922 | 64.4865 | 4187 | 0.00097527 | 6.04 | 6.041 | -3.8023 | 1025.361 | 2711.6266 | -0.0037082
43 |  | 15.7922 | 64.4827 | 4187 | 0.00097521 | 6.041 | 6.042 | -3.8023 | 1025.42 | 2776.1093 | -0.003708
44 |  | 15.7922 | 64.479 | 4187 | 0.00097515 | 6.042 | 6.043 | -3.8023 | 1025.4789 | 2840.5884 | -0.0037078
45 |  | 15.7922 | 64.4753 | 4187 | 0.0009751 | 6.043 | 6.0439 | -3.8023 | 1025.5379 | 2905.0637 | -0.0037076
46 |  | 15.7922 | 64.4716 | 4187 | 0.00097504 | 6.0439 | 6.0449 | -3.8023 | 1025.5969 | 2969.5353 | -0.0037074
47 |  | 15.7922 | 64.4679 | 4187 | 0.00097499 | 6.0449 | 6.0459 | -3.8023 | 1025.6559 | 3034.0032 | -0.0037072
48 |  | 15.7922 | 64.4642 | 4187 | 0.00097493 | 6.0459 | 6.0469 | -3.8023 | 1025.7148 | 3098.4675 | -0.003707
49 |  | 15.7922 | 64.4605 | 4187 | 0.00097487 | 6.0469 | 6.0478 | -3.8023 | 1025.7738 | 3162.928 | -0.0037067
50 |  | 15.7922 | 64.4568 | 4187 | 0.00097482 | 6.0478 | 6.0488 | -3.8023 | 1025.8328 | 3227.3848 | -0.0037065
51 |  | 15.7922 | 64.4531 | 4187 | 0.00097476 | 6.0488 | 6.0498 | -3.8023 | 1025.8918 | 3291.8378 | -0.0037063
52 |  | 15.7922 | 64.4494 | 4187 | 0.00097471 | 6.0498 | 6.0508 | -3.8023 | 1025.9508 | 3356.2872 | -0.0037061
53 |  | 15.7922 | 64.4457 | 4187 | 0.00097465 | 6.0508 | 6.0517 | -3.8023 | 1026.0098 | 3420.7329 | -0.0037059
54 |  | 15.7922 | 64.442 | 4187 | 0.00097459 | 6.0517 | 6.0527 | -3.8023 | 1026.0688 | 3485.1749 | -0.0037057
55 |  | 15.7922 | 64.4383 | 4187 | 0.00097454 | 6.0527 | 6.0537 | -3.8023 | 1026.1278 | 3549.6131 | -0.0037055
56 |  | 15.7922 | 64.4346 | 4187 | 0.00097448 | 6.0537 | 6.0547 | -3.8023 | 1026.1868 | 3614.0477 | -0.0037052
57 |  | 15.7922 | 64.4309 | 4187 | 0.00097443 | 6.0547 | 6.0556 | -3.8023 | 1026.2458 | 3678.4786 | -0.003705
58 |  | 15.7922 | 64.4272 | 4187 | 0.00097437 | 6.0556 | 6.0566 | -3.8023 | 1026.3049 | 3742.9057 | -0.0037048
59 |  | 15.7922 | 64.4234 | 4187 | 0.00097431 | 6.0566 | 6.0576 | -3.8023 | 1026.3639 | 3807.3291 | -0.0037046
60 |  | 15.7922 | 64.4197 | 4187 | 0.00097426 | 6.0576 | 6.0586 | -3.8023 | 1026.4229 | 3871.7489 | -0.0037044
61 |  | 15.7922 | 64.416 | 4187 | 0.0009742 | 6.0586 | 6.0595 | -3.8023 | 1026.4819 | 3936.1649 | -0.0037042
62 |  | 15.7922 | 64.4123 | 4187 | 0.00097415 | 6.0595 | 6.0605 | -3.8023 | 1026.541 | 4000.5773 | -0.003704
63 |  | 15.7922 | 64.4086 | 4187 | 0.00097409 | 6.0605 | 6.0615 | -3.8023 | 1026.6 | 4064.9859 | -0.0037038
64 |  | 15.7922 | 64.4049 | 4187 | 0.00097403 | 6.0615 | 6.0625 | -3.8023 | 1026.659 | 4129.3908 | -0.0037035
65 |  | 15.7922 | 64.4012 | 4187 | 0.00097398 | 6.0625 | 6.0634 | -3.8023 | 1026.7181 | 4193.792 | -0.0037033
66 |  | 15.7922 | 64.3975 | 4187 | 0.00097392 | 6.0634 | 6.0644 | -3.8023 | 1026.7771 | 4258.1895 | -0.0037031
67 |  | 15.7922 | 64.3938 | 4187 | 0.00097387 | 6.0644 | 6.0654 | -3.8023 | 1026.8362 | 4322.5834 | -0.0037029
68 |  | 15.7922 | 64.3901 | 4187 | 0.00097381 | 6.0654 | 6.0663 | -3.8023 | 1026.8952 | 4386.9735 | -0.0037027
69 |  | 15.7922 | 64.3864 | 4187 | 0.00097375 | 6.0663 | 6.0673 | -3.8023 | 1026.9543 | 4451.3599 | -0.0037025
70 |  | 15.7922 | 64.3827 | 4187 | 0.0009737 | 6.0673 | 6.0683 | -3.8023 | 1027.0133 | 4515.7426 | -0.0037023
71 |  | 15.7922 | 64.379 | 4187 | 0.00097364 | 6.0683 | 6.0693 | -3.8023 | 1027.0724 | 4580.1216 | -0.0037021
72 |  | 15.7922 | 64.3753 | 4187 | 0.00097359 | 6.0693 | 6.0702 | -3.8023 | 1027.1314 | 4644.4969 | -0.0037018
73 |  | 15.7922 | 64.3716 | 4187 | 0.00097353 | 6.0702 | 6.0712 | -3.8023 | 1027.1905 | 4708.8685 | -0.0037016
74 |  | 15.7922 | 64.3679 | 4187 | 0.00097347 | 6.0712 | 6.0722 | -3.8023 | 1027.2496 | 4773.2364 | -0.0037014
75 |  | 15.7922 | 64.3642 | 4187 | 0.00097342 | 6.0722 | 6.0732 | -3.8023 | 1027.3087 | 4837.6006 | -0.0037012
76 |  | 15.7922 | 64.3605 | 4187 | 0.00097336 | 6.0732 | 6.0741 | -3.8023 | 1027.3677 | 4901.9611 | -0.003701
77 |  | 15.7922 | 64.3568 | 4187 | 0.00097331 | 6.0741 | 6.0751 | -3.8023 | 1027.4268 | 4966.3179 | -0.0037008
78 |  | 15.7922 | 64.3531 | 4187 | 0.00097325 | 6.0751 | 6.0761 | -3.8023 | 1027.4859 | 5030.671 | -0.0037006
79 |  | 15.7922 | 64.3494 | 4187 | 0.00097319 | 6.0761 | 6.0771 | -3.8023 | 1027.545 | 5095.0204 | -0.0037003
80 |  | 15.7922 | 64.3457 | 4187 | 0.00097314 | 6.0771 | 6.078 | -3.8023 | 1027.6041 | 5159.3661 | -0.0037001
81 |  | 15.7922 | 64.342 | 4187 | 0.00097308 | 6.078 | 6.079 | -3.8023 | 1027.6632 | 5223.7081 | -0.0036999
82 |  | 15.7922 | 64.3383 | 4187 | 0.00097303 | 6.079 | 6.08 | -3.8023 | 1027.7223 | 5288.0464 | -0.0036997
83 |  | 15.7922 | 64.3346 | 4187 | 0.00097297 | 6.08 | 6.0809 | -3.8023 | 1027.7814 | 5352.3809 | -0.0036995
84 |  | 15.7922 | 64.3309 | 4187 | 0.00097291 | 6.0809 | 6.0819 | -3.8023 | 1027.8405 | 5416.7118 | -0.0036993
85 |  | 15.7922 | 64.3272 | 4187 | 0.00097286 | 6.0819 | 6.0829 | -3.8023 | 1027.8996 | 5481.039 | -0.0036991
86 |  | 15.7922 | 64.3235 | 4187 | 0.0009728 | 6.0829 | 6.0839 | -3.8023 | 1027.9587 | 5545.3625 | -0.0036989
87 |  | 15.7922 | 64.3198 | 4187 | 0.00097275 | 6.0839 | 6.0848 | -3.8023 | 1028.0178 | 5609.6823 | -0.0036986
88 |  | 15.7922 | 64.3161 | 4187 | 0.00097269 | 6.0848 | 6.0858 | -3.8023 | 1028.0769 | 5673.9984 | -0.0036984
89 |  | 15.7922 | 64.3124 | 4187 | 0.00097263 | 6.0858 | 6.0868 | -3.8023 | 1028.1361 | 5738.3108 | -0.0036982
90 |  | 15.7922 | 64.3087 | 4187 | 0.00097258 | 6.0868 | 6.0878 | -3.8023 | 1028.1952 | 5802.6195 | -0.003698
91 |  | 15.7922 | 64.305 | 4187 | 0.00097252 | 6.0878 | 6.0887 | -3.8023 | 1028.2543 | 5866.9245 | -0.0036978
92 |  | 15.7922 | 64.3013 | 4187 | 0.00097247 | 6.0887 | 6.0897 | -3.8023 | 1028.3134 | 5931.2258 | -0.0036976
93 |  | 15.7922 | 64.2976 | 4187 | 0.00097241 | 6.0897 | 6.0907 | -3.8023 | 1028.3726 | 5995.5234 | -0.0036974
94 |  | 15.7922 | 64.2939 | 4187 | 0.00097235 | 6.0907 | 6.0916 | -3.8023 | 1028.4317 | 6059.8174 | -0.0036972
95 |  | 15.7922 | 64.2902 | 4187 | 0.0009723 | 6.0916 | 6.0926 | -3.8023 | 1028.4909 | 6124.1076 | -0.0036969
96 |  | 15.7922 | 64.2865 | 4187 | 0.00097224 | 6.0926 | 6.0936 | -3.8023 | 1028.55 | 6188.3941 | -0.0036967
97 |  | 15.7922 | 64.2828 | 4187 | 0.00097219 | 6.0936 | 6.0946 | -3.8023 | 1028.6092 | 6252.6769 | -0.0036965
98 |  | 15.7922 | 64.2791 | 4187 | 0.00097213 | 6.0946 | 6.0955 | -3.8023 | 1028.6683 | 6316.956 | -0.0036963
99 |  | 15.7922 | 64.2754 | 4187 | 0.00097207 | 6.0955 | 6.0965 | -3.8023 | 1028.7275 | 6381.2315 | -0.0036961
100 |  | 15.7922 | 64.2717 | 4187 | 0.00097202 | 6.0965 | 6.0975 | -3.8023 | 1028.7866 | 6445.5032 | -0.0036959
101 |  | 15.7922 | 64.268 | 4187 | 0.00097196 | 6.0975 | 6.0985 | -3.8023 | 1028.8458 | 6509.7712 | -0.0036957
102 |  | 15.7922 | 64.2643 | 4187 | 0.00097191 | 6.0985 | 6.0994 | -3.8023 | 1028.905 | 6574.0356 | -0.0036955
103 |  | 15.7922 | 64.2606 | 4187 | 0.00097185 | 6.0994 | 6.1004 | -3.8023 | 1028.9641 | 6638.2962 | -0.0036952
104 |  | 15.7922 | 64.2569 | 4187 | 0.0009718 | 6.1004 | 6.1014 | -3.8023 | 1029.0233 | 6702.5531 | -0.003695
105 |  | 15.7922 | 64.2533 | 4187 | 0.00097174 | 6.1014 | 6.1023 | -3.8023 | 1029.0825 | 6766.8064 | -0.0036948
106 |  | 15.7922 | 64.2496 | 4187 | 0.00097168 | 6.1023 | 6.1033 | -3.8023 | 1029.1416 | 6831.056 | -0.0036946
107 |  | 15.7922 | 64.2459 | 4187 | 0.00097163 | 6.1033 | 6.1043 | -3.8023 | 1029.2008 | 6895.3018 | -0.0036944
108 |  | 15.7922 | 64.2422 | 4187 | 0.00097157 | 6.1043 | 6.1053 | -3.8023 | 1029.26 | 6959.544 | -0.0036942
109 |  | 15.7922 | 64.2385 | 4187 | 0.00097152 | 6.1053 | 6.1062 | -3.8023 | 1029.3192 | 7023.7825 | -0.003694
110 |  | 15.7922 | 64.2348 | 4187 | 0.00097146 | 6.1062 | 6.1072 | -3.8023 | 1029.3784 | 7088.0173 | -0.0036938
111 |  | 15.7922 | 64.2311 | 4187 | 0.0009714 | 6.1072 | 6.1082 | -3.8023 | 1029.4376 | 7152.2483 | -0.0036935
112 |  | 15.7922 | 64.2274 | 4187 | 0.00097135 | 6.1082 | 6.1091 | -3.8023 | 1029.4968 | 7216.4757 | -0.0036933
113 |  | 15.7922 | 64.2237 | 4187 | 0.00097129 | 6.1091 | 6.1101 | -3.8023 | 1029.556 | 7280.6994 | -0.0036931
114 |  | 15.7922 | 64.22 | 4187 | 0.00097124 | 6.1101 | 6.1111 | -3.8023 | 1029.6152 | 7344.9194 | -0.0036929
115 |  | 15.7922 | 64.2163 | 4187 | 0.00097118 | 6.1111 | 6.1121 | -3.8023 | 1029.6744 | 7409.1358 | -0.0036927
116 |  | 15.7922 | 64.2126 | 4187 | 0.00097112 | 6.1121 | 6.113 | -3.8023 | 1029.7336 | 7473.3484 | -0.0036925
117 |  | 15.7922 | 64.2089 | 4187 | 0.00097107 | 6.113 | 6.114 | -3.8023 | 1029.7929 | 7537.5573 | -0.0036923
118 |  | 15.7922 | 64.2052 | 4187 | 0.00097101 | 6.114 | 6.115 | -3.8023 | 1029.8521 | 7601.7625 | -0.0036921
119 |  | 15.7922 | 64.2015 | 4187 | 0.00097096 | 6.115 | 6.1159 | -3.8023 | 1029.9113 | 7665.9641 | -0.0036918
120 |  | 15.7922 | 64.1979 | 4187 | 0.0009709 | 6.1159 | 6.1169 | -3.8023 | 1029.9705 | 7730.1619 | -0.0036916
121 |  | 15.7922 | 64.1942 | 4187 | 0.00097085 | 6.1169 | 6.1179 | -3.8023 | 1030.0298 | 7794.3561 | -0.0036914
122 |  | 15.7922 | 64.1905 | 4187 | 0.00097079 | 6.1179 | 6.1188 | -3.8023 | 1030.089 | 7858.5466 | -0.0036912
123 |  | 15.7922 | 64.1868 | 4187 | 0.00097073 | 6.1188 | 6.1198 | -3.8023 | 1030.1482 | 7922.7334 | -0.003691
124 |  | 15.7922 | 64.1831 | 4187 | 0.00097068 | 6.1198 | 6.1208 | -3.8023 | 1030.2075 | 7986.9164 | -0.0036908
125 |  | 15.7922 | 64.1794 | 4187 | 0.00097062 | 6.1208 | 6.1218 | -3.8023 | 1030.2667 | 8051.0958 | -0.0036906
126 |  | 15.7922 | 64.1757 | 4187 | 0.00097057 | 6.1218 | 6.1227 | -3.8023 | 1030.326 | 8115.2716 | -0.0036904
127 |  | 15.7922 | 64.172 | 4187 | 0.00097051 | 6.1227 | 6.1237 | -3.8023 | 1030.3852 | 8179.4436 | -0.0036901
128 |  | 15.7922 | 64.1683 | 4187 | 0.00097046 | 6.1237 | 6.1247 | -3.8023 | 1030.4445 | 8243.6119 | -0.0036899
129 |  | 15.7922 | 64.1646 | 4187 | 0.0009704 | 6.1247 | 6.1256 | -3.8023 | 1030.5037 | 8307.7765 | -0.0036897
130 |  | 15.7922 | 64.1609 | 4187 | 0.00097034 | 6.1256 | 6.1266 | -3.8023 | 1030.563 | 8371.9375 | -0.0036895
131 |  | 15.7922 | 64.1573 | 4187 | 0.00097029 | 6.1266 | 6.1276 | -3.8023 | 1030.6223 | 8436.0947 | -0.0036893
132 |  | 15.7922 | 64.1536 | 4187 | 0.00097023 | 6.1276 | 6.1286 | -3.8023 | 1030.6815 | 8500.2483 | -0.0036891
133 |  | 15.7922 | 64.1499 | 4187 | 0.00097018 | 6.1286 | 6.1295 | -3.8023 | 1030.7408 | 8564.3982 | -0.0036889
134 |  | 15.7922 | 64.1462 | 4187 | 0.00097012 | 6.1295 | 6.1305 | -3.8023 | 1030.8001 | 8628.5444 | -0.0036887
135 |  | 15.7922 | 64.1425 | 4187 | 0.00097006 | 6.1305 | 6.1315 | -3.8023 | 1030.8593 | 8692.6869 | -0.0036885
136 |  | 15.7922 | 64.1388 | 4187 | 0.00097001 | 6.1315 | 6.1324 | -3.8023 | 1030.9186 | 8756.8257 | -0.0036882
137 |  | 15.7922 | 64.1351 | 4187 | 0.00096995 | 6.1324 | 6.1334 | -3.8023 | 1030.9779 | 8820.9608 | -0.003688
138 |  | 15.7922 | 64.1314 | 4187 | 0.0009699 | 6.1334 | 6.1344 | -3.8023 | 1031.0372 | 8885.0922 | -0.0036878
139 |  | 15.7922 | 64.1277 | 4187 | 0.00096984 | 6.1344 | 6.1353 | -3.8023 | 1031.0965 | 8949.22 | -0.0036876
140 |  | 15.7922 | 64.1241 | 4187 | 0.00096979 | 6.1353 | 6.1363 | -3.8023 | 1031.1558 | 9013.3441 | -0.0036874
141 |  | 15.7922 | 64.1204 | 4187 | 0.00096973 | 6.1363 | 6.1373 | -3.8023 | 1031.2151 | 9077.4644 | -0.0036872
142 |  | 15.7922 | 64.1167 | 4187 | 0.00096967 | 6.1373 | 6.1383 | -3.8023 | 1031.2744 | 9141.5811 | -0.003687
143 |  | 15.7922 | 64.113 | 4187 | 0.00096962 | 6.1383 | 6.1392 | -3.8023 | 1031.3337 | 9205.6941 | -0.0036868
144 |  | 15.7922 | 64.1093 | 4187 | 0.00096956 | 6.1392 | 6.1402 | -3.8023 | 1031.393 | 9269.8034 | -0.0036865
145 |  | 15.7922 | 64.1056 | 4187 | 0.00096951 | 6.1402 | 6.1412 | -3.8023 | 1031.4523 | 9333.9091 | -0.0036863
146 |  | 15.7922 | 64.1019 | 4187 | 0.00096945 | 6.1412 | 6.1421 | -3.8023 | 1031.5116 | 9398.011 | -0.0036861
147 |  | 15.7922 | 64.0983 | 4187 | 0.0009694 | 6.1421 | 6.1431 | -3.8023 | 1031.571 | 9462.1093 | -0.0036859
148 |  | 15.7922 | 64.0946 | 4187 | 0.00096934 | 6.1431 | 6.1441 | -3.8023 | 1031.6303 | 9526.2038 | -0.0036857
149 |  | 15.7922 | 64.0909 | 4187 | 0.00096928 | 6.1441 | 6.145 | -3.8023 | 1031.6896 | 9590.2947 | -0.0036855
150 |  | 15.7922 | 64.0872 | 4187 | 0.00096923 | 6.145 | 6.146 | -3.8023 | 1031.7489 | 9654.3819 | -0.0036853
151 |  | 15.7922 | 64.0835 | 4187 | 0.00096917 | 6.146 | 6.147 | -3.8023 | 1031.8083 | 9718.4654 | -0.0036851
152 |  | 15.7922 | 64.0798 | 4187 | 0.00096912 | 6.147 | 6.1479 | -3.8023 | 1031.8676 | 9782.5452 | -0.0036848
153 |  | 15.7922 | 64.0761 | 4187 | 0.00096906 | 6.1479 | 6.1489 | -3.8023 | 1031.9269 | 9846.6214 | -0.0036846
154 |  | 15.7922 | 64.0725 | 4187 | 0.00096901 | 6.1489 | 6.1499 | -3.8023 | 1031.9863 | 9910.6938 | -0.0036844
155 |  | 15.7922 | 64.0688 | 4187 | 0.00096895 | 6.1499 | 6.1509 | -3.8023 | 1032.0456 | 9974.7626 | -0.0036842
156 |  | 15.7922 | 64.0651 | 4187 | 0.00096889 | 6.1509 | 6.1518 | -3.8023 | 1032.105 | 10038.8277 | -0.003684
157 |  | 15.7922 | 64.0614 | 4187 | 0.00096884 | 6.1518 | 6.1528 | -3.8023 | 1032.1643 | 10102.8891 | -0.0036838
158 |  | 15.7922 | 64.0577 | 4187 | 0.00096878 | 6.1528 | 6.1538 | -3.8023 | 1032.2237 | 10166.9468 | -0.0036836
159 |  | 15.7922 | 64.054 | 4187 | 0.00096873 | 6.1538 | 6.1547 | -3.8023 | 1032.2831 | 10231.0009 | -0.0036834
160 |  | 15.7922 | 64.0504 | 4187 | 0.00096867 | 6.1547 | 6.1557 | -3.8023 | 1032.3424 | 10295.0512 | -0.0036832
161 |  | 15.7922 | 64.0467 | 4187 | 0.00096862 | 6.1557 | 6.1567 | -3.8023 | 1032.4018 | 10359.0979 | -0.0036829
162 |  | 15.7922 | 64.043 | 4187 | 0.00096856 | 6.1567 | 6.1576 | -3.8023 | 1032.4612 | 10423.1409 | -0.0036827
163 |  | 15.7922 | 64.0393 | 4187 | 0.0009685 | 6.1576 | 6.1586 | -3.8023 | 1032.5205 | 10487.1802 | -0.0036825
164 |  | 15.7922 | 64.0356 | 4187 | 0.00096845 | 6.1586 | 6.1596 | -3.8023 | 1032.5799 | 10551.2158 | -0.0036823
165 |  | 15.7922 | 64.0319 | 4187 | 0.00096839 | 6.1596 | 6.1605 | -3.8023 | 1032.6393 | 10615.2477 | -0.0036821
166 |  | 15.7922 | 64.0283 | 4187 | 0.00096834 | 6.1605 | 6.1615 | -3.8023 | 1032.6987 | 10679.276 | -0.0036819
167 |  | 15.7922 | 64.0246 | 4187 | 0.00096828 | 6.1615 | 6.1625 | -3.8023 | 1032.7581 | 10743.3006 | -0.0036817
168 |  | 15.7922 | 64.0209 | 4187 | 0.00096823 | 6.1625 | 6.1634 | -3.8023 | 1032.8174 | 10807.3215 | -0.0036815
169 |  | 15.7922 | 64.0172 | 4187 | 0.00096817 | 6.1634 | 6.1644 | -3.8023 | 1032.8768 | 10871.3387 | -0.0036812
170 |  | 15.7922 | 64.0135 | 4187 | 0.00096811 | 6.1644 | 6.1654 | -3.8023 | 1032.9362 | 10935.3522 | -0.003681
171 |  | 15.7922 | 64.0099 | 4187 | 0.00096806 | 6.1654 | 6.1663 | -3.8023 | 1032.9956 | 10999.3621 | -0.0036808
172 |  | 15.7922 | 64.0062 | 4187 | 0.000968 | 6.1663 | 6.1673 | -3.8023 | 1033.055 | 11063.3682 | -0.0036806
173 |  | 15.7922 | 64.0025 | 4187 | 0.00096795 | 6.1673 | 6.1683 | -3.8023 | 1033.1145 | 11127.3707 | -0.0036804
174 |  | 15.7922 | 63.9988 | 4187 | 0.00096789 | 6.1683 | 6.1693 | -3.8023 | 1033.1739 | 11191.3695 | -0.0036802
175 |  | 15.7922 | 63.9951 | 4187 | 0.00096784 | 6.1693 | 6.1702 | -3.8023 | 1033.2333 | 11255.3647 | -0.00368
176 |  | 15.7922 | 63.9914 | 4187 | 0.00096778 | 6.1702 | 6.1712 | -3.8023 | 1033.2927 | 11319.3561 | -0.0036798
177 |  | 15.7922 | 63.9878 | 4187 | 0.00096772 | 6.1712 | 6.1722 | -3.8023 | 1033.3521 | 11383.3439 | -0.0036796
178 |  | 15.7922 | 63.9841 | 4187 | 0.00096767 | 6.1722 | 6.1731 | -3.8023 | 1033.4115 | 11447.328 | -0.0036793
179 |  | 15.7922 | 63.9804 | 4187 | 0.00096761 | 6.1731 | 6.1741 | -3.8023 | 1033.471 | 11511.3084 | -0.0036791
180 |  | 15.7922 | 63.9767 | 4187 | 0.00096756 | 6.1741 | 6.1751 | -3.8023 | 1033.5304 | 11575.2851 | -0.0036789
181 |  | 15.7922 | 63.9731 | 4187 | 0.0009675 | 6.1751 | 6.176 | -3.8023 | 1033.5898 | 11639.2582 | -0.0036787
182 |  | 15.7922 | 63.9694 | 4187 | 0.00096745 | 6.176 | 6.177 | -3.8023 | 1033.6493 | 11703.2275 | -0.0036785
183 |  | 15.7922 | 63.9657 | 4187 | 0.00096739 | 6.177 | 6.178 | -3.8023 | 1033.7087 | 11767.1932 | -0.0036783
184 |  | 15.7922 | 63.962 | 4187 | 0.00096733 | 6.178 | 6.1789 | -3.8023 | 1033.7682 | 11831.1552 | -0.0036781
185 |  | 15.7922 | 63.9583 | 4187 | 0.00096728 | 6.1789 | 6.1799 | -3.8023 | 1033.8276 | 11895.1136 | -0.0036779
186 |  | 15.7922 | 63.9547 | 4187 | 0.00096722 | 6.1799 | 6.1809 | -3.8023 | 1033.8871 | 11959.0682 | -0.0036777
187 |  | 15.7922 | 63.951 | 4187 | 0.00096717 | 6.1809 | 6.1818 | -3.8023 | 1033.9465 | 12023.0192 | -0.0036774
188 |  | 15.7922 | 63.9473 | 4187 | 0.00096711 | 6.1818 | 6.1828 | -3.8023 | 1034.006 | 12086.9665 | -0.0036772
189 |  | 15.7922 | 63.9436 | 4187 | 0.00096706 | 6.1828 | 6.1838 | -3.8023 | 1034.0655 | 12150.9102 | -0.003677
190 |  | 15.7922 | 63.94 | 4187 | 0.000967 | 6.1838 | 6.1847 | -3.8023 | 1034.1249 | 12214.8501 | -0.0036768
191 |  | 15.7922 | 63.9363 | 4187 | 0.00096695 | 6.1847 | 6.1857 | -3.8023 | 1034.1844 | 12278.7864 | -0.0036766
192 |  | 15.7922 | 63.9326 | 4187 | 0.00096689 | 6.1857 | 6.1867 | -3.8023 | 1034.2439 | 12342.719 | -0.0036764
193 |  | 15.7922 | 63.9289 | 4187 | 0.00096683 | 6.1867 | 6.1876 | -3.8023 | 1034.3033 | 12406.6479 | -0.0036762
194 |  | 15.7922 | 63.9252 | 4187 | 0.00096678 | 6.1876 | 6.1886 | -3.8023 | 1034.3628 | 12470.5731 | -0.003676
195 |  | 15.7922 | 63.9216 | 4187 | 0.00096672 | 6.1886 | 6.1896 | -3.8023 | 1034.4223 | 12534.4947 | -0.0036757
196 |  | 15.7922 | 63.9179 | 4187 | 0.00096667 | 6.1896 | 6.1905 | -3.8023 | 1034.4818 | 12598.4126 | -0.0036755
197 |  | 15.7922 | 63.9142 | 4187 | 0.00096661 | 6.1905 | 6.1915 | -3.8023 | 1034.5413 | 12662.3268 | -0.0036753
198 |  | 15.7922 | 63.9105 | 4187 | 0.00096656 | 6.1915 | 6.1925 | -3.8023 | 1034.6008 | 12726.2374 | -0.0036751
199 |  | 15.7922 | 63.9069 | 4187 | 0.0009665 | 6.1925 | 6.1934 | -3.8023 | 1034.6603 | 12790.1442 | -0.0036749
200 |  | 15.7922 | 63.9032 | 4187 | 0.00096645 | 6.1934 | 6.1944 | -3.8023 | 1034.7198 | 12854.0474 | -0.0036747
201 |  | 15.7922 | 63.8995 | 4187 | 0.00096639 | 6.1944 | 6.1954 | -3.8023 | 1034.7793 | 12917.9469 | -0.0036745
202 |  | 15.7922 | 63.8958 | 4187 | 0.00096633 | 6.1954 | 6.1963 | -3.8023 | 1034.8388 | 12981.8428 | -0.0036743
203 |  | 15.7922 | 63.8922 | 4187 | 0.00096628 | 6.1963 | 6.1973 | -3.8023 | 1034.8983 | 13045.735 | -0.0036741
204 |  | 15.7922 | 63.8885 | 4187 | 0.00096622 | 6.1973 | 6.1983 | -3.8023 | 1034.9578 | 13109.6235 | -0.0036738
205 |  | 15.7922 | 63.8848 | 4187 | 0.00096617 | 6.1983 | 6.1992 | -3.8023 | 1035.0173 | 13173.5083 | -0.0036736
206 |  | 15.7922 | 63.8811 | 4187 | 0.00096611 | 6.1992 | 6.2002 | -3.8023 | 1035.0768 | 13237.3894 | -0.0036734
207 |  | 15.7922 | 63.8775 | 4187 | 0.00096606 | 6.2002 | 6.2012 | -3.8023 | 1035.1364 | 13301.2669 | -0.0036732
208 |  | 15.7922 | 63.8738 | 4187 | 0.000966 | 6.2012 | 6.2021 | -3.8023 | 1035.1959 | 13365.1407 | -0.003673
209 |  | 15.7922 | 63.8701 | 4187 | 0.00096595 | 6.2021 | 6.2031 | -3.8023 | 1035.2554 | 13429.0108 | -0.0036728
210 |  | 15.7922 | 63.8665 | 4187 | 0.00096589 | 6.2031 | 6.2041 | -3.8023 | 1035.315 | 13492.8773 | -0.0036726
211 |  | 15.7922 | 63.8628 | 4187 | 0.00096583 | 6.2041 | 6.205 | -3.8023 | 1035.3745 | 13556.7401 | -0.0036724
212 |  | 15.7922 | 63.8591 | 4187 | 0.00096578 | 6.205 | 6.206 | -3.8023 | 1035.434 | 13620.5992 | -0.0036722
213 |  | 15.7922 | 63.8554 | 4187 | 0.00096572 | 6.206 | 6.207 | -3.8023 | 1035.4936 | 13684.4546 | -0.0036719
214 |  | 15.7922 | 63.8518 | 4187 | 0.00096567 | 6.207 | 6.2079 | -3.8023 | 1035.5531 | 13748.3064 | -0.0036717
215 |  | 15.7922 | 63.8481 | 4187 | 0.00096561 | 6.2079 | 6.2089 | -3.8023 | 1035.6127 | 13812.1545 | -0.0036715
216 |  | 15.7922 | 63.8444 | 4187 | 0.00096556 | 6.2089 | 6.2099 | -3.8023 | 1035.6722 | 13875.9989 | -0.0036713
217 |  | 15.7922 | 63.8408 | 4187 | 0.0009655 | 6.2099 | 6.2108 | -3.8023 | 1035.7318 | 13939.8397 | -0.0036711
218 |  | 15.7922 | 63.8371 | 4187 | 0.00096545 | 6.2108 | 6.2118 | -3.8023 | 1035.7914 | 14003.6767 | -0.0036709
219 |  | 15.7922 | 63.8334 | 4187 | 0.00096539 | 6.2118 | 6.2128 | -3.8023 | 1035.8509 | 14067.5101 | -0.0036707
220 |  | 15.7922 | 63.8297 | 4187 | 0.00096533 | 6.2128 | 6.2137 | -3.8023 | 1035.9105 | 14131.3399 | -0.0036705
221 |  | 15.7922 | 63.8261 | 4187 | 0.00096528 | 6.2137 | 6.2147 | -3.8023 | 1035.9701 | 14195.1659 | -0.0036703
222 |  | 15.7922 | 63.8224 | 4187 | 0.00096522 | 6.2147 | 6.2156 | -3.8023 | 1036.0296 | 14258.9883 | -0.00367
223 |  | 15.7922 | 63.8187 | 4187 | 0.00096517 | 6.2156 | 6.2166 | -3.8023 | 1036.0892 | 14322.8071 | -0.0036698
224 |  | 15.7922 | 63.8151 | 4187 | 0.00096511 | 6.2166 | 6.2176 | -3.8023 | 1036.1488 | 14386.6221 | -0.0036696
225 |  | 15.7922 | 63.8114 | 4187 | 0.00096506 | 6.2176 | 6.2185 | -3.8023 | 1036.2084 | 14450.4335 | -0.0036694
226 |  | 15.7922 | 63.8077 | 4187 | 0.000965 | 6.2185 | 6.2195 | -3.8023 | 1036.268 | 14514.2412 | -0.0036692
227 |  | 15.7922 | 63.8041 | 4187 | 0.00096495 | 6.2195 | 6.2205 | -3.8023 | 1036.3276 | 14578.0453 | -0.003669
228 |  | 15.7922 | 63.8004 | 4187 | 0.00096489 | 6.2205 | 6.2214 | -3.8023 | 1036.3872 | 14641.8457 | -0.0036688
229 |  | 15.7922 | 63.7967 | 4187 | 0.00096483 | 6.2214 | 6.2224 | -3.8023 | 1036.4468 | 14705.6424 | -0.0036686
230 |  | 15.7922 | 63.793 | 4187 | 0.00096478 | 6.2224 | 6.2234 | -3.8023 | 1036.5064 | 14769.4354 | -0.0036684
231 |  | 15.7922 | 63.7894 | 4187 | 0.00096472 | 6.2234 | 6.2243 | -3.8023 | 1036.566 | 14833.2248 | -0.0036681
232 |  | 15.7922 | 63.7857 | 4187 | 0.00096467 | 6.2243 | 6.2253 | -3.8023 | 1036.6256 | 14897.0105 | -0.0036679
233 |  | 15.7922 | 63.782 | 4187 | 0.00096461 | 6.2253 | 6.2263 | -3.8023 | 1036.6852 | 14960.7926 | -0.0036677
234 |  | 15.7922 | 63.7784 | 4187 | 0.00096456 | 6.2263 | 6.2272 | -3.8023 | 1036.7448 | 15024.5709 | -0.0036675
235 |  | 15.7922 | 63.7747 | 4187 | 0.0009645 | 6.2272 | 6.2282 | -3.8023 | 1036.8044 | 15088.3456 | -0.0036673
236 |  | 15.7922 | 63.771 | 4187 | 0.00096445 | 6.2282 | 6.2292 | -3.8023 | 1036.8641 | 15152.1167 | -0.0036671

## CLX200
|  |  | buis | verlies W/M | L /°C/sec
diam | wandikte |  | inhoud l/m |  | W/M
200 | 11.4 | 3.1416 | 24.6614 | 71.9347 | 4187
[8 empty] | J/sec/mtr | aantal mtr. | verlies
|  | buis | verlies W/M | L /°C/sec | verlies temp | begintemp | eindtemp | verlies | bij 1°C | totaal J/sec
|  | inhoud L |  | W/M | °C per M | °C | °C | per m°C | daling | aantal mtr
1 | 200 | 24.6614 | 71.9347 | 4187 | 0.00069666 | 6 | 6.0007 | -4.2315 | 1435.4296 | 71.9347 | -0.0029479
2 |  | 24.6614 | 71.9317 | 4187 | 0.00069663 | 6.0007 | 6.0014 | -4.2315 | 1435.4885 | 143.8664 | -0.0029477
3 |  | 24.6614 | 71.9288 | 4187 | 0.0006966 | 6.0014 | 6.0021 | -4.2315 | 1435.5473 | 215.7952 | -0.0029476
4 |  | 24.6614 | 71.9258 | 4187 | 0.00069657 | 6.0021 | 6.0028 | -4.2315 | 1435.6061 | 287.7211 | -0.0029475
5 |  | 24.6614 | 71.9229 | 4187 | 0.00069654 | 6.0028 | 6.0035 | -4.2315 | 1435.6649 | 359.644 | -0.0029474
6 |  | 24.6614 | 71.92 | 4187 | 0.00069651 | 6.0035 | 6.0042 | -4.2315 | 1435.7238 | 431.5639 | -0.0029473
7 |  | 24.6614 | 71.917 | 4187 | 0.00069648 | 6.0042 | 6.0049 | -4.2315 | 1435.7826 | 503.4809 | -0.0029471
8 |  | 24.6614 | 71.9141 | 4187 | 0.00069646 | 6.0049 | 6.0056 | -4.2315 | 1435.8415 | 575.395 | -0.002947
9 |  | 24.6614 | 71.9111 | 4187 | 0.00069643 | 6.0056 | 6.0063 | -4.2315 | 1435.9003 | 647.3061 | -0.0029469
10 |  | 24.6614 | 71.9082 | 4187 | 0.0006964 | 6.0063 | 6.007 | -4.2315 | 1435.9592 | 719.2143 | -0.0029468
11 |  | 24.6614 | 71.9052 | 4187 | 0.00069637 | 6.007 | 6.0077 | -4.2315 | 1436.018 | 791.1195 | -0.0029467
12 |  | 24.6614 | 71.9023 | 4187 | 0.00069634 | 6.0077 | 6.0084 | -4.2315 | 1436.0768 | 863.0217 | -0.0029465
13 |  | 24.6614 | 71.8993 | 4187 | 0.00069631 | 6.0084 | 6.0091 | -4.2315 | 1436.1357 | 934.9211 | -0.0029464
14 |  | 24.6614 | 71.8964 | 4187 | 0.00069628 | 6.0091 | 6.0098 | -4.2315 | 1436.1946 | 1006.8174 | -0.0029463
15 |  | 24.6614 | 71.8934 | 4187 | 0.00069626 | 6.0098 | 6.0104 | -4.2315 | 1436.2534 | 1078.7109 | -0.0029462
16 |  | 24.6614 | 71.8905 | 4187 | 0.00069623 | 6.0104 | 6.0111 | -4.2315 | 1436.3123 | 1150.6013 | -0.0029461
17 |  | 24.6614 | 71.8875 | 4187 | 0.0006962 | 6.0111 | 6.0118 | -4.2315 | 1436.3711 | 1222.4889 | -0.0029459
18 |  | 24.6614 | 71.8846 | 4187 | 0.00069617 | 6.0118 | 6.0125 | -4.2315 | 1436.43 | 1294.3735 | -0.0029458
19 |  | 24.6614 | 71.8816 | 4187 | 0.00069614 | 6.0125 | 6.0132 | -4.2315 | 1436.4889 | 1366.2551 | -0.0029457
20 |  | 24.6614 | 71.8787 | 4187 | 0.00069611 | 6.0132 | 6.0139 | -4.2315 | 1436.5477 | 1438.1338 | -0.0029456
21 |  | 24.6614 | 71.8758 | 4187 | 0.00069608 | 6.0139 | 6.0146 | -4.2315 | 1436.6066 | 1510.0096 | -0.0029454
22 |  | 24.6614 | 71.8728 | 4187 | 0.00069606 | 6.0146 | 6.0153 | -4.2315 | 1436.6655 | 1581.8824 | -0.0029453
23 |  | 24.6614 | 71.8699 | 4187 | 0.00069603 | 6.0153 | 6.016 | -4.2315 | 1436.7244 | 1653.7523 | -0.0029452
24 |  | 24.6614 | 71.8669 | 4187 | 0.000696 | 6.016 | 6.0167 | -4.2315 | 1436.7832 | 1725.6192 | -0.0029451
25 |  | 24.6614 | 71.864 | 4187 | 0.00069597 | 6.0167 | 6.0174 | -4.2315 | 1436.8421 | 1797.4831 | -0.002945
26 |  | 24.6614 | 71.861 | 4187 | 0.00069594 | 6.0174 | 6.0181 | -4.2315 | 1436.901 | 1869.3442 | -0.0029448
27 |  | 24.6614 | 71.8581 | 4187 | 0.00069591 | 6.0181 | 6.0188 | -4.2315 | 1436.9599 | 1941.2023 | -0.0029447
28 |  | 24.6614 | 71.8551 | 4187 | 0.00069589 | 6.0188 | 6.0195 | -4.2315 | 1437.0188 | 2013.0574 | -0.0029446
29 |  | 24.6614 | 71.8522 | 4187 | 0.00069586 | 6.0195 | 6.0202 | -4.2315 | 1437.0777 | 2084.9096 | -0.0029445
30 |  | 24.6614 | 71.8492 | 4187 | 0.00069583 | 6.0202 | 6.0209 | -4.2315 | 1437.1366 | 2156.7588 | -0.0029444
31 |  | 24.6614 | 71.8463 | 4187 | 0.0006958 | 6.0209 | 6.0216 | -4.2315 | 1437.1955 | 2228.6051 | -0.0029442
32 |  | 24.6614 | 71.8434 | 4187 | 0.00069577 | 6.0216 | 6.0223 | -4.2315 | 1437.2544 | 2300.4485 | -0.0029441
33 |  | 24.6614 | 71.8404 | 4187 | 0.00069574 | 6.0223 | 6.023 | -4.2315 | 1437.3133 | 2372.2889 | -0.002944
34 |  | 24.6614 | 71.8375 | 4187 | 0.00069571 | 6.023 | 6.0237 | -4.2315 | 1437.3722 | 2444.1264 | -0.0029439
35 |  | 24.6614 | 71.8345 | 4187 | 0.00069569 | 6.0237 | 6.0244 | -4.2315 | 1437.4311 | 2515.9609 | -0.0029438
36 |  | 24.6614 | 71.8316 | 4187 | 0.00069566 | 6.0244 | 6.0251 | -4.2315 | 1437.49 | 2587.7925 | -0.0029436
37 |  | 24.6614 | 71.8286 | 4187 | 0.00069563 | 6.0251 | 6.0258 | -4.2315 | 1437.5489 | 2659.6212 | -0.0029435
38 |  | 24.6614 | 71.8257 | 4187 | 0.0006956 | 6.0258 | 6.0265 | -4.2315 | 1437.6078 | 2731.4469 | -0.0029434
39 |  | 24.6614 | 71.8228 | 4187 | 0.00069557 | 6.0265 | 6.0271 | -4.2315 | 1437.6667 | 2803.2696 | -0.0029433
40 |  | 24.6614 | 71.8198 | 4187 | 0.00069554 | 6.0271 | 6.0278 | -4.2315 | 1437.7256 | 2875.0894 | -0.0029432
41 |  | 24.6614 | 71.8169 | 4187 | 0.00069551 | 6.0278 | 6.0285 | -4.2315 | 1437.7846 | 2946.9063 | -0.002943
42 |  | 24.6614 | 71.8139 | 4187 | 0.00069549 | 6.0285 | 6.0292 | -4.2315 | 1437.8435 | 3018.7202 | -0.0029429
43 |  | 24.6614 | 71.811 | 4187 | 0.00069546 | 6.0292 | 6.0299 | -4.2315 | 1437.9024 | 3090.5312 | -0.0029428
44 |  | 24.6614 | 71.808 | 4187 | 0.00069543 | 6.0299 | 6.0306 | -4.2315 | 1437.9613 | 3162.3392 | -0.0029427
45 |  | 24.6614 | 71.8051 | 4187 | 0.0006954 | 6.0306 | 6.0313 | -4.2315 | 1438.0203 | 3234.1443 | -0.0029426
46 |  | 24.6614 | 71.8022 | 4187 | 0.00069537 | 6.0313 | 6.032 | -4.2315 | 1438.0792 | 3305.9465 | -0.0029424
47 |  | 24.6614 | 71.7992 | 4187 | 0.00069534 | 6.032 | 6.0327 | -4.2315 | 1438.1381 | 3377.7457 | -0.0029423
48 |  | 24.6614 | 71.7963 | 4187 | 0.00069532 | 6.0327 | 6.0334 | -4.2315 | 1438.1971 | 3449.542 | -0.0029422
49 |  | 24.6614 | 71.7933 | 4187 | 0.00069529 | 6.0334 | 6.0341 | -4.2315 | 1438.256 | 3521.3353 | -0.0029421
50 |  | 24.6614 | 71.7904 | 4187 | 0.00069526 | 6.0341 | 6.0348 | -4.2315 | 1438.3149 | 3593.1257 | -0.002942
51 |  | 24.6614 | 71.7874 | 4187 | 0.00069523 | 6.0348 | 6.0355 | -4.2315 | 1438.3739 | 3664.9131 | -0.0029418
52 |  | 24.6614 | 71.7845 | 4187 | 0.0006952 | 6.0355 | 6.0362 | -4.2315 | 1438.4328 | 3736.6976 | -0.0029417
53 |  | 24.6614 | 71.7816 | 4187 | 0.00069517 | 6.0362 | 6.0369 | -4.2315 | 1438.4918 | 3808.4792 | -0.0029416
54 |  | 24.6614 | 71.7786 | 4187 | 0.00069514 | 6.0369 | 6.0376 | -4.2315 | 1438.5507 | 3880.2578 | -0.0029415
55 |  | 24.6614 | 71.7757 | 4187 | 0.00069512 | 6.0376 | 6.0383 | -4.2315 | 1438.6097 | 3952.0335 | -0.0029413
56 |  | 24.6614 | 71.7727 | 4187 | 0.00069509 | 6.0383 | 6.039 | -4.2315 | 1438.6686 | 4023.8062 | -0.0029412
57 |  | 24.6614 | 71.7698 | 4187 | 0.00069506 | 6.039 | 6.0397 | -4.2315 | 1438.7276 | 4095.576 | -0.0029411
58 |  | 24.6614 | 71.7669 | 4187 | 0.00069503 | 6.0397 | 6.0404 | -4.2315 | 1438.7866 | 4167.3429 | -0.002941
59 |  | 24.6614 | 71.7639 | 4187 | 0.000695 | 6.0404 | 6.0411 | -4.2315 | 1438.8455 | 4239.1068 | -0.0029409
60 |  | 24.6614 | 71.761 | 4187 | 0.00069497 | 6.0411 | 6.0417 | -4.2315 | 1438.9045 | 4310.8678 | -0.0029407
61 |  | 24.6614 | 71.758 | 4187 | 0.00069494 | 6.0417 | 6.0424 | -4.2315 | 1438.9635 | 4382.6258 | -0.0029406
62 |  | 24.6614 | 71.7551 | 4187 | 0.00069492 | 6.0424 | 6.0431 | -4.2315 | 1439.0224 | 4454.3809 | -0.0029405
63 |  | 24.6614 | 71.7521 | 4187 | 0.00069489 | 6.0431 | 6.0438 | -4.2315 | 1439.0814 | 4526.133 | -0.0029404
64 |  | 24.6614 | 71.7492 | 4187 | 0.00069486 | 6.0438 | 6.0445 | -4.2315 | 1439.1404 | 4597.8822 | -0.0029403
65 |  | 24.6614 | 71.7463 | 4187 | 0.00069483 | 6.0445 | 6.0452 | -4.2315 | 1439.1994 | 4669.6285 | -0.0029401
66 |  | 24.6614 | 71.7433 | 4187 | 0.0006948 | 6.0452 | 6.0459 | -4.2315 | 1439.2583 | 4741.3718 | -0.00294
67 |  | 24.6614 | 71.7404 | 4187 | 0.00069477 | 6.0459 | 6.0466 | -4.2315 | 1439.3173 | 4813.1122 | -0.0029399
68 |  | 24.6614 | 71.7374 | 4187 | 0.00069475 | 6.0466 | 6.0473 | -4.2315 | 1439.3763 | 4884.8497 | -0.0029398
69 |  | 24.6614 | 71.7345 | 4187 | 0.00069472 | 6.0473 | 6.048 | -4.2315 | 1439.4353 | 4956.5842 | -0.0029397
70 |  | 24.6614 | 71.7316 | 4187 | 0.00069469 | 6.048 | 6.0487 | -4.2315 | 1439.4943 | 5028.3157 | -0.0029395
71 |  | 24.6614 | 71.7286 | 4187 | 0.00069466 | 6.0487 | 6.0494 | -4.2315 | 1439.5533 | 5100.0444 | -0.0029394
72 |  | 24.6614 | 71.7257 | 4187 | 0.00069463 | 6.0494 | 6.0501 | -4.2315 | 1439.6123 | 5171.7701 | -0.0029393
73 |  | 24.6614 | 71.7228 | 4187 | 0.0006946 | 6.0501 | 6.0508 | -4.2315 | 1439.6713 | 5243.4928 | -0.0029392
74 |  | 24.6614 | 71.7198 | 4187 | 0.00069457 | 6.0508 | 6.0515 | -4.2315 | 1439.7303 | 5315.2126 | -0.0029391
75 |  | 24.6614 | 71.7169 | 4187 | 0.00069455 | 6.0515 | 6.0522 | -4.2315 | 1439.7893 | 5386.9295 | -0.0029389
76 |  | 24.6614 | 71.7139 | 4187 | 0.00069452 | 6.0522 | 6.0529 | -4.2315 | 1439.8483 | 5458.6434 | -0.0029388
77 |  | 24.6614 | 71.711 | 4187 | 0.00069449 | 6.0529 | 6.0536 | -4.2315 | 1439.9073 | 5530.3544 | -0.0029387
78 |  | 24.6614 | 71.7081 | 4187 | 0.00069446 | 6.0536 | 6.0543 | -4.2315 | 1439.9663 | 5602.0625 | -0.0029386
79 |  | 24.6614 | 71.7051 | 4187 | 0.00069443 | 6.0543 | 6.0549 | -4.2315 | 1440.0253 | 5673.7676 | -0.0029385
80 |  | 24.6614 | 71.7022 | 4187 | 0.0006944 | 6.0549 | 6.0556 | -4.2315 | 1440.0843 | 5745.4698 | -0.0029383
81 |  | 24.6614 | 71.6992 | 4187 | 0.00069438 | 6.0556 | 6.0563 | -4.2315 | 1440.1433 | 5817.169 | -0.0029382
82 |  | 24.6614 | 71.6963 | 4187 | 0.00069435 | 6.0563 | 6.057 | -4.2315 | 1440.2024 | 5888.8653 | -0.0029381
83 |  | 24.6614 | 71.6934 | 4187 | 0.00069432 | 6.057 | 6.0577 | -4.2315 | 1440.2614 | 5960.5587 | -0.002938
84 |  | 24.6614 | 71.6904 | 4187 | 0.00069429 | 6.0577 | 6.0584 | -4.2315 | 1440.3204 | 6032.2491 | -0.0029379
85 |  | 24.6614 | 71.6875 | 4187 | 0.00069426 | 6.0584 | 6.0591 | -4.2315 | 1440.3794 | 6103.9366 | -0.0029377
86 |  | 24.6614 | 71.6846 | 4187 | 0.00069423 | 6.0591 | 6.0598 | -4.2315 | 1440.4385 | 6175.6212 | -0.0029376
87 |  | 24.6614 | 71.6816 | 4187 | 0.0006942 | 6.0598 | 6.0605 | -4.2315 | 1440.4975 | 6247.3028 | -0.0029375
88 |  | 24.6614 | 71.6787 | 4187 | 0.00069418 | 6.0605 | 6.0612 | -4.2315 | 1440.5565 | 6318.9815 | -0.0029374
89 |  | 24.6614 | 71.6757 | 4187 | 0.00069415 | 6.0612 | 6.0619 | -4.2315 | 1440.6156 | 6390.6572 | -0.0029373
90 |  | 24.6614 | 71.6728 | 4187 | 0.00069412 | 6.0619 | 6.0626 | -4.2315 | 1440.6746 | 6462.33 | -0.0029371
91 |  | 24.6614 | 71.6699 | 4187 | 0.00069409 | 6.0626 | 6.0633 | -4.2315 | 1440.7336 | 6533.9999 | -0.002937
92 |  | 24.6614 | 71.6669 | 4187 | 0.00069406 | 6.0633 | 6.064 | -4.2315 | 1440.7927 | 6605.6668 | -0.0029369
93 |  | 24.6614 | 71.664 | 4187 | 0.00069403 | 6.064 | 6.0647 | -4.2315 | 1440.8517 | 6677.3308 | -0.0029368
94 |  | 24.6614 | 71.6611 | 4187 | 0.00069401 | 6.0647 | 6.0654 | -4.2315 | 1440.9108 | 6748.9918 | -0.0029367
95 |  | 24.6614 | 71.6581 | 4187 | 0.00069398 | 6.0654 | 6.0661 | -4.2315 | 1440.9698 | 6820.6499 | -0.0029365
96 |  | 24.6614 | 71.6552 | 4187 | 0.00069395 | 6.0661 | 6.0667 | -4.2315 | 1441.0289 | 6892.3051 | -0.0029364
97 |  | 24.6614 | 71.6522 | 4187 | 0.00069392 | 6.0667 | 6.0674 | -4.2315 | 1441.0879 | 6963.9574 | -0.0029363
98 |  | 24.6614 | 71.6493 | 4187 | 0.00069389 | 6.0674 | 6.0681 | -4.2315 | 1441.147 | 7035.6067 | -0.0029362
99 |  | 24.6614 | 71.6464 | 4187 | 0.00069386 | 6.0681 | 6.0688 | -4.2315 | 1441.206 | 7107.253 | -0.002936
100 |  | 24.6614 | 71.6434 | 4187 | 0.00069383 | 6.0688 | 6.0695 | -4.2315 | 1441.2651 | 7178.8965 | -0.0029359
101 |  | 24.6614 | 71.6405 | 4187 | 0.00069381 | 6.0695 | 6.0702 | -4.2315 | 1441.3242 | 7250.537 | -0.0029358
102 |  | 24.6614 | 71.6376 | 4187 | 0.00069378 | 6.0702 | 6.0709 | -4.2315 | 1441.3832 | 7322.1745 | -0.0029357
103 |  | 24.6614 | 71.6346 | 4187 | 0.00069375 | 6.0709 | 6.0716 | -4.2315 | 1441.4423 | 7393.8092 | -0.0029356
104 |  | 24.6614 | 71.6317 | 4187 | 0.00069372 | 6.0716 | 6.0723 | -4.2315 | 1441.5014 | 7465.4409 | -0.0029354
105 |  | 24.6614 | 71.6288 | 4187 | 0.00069369 | 6.0723 | 6.073 | -4.2315 | 1441.5605 | 7537.0696 | -0.0029353
106 |  | 24.6614 | 71.6258 | 4187 | 0.00069366 | 6.073 | 6.0737 | -4.2315 | 1441.6195 | 7608.6954 | -0.0029352
107 |  | 24.6614 | 71.6229 | 4187 | 0.00069364 | 6.0737 | 6.0744 | -4.2315 | 1441.6786 | 7680.3183 | -0.0029351
108 |  | 24.6614 | 71.62 | 4187 | 0.00069361 | 6.0744 | 6.0751 | -4.2315 | 1441.7377 | 7751.9383 | -0.002935
109 |  | 24.6614 | 71.617 | 4187 | 0.00069358 | 6.0751 | 6.0758 | -4.2315 | 1441.7968 | 7823.5553 | -0.0029348
110 |  | 24.6614 | 71.6141 | 4187 | 0.00069355 | 6.0758 | 6.0765 | -4.2315 | 1441.8559 | 7895.1694 | -0.0029347
111 |  | 24.6614 | 71.6111 | 4187 | 0.00069352 | 6.0765 | 6.0772 | -4.2315 | 1441.915 | 7966.7805 | -0.0029346
112 |  | 24.6614 | 71.6082 | 4187 | 0.00069349 | 6.0772 | 6.0778 | -4.2315 | 1441.9741 | 8038.3887 | -0.0029345
113 |  | 24.6614 | 71.6053 | 4187 | 0.00069347 | 6.0778 | 6.0785 | -4.2315 | 1442.0331 | 8109.994 | -0.0029344
114 |  | 24.6614 | 71.6023 | 4187 | 0.00069344 | 6.0785 | 6.0792 | -4.2315 | 1442.0922 | 8181.5964 | -0.0029342
115 |  | 24.6614 | 71.5994 | 4187 | 0.00069341 | 6.0792 | 6.0799 | -4.2315 | 1442.1513 | 8253.1958 | -0.0029341
116 |  | 24.6614 | 71.5965 | 4187 | 0.00069338 | 6.0799 | 6.0806 | -4.2315 | 1442.2104 | 8324.7923 | -0.002934
117 |  | 24.6614 | 71.5935 | 4187 | 0.00069335 | 6.0806 | 6.0813 | -4.2315 | 1442.2695 | 8396.3858 | -0.0029339
118 |  | 24.6614 | 71.5906 | 4187 | 0.00069332 | 6.0813 | 6.082 | -4.2315 | 1442.3287 | 8467.9764 | -0.0029338
119 |  | 24.6614 | 71.5877 | 4187 | 0.00069329 | 6.082 | 6.0827 | -4.2315 | 1442.3878 | 8539.5641 | -0.0029336
120 |  | 24.6614 | 71.5847 | 4187 | 0.00069327 | 6.0827 | 6.0834 | -4.2315 | 1442.4469 | 8611.1488 | -0.0029335
121 |  | 24.6614 | 71.5818 | 4187 | 0.00069324 | 6.0834 | 6.0841 | -4.2315 | 1442.506 | 8682.7306 | -0.0029334
122 |  | 24.6614 | 71.5789 | 4187 | 0.00069321 | 6.0841 | 6.0848 | -4.2315 | 1442.5651 | 8754.3095 | -0.0029333
123 |  | 24.6614 | 71.5759 | 4187 | 0.00069318 | 6.0848 | 6.0855 | -4.2315 | 1442.6242 | 8825.8854 | -0.0029332
124 |  | 24.6614 | 71.573 | 4187 | 0.00069315 | 6.0855 | 6.0862 | -4.2315 | 1442.6833 | 8897.4584 | -0.002933
125 |  | 24.6614 | 71.5701 | 4187 | 0.00069312 | 6.0862 | 6.0869 | -4.2315 | 1442.7425 | 8969.0285 | -0.0029329
126 |  | 24.6614 | 71.5671 | 4187 | 0.0006931 | 6.0869 | 6.0876 | -4.2315 | 1442.8016 | 9040.5957 | -0.0029328
127 |  | 24.6614 | 71.5642 | 4187 | 0.00069307 | 6.0876 | 6.0882 | -4.2315 | 1442.8607 | 9112.1599 | -0.0029327
128 |  | 24.6614 | 71.5613 | 4187 | 0.00069304 | 6.0882 | 6.0889 | -4.2315 | 1442.9198 | 9183.7211 | -0.0029326
129 |  | 24.6614 | 71.5583 | 4187 | 0.00069301 | 6.0889 | 6.0896 | -4.2315 | 1442.979 | 9255.2795 | -0.0029324
130 |  | 24.6614 | 71.5554 | 4187 | 0.00069298 | 6.0896 | 6.0903 | -4.2315 | 1443.0381 | 9326.8349 | -0.0029323
131 |  | 24.6614 | 71.5525 | 4187 | 0.00069295 | 6.0903 | 6.091 | -4.2315 | 1443.0973 | 9398.3874 | -0.0029322
132 |  | 24.6614 | 71.5495 | 4187 | 0.00069293 | 6.091 | 6.0917 | -4.2315 | 1443.1564 | 9469.9369 | -0.0029321
133 |  | 24.6614 | 71.5466 | 4187 | 0.0006929 | 6.0917 | 6.0924 | -4.2315 | 1443.2155 | 9541.4835 | -0.002932
134 |  | 24.6614 | 71.5437 | 4187 | 0.00069287 | 6.0924 | 6.0931 | -4.2315 | 1443.2747 | 9613.0272 | -0.0029318
135 |  | 24.6614 | 71.5407 | 4187 | 0.00069284 | 6.0931 | 6.0938 | -4.2315 | 1443.3338 | 9684.568 | -0.0029317
136 |  | 24.6614 | 71.5378 | 4187 | 0.00069281 | 6.0938 | 6.0945 | -4.2315 | 1443.393 | 9756.1058 | -0.0029316
137 |  | 24.6614 | 71.5349 | 4187 | 0.00069278 | 6.0945 | 6.0952 | -4.2315 | 1443.4521 | 9827.6407 | -0.0029315
138 |  | 24.6614 | 71.532 | 4187 | 0.00069276 | 6.0952 | 6.0959 | -4.2315 | 1443.5113 | 9899.1726 | -0.0029314
139 |  | 24.6614 | 71.529 | 4187 | 0.00069273 | 6.0959 | 6.0966 | -4.2315 | 1443.5704 | 9970.7016 | -0.0029312
140 |  | 24.6614 | 71.5261 | 4187 | 0.0006927 | 6.0966 | 6.0973 | -4.2315 | 1443.6296 | 10042.2277 | -0.0029311
141 |  | 24.6614 | 71.5232 | 4187 | 0.00069267 | 6.0973 | 6.0979 | -4.2315 | 1443.6888 | 10113.7509 | -0.002931
142 |  | 24.6614 | 71.5202 | 4187 | 0.00069264 | 6.0979 | 6.0986 | -4.2315 | 1443.7479 | 10185.2711 | -0.0029309
143 |  | 24.6614 | 71.5173 | 4187 | 0.00069261 | 6.0986 | 6.0993 | -4.2315 | 1443.8071 | 10256.7884 | -0.0029308
144 |  | 24.6614 | 71.5144 | 4187 | 0.00069258 | 6.0993 | 6.1 | -4.2315 | 1443.8663 | 10328.3028 | -0.0029306
145 |  | 24.6614 | 71.5114 | 4187 | 0.00069256 | 6.1 | 6.1007 | -4.2315 | 1443.9254 | 10399.8142 | -0.0029305
146 |  | 24.6614 | 71.5085 | 4187 | 0.00069253 | 6.1007 | 6.1014 | -4.2315 | 1443.9846 | 10471.3227 | -0.0029304
147 |  | 24.6614 | 71.5056 | 4187 | 0.0006925 | 6.1014 | 6.1021 | -4.2315 | 1444.0438 | 10542.8283 | -0.0029303
148 |  | 24.6614 | 71.5026 | 4187 | 0.00069247 | 6.1021 | 6.1028 | -4.2315 | 1444.103 | 10614.331 | -0.0029302
149 |  | 24.6614 | 71.4997 | 4187 | 0.00069244 | 6.1028 | 6.1035 | -4.2315 | 1444.1621 | 10685.8307 | -0.00293
150 |  | 24.6614 | 71.4968 | 4187 | 0.00069241 | 6.1035 | 6.1042 | -4.2315 | 1444.2213 | 10757.3275 | -0.0029299
151 |  | 24.6614 | 71.4939 | 4187 | 0.00069239 | 6.1042 | 6.1049 | -4.2315 | 1444.2805 | 10828.8213 | -0.0029298
152 |  | 24.6614 | 71.4909 | 4187 | 0.00069236 | 6.1049 | 6.1056 | -4.2315 | 1444.3397 | 10900.3122 | -0.0029297
153 |  | 24.6614 | 71.488 | 4187 | 0.00069233 | 6.1056 | 6.1063 | -4.2315 | 1444.3989 | 10971.8002 | -0.0029296
154 |  | 24.6614 | 71.4851 | 4187 | 0.0006923 | 6.1063 | 6.1069 | -4.2315 | 1444.4581 | 11043.2853 | -0.0029294
155 |  | 24.6614 | 71.4821 | 4187 | 0.00069227 | 6.1069 | 6.1076 | -4.2315 | 1444.5173 | 11114.7674 | -0.0029293
156 |  | 24.6614 | 71.4792 | 4187 | 0.00069224 | 6.1076 | 6.1083 | -4.2315 | 1444.5765 | 11186.2467 | -0.0029292
157 |  | 24.6614 | 71.4763 | 4187 | 0.00069222 | 6.1083 | 6.109 | -4.2315 | 1444.6357 | 11257.7229 | -0.0029291
158 |  | 24.6614 | 71.4734 | 4187 | 0.00069219 | 6.109 | 6.1097 | -4.2315 | 1444.6949 | 11329.1963 | -0.002929
159 |  | 24.6614 | 71.4704 | 4187 | 0.00069216 | 6.1097 | 6.1104 | -4.2315 | 1444.7541 | 11400.6667 | -0.0029288
160 |  | 24.6614 | 71.4675 | 4187 | 0.00069213 | 6.1104 | 6.1111 | -4.2315 | 1444.8133 | 11472.1342 | -0.0029287
161 |  | 24.6614 | 71.4646 | 4187 | 0.0006921 | 6.1111 | 6.1118 | -4.2315 | 1444.8725 | 11543.5988 | -0.0029286
162 |  | 24.6614 | 71.4616 | 4187 | 0.00069207 | 6.1118 | 6.1125 | -4.2315 | 1444.9317 | 11615.0604 | -0.0029285
163 |  | 24.6614 | 71.4587 | 4187 | 0.00069205 | 6.1125 | 6.1132 | -4.2315 | 1444.9909 | 11686.5191 | -0.0029284
164 |  | 24.6614 | 71.4558 | 4187 | 0.00069202 | 6.1132 | 6.1139 | -4.2315 | 1445.0502 | 11757.9749 | -0.0029282
165 |  | 24.6614 | 71.4529 | 4187 | 0.00069199 | 6.1139 | 6.1146 | -4.2315 | 1445.1094 | 11829.4277 | -0.0029281
166 |  | 24.6614 | 71.4499 | 4187 | 0.00069196 | 6.1146 | 6.1153 | -4.2315 | 1445.1686 | 11900.8777 | -0.002928
167 |  | 24.6614 | 71.447 | 4187 | 0.00069193 | 6.1153 | 6.1159 | -4.2315 | 1445.2278 | 11972.3247 | -0.0029279
168 |  | 24.6614 | 71.4441 | 4187 | 0.0006919 | 6.1159 | 6.1166 | -4.2315 | 1445.2871 | 12043.7687 | -0.0029278
169 |  | 24.6614 | 71.4411 | 4187 | 0.00069188 | 6.1166 | 6.1173 | -4.2315 | 1445.3463 | 12115.2099 | -0.0029276
170 |  | 24.6614 | 71.4382 | 4187 | 0.00069185 | 6.1173 | 6.118 | -4.2315 | 1445.4055 | 12186.6481 | -0.0029275
171 |  | 24.6614 | 71.4353 | 4187 | 0.00069182 | 6.118 | 6.1187 | -4.2315 | 1445.4648 | 12258.0834 | -0.0029274
172 |  | 24.6614 | 71.4324 | 4187 | 0.00069179 | 6.1187 | 6.1194 | -4.2315 | 1445.524 | 12329.5157 | -0.0029273
173 |  | 24.6614 | 71.4294 | 4187 | 0.00069176 | 6.1194 | 6.1201 | -4.2315 | 1445.5832 | 12400.9451 | -0.0029272
174 |  | 24.6614 | 71.4265 | 4187 | 0.00069173 | 6.1201 | 6.1208 | -4.2315 | 1445.6425 | 12472.3716 | -0.002927
175 |  | 24.6614 | 71.4236 | 4187 | 0.00069171 | 6.1208 | 6.1215 | -4.2315 | 1445.7017 | 12543.7952 | -0.0029269
176 |  | 24.6614 | 71.4206 | 4187 | 0.00069168 | 6.1215 | 6.1222 | -4.2315 | 1445.761 | 12615.2159 | -0.0029268
177 |  | 24.6614 | 71.4177 | 4187 | 0.00069165 | 6.1222 | 6.1229 | -4.2315 | 1445.8202 | 12686.6336 | -0.0029267
178 |  | 24.6614 | 71.4148 | 4187 | 0.00069162 | 6.1229 | 6.1236 | -4.2315 | 1445.8795 | 12758.0484 | -0.0029266
179 |  | 24.6614 | 71.4119 | 4187 | 0.00069159 | 6.1236 | 6.1242 | -4.2315 | 1445.9387 | 12829.4602 | -0.0029264
180 |  | 24.6614 | 71.4089 | 4187 | 0.00069156 | 6.1242 | 6.1249 | -4.2315 | 1445.998 | 12900.8692 | -0.0029263
181 |  | 24.6614 | 71.406 | 4187 | 0.00069154 | 6.1249 | 6.1256 | -4.2315 | 1446.0572 | 12972.2752 | -0.0029262
182 |  | 24.6614 | 71.4031 | 4187 | 0.00069151 | 6.1256 | 6.1263 | -4.2315 | 1446.1165 | 13043.6783 | -0.0029261
183 |  | 24.6614 | 71.4002 | 4187 | 0.00069148 | 6.1263 | 6.127 | -4.2315 | 1446.1758 | 13115.0784 | -0.002926
184 |  | 24.6614 | 71.3972 | 4187 | 0.00069145 | 6.127 | 6.1277 | -4.2315 | 1446.235 | 13186.4757 | -0.0029258
185 |  | 24.6614 | 71.3943 | 4187 | 0.00069142 | 6.1277 | 6.1284 | -4.2315 | 1446.2943 | 13257.87 | -0.0029257
186 |  | 24.6614 | 71.3914 | 4187 | 0.00069139 | 6.1284 | 6.1291 | -4.2315 | 1446.3536 | 13329.2614 | -0.0029256
187 |  | 24.6614 | 71.3885 | 4187 | 0.00069137 | 6.1291 | 6.1298 | -4.2315 | 1446.4128 | 13400.6498 | -0.0029255
188 |  | 24.6614 | 71.3855 | 4187 | 0.00069134 | 6.1298 | 6.1305 | -4.2315 | 1446.4721 | 13472.0354 | -0.0029254
189 |  | 24.6614 | 71.3826 | 4187 | 0.00069131 | 6.1305 | 6.1312 | -4.2315 | 1446.5314 | 13543.418 | -0.0029252
190 |  | 24.6614 | 71.3797 | 4187 | 0.00069128 | 6.1312 | 6.1319 | -4.2315 | 1446.5907 | 13614.7977 | -0.0029251
191 |  | 24.6614 | 71.3768 | 4187 | 0.00069125 | 6.1319 | 6.1325 | -4.2315 | 1446.65 | 13686.1744 | -0.002925
192 |  | 24.6614 | 71.3738 | 4187 | 0.00069122 | 6.1325 | 6.1332 | -4.2315 | 1446.7092 | 13757.5483 | -0.0029249
193 |  | 24.6614 | 71.3709 | 4187 | 0.0006912 | 6.1332 | 6.1339 | -4.2315 | 1446.7685 | 13828.9192 | -0.0029248
194 |  | 24.6614 | 71.368 | 4187 | 0.00069117 | 6.1339 | 6.1346 | -4.2315 | 1446.8278 | 13900.2871 | -0.0029246
195 |  | 24.6614 | 71.3651 | 4187 | 0.00069114 | 6.1346 | 6.1353 | -4.2315 | 1446.8871 | 13971.6522 | -0.0029245
196 |  | 24.6614 | 71.3621 | 4187 | 0.00069111 | 6.1353 | 6.136 | -4.2315 | 1446.9464 | 14043.0143 | -0.0029244
197 |  | 24.6614 | 71.3592 | 4187 | 0.00069108 | 6.136 | 6.1367 | -4.2315 | 1447.0057 | 14114.3736 | -0.0029243
198 |  | 24.6614 | 71.3563 | 4187 | 0.00069105 | 6.1367 | 6.1374 | -4.2315 | 1447.065 | 14185.7298 | -0.0029242
199 |  | 24.6614 | 71.3534 | 4187 | 0.00069103 | 6.1374 | 6.1381 | -4.2315 | 1447.1243 | 14257.0832 | -0.002924
200 |  | 24.6614 | 71.3504 | 4187 | 0.000691 | 6.1381 | 6.1388 | -4.2315 | 1447.1836 | 14328.4336 | -0.0029239
201 |  | 24.6614 | 71.3475 | 4187 | 0.00069097 | 6.1388 | 6.1395 | -4.2315 | 1447.2429 | 14399.7811 | -0.0029238
202 |  | 24.6614 | 71.3446 | 4187 | 0.00069094 | 6.1395 | 6.1401 | -4.2315 | 1447.3022 | 14471.1257 | -0.0029237
203 |  | 24.6614 | 71.3417 | 4187 | 0.00069091 | 6.1401 | 6.1408 | -4.2315 | 1447.3615 | 14542.4674 | -0.0029236
204 |  | 24.6614 | 71.3387 | 4187 | 0.00069088 | 6.1408 | 6.1415 | -4.2315 | 1447.4209 | 14613.8061 | -0.0029234
205 |  | 24.6614 | 71.3358 | 4187 | 0.00069086 | 6.1415 | 6.1422 | -4.2315 | 1447.4802 | 14685.142 | -0.0029233
206 |  | 24.6614 | 71.3329 | 4187 | 0.00069083 | 6.1422 | 6.1429 | -4.2315 | 1447.5395 | 14756.4749 | -0.0029232
207 |  | 24.6614 | 71.33 | 4187 | 0.0006908 | 6.1429 | 6.1436 | -4.2315 | 1447.5988 | 14827.8048 | -0.0029231
208 |  | 24.6614 | 71.327 | 4187 | 0.00069077 | 6.1436 | 6.1443 | -4.2315 | 1447.6581 | 14899.1319 | -0.002923
209 |  | 24.6614 | 71.3241 | 4187 | 0.00069074 | 6.1443 | 6.145 | -4.2315 | 1447.7175 | 14970.456 | -0.0029228
210 |  | 24.6614 | 71.3212 | 4187 | 0.00069071 | 6.145 | 6.1457 | -4.2315 | 1447.7768 | 15041.7772 | -0.0029227
211 |  | 24.6614 | 71.3183 | 4187 | 0.00069069 | 6.1457 | 6.1464 | -4.2315 | 1447.8361 | 15113.0955 | -0.0029226
212 |  | 24.6614 | 71.3154 | 4187 | 0.00069066 | 6.1464 | 6.1471 | -4.2315 | 1447.8955 | 15184.4109 | -0.0029225
213 |  | 24.6614 | 71.3124 | 4187 | 0.00069063 | 6.1471 | 6.1477 | -4.2315 | 1447.9548 | 15255.7233 | -0.0029224
214 |  | 24.6614 | 71.3095 | 4187 | 0.0006906 | 6.1477 | 6.1484 | -4.2315 | 1448.0141 | 15327.0328 | -0.0029222
215 |  | 24.6614 | 71.3066 | 4187 | 0.00069057 | 6.1484 | 6.1491 | -4.2315 | 1448.0735 | 15398.3394 | -0.0029221
216 |  | 24.6614 | 71.3037 | 4187 | 0.00069054 | 6.1491 | 6.1498 | -4.2315 | 1448.1328 | 15469.6431 | -0.002922
217 |  | 24.6614 | 71.3007 | 4187 | 0.00069052 | 6.1498 | 6.1505 | -4.2315 | 1448.1922 | 15540.9438 | -0.0029219
218 |  | 24.6614 | 71.2978 | 4187 | 0.00069049 | 6.1505 | 6.1512 | -4.2315 | 1448.2515 | 15612.2416 | -0.0029218
219 |  | 24.6614 | 71.2949 | 4187 | 0.00069046 | 6.1512 | 6.1519 | -4.2315 | 1448.3109 | 15683.5365 | -0.0029216
220 |  | 24.6614 | 71.292 | 4187 | 0.00069043 | 6.1519 | 6.1526 | -4.2315 | 1448.3702 | 15754.8285 | -0.0029215
221 |  | 24.6614 | 71.2891 | 4187 | 0.0006904 | 6.1526 | 6.1533 | -4.2315 | 1448.4296 | 15826.1176 | -0.0029214
222 |  | 24.6614 | 71.2861 | 4187 | 0.00069037 | 6.1533 | 6.154 | -4.2315 | 1448.4889 | 15897.4037 | -0.0029213
223 |  | 24.6614 | 71.2832 | 4187 | 0.00069035 | 6.154 | 6.1546 | -4.2315 | 1448.5483 | 15968.6869 | -0.0029212
224 |  | 24.6614 | 71.2803 | 4187 | 0.00069032 | 6.1546 | 6.1553 | -4.2315 | 1448.6077 | 16039.9672 | -0.002921
225 |  | 24.6614 | 71.2774 | 4187 | 0.00069029 | 6.1553 | 6.156 | -4.2315 | 1448.667 | 16111.2446 | -0.0029209
226 |  | 24.6614 | 71.2745 | 4187 | 0.00069026 | 6.156 | 6.1567 | -4.2315 | 1448.7264 | 16182.5191 | -0.0029208
227 |  | 24.6614 | 71.2715 | 4187 | 0.00069023 | 6.1567 | 6.1574 | -4.2315 | 1448.7858 | 16253.7906 | -0.0029207
228 |  | 24.6614 | 71.2686 | 4187 | 0.0006902 | 6.1574 | 6.1581 | -4.2315 | 1448.8451 | 16325.0592 | -0.0029206
229 |  | 24.6614 | 71.2657 | 4187 | 0.00069018 | 6.1581 | 6.1588 | -4.2315 | 1448.9045 | 16396.3249 | -0.0029204
230 |  | 24.6614 | 71.2628 | 4187 | 0.00069015 | 6.1588 | 6.1595 | -4.2315 | 1448.9639 | 16467.5877 | -0.0029203
231 |  | 24.6614 | 71.2599 | 4187 | 0.00069012 | 6.1595 | 6.1602 | -4.2315 | 1449.0233 | 16538.8475 | -0.0029202
232 |  | 24.6614 | 71.2569 | 4187 | 0.00069009 | 6.1602 | 6.1609 | -4.2315 | 1449.0827 | 16610.1045 | -0.0029201
233 |  | 24.6614 | 71.254 | 4187 | 0.00069006 | 6.1609 | 6.1616 | -4.2315 | 1449.1421 | 16681.3585 | -0.00292
234 |  | 24.6614 | 71.2511 | 4187 | 0.00069004 | 6.1616 | 6.1622 | -4.2315 | 1449.2014 | 16752.6096 | -0.0029199
235 |  | 24.6614 | 71.2482 | 4187 | 0.00069001 | 6.1622 | 6.1629 | -4.2315 | 1449.2608 | 16823.8577 | -0.0029197
236 |  | 24.6614 | 71.2453 | 4187 | 0.00068998 | 6.1629 | 6.1636 | -4.2315 | 1449.3202 | 16895.103 | -0.0029196

## CLX250
|  |  | buis | verlies W/M | L /°C/sec
diam | wandikte |  | inhoud l/m |  | W/M
250 | 14.2 | 3.1416 | 38.5682 | 79.3406 | 4187
[8 empty] | J/sec/mtr | aantal mtr. | verlies
|  | buis | verlies W/M | L /°C/sec | verlies temp | begintemp | eindtemp | verlies | bij 1°C | totaal J/sec
|  | inhoud L |  | W/M | °C per M | °C | °C | per m°C | daling | aantal mtr
1 | 250 | 38.5682 | 79.3406 | 4187 | 0.00049132 | 6 | 6.0005 | -4.6671 | 2035.3385 | 79.3406 | -0.002293
2 |  | 38.5682 | 79.3383 | 4187 | 0.0004913 | 6.0005 | 6.001 | -4.6671 | 2035.3973 | 158.679 | -0.002293
3 |  | 38.5682 | 79.3361 | 4187 | 0.00049129 | 6.001 | 6.0015 | -4.6671 | 2035.4561 | 238.015 | -0.0022929
4 |  | 38.5682 | 79.3338 | 4187 | 0.00049128 | 6.0015 | 6.002 | -4.6671 | 2035.515 | 317.3488 | -0.0022928
5 |  | 38.5682 | 79.3315 | 4187 | 0.00049126 | 6.002 | 6.0025 | -4.6671 | 2035.5738 | 396.6803 | -0.0022928
6 |  | 38.5682 | 79.3292 | 4187 | 0.00049125 | 6.0025 | 6.0029 | -4.6671 | 2035.6326 | 476.0095 | -0.0022927
7 |  | 38.5682 | 79.3269 | 4187 | 0.00049123 | 6.0029 | 6.0034 | -4.6671 | 2035.6915 | 555.3363 | -0.0022926
8 |  | 38.5682 | 79.3246 | 4187 | 0.00049122 | 6.0034 | 6.0039 | -4.6671 | 2035.7503 | 634.6609 | -0.0022926
9 |  | 38.5682 | 79.3223 | 4187 | 0.00049121 | 6.0039 | 6.0044 | -4.6671 | 2035.8091 | 713.9832 | -0.0022925
10 |  | 38.5682 | 79.32 | 4187 | 0.00049119 | 6.0044 | 6.0049 | -4.6671 | 2035.868 | 793.3032 | -0.0022924
11 |  | 38.5682 | 79.3177 | 4187 | 0.00049118 | 6.0049 | 6.0054 | -4.6671 | 2035.9268 | 872.621 | -0.0022924
12 |  | 38.5682 | 79.3154 | 4187 | 0.00049116 | 6.0054 | 6.0059 | -4.6671 | 2035.9857 | 951.9364 | -0.0022923
13 |  | 38.5682 | 79.3131 | 4187 | 0.00049115 | 6.0059 | 6.0064 | -4.6671 | 2036.0445 | 1031.2495 | -0.0022922
14 |  | 38.5682 | 79.3108 | 4187 | 0.00049113 | 6.0064 | 6.0069 | -4.6671 | 2036.1033 | 1110.5603 | -0.0022922
15 |  | 38.5682 | 79.3085 | 4187 | 0.00049112 | 6.0069 | 6.0074 | -4.6671 | 2036.1622 | 1189.8689 | -0.0022921
16 |  | 38.5682 | 79.3063 | 4187 | 0.00049111 | 6.0074 | 6.0079 | -4.6671 | 2036.221 | 1269.1751 | -0.002292
17 |  | 38.5682 | 79.304 | 4187 | 0.00049109 | 6.0079 | 6.0084 | -4.6671 | 2036.2799 | 1348.4791 | -0.002292
18 |  | 38.5682 | 79.3017 | 4187 | 0.00049108 | 6.0084 | 6.0088 | -4.6671 | 2036.3387 | 1427.7808 | -0.0022919
19 |  | 38.5682 | 79.2994 | 4187 | 0.00049106 | 6.0088 | 6.0093 | -4.6671 | 2036.3976 | 1507.0802 | -0.0022918
20 |  | 38.5682 | 79.2971 | 4187 | 0.00049105 | 6.0093 | 6.0098 | -4.6671 | 2036.4565 | 1586.3772 | -0.0022918
21 |  | 38.5682 | 79.2948 | 4187 | 0.00049103 | 6.0098 | 6.0103 | -4.6671 | 2036.5153 | 1665.672 | -0.0022917
22 |  | 38.5682 | 79.2925 | 4187 | 0.00049102 | 6.0103 | 6.0108 | -4.6671 | 2036.5742 | 1744.9645 | -0.0022916
23 |  | 38.5682 | 79.2902 | 4187 | 0.00049101 | 6.0108 | 6.0113 | -4.6671 | 2036.633 | 1824.2547 | -0.0022916
24 |  | 38.5682 | 79.2879 | 4187 | 0.00049099 | 6.0113 | 6.0118 | -4.6671 | 2036.6919 | 1903.5427 | -0.0022915
25 |  | 38.5682 | 79.2856 | 4187 | 0.00049098 | 6.0118 | 6.0123 | -4.6671 | 2036.7508 | 1982.8283 | -0.0022914
26 |  | 38.5682 | 79.2833 | 4187 | 0.00049096 | 6.0123 | 6.0128 | -4.6671 | 2036.8096 | 2062.1116 | -0.0022914
27 |  | 38.5682 | 79.281 | 4187 | 0.00049095 | 6.0128 | 6.0133 | -4.6671 | 2036.8685 | 2141.3927 | -0.0022913
28 |  | 38.5682 | 79.2788 | 4187 | 0.00049094 | 6.0133 | 6.0138 | -4.6671 | 2036.9274 | 2220.6714 | -0.0022912
29 |  | 38.5682 | 79.2765 | 4187 | 0.00049092 | 6.0138 | 6.0142 | -4.6671 | 2036.9862 | 2299.9479 | -0.0022912
30 |  | 38.5682 | 79.2742 | 4187 | 0.00049091 | 6.0142 | 6.0147 | -4.6671 | 2037.0451 | 2379.2221 | -0.0022911
31 |  | 38.5682 | 79.2719 | 4187 | 0.00049089 | 6.0147 | 6.0152 | -4.6671 | 2037.104 | 2458.4939 | -0.002291
32 |  | 38.5682 | 79.2696 | 4187 | 0.00049088 | 6.0152 | 6.0157 | -4.6671 | 2037.1629 | 2537.7635 | -0.002291
33 |  | 38.5682 | 79.2673 | 4187 | 0.00049086 | 6.0157 | 6.0162 | -4.6671 | 2037.2217 | 2617.0308 | -0.0022909
34 |  | 38.5682 | 79.265 | 4187 | 0.00049085 | 6.0162 | 6.0167 | -4.6671 | 2037.2806 | 2696.2958 | -0.0022908
35 |  | 38.5682 | 79.2627 | 4187 | 0.00049084 | 6.0167 | 6.0172 | -4.6671 | 2037.3395 | 2775.5585 | -0.0022908
36 |  | 38.5682 | 79.2604 | 4187 | 0.00049082 | 6.0172 | 6.0177 | -4.6671 | 2037.3984 | 2854.819 | -0.0022907
37 |  | 38.5682 | 79.2581 | 4187 | 0.00049081 | 6.0177 | 6.0182 | -4.6671 | 2037.4573 | 2934.0771 | -0.0022906
38 |  | 38.5682 | 79.2558 | 4187 | 0.00049079 | 6.0182 | 6.0187 | -4.6671 | 2037.5162 | 3013.3329 | -0.0022906
39 |  | 38.5682 | 79.2536 | 4187 | 0.00049078 | 6.0187 | 6.0192 | -4.6671 | 2037.575 | 3092.5865 | -0.0022905
40 |  | 38.5682 | 79.2513 | 4187 | 0.00049077 | 6.0192 | 6.0196 | -4.6671 | 2037.6339 | 3171.8378 | -0.0022904
41 |  | 38.5682 | 79.249 | 4187 | 0.00049075 | 6.0196 | 6.0201 | -4.6671 | 2037.6928 | 3251.0867 | -0.0022904
42 |  | 38.5682 | 79.2467 | 4187 | 0.00049074 | 6.0201 | 6.0206 | -4.6671 | 2037.7517 | 3330.3334 | -0.0022903
43 |  | 38.5682 | 79.2444 | 4187 | 0.00049072 | 6.0206 | 6.0211 | -4.6671 | 2037.8106 | 3409.5778 | -0.0022903
44 |  | 38.5682 | 79.2421 | 4187 | 0.00049071 | 6.0211 | 6.0216 | -4.6671 | 2037.8695 | 3488.8199 | -0.0022902
45 |  | 38.5682 | 79.2398 | 4187 | 0.00049069 | 6.0216 | 6.0221 | -4.6671 | 2037.9284 | 3568.0597 | -0.0022901
46 |  | 38.5682 | 79.2375 | 4187 | 0.00049068 | 6.0221 | 6.0226 | -4.6671 | 2037.9873 | 3647.2972 | -0.0022901
47 |  | 38.5682 | 79.2352 | 4187 | 0.00049067 | 6.0226 | 6.0231 | -4.6671 | 2038.0462 | 3726.5325 | -0.00229
48 |  | 38.5682 | 79.2329 | 4187 | 0.00049065 | 6.0231 | 6.0236 | -4.6671 | 2038.1051 | 3805.7654 | -0.0022899
49 |  | 38.5682 | 79.2307 | 4187 | 0.00049064 | 6.0236 | 6.0241 | -4.6671 | 2038.164 | 3884.9961 | -0.0022899
50 |  | 38.5682 | 79.2284 | 4187 | 0.00049062 | 6.0241 | 6.0245 | -4.6671 | 2038.2229 | 3964.2244 | -0.0022898
51 |  | 38.5682 | 79.2261 | 4187 | 0.00049061 | 6.0245 | 6.025 | -4.6671 | 2038.2818 | 4043.4505 | -0.0022897
52 |  | 38.5682 | 79.2238 | 4187 | 0.0004906 | 6.025 | 6.0255 | -4.6671 | 2038.3407 | 4122.6743 | -0.0022897
53 |  | 38.5682 | 79.2215 | 4187 | 0.00049058 | 6.0255 | 6.026 | -4.6671 | 2038.3997 | 4201.8958 | -0.0022896
54 |  | 38.5682 | 79.2192 | 4187 | 0.00049057 | 6.026 | 6.0265 | -4.6671 | 2038.4586 | 4281.115 | -0.0022895
55 |  | 38.5682 | 79.2169 | 4187 | 0.00049055 | 6.0265 | 6.027 | -4.6671 | 2038.5175 | 4360.3319 | -0.0022895
56 |  | 38.5682 | 79.2146 | 4187 | 0.00049054 | 6.027 | 6.0275 | -4.6671 | 2038.5764 | 4439.5465 | -0.0022894
57 |  | 38.5682 | 79.2123 | 4187 | 0.00049052 | 6.0275 | 6.028 | -4.6671 | 2038.6353 | 4518.7588 | -0.0022893
58 |  | 38.5682 | 79.21 | 4187 | 0.00049051 | 6.028 | 6.0285 | -4.6671 | 2038.6942 | 4597.9689 | -0.0022893
59 |  | 38.5682 | 79.2078 | 4187 | 0.0004905 | 6.0285 | 6.029 | -4.6671 | 2038.7532 | 4677.1766 | -0.0022892
60 |  | 38.5682 | 79.2055 | 4187 | 0.00049048 | 6.029 | 6.0295 | -4.6671 | 2038.8121 | 4756.3821 | -0.0022891
61 |  | 38.5682 | 79.2032 | 4187 | 0.00049047 | 6.0295 | 6.0299 | -4.6671 | 2038.871 | 4835.5853 | -0.0022891
62 |  | 38.5682 | 79.2009 | 4187 | 0.00049045 | 6.0299 | 6.0304 | -4.6671 | 2038.9299 | 4914.7862 | -0.002289
63 |  | 38.5682 | 79.1986 | 4187 | 0.00049044 | 6.0304 | 6.0309 | -4.6671 | 2038.9889 | 4993.9848 | -0.0022889
64 |  | 38.5682 | 79.1963 | 4187 | 0.00049042 | 6.0309 | 6.0314 | -4.6671 | 2039.0478 | 5073.1811 | -0.0022889
65 |  | 38.5682 | 79.194 | 4187 | 0.00049041 | 6.0314 | 6.0319 | -4.6671 | 2039.1067 | 5152.3751 | -0.0022888
66 |  | 38.5682 | 79.1917 | 4187 | 0.0004904 | 6.0319 | 6.0324 | -4.6671 | 2039.1657 | 5231.5668 | -0.0022887
67 |  | 38.5682 | 79.1894 | 4187 | 0.00049038 | 6.0324 | 6.0329 | -4.6671 | 2039.2246 | 5310.7563 | -0.0022887
68 |  | 38.5682 | 79.1872 | 4187 | 0.00049037 | 6.0329 | 6.0334 | -4.6671 | 2039.2835 | 5389.9434 | -0.0022886
69 |  | 38.5682 | 79.1849 | 4187 | 0.00049035 | 6.0334 | 6.0339 | -4.6671 | 2039.3425 | 5469.1283 | -0.0022885
70 |  | 38.5682 | 79.1826 | 4187 | 0.00049034 | 6.0339 | 6.0344 | -4.6671 | 2039.4014 | 5548.3109 | -0.0022885
71 |  | 38.5682 | 79.1803 | 4187 | 0.00049033 | 6.0344 | 6.0348 | -4.6671 | 2039.4604 | 5627.4912 | -0.0022884
72 |  | 38.5682 | 79.178 | 4187 | 0.00049031 | 6.0348 | 6.0353 | -4.6671 | 2039.5193 | 5706.6692 | -0.0022883
73 |  | 38.5682 | 79.1757 | 4187 | 0.0004903 | 6.0353 | 6.0358 | -4.6671 | 2039.5783 | 5785.8449 | -0.0022883
74 |  | 38.5682 | 79.1734 | 4187 | 0.00049028 | 6.0358 | 6.0363 | -4.6671 | 2039.6372 | 5865.0183 | -0.0022882
75 |  | 38.5682 | 79.1711 | 4187 | 0.00049027 | 6.0363 | 6.0368 | -4.6671 | 2039.6961 | 5944.1894 | -0.0022881
76 |  | 38.5682 | 79.1688 | 4187 | 0.00049025 | 6.0368 | 6.0373 | -4.6671 | 2039.7551 | 6023.3583 | -0.0022881
77 |  | 38.5682 | 79.1666 | 4187 | 0.00049024 | 6.0373 | 6.0378 | -4.6671 | 2039.8141 | 6102.5249 | -0.002288
78 |  | 38.5682 | 79.1643 | 4187 | 0.00049023 | 6.0378 | 6.0383 | -4.6671 | 2039.873 | 6181.6891 | -0.0022879
79 |  | 38.5682 | 79.162 | 4187 | 0.00049021 | 6.0383 | 6.0388 | -4.6671 | 2039.932 | 6260.8511 | -0.0022879
80 |  | 38.5682 | 79.1597 | 4187 | 0.0004902 | 6.0388 | 6.0393 | -4.6671 | 2039.9909 | 6340.0108 | -0.0022878
81 |  | 38.5682 | 79.1574 | 4187 | 0.00049018 | 6.0393 | 6.0398 | -4.6671 | 2040.0499 | 6419.1682 | -0.0022877
82 |  | 38.5682 | 79.1551 | 4187 | 0.00049017 | 6.0398 | 6.0402 | -4.6671 | 2040.1088 | 6498.3233 | -0.0022877
83 |  | 38.5682 | 79.1528 | 4187 | 0.00049016 | 6.0402 | 6.0407 | -4.6671 | 2040.1678 | 6577.4762 | -0.0022876
84 |  | 38.5682 | 79.1505 | 4187 | 0.00049014 | 6.0407 | 6.0412 | -4.6671 | 2040.2268 | 6656.6267 | -0.0022875
85 |  | 38.5682 | 79.1483 | 4187 | 0.00049013 | 6.0412 | 6.0417 | -4.6671 | 2040.2857 | 6735.775 | -0.0022875
86 |  | 38.5682 | 79.146 | 4187 | 0.00049011 | 6.0417 | 6.0422 | -4.6671 | 2040.3447 | 6814.9209 | -0.0022874
87 |  | 38.5682 | 79.1437 | 4187 | 0.0004901 | 6.0422 | 6.0427 | -4.6671 | 2040.4037 | 6894.0646 | -0.0022873
88 |  | 38.5682 | 79.1414 | 4187 | 0.00049008 | 6.0427 | 6.0432 | -4.6671 | 2040.4626 | 6973.206 | -0.0022873
89 |  | 38.5682 | 79.1391 | 4187 | 0.00049007 | 6.0432 | 6.0437 | -4.6671 | 2040.5216 | 7052.3451 | -0.0022872
90 |  | 38.5682 | 79.1368 | 4187 | 0.00049006 | 6.0437 | 6.0442 | -4.6671 | 2040.5806 | 7131.482 | -0.0022871
91 |  | 38.5682 | 79.1345 | 4187 | 0.00049004 | 6.0442 | 6.0447 | -4.6671 | 2040.6396 | 7210.6165 | -0.0022871
92 |  | 38.5682 | 79.1322 | 4187 | 0.00049003 | 6.0447 | 6.0451 | -4.6671 | 2040.6986 | 7289.7487 | -0.002287
93 |  | 38.5682 | 79.13 | 4187 | 0.00049001 | 6.0451 | 6.0456 | -4.6671 | 2040.7575 | 7368.8787 | -0.0022869
94 |  | 38.5682 | 79.1277 | 4187 | 0.00049 | 6.0456 | 6.0461 | -4.6671 | 2040.8165 | 7448.0064 | -0.0022869
95 |  | 38.5682 | 79.1254 | 4187 | 0.00048999 | 6.0461 | 6.0466 | -4.6671 | 2040.8755 | 7527.1318 | -0.0022868
96 |  | 38.5682 | 79.1231 | 4187 | 0.00048997 | 6.0466 | 6.0471 | -4.6671 | 2040.9345 | 7606.2549 | -0.0022867
97 |  | 38.5682 | 79.1208 | 4187 | 0.00048996 | 6.0471 | 6.0476 | -4.6671 | 2040.9935 | 7685.3757 | -0.0022867
98 |  | 38.5682 | 79.1185 | 4187 | 0.00048994 | 6.0476 | 6.0481 | -4.6671 | 2041.0525 | 7764.4942 | -0.0022866
99 |  | 38.5682 | 79.1162 | 4187 | 0.00048993 | 6.0481 | 6.0486 | -4.6671 | 2041.1114 | 7843.6104 | -0.0022865
100 |  | 38.5682 | 79.114 | 4187 | 0.00048991 | 6.0486 | 6.0491 | -4.6671 | 2041.1704 | 7922.7244 | -0.0022865
101 |  | 38.5682 | 79.1117 | 4187 | 0.0004899 | 6.0491 | 6.0496 | -4.6671 | 2041.2294 | 8001.836 | -0.0022864
102 |  | 38.5682 | 79.1094 | 4187 | 0.00048989 | 6.0496 | 6.05 | -4.6671 | 2041.2884 | 8080.9454 | -0.0022863
103 |  | 38.5682 | 79.1071 | 4187 | 0.00048987 | 6.05 | 6.0505 | -4.6671 | 2041.3474 | 8160.0525 | -0.0022863
104 |  | 38.5682 | 79.1048 | 4187 | 0.00048986 | 6.0505 | 6.051 | -4.6671 | 2041.4064 | 8239.1573 | -0.0022862
105 |  | 38.5682 | 79.1025 | 4187 | 0.00048984 | 6.051 | 6.0515 | -4.6671 | 2041.4654 | 8318.2598 | -0.0022862
106 |  | 38.5682 | 79.1002 | 4187 | 0.00048983 | 6.0515 | 6.052 | -4.6671 | 2041.5244 | 8397.3601 | -0.0022861
107 |  | 38.5682 | 79.0979 | 4187 | 0.00048982 | 6.052 | 6.0525 | -4.6671 | 2041.5834 | 8476.458 | -0.002286
108 |  | 38.5682 | 79.0957 | 4187 | 0.0004898 | 6.0525 | 6.053 | -4.6671 | 2041.6424 | 8555.5537 | -0.002286
109 |  | 38.5682 | 79.0934 | 4187 | 0.00048979 | 6.053 | 6.0535 | -4.6671 | 2041.7014 | 8634.6471 | -0.0022859
110 |  | 38.5682 | 79.0911 | 4187 | 0.00048977 | 6.0535 | 6.054 | -4.6671 | 2041.7605 | 8713.7382 | -0.0022858
111 |  | 38.5682 | 79.0888 | 4187 | 0.00048976 | 6.054 | 6.0544 | -4.6671 | 2041.8195 | 8792.827 | -0.0022858
112 |  | 38.5682 | 79.0865 | 4187 | 0.00048975 | 6.0544 | 6.0549 | -4.6671 | 2041.8785 | 8871.9135 | -0.0022857
113 |  | 38.5682 | 79.0842 | 4187 | 0.00048973 | 6.0549 | 6.0554 | -4.6671 | 2041.9375 | 8950.9977 | -0.0022856
114 |  | 38.5682 | 79.0819 | 4187 | 0.00048972 | 6.0554 | 6.0559 | -4.6671 | 2041.9965 | 9030.0797 | -0.0022856
115 |  | 38.5682 | 79.0797 | 4187 | 0.0004897 | 6.0559 | 6.0564 | -4.6671 | 2042.0555 | 9109.1593 | -0.0022855
116 |  | 38.5682 | 79.0774 | 4187 | 0.00048969 | 6.0564 | 6.0569 | -4.6671 | 2042.1145 | 9188.2367 | -0.0022854
117 |  | 38.5682 | 79.0751 | 4187 | 0.00048967 | 6.0569 | 6.0574 | -4.6671 | 2042.1736 | 9267.3118 | -0.0022854
118 |  | 38.5682 | 79.0728 | 4187 | 0.00048966 | 6.0574 | 6.0579 | -4.6671 | 2042.2326 | 9346.3846 | -0.0022853
119 |  | 38.5682 | 79.0705 | 4187 | 0.00048965 | 6.0579 | 6.0584 | -4.6671 | 2042.2916 | 9425.4551 | -0.0022852
120 |  | 38.5682 | 79.0682 | 4187 | 0.00048963 | 6.0584 | 6.0589 | -4.6671 | 2042.3506 | 9504.5234 | -0.0022852
121 |  | 38.5682 | 79.066 | 4187 | 0.00048962 | 6.0589 | 6.0593 | -4.6671 | 2042.4097 | 9583.5893 | -0.0022851
122 |  | 38.5682 | 79.0637 | 4187 | 0.0004896 | 6.0593 | 6.0598 | -4.6671 | 2042.4687 | 9662.653 | -0.002285
123 |  | 38.5682 | 79.0614 | 4187 | 0.00048959 | 6.0598 | 6.0603 | -4.6671 | 2042.5277 | 9741.7144 | -0.002285
124 |  | 38.5682 | 79.0591 | 4187 | 0.00048958 | 6.0603 | 6.0608 | -4.6671 | 2042.5868 | 9820.7735 | -0.0022849
125 |  | 38.5682 | 79.0568 | 4187 | 0.00048956 | 6.0608 | 6.0613 | -4.6671 | 2042.6458 | 9899.8303 | -0.0022848
126 |  | 38.5682 | 79.0545 | 4187 | 0.00048955 | 6.0613 | 6.0618 | -4.6671 | 2042.7048 | 9978.8848 | -0.0022848
127 |  | 38.5682 | 79.0522 | 4187 | 0.00048953 | 6.0618 | 6.0623 | -4.6671 | 2042.7639 | 10057.937 | -0.0022847
128 |  | 38.5682 | 79.05 | 4187 | 0.00048952 | 6.0623 | 6.0628 | -4.6671 | 2042.8229 | 10136.987 | -0.0022846
129 |  | 38.5682 | 79.0477 | 4187 | 0.0004895 | 6.0628 | 6.0633 | -4.6671 | 2042.882 | 10216.0347 | -0.0022846
130 |  | 38.5682 | 79.0454 | 4187 | 0.00048949 | 6.0633 | 6.0638 | -4.6671 | 2042.941 | 10295.08 | -0.0022845
131 |  | 38.5682 | 79.0431 | 4187 | 0.00048948 | 6.0638 | 6.0642 | -4.6671 | 2043 | 10374.1232 | -0.0022844
132 |  | 38.5682 | 79.0408 | 4187 | 0.00048946 | 6.0642 | 6.0647 | -4.6671 | 2043.0591 | 10453.164 | -0.0022844
133 |  | 38.5682 | 79.0385 | 4187 | 0.00048945 | 6.0647 | 6.0652 | -4.6671 | 2043.1181 | 10532.2025 | -0.0022843
134 |  | 38.5682 | 79.0362 | 4187 | 0.00048943 | 6.0652 | 6.0657 | -4.6671 | 2043.1772 | 10611.2388 | -0.0022842
135 |  | 38.5682 | 79.034 | 4187 | 0.00048942 | 6.0657 | 6.0662 | -4.6671 | 2043.2362 | 10690.2727 | -0.0022842
136 |  | 38.5682 | 79.0317 | 4187 | 0.00048941 | 6.0662 | 6.0667 | -4.6671 | 2043.2953 | 10769.3044 | -0.0022841
137 |  | 38.5682 | 79.0294 | 4187 | 0.00048939 | 6.0667 | 6.0672 | -4.6671 | 2043.3543 | 10848.3338 | -0.002284
138 |  | 38.5682 | 79.0271 | 4187 | 0.00048938 | 6.0672 | 6.0677 | -4.6671 | 2043.4134 | 10927.3609 | -0.002284
139 |  | 38.5682 | 79.0248 | 4187 | 0.00048936 | 6.0677 | 6.0682 | -4.6671 | 2043.4725 | 11006.3857 | -0.0022839
140 |  | 38.5682 | 79.0225 | 4187 | 0.00048935 | 6.0682 | 6.0686 | -4.6671 | 2043.5315 | 11085.4083 | -0.0022838
141 |  | 38.5682 | 79.0203 | 4187 | 0.00048933 | 6.0686 | 6.0691 | -4.6671 | 2043.5906 | 11164.4285 | -0.0022838
142 |  | 38.5682 | 79.018 | 4187 | 0.00048932 | 6.0691 | 6.0696 | -4.6671 | 2043.6496 | 11243.4465 | -0.0022837
143 |  | 38.5682 | 79.0157 | 4187 | 0.00048931 | 6.0696 | 6.0701 | -4.6671 | 2043.7087 | 11322.4622 | -0.0022836
144 |  | 38.5682 | 79.0134 | 4187 | 0.00048929 | 6.0701 | 6.0706 | -4.6671 | 2043.7678 | 11401.4756 | -0.0022836
145 |  | 38.5682 | 79.0111 | 4187 | 0.00048928 | 6.0706 | 6.0711 | -4.6671 | 2043.8268 | 11480.4868 | -0.0022835
146 |  | 38.5682 | 79.0088 | 4187 | 0.00048926 | 6.0711 | 6.0716 | -4.6671 | 2043.8859 | 11559.4956 | -0.0022834
147 |  | 38.5682 | 79.0066 | 4187 | 0.00048925 | 6.0716 | 6.0721 | -4.6671 | 2043.945 | 11638.5022 | -0.0022834
148 |  | 38.5682 | 79.0043 | 4187 | 0.00048924 | 6.0721 | 6.0726 | -4.6671 | 2044.0041 | 11717.5064 | -0.0022833
149 |  | 38.5682 | 79.002 | 4187 | 0.00048922 | 6.0726 | 6.0731 | -4.6671 | 2044.0631 | 11796.5084 | -0.0022832
150 |  | 38.5682 | 78.9997 | 4187 | 0.00048921 | 6.0731 | 6.0735 | -4.6671 | 2044.1222 | 11875.5081 | -0.0022832
151 |  | 38.5682 | 78.9974 | 4187 | 0.00048919 | 6.0735 | 6.074 | -4.6671 | 2044.1813 | 11954.5056 | -0.0022831
152 |  | 38.5682 | 78.9951 | 4187 | 0.00048918 | 6.074 | 6.0745 | -4.6671 | 2044.2404 | 12033.5007 | -0.002283
153 |  | 38.5682 | 78.9929 | 4187 | 0.00048917 | 6.0745 | 6.075 | -4.6671 | 2044.2995 | 12112.4936 | -0.002283
154 |  | 38.5682 | 78.9906 | 4187 | 0.00048915 | 6.075 | 6.0755 | -4.6671 | 2044.3585 | 12191.4841 | -0.0022829
155 |  | 38.5682 | 78.9883 | 4187 | 0.00048914 | 6.0755 | 6.076 | -4.6671 | 2044.4176 | 12270.4724 | -0.0022828
156 |  | 38.5682 | 78.986 | 4187 | 0.00048912 | 6.076 | 6.0765 | -4.6671 | 2044.4767 | 12349.4584 | -0.0022828
157 |  | 38.5682 | 78.9837 | 4187 | 0.00048911 | 6.0765 | 6.077 | -4.6671 | 2044.5358 | 12428.4422 | -0.0022827
158 |  | 38.5682 | 78.9814 | 4187 | 0.00048909 | 6.077 | 6.0775 | -4.6671 | 2044.5949 | 12507.4236 | -0.0022827
159 |  | 38.5682 | 78.9792 | 4187 | 0.00048908 | 6.0775 | 6.0779 | -4.6671 | 2044.654 | 12586.4028 | -0.0022826
160 |  | 38.5682 | 78.9769 | 4187 | 0.00048907 | 6.0779 | 6.0784 | -4.6671 | 2044.7131 | 12665.3797 | -0.0022825
161 |  | 38.5682 | 78.9746 | 4187 | 0.00048905 | 6.0784 | 6.0789 | -4.6671 | 2044.7722 | 12744.3543 | -0.0022825
162 |  | 38.5682 | 78.9723 | 4187 | 0.00048904 | 6.0789 | 6.0794 | -4.6671 | 2044.8313 | 12823.3266 | -0.0022824
163 |  | 38.5682 | 78.97 | 4187 | 0.00048902 | 6.0794 | 6.0799 | -4.6671 | 2044.8904 | 12902.2966 | -0.0022823
164 |  | 38.5682 | 78.9678 | 4187 | 0.00048901 | 6.0799 | 6.0804 | -4.6671 | 2044.9495 | 12981.2644 | -0.0022823
165 |  | 38.5682 | 78.9655 | 4187 | 0.000489 | 6.0804 | 6.0809 | -4.6671 | 2045.0086 | 13060.2298 | -0.0022822
166 |  | 38.5682 | 78.9632 | 4187 | 0.00048898 | 6.0809 | 6.0814 | -4.6671 | 2045.0677 | 13139.193 | -0.0022821
167 |  | 38.5682 | 78.9609 | 4187 | 0.00048897 | 6.0814 | 6.0819 | -4.6671 | 2045.1268 | 13218.1539 | -0.0022821
168 |  | 38.5682 | 78.9586 | 4187 | 0.00048895 | 6.0819 | 6.0823 | -4.6671 | 2045.1859 | 13297.1125 | -0.002282
169 |  | 38.5682 | 78.9563 | 4187 | 0.00048894 | 6.0823 | 6.0828 | -4.6671 | 2045.245 | 13376.0689 | -0.0022819
170 |  | 38.5682 | 78.9541 | 4187 | 0.00048892 | 6.0828 | 6.0833 | -4.6671 | 2045.3041 | 13455.0229 | -0.0022819
171 |  | 38.5682 | 78.9518 | 4187 | 0.00048891 | 6.0833 | 6.0838 | -4.6671 | 2045.3632 | 13533.9747 | -0.0022818
172 |  | 38.5682 | 78.9495 | 4187 | 0.0004889 | 6.0838 | 6.0843 | -4.6671 | 2045.4224 | 13612.9242 | -0.0022817
173 |  | 38.5682 | 78.9472 | 4187 | 0.00048888 | 6.0843 | 6.0848 | -4.6671 | 2045.4815 | 13691.8714 | -0.0022817
174 |  | 38.5682 | 78.9449 | 4187 | 0.00048887 | 6.0848 | 6.0853 | -4.6671 | 2045.5406 | 13770.8164 | -0.0022816
175 |  | 38.5682 | 78.9427 | 4187 | 0.00048885 | 6.0853 | 6.0858 | -4.6671 | 2045.5997 | 13849.759 | -0.0022815
176 |  | 38.5682 | 78.9404 | 4187 | 0.00048884 | 6.0858 | 6.0863 | -4.6671 | 2045.6588 | 13928.6994 | -0.0022815
177 |  | 38.5682 | 78.9381 | 4187 | 0.00048883 | 6.0863 | 6.0867 | -4.6671 | 2045.718 | 14007.6375 | -0.0022814
178 |  | 38.5682 | 78.9358 | 4187 | 0.00048881 | 6.0867 | 6.0872 | -4.6671 | 2045.7771 | 14086.5733 | -0.0022813
179 |  | 38.5682 | 78.9335 | 4187 | 0.0004888 | 6.0872 | 6.0877 | -4.6671 | 2045.8362 | 14165.5068 | -0.0022813
180 |  | 38.5682 | 78.9312 | 4187 | 0.00048878 | 6.0877 | 6.0882 | -4.6671 | 2045.8953 | 14244.438 | -0.0022812
181 |  | 38.5682 | 78.929 | 4187 | 0.00048877 | 6.0882 | 6.0887 | -4.6671 | 2045.9545 | 14323.367 | -0.0022811
182 |  | 38.5682 | 78.9267 | 4187 | 0.00048876 | 6.0887 | 6.0892 | -4.6671 | 2046.0136 | 14402.2937 | -0.0022811
183 |  | 38.5682 | 78.9244 | 4187 | 0.00048874 | 6.0892 | 6.0897 | -4.6671 | 2046.0727 | 14481.2181 | -0.002281
184 |  | 38.5682 | 78.9221 | 4187 | 0.00048873 | 6.0897 | 6.0902 | -4.6671 | 2046.1319 | 14560.1402 | -0.0022809
185 |  | 38.5682 | 78.9198 | 4187 | 0.00048871 | 6.0902 | 6.0907 | -4.6671 | 2046.191 | 14639.06 | -0.0022809
186 |  | 38.5682 | 78.9176 | 4187 | 0.0004887 | 6.0907 | 6.0911 | -4.6671 | 2046.2501 | 14717.9776 | -0.0022808
187 |  | 38.5682 | 78.9153 | 4187 | 0.00048868 | 6.0911 | 6.0916 | -4.6671 | 2046.3093 | 14796.8929 | -0.0022807
188 |  | 38.5682 | 78.913 | 4187 | 0.00048867 | 6.0916 | 6.0921 | -4.6671 | 2046.3684 | 14875.8059 | -0.0022807
189 |  | 38.5682 | 78.9107 | 4187 | 0.00048866 | 6.0921 | 6.0926 | -4.6671 | 2046.4276 | 14954.7166 | -0.0022806
190 |  | 38.5682 | 78.9084 | 4187 | 0.00048864 | 6.0926 | 6.0931 | -4.6671 | 2046.4867 | 15033.625 | -0.0022805
191 |  | 38.5682 | 78.9062 | 4187 | 0.00048863 | 6.0931 | 6.0936 | -4.6671 | 2046.5459 | 15112.5312 | -0.0022805
192 |  | 38.5682 | 78.9039 | 4187 | 0.00048861 | 6.0936 | 6.0941 | -4.6671 | 2046.605 | 15191.435 | -0.0022804
193 |  | 38.5682 | 78.9016 | 4187 | 0.0004886 | 6.0941 | 6.0946 | -4.6671 | 2046.6642 | 15270.3366 | -0.0022803
194 |  | 38.5682 | 78.8993 | 4187 | 0.00048859 | 6.0946 | 6.0951 | -4.6671 | 2046.7233 | 15349.236 | -0.0022803
195 |  | 38.5682 | 78.897 | 4187 | 0.00048857 | 6.0951 | 6.0955 | -4.6671 | 2046.7825 | 15428.133 | -0.0022802
196 |  | 38.5682 | 78.8948 | 4187 | 0.00048856 | 6.0955 | 6.096 | -4.6671 | 2046.8416 | 15507.0277 | -0.0022801
197 |  | 38.5682 | 78.8925 | 4187 | 0.00048854 | 6.096 | 6.0965 | -4.6671 | 2046.9008 | 15585.9202 | -0.0022801
198 |  | 38.5682 | 78.8902 | 4187 | 0.00048853 | 6.0965 | 6.097 | -4.6671 | 2046.9599 | 15664.8104 | -0.00228
199 |  | 38.5682 | 78.8879 | 4187 | 0.00048852 | 6.097 | 6.0975 | -4.6671 | 2047.0191 | 15743.6983 | -0.0022799
200 |  | 38.5682 | 78.8856 | 4187 | 0.0004885 | 6.0975 | 6.098 | -4.6671 | 2047.0783 | 15822.5839 | -0.0022799
201 |  | 38.5682 | 78.8834 | 4187 | 0.00048849 | 6.098 | 6.0985 | -4.6671 | 2047.1374 | 15901.4673 | -0.0022798
202 |  | 38.5682 | 78.8811 | 4187 | 0.00048847 | 6.0985 | 6.099 | -4.6671 | 2047.1966 | 15980.3484 | -0.0022798
203 |  | 38.5682 | 78.8788 | 4187 | 0.00048846 | 6.099 | 6.0994 | -4.6671 | 2047.2558 | 16059.2272 | -0.0022797
204 |  | 38.5682 | 78.8765 | 4187 | 0.00048844 | 6.0994 | 6.0999 | -4.6671 | 2047.3149 | 16138.1037 | -0.0022796
205 |  | 38.5682 | 78.8742 | 4187 | 0.00048843 | 6.0999 | 6.1004 | -4.6671 | 2047.3741 | 16216.9779 | -0.0022796
206 |  | 38.5682 | 78.872 | 4187 | 0.00048842 | 6.1004 | 6.1009 | -4.6671 | 2047.4333 | 16295.8499 | -0.0022795
207 |  | 38.5682 | 78.8697 | 4187 | 0.0004884 | 6.1009 | 6.1014 | -4.6671 | 2047.4925 | 16374.7195 | -0.0022794
208 |  | 38.5682 | 78.8674 | 4187 | 0.00048839 | 6.1014 | 6.1019 | -4.6671 | 2047.5516 | 16453.5869 | -0.0022794
209 |  | 38.5682 | 78.8651 | 4187 | 0.00048837 | 6.1019 | 6.1024 | -4.6671 | 2047.6108 | 16532.452 | -0.0022793
210 |  | 38.5682 | 78.8628 | 4187 | 0.00048836 | 6.1024 | 6.1029 | -4.6671 | 2047.67 | 16611.3149 | -0.0022792
211 |  | 38.5682 | 78.8606 | 4187 | 0.00048835 | 6.1029 | 6.1034 | -4.6671 | 2047.7292 | 16690.1754 | -0.0022792
212 |  | 38.5682 | 78.8583 | 4187 | 0.00048833 | 6.1034 | 6.1038 | -4.6671 | 2047.7884 | 16769.0337 | -0.0022791
213 |  | 38.5682 | 78.856 | 4187 | 0.00048832 | 6.1038 | 6.1043 | -4.6671 | 2047.8475 | 16847.8897 | -0.002279
214 |  | 38.5682 | 78.8537 | 4187 | 0.0004883 | 6.1043 | 6.1048 | -4.6671 | 2047.9067 | 16926.7434 | -0.002279
215 |  | 38.5682 | 78.8514 | 4187 | 0.00048829 | 6.1048 | 6.1053 | -4.6671 | 2047.9659 | 17005.5949 | -0.0022789
216 |  | 38.5682 | 78.8492 | 4187 | 0.00048828 | 6.1053 | 6.1058 | -4.6671 | 2048.0251 | 17084.444 | -0.0022788
217 |  | 38.5682 | 78.8469 | 4187 | 0.00048826 | 6.1058 | 6.1063 | -4.6671 | 2048.0843 | 17163.2909 | -0.0022788
218 |  | 38.5682 | 78.8446 | 4187 | 0.00048825 | 6.1063 | 6.1068 | -4.6671 | 2048.1435 | 17242.1355 | -0.0022787
219 |  | 38.5682 | 78.8423 | 4187 | 0.00048823 | 6.1068 | 6.1073 | -4.6671 | 2048.2027 | 17320.9778 | -0.0022786
220 |  | 38.5682 | 78.84 | 4187 | 0.00048822 | 6.1073 | 6.1077 | -4.6671 | 2048.2619 | 17399.8179 | -0.0022786
221 |  | 38.5682 | 78.8378 | 4187 | 0.0004882 | 6.1077 | 6.1082 | -4.6671 | 2048.3211 | 17478.6557 | -0.0022785
222 |  | 38.5682 | 78.8355 | 4187 | 0.00048819 | 6.1082 | 6.1087 | -4.6671 | 2048.3803 | 17557.4911 | -0.0022784
223 |  | 38.5682 | 78.8332 | 4187 | 0.00048818 | 6.1087 | 6.1092 | -4.6671 | 2048.4395 | 17636.3244 | -0.0022784
224 |  | 38.5682 | 78.8309 | 4187 | 0.00048816 | 6.1092 | 6.1097 | -4.6671 | 2048.4987 | 17715.1553 | -0.0022783
225 |  | 38.5682 | 78.8287 | 4187 | 0.00048815 | 6.1097 | 6.1102 | -4.6671 | 2048.5579 | 17793.9839 | -0.0022782
226 |  | 38.5682 | 78.8264 | 4187 | 0.00048813 | 6.1102 | 6.1107 | -4.6671 | 2048.6171 | 17872.8103 | -0.0022782
227 |  | 38.5682 | 78.8241 | 4187 | 0.00048812 | 6.1107 | 6.1112 | -4.6671 | 2048.6763 | 17951.6344 | -0.0022781
228 |  | 38.5682 | 78.8218 | 4187 | 0.00048811 | 6.1112 | 6.1117 | -4.6671 | 2048.7355 | 18030.4562 | -0.002278
229 |  | 38.5682 | 78.8195 | 4187 | 0.00048809 | 6.1117 | 6.1121 | -4.6671 | 2048.7947 | 18109.2758 | -0.002278
230 |  | 38.5682 | 78.8173 | 4187 | 0.00048808 | 6.1121 | 6.1126 | -4.6671 | 2048.8539 | 18188.093 | -0.0022779
231 |  | 38.5682 | 78.815 | 4187 | 0.00048806 | 6.1126 | 6.1131 | -4.6671 | 2048.9132 | 18266.908 | -0.0022778
232 |  | 38.5682 | 78.8127 | 4187 | 0.00048805 | 6.1131 | 6.1136 | -4.6671 | 2048.9724 | 18345.7207 | -0.0022778
233 |  | 38.5682 | 78.8104 | 4187 | 0.00048804 | 6.1136 | 6.1141 | -4.6671 | 2049.0316 | 18424.5312 | -0.0022777
234 |  | 38.5682 | 78.8082 | 4187 | 0.00048802 | 6.1141 | 6.1146 | -4.6671 | 2049.0908 | 18503.3393 | -0.0022776
235 |  | 38.5682 | 78.8059 | 4187 | 0.00048801 | 6.1146 | 6.1151 | -4.6671 | 2049.15 | 18582.1452 | -0.0022776
236 |  | 38.5682 | 78.8036 | 4187 | 0.00048799 | 6.1151 | 6.1156 | -4.6671 | 2049.2093 | 18660.9488 | -0.0022775

## CLX315
|  |  | buis | verlies W/M | L /°C/sec
diam | wandikte |  | inhoud l/m |  | W/M
315 | 17.9 | 3.1416 | 61.2239 | 86.5074 | 4187
[8 empty] | J/sec/mtr | aantal mtr. | verlies
|  | buis | verlies W/M | L /°C/sec | verlies temp | begintemp | eindtemp | verlies | bij 1°C | totaal J/sec
|  | inhoud L |  | W/M | °C per M | °C | °C | per m°C | daling | aantal mtr
1 | 315 | 61.2239 | 86.5074 | 4187 | 0.00033747 | 6 | 6.0003 | -5.0887 | 2963.2641 | 86.5074 | -0.0017173
2 |  | 61.2239 | 86.5057 | 4187 | 0.00033746 | 6.0003 | 6.0007 | -5.0887 | 2963.323 | 173.0131 | -0.0017172
3 |  | 61.2239 | 86.504 | 4187 | 0.00033745 | 6.0007 | 6.001 | -5.0887 | 2963.3818 | 259.5171 | -0.0017172
4 |  | 61.2239 | 86.5023 | 4187 | 0.00033745 | 6.001 | 6.0013 | -5.0887 | 2963.4406 | 346.0193 | -0.0017171
5 |  | 61.2239 | 86.5005 | 4187 | 0.00033744 | 6.0013 | 6.0017 | -5.0887 | 2963.4995 | 432.5199 | -0.0017171
6 |  | 61.2239 | 86.4988 | 4187 | 0.00033743 | 6.0017 | 6.002 | -5.0887 | 2963.5583 | 519.0187 | -0.0017171
7 |  | 61.2239 | 86.4971 | 4187 | 0.00033743 | 6.002 | 6.0024 | -5.0887 | 2963.6171 | 605.5158 | -0.001717
8 |  | 61.2239 | 86.4954 | 4187 | 0.00033742 | 6.0024 | 6.0027 | -5.0887 | 2963.6759 | 692.0112 | -0.001717
9 |  | 61.2239 | 86.4937 | 4187 | 0.00033741 | 6.0027 | 6.003 | -5.0887 | 2963.7348 | 778.5049 | -0.001717
10 |  | 61.2239 | 86.492 | 4187 | 0.00033741 | 6.003 | 6.0034 | -5.0887 | 2963.7936 | 864.9968 | -0.0017169
11 |  | 61.2239 | 86.4902 | 4187 | 0.0003374 | 6.0034 | 6.0037 | -5.0887 | 2963.8524 | 951.4871 | -0.0017169
12 |  | 61.2239 | 86.4885 | 4187 | 0.00033739 | 6.0037 | 6.004 | -5.0887 | 2963.9113 | 1037.9756 | -0.0017169
13 |  | 61.2239 | 86.4868 | 4187 | 0.00033739 | 6.004 | 6.0044 | -5.0887 | 2963.9701 | 1124.4624 | -0.0017168
14 |  | 61.2239 | 86.4851 | 4187 | 0.00033738 | 6.0044 | 6.0047 | -5.0887 | 2964.029 | 1210.9475 | -0.0017168
15 |  | 61.2239 | 86.4834 | 4187 | 0.00033737 | 6.0047 | 6.0051 | -5.0887 | 2964.0878 | 1297.4308 | -0.0017168
16 |  | 61.2239 | 86.4817 | 4187 | 0.00033737 | 6.0051 | 6.0054 | -5.0887 | 2964.1466 | 1383.9125 | -0.0017167
17 |  | 61.2239 | 86.4799 | 4187 | 0.00033736 | 6.0054 | 6.0057 | -5.0887 | 2964.2055 | 1470.3924 | -0.0017167
18 |  | 61.2239 | 86.4782 | 4187 | 0.00033735 | 6.0057 | 6.0061 | -5.0887 | 2964.2643 | 1556.8706 | -0.0017167
19 |  | 61.2239 | 86.4765 | 4187 | 0.00033735 | 6.0061 | 6.0064 | -5.0887 | 2964.3232 | 1643.3472 | -0.0017166
20 |  | 61.2239 | 86.4748 | 4187 | 0.00033734 | 6.0064 | 6.0067 | -5.0887 | 2964.382 | 1729.8219 | -0.0017166
21 |  | 61.2239 | 86.4731 | 4187 | 0.00033733 | 6.0067 | 6.0071 | -5.0887 | 2964.4409 | 1816.295 | -0.0017166
22 |  | 61.2239 | 86.4714 | 4187 | 0.00033733 | 6.0071 | 6.0074 | -5.0887 | 2964.4997 | 1902.7664 | -0.0017165
23 |  | 61.2239 | 86.4696 | 4187 | 0.00033732 | 6.0074 | 6.0078 | -5.0887 | 2964.5586 | 1989.236 | -0.0017165
24 |  | 61.2239 | 86.4679 | 4187 | 0.00033731 | 6.0078 | 6.0081 | -5.0887 | 2964.6174 | 2075.7039 | -0.0017165
25 |  | 61.2239 | 86.4662 | 4187 | 0.0003373 | 6.0081 | 6.0084 | -5.0887 | 2964.6763 | 2162.1701 | -0.0017164
26 |  | 61.2239 | 86.4645 | 4187 | 0.0003373 | 6.0084 | 6.0088 | -5.0887 | 2964.7351 | 2248.6346 | -0.0017164
27 |  | 61.2239 | 86.4628 | 4187 | 0.00033729 | 6.0088 | 6.0091 | -5.0887 | 2964.794 | 2335.0974 | -0.0017164
28 |  | 61.2239 | 86.4611 | 4187 | 0.00033728 | 6.0091 | 6.0094 | -5.0887 | 2964.8528 | 2421.5584 | -0.0017163
29 |  | 61.2239 | 86.4593 | 4187 | 0.00033728 | 6.0094 | 6.0098 | -5.0887 | 2964.9117 | 2508.0178 | -0.0017163
30 |  | 61.2239 | 86.4576 | 4187 | 0.00033727 | 6.0098 | 6.0101 | -5.0887 | 2964.9705 | 2594.4754 | -0.0017163
31 |  | 61.2239 | 86.4559 | 4187 | 0.00033726 | 6.0101 | 6.0105 | -5.0887 | 2965.0294 | 2680.9313 | -0.0017162
32 |  | 61.2239 | 86.4542 | 4187 | 0.00033726 | 6.0105 | 6.0108 | -5.0887 | 2965.0883 | 2767.3855 | -0.0017162
33 |  | 61.2239 | 86.4525 | 4187 | 0.00033725 | 6.0108 | 6.0111 | -5.0887 | 2965.1471 | 2853.838 | -0.0017162
34 |  | 61.2239 | 86.4508 | 4187 | 0.00033724 | 6.0111 | 6.0115 | -5.0887 | 2965.206 | 2940.2887 | -0.0017161
35 |  | 61.2239 | 86.449 | 4187 | 0.00033724 | 6.0115 | 6.0118 | -5.0887 | 2965.2648 | 3026.7378 | -0.0017161
36 |  | 61.2239 | 86.4473 | 4187 | 0.00033723 | 6.0118 | 6.0121 | -5.0887 | 2965.3237 | 3113.1851 | -0.0017161
37 |  | 61.2239 | 86.4456 | 4187 | 0.00033722 | 6.0121 | 6.0125 | -5.0887 | 2965.3826 | 3199.6307 | -0.001716
38 |  | 61.2239 | 86.4439 | 4187 | 0.00033722 | 6.0125 | 6.0128 | -5.0887 | 2965.4414 | 3286.0746 | -0.001716
39 |  | 61.2239 | 86.4422 | 4187 | 0.00033721 | 6.0128 | 6.0132 | -5.0887 | 2965.5003 | 3372.5168 | -0.001716
40 |  | 61.2239 | 86.4405 | 4187 | 0.0003372 | 6.0132 | 6.0135 | -5.0887 | 2965.5592 | 3458.9572 | -0.0017159
41 |  | 61.2239 | 86.4387 | 4187 | 0.0003372 | 6.0135 | 6.0138 | -5.0887 | 2965.618 | 3545.396 | -0.0017159
42 |  | 61.2239 | 86.437 | 4187 | 0.00033719 | 6.0138 | 6.0142 | -5.0887 | 2965.6769 | 3631.833 | -0.0017159
43 |  | 61.2239 | 86.4353 | 4187 | 0.00033718 | 6.0142 | 6.0145 | -5.0887 | 2965.7358 | 3718.2683 | -0.0017158
44 |  | 61.2239 | 86.4336 | 4187 | 0.00033718 | 6.0145 | 6.0148 | -5.0887 | 2965.7947 | 3804.7019 | -0.0017158
45 |  | 61.2239 | 86.4319 | 4187 | 0.00033717 | 6.0148 | 6.0152 | -5.0887 | 2965.8535 | 3891.1338 | -0.0017158
46 |  | 61.2239 | 86.4302 | 4187 | 0.00033716 | 6.0152 | 6.0155 | -5.0887 | 2965.9124 | 3977.564 | -0.0017157
47 |  | 61.2239 | 86.4285 | 4187 | 0.00033716 | 6.0155 | 6.0159 | -5.0887 | 2965.9713 | 4063.9924 | -0.0017157
48 |  | 61.2239 | 86.4267 | 4187 | 0.00033715 | 6.0159 | 6.0162 | -5.0887 | 2966.0302 | 4150.4192 | -0.0017157
49 |  | 61.2239 | 86.425 | 4187 | 0.00033714 | 6.0162 | 6.0165 | -5.0887 | 2966.089 | 4236.8442 | -0.0017156
50 |  | 61.2239 | 86.4233 | 4187 | 0.00033714 | 6.0165 | 6.0169 | -5.0887 | 2966.1479 | 4323.2675 | -0.0017156
51 |  | 61.2239 | 86.4216 | 4187 | 0.00033713 | 6.0169 | 6.0172 | -5.0887 | 2966.2068 | 4409.6891 | -0.0017155
52 |  | 61.2239 | 86.4199 | 4187 | 0.00033712 | 6.0172 | 6.0175 | -5.0887 | 2966.2657 | 4496.1089 | -0.0017155
53 |  | 61.2239 | 86.4182 | 4187 | 0.00033712 | 6.0175 | 6.0179 | -5.0887 | 2966.3246 | 4582.5271 | -0.0017155
54 |  | 61.2239 | 86.4164 | 4187 | 0.00033711 | 6.0179 | 6.0182 | -5.0887 | 2966.3835 | 4668.9435 | -0.0017154
55 |  | 61.2239 | 86.4147 | 4187 | 0.0003371 | 6.0182 | 6.0186 | -5.0887 | 2966.4424 | 4755.3583 | -0.0017154
56 |  | 61.2239 | 86.413 | 4187 | 0.0003371 | 6.0186 | 6.0189 | -5.0887 | 2966.5012 | 4841.7713 | -0.0017154
57 |  | 61.2239 | 86.4113 | 4187 | 0.00033709 | 6.0189 | 6.0192 | -5.0887 | 2966.5601 | 4928.1826 | -0.0017153
58 |  | 61.2239 | 86.4096 | 4187 | 0.00033708 | 6.0192 | 6.0196 | -5.0887 | 2966.619 | 5014.5921 | -0.0017153
59 |  | 61.2239 | 86.4079 | 4187 | 0.00033708 | 6.0196 | 6.0199 | -5.0887 | 2966.6779 | 5101 | -0.0017153
60 |  | 61.2239 | 86.4061 | 4187 | 0.00033707 | 6.0199 | 6.0202 | -5.0887 | 2966.7368 | 5187.4062 | -0.0017152
61 |  | 61.2239 | 86.4044 | 4187 | 0.00033706 | 6.0202 | 6.0206 | -5.0887 | 2966.7957 | 5273.8106 | -0.0017152
62 |  | 61.2239 | 86.4027 | 4187 | 0.00033706 | 6.0206 | 6.0209 | -5.0887 | 2966.8546 | 5360.2133 | -0.0017152
63 |  | 61.2239 | 86.401 | 4187 | 0.00033705 | 6.0209 | 6.0212 | -5.0887 | 2966.9135 | 5446.6143 | -0.0017151
64 |  | 61.2239 | 86.3993 | 4187 | 0.00033704 | 6.0212 | 6.0216 | -5.0887 | 2966.9724 | 5533.0136 | -0.0017151
65 |  | 61.2239 | 86.3976 | 4187 | 0.00033704 | 6.0216 | 6.0219 | -5.0887 | 2967.0313 | 5619.4112 | -0.0017151
66 |  | 61.2239 | 86.3959 | 4187 | 0.00033703 | 6.0219 | 6.0223 | -5.0887 | 2967.0902 | 5705.807 | -0.001715
67 |  | 61.2239 | 86.3941 | 4187 | 0.00033702 | 6.0223 | 6.0226 | -5.0887 | 2967.1491 | 5792.2012 | -0.001715
68 |  | 61.2239 | 86.3924 | 4187 | 0.00033702 | 6.0226 | 6.0229 | -5.0887 | 2967.208 | 5878.5936 | -0.001715
69 |  | 61.2239 | 86.3907 | 4187 | 0.00033701 | 6.0229 | 6.0233 | -5.0887 | 2967.2669 | 5964.9843 | -0.0017149
70 |  | 61.2239 | 86.389 | 4187 | 0.000337 | 6.0233 | 6.0236 | -5.0887 | 2967.3258 | 6051.3733 | -0.0017149
71 |  | 61.2239 | 86.3873 | 4187 | 0.000337 | 6.0236 | 6.0239 | -5.0887 | 2967.3847 | 6137.7606 | -0.0017149
72 |  | 61.2239 | 86.3856 | 4187 | 0.00033699 | 6.0239 | 6.0243 | -5.0887 | 2967.4436 | 6224.1462 | -0.0017148
73 |  | 61.2239 | 86.3839 | 4187 | 0.00033698 | 6.0243 | 6.0246 | -5.0887 | 2967.5025 | 6310.53 | -0.0017148
74 |  | 61.2239 | 86.3821 | 4187 | 0.00033698 | 6.0246 | 6.025 | -5.0887 | 2967.5614 | 6396.9122 | -0.0017148
75 |  | 61.2239 | 86.3804 | 4187 | 0.00033697 | 6.025 | 6.0253 | -5.0887 | 2967.6203 | 6483.2926 | -0.0017147
76 |  | 61.2239 | 86.3787 | 4187 | 0.00033696 | 6.0253 | 6.0256 | -5.0887 | 2967.6792 | 6569.6713 | -0.0017147
77 |  | 61.2239 | 86.377 | 4187 | 0.00033696 | 6.0256 | 6.026 | -5.0887 | 2967.7382 | 6656.0483 | -0.0017147
78 |  | 61.2239 | 86.3753 | 4187 | 0.00033695 | 6.026 | 6.0263 | -5.0887 | 2967.7971 | 6742.4236 | -0.0017146
79 |  | 61.2239 | 86.3736 | 4187 | 0.00033694 | 6.0263 | 6.0266 | -5.0887 | 2967.856 | 6828.7971 | -0.0017146
80 |  | 61.2239 | 86.3719 | 4187 | 0.00033694 | 6.0266 | 6.027 | -5.0887 | 2967.9149 | 6915.169 | -0.0017146
81 |  | 61.2239 | 86.3701 | 4187 | 0.00033693 | 6.027 | 6.0273 | -5.0887 | 2967.9738 | 7001.5391 | -0.0017145
82 |  | 61.2239 | 86.3684 | 4187 | 0.00033692 | 6.0273 | 6.0276 | -5.0887 | 2968.0327 | 7087.9076 | -0.0017145
83 |  | 61.2239 | 86.3667 | 4187 | 0.00033692 | 6.0276 | 6.028 | -5.0887 | 2968.0917 | 7174.2743 | -0.0017145
84 |  | 61.2239 | 86.365 | 4187 | 0.00033691 | 6.028 | 6.0283 | -5.0887 | 2968.1506 | 7260.6393 | -0.0017144
85 |  | 61.2239 | 86.3633 | 4187 | 0.0003369 | 6.0283 | 6.0287 | -5.0887 | 2968.2095 | 7347.0025 | -0.0017144
86 |  | 61.2239 | 86.3616 | 4187 | 0.0003369 | 6.0287 | 6.029 | -5.0887 | 2968.2684 | 7433.3641 | -0.0017144
87 |  | 61.2239 | 86.3598 | 4187 | 0.00033689 | 6.029 | 6.0293 | -5.0887 | 2968.3273 | 7519.7239 | -0.0017143
88 |  | 61.2239 | 86.3581 | 4187 | 0.00033688 | 6.0293 | 6.0297 | -5.0887 | 2968.3863 | 7606.0821 | -0.0017143
89 |  | 61.2239 | 86.3564 | 4187 | 0.00033688 | 6.0297 | 6.03 | -5.0887 | 2968.4452 | 7692.4385 | -0.0017143
90 |  | 61.2239 | 86.3547 | 4187 | 0.00033687 | 6.03 | 6.0303 | -5.0887 | 2968.5041 | 7778.7932 | -0.0017142
91 |  | 61.2239 | 86.353 | 4187 | 0.00033686 | 6.0303 | 6.0307 | -5.0887 | 2968.563 | 7865.1462 | -0.0017142
92 |  | 61.2239 | 86.3513 | 4187 | 0.00033686 | 6.0307 | 6.031 | -5.0887 | 2968.622 | 7951.4975 | -0.0017142
93 |  | 61.2239 | 86.3496 | 4187 | 0.00033685 | 6.031 | 6.0314 | -5.0887 | 2968.6809 | 8037.847 | -0.0017141
94 |  | 61.2239 | 86.3479 | 4187 | 0.00033684 | 6.0314 | 6.0317 | -5.0887 | 2968.7398 | 8124.1949 | -0.0017141
95 |  | 61.2239 | 86.3461 | 4187 | 0.00033684 | 6.0317 | 6.032 | -5.0887 | 2968.7988 | 8210.541 | -0.0017141
96 |  | 61.2239 | 86.3444 | 4187 | 0.00033683 | 6.032 | 6.0324 | -5.0887 | 2968.8577 | 8296.8855 | -0.001714
97 |  | 61.2239 | 86.3427 | 4187 | 0.00033682 | 6.0324 | 6.0327 | -5.0887 | 2968.9166 | 8383.2282 | -0.001714
98 |  | 61.2239 | 86.341 | 4187 | 0.00033682 | 6.0327 | 6.033 | -5.0887 | 2968.9756 | 8469.5692 | -0.0017139
99 |  | 61.2239 | 86.3393 | 4187 | 0.00033681 | 6.033 | 6.0334 | -5.0887 | 2969.0345 | 8555.9084 | -0.0017139
100 |  | 61.2239 | 86.3376 | 4187 | 0.0003368 | 6.0334 | 6.0337 | -5.0887 | 2969.0935 | 8642.246 | -0.0017139
101 |  | 61.2239 | 86.3359 | 4187 | 0.0003368 | 6.0337 | 6.0341 | -5.0887 | 2969.1524 | 8728.5819 | -0.0017138
102 |  | 61.2239 | 86.3341 | 4187 | 0.00033679 | 6.0341 | 6.0344 | -5.0887 | 2969.2113 | 8814.916 | -0.0017138
103 |  | 61.2239 | 86.3324 | 4187 | 0.00033678 | 6.0344 | 6.0347 | -5.0887 | 2969.2703 | 8901.2484 | -0.0017138
104 |  | 61.2239 | 86.3307 | 4187 | 0.00033678 | 6.0347 | 6.0351 | -5.0887 | 2969.3292 | 8987.5791 | -0.0017137
105 |  | 61.2239 | 86.329 | 4187 | 0.00033677 | 6.0351 | 6.0354 | -5.0887 | 2969.3882 | 9073.9081 | -0.0017137
106 |  | 61.2239 | 86.3273 | 4187 | 0.00033676 | 6.0354 | 6.0357 | -5.0887 | 2969.4471 | 9160.2354 | -0.0017137
107 |  | 61.2239 | 86.3256 | 4187 | 0.00033676 | 6.0357 | 6.0361 | -5.0887 | 2969.5061 | 9246.561 | -0.0017136
108 |  | 61.2239 | 86.3239 | 4187 | 0.00033675 | 6.0361 | 6.0364 | -5.0887 | 2969.565 | 9332.8848 | -0.0017136
109 |  | 61.2239 | 86.3221 | 4187 | 0.00033674 | 6.0364 | 6.0367 | -5.0887 | 2969.624 | 9419.207 | -0.0017136
110 |  | 61.2239 | 86.3204 | 4187 | 0.00033674 | 6.0367 | 6.0371 | -5.0887 | 2969.6829 | 9505.5274 | -0.0017135
111 |  | 61.2239 | 86.3187 | 4187 | 0.00033673 | 6.0371 | 6.0374 | -5.0887 | 2969.7419 | 9591.8461 | -0.0017135
112 |  | 61.2239 | 86.317 | 4187 | 0.00033672 | 6.0374 | 6.0378 | -5.0887 | 2969.8008 | 9678.1631 | -0.0017135
113 |  | 61.2239 | 86.3153 | 4187 | 0.00033672 | 6.0378 | 6.0381 | -5.0887 | 2969.8598 | 9764.4784 | -0.0017134
114 |  | 61.2239 | 86.3136 | 4187 | 0.00033671 | 6.0381 | 6.0384 | -5.0887 | 2969.9187 | 9850.792 | -0.0017134
115 |  | 61.2239 | 86.3119 | 4187 | 0.0003367 | 6.0384 | 6.0388 | -5.0887 | 2969.9777 | 9937.1038 | -0.0017134
116 |  | 61.2239 | 86.3101 | 4187 | 0.0003367 | 6.0388 | 6.0391 | -5.0887 | 2970.0366 | 10023.414 | -0.0017133
117 |  | 61.2239 | 86.3084 | 4187 | 0.00033669 | 6.0391 | 6.0394 | -5.0887 | 2970.0956 | 10109.7224 | -0.0017133
118 |  | 61.2239 | 86.3067 | 4187 | 0.00033668 | 6.0394 | 6.0398 | -5.0887 | 2970.1546 | 10196.0292 | -0.0017133
119 |  | 61.2239 | 86.305 | 4187 | 0.00033668 | 6.0398 | 6.0401 | -5.0887 | 2970.2135 | 10282.3342 | -0.0017132
120 |  | 61.2239 | 86.3033 | 4187 | 0.00033667 | 6.0401 | 6.0404 | -5.0887 | 2970.2725 | 10368.6375 | -0.0017132
121 |  | 61.2239 | 86.3016 | 4187 | 0.00033666 | 6.0404 | 6.0408 | -5.0887 | 2970.3315 | 10454.939 | -0.0017132
122 |  | 61.2239 | 86.2999 | 4187 | 0.00033666 | 6.0408 | 6.0411 | -5.0887 | 2970.3904 | 10541.2389 | -0.0017131
123 |  | 61.2239 | 86.2982 | 4187 | 0.00033665 | 6.0411 | 6.0415 | -5.0887 | 2970.4494 | 10627.5371 | -0.0017131
124 |  | 61.2239 | 86.2964 | 4187 | 0.00033664 | 6.0415 | 6.0418 | -5.0887 | 2970.5084 | 10713.8335 | -0.0017131
125 |  | 61.2239 | 86.2947 | 4187 | 0.00033664 | 6.0418 | 6.0421 | -5.0887 | 2970.5673 | 10800.1282 | -0.001713
126 |  | 61.2239 | 86.293 | 4187 | 0.00033663 | 6.0421 | 6.0425 | -5.0887 | 2970.6263 | 10886.4212 | -0.001713
127 |  | 61.2239 | 86.2913 | 4187 | 0.00033662 | 6.0425 | 6.0428 | -5.0887 | 2970.6853 | 10972.7126 | -0.001713
128 |  | 61.2239 | 86.2896 | 4187 | 0.00033662 | 6.0428 | 6.0431 | -5.0887 | 2970.7442 | 11059.0021 | -0.0017129
129 |  | 61.2239 | 86.2879 | 4187 | 0.00033661 | 6.0431 | 6.0435 | -5.0887 | 2970.8032 | 11145.29 | -0.0017129
130 |  | 61.2239 | 86.2862 | 4187 | 0.0003366 | 6.0435 | 6.0438 | -5.0887 | 2970.8622 | 11231.5762 | -0.0017129
131 |  | 61.2239 | 86.2845 | 4187 | 0.0003366 | 6.0438 | 6.0442 | -5.0887 | 2970.9212 | 11317.8606 | -0.0017128
132 |  | 61.2239 | 86.2827 | 4187 | 0.00033659 | 6.0442 | 6.0445 | -5.0887 | 2970.9801 | 11404.1434 | -0.0017128
133 |  | 61.2239 | 86.281 | 4187 | 0.00033658 | 6.0445 | 6.0448 | -5.0887 | 2971.0391 | 11490.4244 | -0.0017128
134 |  | 61.2239 | 86.2793 | 4187 | 0.00033658 | 6.0448 | 6.0452 | -5.0887 | 2971.0981 | 11576.7037 | -0.0017127
135 |  | 61.2239 | 86.2776 | 4187 | 0.00033657 | 6.0452 | 6.0455 | -5.0887 | 2971.1571 | 11662.9813 | -0.0017127
136 |  | 61.2239 | 86.2759 | 4187 | 0.00033656 | 6.0455 | 6.0458 | -5.0887 | 2971.2161 | 11749.2572 | -0.0017127
137 |  | 61.2239 | 86.2742 | 4187 | 0.00033656 | 6.0458 | 6.0462 | -5.0887 | 2971.275 | 11835.5314 | -0.0017126
138 |  | 61.2239 | 86.2725 | 4187 | 0.00033655 | 6.0462 | 6.0465 | -5.0887 | 2971.334 | 11921.8038 | -0.0017126
139 |  | 61.2239 | 86.2708 | 4187 | 0.00033654 | 6.0465 | 6.0468 | -5.0887 | 2971.393 | 12008.0746 | -0.0017126
140 |  | 61.2239 | 86.269 | 4187 | 0.00033654 | 6.0468 | 6.0472 | -5.0887 | 2971.452 | 12094.3436 | -0.0017125
141 |  | 61.2239 | 86.2673 | 4187 | 0.00033653 | 6.0472 | 6.0475 | -5.0887 | 2971.511 | 12180.611 | -0.0017125
142 |  | 61.2239 | 86.2656 | 4187 | 0.00033652 | 6.0475 | 6.0479 | -5.0887 | 2971.57 | 12266.8766 | -0.0017125
143 |  | 61.2239 | 86.2639 | 4187 | 0.00033652 | 6.0479 | 6.0482 | -5.0887 | 2971.629 | 12353.1405 | -0.0017124
144 |  | 61.2239 | 86.2622 | 4187 | 0.00033651 | 6.0482 | 6.0485 | -5.0887 | 2971.6879 | 12439.4027 | -0.0017124
145 |  | 61.2239 | 86.2605 | 4187 | 0.0003365 | 6.0485 | 6.0489 | -5.0887 | 2971.7469 | 12525.6631 | -0.0017124
146 |  | 61.2239 | 86.2588 | 4187 | 0.0003365 | 6.0489 | 6.0492 | -5.0887 | 2971.8059 | 12611.9219 | -0.0017123
147 |  | 61.2239 | 86.2571 | 4187 | 0.00033649 | 6.0492 | 6.0495 | -5.0887 | 2971.8649 | 12698.1789 | -0.0017123
148 |  | 61.2239 | 86.2553 | 4187 | 0.00033648 | 6.0495 | 6.0499 | -5.0887 | 2971.9239 | 12784.4343 | -0.0017122
149 |  | 61.2239 | 86.2536 | 4187 | 0.00033648 | 6.0499 | 6.0502 | -5.0887 | 2971.9829 | 12870.6879 | -0.0017122
150 |  | 61.2239 | 86.2519 | 4187 | 0.00033647 | 6.0502 | 6.0505 | -5.0887 | 2972.0419 | 12956.9398 | -0.0017122
151 |  | 61.2239 | 86.2502 | 4187 | 0.00033646 | 6.0505 | 6.0509 | -5.0887 | 2972.1009 | 13043.19 | -0.0017121
152 |  | 61.2239 | 86.2485 | 4187 | 0.00033646 | 6.0509 | 6.0512 | -5.0887 | 2972.1599 | 13129.4385 | -0.0017121
153 |  | 61.2239 | 86.2468 | 4187 | 0.00033645 | 6.0512 | 6.0516 | -5.0887 | 2972.2189 | 13215.6853 | -0.0017121
154 |  | 61.2239 | 86.2451 | 4187 | 0.00033644 | 6.0516 | 6.0519 | -5.0887 | 2972.2779 | 13301.9304 | -0.001712
155 |  | 61.2239 | 86.2434 | 4187 | 0.00033644 | 6.0519 | 6.0522 | -5.0887 | 2972.3369 | 13388.1737 | -0.001712
156 |  | 61.2239 | 86.2416 | 4187 | 0.00033643 | 6.0522 | 6.0526 | -5.0887 | 2972.3959 | 13474.4153 | -0.001712
157 |  | 61.2239 | 86.2399 | 4187 | 0.00033642 | 6.0526 | 6.0529 | -5.0887 | 2972.4549 | 13560.6553 | -0.0017119
158 |  | 61.2239 | 86.2382 | 4187 | 0.00033642 | 6.0529 | 6.0532 | -5.0887 | 2972.5139 | 13646.8935 | -0.0017119
159 |  | 61.2239 | 86.2365 | 4187 | 0.00033641 | 6.0532 | 6.0536 | -5.0887 | 2972.5729 | 13733.13 | -0.0017119
160 |  | 61.2239 | 86.2348 | 4187 | 0.0003364 | 6.0536 | 6.0539 | -5.0887 | 2972.632 | 13819.3648 | -0.0017118
161 |  | 61.2239 | 86.2331 | 4187 | 0.0003364 | 6.0539 | 6.0542 | -5.0887 | 2972.691 | 13905.5979 | -0.0017118
162 |  | 61.2239 | 86.2314 | 4187 | 0.00033639 | 6.0542 | 6.0546 | -5.0887 | 2972.75 | 13991.8292 | -0.0017118
163 |  | 61.2239 | 86.2297 | 4187 | 0.00033638 | 6.0546 | 6.0549 | -5.0887 | 2972.809 | 14078.0589 | -0.0017117
164 |  | 61.2239 | 86.2279 | 4187 | 0.00033638 | 6.0549 | 6.0553 | -5.0887 | 2972.868 | 14164.2869 | -0.0017117
165 |  | 61.2239 | 86.2262 | 4187 | 0.00033637 | 6.0553 | 6.0556 | -5.0887 | 2972.927 | 14250.5131 | -0.0017117
166 |  | 61.2239 | 86.2245 | 4187 | 0.00033636 | 6.0556 | 6.0559 | -5.0887 | 2972.986 | 14336.7376 | -0.0017116
167 |  | 61.2239 | 86.2228 | 4187 | 0.00033636 | 6.0559 | 6.0563 | -5.0887 | 2973.0451 | 14422.9604 | -0.0017116
168 |  | 61.2239 | 86.2211 | 4187 | 0.00033635 | 6.0563 | 6.0566 | -5.0887 | 2973.1041 | 14509.1815 | -0.0017116
169 |  | 61.2239 | 86.2194 | 4187 | 0.00033634 | 6.0566 | 6.0569 | -5.0887 | 2973.1631 | 14595.4009 | -0.0017115
170 |  | 61.2239 | 86.2177 | 4187 | 0.00033634 | 6.0569 | 6.0573 | -5.0887 | 2973.2221 | 14681.6186 | -0.0017115
171 |  | 61.2239 | 86.216 | 4187 | 0.00033633 | 6.0573 | 6.0576 | -5.0887 | 2973.2811 | 14767.8346 | -0.0017115
172 |  | 61.2239 | 86.2143 | 4187 | 0.00033632 | 6.0576 | 6.0579 | -5.0887 | 2973.3402 | 14854.0488 | -0.0017114
173 |  | 61.2239 | 86.2125 | 4187 | 0.00033632 | 6.0579 | 6.0583 | -5.0887 | 2973.3992 | 14940.2613 | -0.0017114
174 |  | 61.2239 | 86.2108 | 4187 | 0.00033631 | 6.0583 | 6.0586 | -5.0887 | 2973.4582 | 15026.4722 | -0.0017114
175 |  | 61.2239 | 86.2091 | 4187 | 0.0003363 | 6.0586 | 6.059 | -5.0887 | 2973.5172 | 15112.6813 | -0.0017113
176 |  | 61.2239 | 86.2074 | 4187 | 0.0003363 | 6.059 | 6.0593 | -5.0887 | 2973.5763 | 15198.8887 | -0.0017113
177 |  | 61.2239 | 86.2057 | 4187 | 0.00033629 | 6.0593 | 6.0596 | -5.0887 | 2973.6353 | 15285.0944 | -0.0017113
178 |  | 61.2239 | 86.204 | 4187 | 0.00033628 | 6.0596 | 6.06 | -5.0887 | 2973.6943 | 15371.2984 | -0.0017112
179 |  | 61.2239 | 86.2023 | 4187 | 0.00033628 | 6.06 | 6.0603 | -5.0887 | 2973.7534 | 15457.5007 | -0.0017112
180 |  | 61.2239 | 86.2006 | 4187 | 0.00033627 | 6.0603 | 6.0606 | -5.0887 | 2973.8124 | 15543.7012 | -0.0017112
181 |  | 61.2239 | 86.1989 | 4187 | 0.00033626 | 6.0606 | 6.061 | -5.0887 | 2973.8714 | 15629.9001 | -0.0017111
182 |  | 61.2239 | 86.1971 | 4187 | 0.00033626 | 6.061 | 6.0613 | -5.0887 | 2973.9305 | 15716.0972 | -0.0017111
183 |  | 61.2239 | 86.1954 | 4187 | 0.00033625 | 6.0613 | 6.0616 | -5.0887 | 2973.9895 | 15802.2926 | -0.0017111
184 |  | 61.2239 | 86.1937 | 4187 | 0.00033624 | 6.0616 | 6.062 | -5.0887 | 2974.0485 | 15888.4864 | -0.001711
185 |  | 61.2239 | 86.192 | 4187 | 0.00033624 | 6.062 | 6.0623 | -5.0887 | 2974.1076 | 15974.6784 | -0.001711
186 |  | 61.2239 | 86.1903 | 4187 | 0.00033623 | 6.0623 | 6.0627 | -5.0887 | 2974.1666 | 16060.8687 | -0.001711
187 |  | 61.2239 | 86.1886 | 4187 | 0.00033622 | 6.0627 | 6.063 | -5.0887 | 2974.2257 | 16147.0573 | -0.0017109
188 |  | 61.2239 | 86.1869 | 4187 | 0.00033622 | 6.063 | 6.0633 | -5.0887 | 2974.2847 | 16233.2441 | -0.0017109
189 |  | 61.2239 | 86.1852 | 4187 | 0.00033621 | 6.0633 | 6.0637 | -5.0887 | 2974.3437 | 16319.4293 | -0.0017109
190 |  | 61.2239 | 86.1835 | 4187 | 0.0003362 | 6.0637 | 6.064 | -5.0887 | 2974.4028 | 16405.6127 | -0.0017108
191 |  | 61.2239 | 86.1817 | 4187 | 0.0003362 | 6.064 | 6.0643 | -5.0887 | 2974.4618 | 16491.7945 | -0.0017108
192 |  | 61.2239 | 86.18 | 4187 | 0.00033619 | 6.0643 | 6.0647 | -5.0887 | 2974.5209 | 16577.9745 | -0.0017108
193 |  | 61.2239 | 86.1783 | 4187 | 0.00033618 | 6.0647 | 6.065 | -5.0887 | 2974.5799 | 16664.1528 | -0.0017107
194 |  | 61.2239 | 86.1766 | 4187 | 0.00033618 | 6.065 | 6.0653 | -5.0887 | 2974.639 | 16750.3295 | -0.0017107
195 |  | 61.2239 | 86.1749 | 4187 | 0.00033617 | 6.0653 | 6.0657 | -5.0887 | 2974.698 | 16836.5044 | -0.0017107
196 |  | 61.2239 | 86.1732 | 4187 | 0.00033616 | 6.0657 | 6.066 | -5.0887 | 2974.7571 | 16922.6775 | -0.0017106
197 |  | 61.2239 | 86.1715 | 4187 | 0.00033616 | 6.066 | 6.0664 | -5.0887 | 2974.8161 | 17008.849 | -0.0017106
198 |  | 61.2239 | 86.1698 | 4187 | 0.00033615 | 6.0664 | 6.0667 | -5.0887 | 2974.8752 | 17095.0188 | -0.0017105
199 |  | 61.2239 | 86.1681 | 4187 | 0.00033614 | 6.0667 | 6.067 | -5.0887 | 2974.9342 | 17181.1868 | -0.0017105
200 |  | 61.2239 | 86.1663 | 4187 | 0.00033614 | 6.067 | 6.0674 | -5.0887 | 2974.9933 | 17267.3532 | -0.0017105
201 |  | 61.2239 | 86.1646 | 4187 | 0.00033613 | 6.0674 | 6.0677 | -5.0887 | 2975.0524 | 17353.5178 | -0.0017104
202 |  | 61.2239 | 86.1629 | 4187 | 0.00033612 | 6.0677 | 6.068 | -5.0887 | 2975.1114 | 17439.6808 | -0.0017104
203 |  | 61.2239 | 86.1612 | 4187 | 0.00033612 | 6.068 | 6.0684 | -5.0887 | 2975.1705 | 17525.842 | -0.0017104
204 |  | 61.2239 | 86.1595 | 4187 | 0.00033611 | 6.0684 | 6.0687 | -5.0887 | 2975.2295 | 17612.0015 | -0.0017103
205 |  | 61.2239 | 86.1578 | 4187 | 0.0003361 | 6.0687 | 6.069 | -5.0887 | 2975.2886 | 17698.1593 | -0.0017103
206 |  | 61.2239 | 86.1561 | 4187 | 0.0003361 | 6.069 | 6.0694 | -5.0887 | 2975.3477 | 17784.3154 | -0.0017103
207 |  | 61.2239 | 86.1544 | 4187 | 0.00033609 | 6.0694 | 6.0697 | -5.0887 | 2975.4067 | 17870.4697 | -0.0017102
208 |  | 61.2239 | 86.1527 | 4187 | 0.00033608 | 6.0697 | 6.07 | -5.0887 | 2975.4658 | 17956.6224 | -0.0017102
209 |  | 61.2239 | 86.151 | 4187 | 0.00033608 | 6.07 | 6.0704 | -5.0887 | 2975.5249 | 18042.7733 | -0.0017102
210 |  | 61.2239 | 86.1492 | 4187 | 0.00033607 | 6.0704 | 6.0707 | -5.0887 | 2975.5839 | 18128.9226 | -0.0017101
211 |  | 61.2239 | 86.1475 | 4187 | 0.00033606 | 6.0707 | 6.0711 | -5.0887 | 2975.643 | 18215.0701 | -0.0017101
212 |  | 61.2239 | 86.1458 | 4187 | 0.00033606 | 6.0711 | 6.0714 | -5.0887 | 2975.7021 | 18301.2159 | -0.0017101
213 |  | 61.2239 | 86.1441 | 4187 | 0.00033605 | 6.0714 | 6.0717 | -5.0887 | 2975.7611 | 18387.3601 | -0.00171
214 |  | 61.2239 | 86.1424 | 4187 | 0.00033604 | 6.0717 | 6.0721 | -5.0887 | 2975.8202 | 18473.5025 | -0.00171
215 |  | 61.2239 | 86.1407 | 4187 | 0.00033604 | 6.0721 | 6.0724 | -5.0887 | 2975.8793 | 18559.6431 | -0.00171
216 |  | 61.2239 | 86.139 | 4187 | 0.00033603 | 6.0724 | 6.0727 | -5.0887 | 2975.9384 | 18645.7821 | -0.0017099
217 |  | 61.2239 | 86.1373 | 4187 | 0.00033602 | 6.0727 | 6.0731 | -5.0887 | 2975.9974 | 18731.9194 | -0.0017099
218 |  | 61.2239 | 86.1356 | 4187 | 0.00033602 | 6.0731 | 6.0734 | -5.0887 | 2976.0565 | 18818.055 | -0.0017099
219 |  | 61.2239 | 86.1339 | 4187 | 0.00033601 | 6.0734 | 6.0737 | -5.0887 | 2976.1156 | 18904.1888 | -0.0017098
220 |  | 61.2239 | 86.1321 | 4187 | 0.000336 | 6.0737 | 6.0741 | -5.0887 | 2976.1747 | 18990.321 | -0.0017098
221 |  | 61.2239 | 86.1304 | 4187 | 0.000336 | 6.0741 | 6.0744 | -5.0887 | 2976.2338 | 19076.4514 | -0.0017098
222 |  | 61.2239 | 86.1287 | 4187 | 0.00033599 | 6.0744 | 6.0748 | -5.0887 | 2976.2928 | 19162.5801 | -0.0017097
223 |  | 61.2239 | 86.127 | 4187 | 0.00033598 | 6.0748 | 6.0751 | -5.0887 | 2976.3519 | 19248.7071 | -0.0017097
224 |  | 61.2239 | 86.1253 | 4187 | 0.00033598 | 6.0751 | 6.0754 | -5.0887 | 2976.411 | 19334.8324 | -0.0017097
225 |  | 61.2239 | 86.1236 | 4187 | 0.00033597 | 6.0754 | 6.0758 | -5.0887 | 2976.4701 | 19420.956 | -0.0017096
226 |  | 61.2239 | 86.1219 | 4187 | 0.00033596 | 6.0758 | 6.0761 | -5.0887 | 2976.5292 | 19507.0779 | -0.0017096
227 |  | 61.2239 | 86.1202 | 4187 | 0.00033596 | 6.0761 | 6.0764 | -5.0887 | 2976.5883 | 19593.1981 | -0.0017096
228 |  | 61.2239 | 86.1185 | 4187 | 0.00033595 | 6.0764 | 6.0768 | -5.0887 | 2976.6473 | 19679.3166 | -0.0017095
229 |  | 61.2239 | 86.1168 | 4187 | 0.00033594 | 6.0768 | 6.0771 | -5.0887 | 2976.7064 | 19765.4333 | -0.0017095
230 |  | 61.2239 | 86.115 | 4187 | 0.00033594 | 6.0771 | 6.0774 | -5.0887 | 2976.7655 | 19851.5484 | -0.0017095
231 |  | 61.2239 | 86.1133 | 4187 | 0.00033593 | 6.0774 | 6.0778 | -5.0887 | 2976.8246 | 19937.6617 | -0.0017094
232 |  | 61.2239 | 86.1116 | 4187 | 0.00033592 | 6.0778 | 6.0781 | -5.0887 | 2976.8837 | 20023.7733 | -0.0017094
233 |  | 61.2239 | 86.1099 | 4187 | 0.00033592 | 6.0781 | 6.0784 | -5.0887 | 2976.9428 | 20109.8832 | -0.0017094
234 |  | 61.2239 | 86.1082 | 4187 | 0.00033591 | 6.0784 | 6.0788 | -5.0887 | 2977.0019 | 20195.9915 | -0.0017093
235 |  | 61.2239 | 86.1065 | 4187 | 0.0003359 | 6.0788 | 6.0791 | -5.0887 | 2977.061 | 20282.098 | -0.0017093
236 |  | 61.2239 | 86.1048 | 4187 | 0.0003359 | 6.0791 | 6.0795 | -5.0887 | 2977.1201 | 20368.2027 | -0.0017093

## CLX355
|  |  | buis | verlies W/M | L /°C/sec
diam | wandikte |  | inhoud l/m |  | W/M
355 | 20.1 | 3.1416 | 77.8322 | 90.28 | 4187
[8 empty] | J/sec/mtr | aantal mtr. | verlies
|  | buis | verlies W/M | L /°C/sec | verlies temp | begintemp | eindtemp | verlies | bij 1°C | totaal J/sec
|  | inhoud L |  | W/M | °C per M | °C | °C | per m°C | daling | aantal mtr
1 | 355 | 77.8322 | 90.28 | 4187 | 0.00027703 | 6 | 6.0003 | -5.3106 | 3609.6967 | 90.28 | -0.0014712
2 |  | 77.8322 | 90.2785 | 4187 | 0.00027703 | 6.0003 | 6.0006 | -5.3106 | 3609.7555 | 180.5585 | -0.0014712
3 |  | 77.8322 | 90.2771 | 4187 | 0.00027702 | 6.0006 | 6.0008 | -5.3106 | 3609.8143 | 270.8356 | -0.0014712
4 |  | 77.8322 | 90.2756 | 4187 | 0.00027702 | 6.0008 | 6.0011 | -5.3106 | 3609.8731 | 361.1112 | -0.0014711
5 |  | 77.8322 | 90.2741 | 4187 | 0.00027701 | 6.0011 | 6.0014 | -5.3106 | 3609.932 | 451.3853 | -0.0014711
6 |  | 77.8322 | 90.2727 | 4187 | 0.00027701 | 6.0014 | 6.0017 | -5.3106 | 3609.9908 | 541.658 | -0.0014711
7 |  | 77.8322 | 90.2712 | 4187 | 0.000277 | 6.0017 | 6.0019 | -5.3106 | 3610.0496 | 631.9292 | -0.0014711
8 |  | 77.8322 | 90.2697 | 4187 | 0.000277 | 6.0019 | 6.0022 | -5.3106 | 3610.1084 | 722.1989 | -0.001471
9 |  | 77.8322 | 90.2682 | 4187 | 0.000277 | 6.0022 | 6.0025 | -5.3106 | 3610.1673 | 812.4671 | -0.001471
10 |  | 77.8322 | 90.2668 | 4187 | 0.00027699 | 6.0025 | 6.0028 | -5.3106 | 3610.2261 | 902.7339 | -0.001471
11 |  | 77.8322 | 90.2653 | 4187 | 0.00027699 | 6.0028 | 6.003 | -5.3106 | 3610.2849 | 992.9992 | -0.001471
12 |  | 77.8322 | 90.2638 | 4187 | 0.00027698 | 6.003 | 6.0033 | -5.3106 | 3610.3438 | 1083.263 | -0.0014709
13 |  | 77.8322 | 90.2624 | 4187 | 0.00027698 | 6.0033 | 6.0036 | -5.3106 | 3610.4026 | 1173.5253 | -0.0014709
14 |  | 77.8322 | 90.2609 | 4187 | 0.00027697 | 6.0036 | 6.0039 | -5.3106 | 3610.4614 | 1263.7862 | -0.0014709
15 |  | 77.8322 | 90.2594 | 4187 | 0.00027697 | 6.0039 | 6.0042 | -5.3106 | 3610.5203 | 1354.0456 | -0.0014709
16 |  | 77.8322 | 90.2579 | 4187 | 0.00027696 | 6.0042 | 6.0044 | -5.3106 | 3610.5791 | 1444.3036 | -0.0014708
17 |  | 77.8322 | 90.2565 | 4187 | 0.00027696 | 6.0044 | 6.0047 | -5.3106 | 3610.638 | 1534.56 | -0.0014708
18 |  | 77.8322 | 90.255 | 4187 | 0.00027695 | 6.0047 | 6.005 | -5.3106 | 3610.6968 | 1624.815 | -0.0014708
19 |  | 77.8322 | 90.2535 | 4187 | 0.00027695 | 6.005 | 6.0053 | -5.3106 | 3610.7556 | 1715.0686 | -0.0014708
20 |  | 77.8322 | 90.2521 | 4187 | 0.00027695 | 6.0053 | 6.0055 | -5.3106 | 3610.8145 | 1805.3206 | -0.0014707
21 |  | 77.8322 | 90.2506 | 4187 | 0.00027694 | 6.0055 | 6.0058 | -5.3106 | 3610.8733 | 1895.5712 | -0.0014707
22 |  | 77.8322 | 90.2491 | 4187 | 0.00027694 | 6.0058 | 6.0061 | -5.3106 | 3610.9322 | 1985.8203 | -0.0014707
23 |  | 77.8322 | 90.2476 | 4187 | 0.00027693 | 6.0061 | 6.0064 | -5.3106 | 3610.991 | 2076.068 | -0.0014707
24 |  | 77.8322 | 90.2462 | 4187 | 0.00027693 | 6.0064 | 6.0066 | -5.3106 | 3611.0499 | 2166.3142 | -0.0014706
25 |  | 77.8322 | 90.2447 | 4187 | 0.00027692 | 6.0066 | 6.0069 | -5.3106 | 3611.1087 | 2256.5589 | -0.0014706
26 |  | 77.8322 | 90.2432 | 4187 | 0.00027692 | 6.0069 | 6.0072 | -5.3106 | 3611.1676 | 2346.8021 | -0.0014706
27 |  | 77.8322 | 90.2418 | 4187 | 0.00027691 | 6.0072 | 6.0075 | -5.3106 | 3611.2264 | 2437.0439 | -0.0014706
28 |  | 77.8322 | 90.2403 | 4187 | 0.00027691 | 6.0075 | 6.0078 | -5.3106 | 3611.2853 | 2527.2842 | -0.0014706
29 |  | 77.8322 | 90.2388 | 4187 | 0.00027691 | 6.0078 | 6.008 | -5.3106 | 3611.3441 | 2617.523 | -0.0014705
30 |  | 77.8322 | 90.2374 | 4187 | 0.0002769 | 6.008 | 6.0083 | -5.3106 | 3611.403 | 2707.7603 | -0.0014705
31 |  | 77.8322 | 90.2359 | 4187 | 0.0002769 | 6.0083 | 6.0086 | -5.3106 | 3611.4618 | 2797.9962 | -0.0014705
32 |  | 77.8322 | 90.2344 | 4187 | 0.00027689 | 6.0086 | 6.0089 | -5.3106 | 3611.5207 | 2888.2306 | -0.0014705
33 |  | 77.8322 | 90.2329 | 4187 | 0.00027689 | 6.0089 | 6.0091 | -5.3106 | 3611.5795 | 2978.4636 | -0.0014704
34 |  | 77.8322 | 90.2315 | 4187 | 0.00027688 | 6.0091 | 6.0094 | -5.3106 | 3611.6384 | 3068.695 | -0.0014704
35 |  | 77.8322 | 90.23 | 4187 | 0.00027688 | 6.0094 | 6.0097 | -5.3106 | 3611.6972 | 3158.925 | -0.0014704
36 |  | 77.8322 | 90.2285 | 4187 | 0.00027687 | 6.0097 | 6.01 | -5.3106 | 3611.7561 | 3249.1536 | -0.0014704
37 |  | 77.8322 | 90.2271 | 4187 | 0.00027687 | 6.01 | 6.0102 | -5.3106 | 3611.8149 | 3339.3806 | -0.0014703
38 |  | 77.8322 | 90.2256 | 4187 | 0.00027686 | 6.0102 | 6.0105 | -5.3106 | 3611.8738 | 3429.6062 | -0.0014703
39 |  | 77.8322 | 90.2241 | 4187 | 0.00027686 | 6.0105 | 6.0108 | -5.3106 | 3611.9327 | 3519.8303 | -0.0014703
40 |  | 77.8322 | 90.2226 | 4187 | 0.00027686 | 6.0108 | 6.0111 | -5.3106 | 3611.9915 | 3610.053 | -0.0014703
41 |  | 77.8322 | 90.2212 | 4187 | 0.00027685 | 6.0111 | 6.0114 | -5.3106 | 3612.0504 | 3700.2741 | -0.0014702
42 |  | 77.8322 | 90.2197 | 4187 | 0.00027685 | 6.0114 | 6.0116 | -5.3106 | 3612.1092 | 3790.4939 | -0.0014702
43 |  | 77.8322 | 90.2182 | 4187 | 0.00027684 | 6.0116 | 6.0119 | -5.3106 | 3612.1681 | 3880.7121 | -0.0014702
44 |  | 77.8322 | 90.2168 | 4187 | 0.00027684 | 6.0119 | 6.0122 | -5.3106 | 3612.227 | 3970.9289 | -0.0014702
45 |  | 77.8322 | 90.2153 | 4187 | 0.00027683 | 6.0122 | 6.0125 | -5.3106 | 3612.2858 | 4061.1442 | -0.0014701
46 |  | 77.8322 | 90.2138 | 4187 | 0.00027683 | 6.0125 | 6.0127 | -5.3106 | 3612.3447 | 4151.358 | -0.0014701
47 |  | 77.8322 | 90.2124 | 4187 | 0.00027682 | 6.0127 | 6.013 | -5.3106 | 3612.4036 | 4241.5703 | -0.0014701
48 |  | 77.8322 | 90.2109 | 4187 | 0.00027682 | 6.013 | 6.0133 | -5.3106 | 3612.4624 | 4331.7812 | -0.0014701
49 |  | 77.8322 | 90.2094 | 4187 | 0.00027681 | 6.0133 | 6.0136 | -5.3106 | 3612.5213 | 4421.9906 | -0.0014701
50 |  | 77.8322 | 90.2079 | 4187 | 0.00027681 | 6.0136 | 6.0138 | -5.3106 | 3612.5802 | 4512.1986 | -0.00147
51 |  | 77.8322 | 90.2065 | 4187 | 0.00027681 | 6.0138 | 6.0141 | -5.3106 | 3612.6391 | 4602.4051 | -0.00147
52 |  | 77.8322 | 90.205 | 4187 | 0.0002768 | 6.0141 | 6.0144 | -5.3106 | 3612.6979 | 4692.6101 | -0.00147
53 |  | 77.8322 | 90.2035 | 4187 | 0.0002768 | 6.0144 | 6.0147 | -5.3106 | 3612.7568 | 4782.8136 | -0.00147
54 |  | 77.8322 | 90.2021 | 4187 | 0.00027679 | 6.0147 | 6.015 | -5.3106 | 3612.8157 | 4873.0157 | -0.0014699
55 |  | 77.8322 | 90.2006 | 4187 | 0.00027679 | 6.015 | 6.0152 | -5.3106 | 3612.8745 | 4963.2163 | -0.0014699
56 |  | 77.8322 | 90.1991 | 4187 | 0.00027678 | 6.0152 | 6.0155 | -5.3106 | 3612.9334 | 5053.4154 | -0.0014699
57 |  | 77.8322 | 90.1977 | 4187 | 0.00027678 | 6.0155 | 6.0158 | -5.3106 | 3612.9923 | 5143.613 | -0.0014699
58 |  | 77.8322 | 90.1962 | 4187 | 0.00027677 | 6.0158 | 6.0161 | -5.3106 | 3613.0512 | 5233.8092 | -0.0014698
59 |  | 77.8322 | 90.1947 | 4187 | 0.00027677 | 6.0161 | 6.0163 | -5.3106 | 3613.1101 | 5324.004 | -0.0014698
60 |  | 77.8322 | 90.1932 | 4187 | 0.00027677 | 6.0163 | 6.0166 | -5.3106 | 3613.1689 | 5414.1972 | -0.0014698
61 |  | 77.8322 | 90.1918 | 4187 | 0.00027676 | 6.0166 | 6.0169 | -5.3106 | 3613.2278 | 5504.389 | -0.0014698
62 |  | 77.8322 | 90.1903 | 4187 | 0.00027676 | 6.0169 | 6.0172 | -5.3106 | 3613.2867 | 5594.5793 | -0.0014697
63 |  | 77.8322 | 90.1888 | 4187 | 0.00027675 | 6.0172 | 6.0174 | -5.3106 | 3613.3456 | 5684.7681 | -0.0014697
64 |  | 77.8322 | 90.1874 | 4187 | 0.00027675 | 6.0174 | 6.0177 | -5.3106 | 3613.4045 | 5774.9555 | -0.0014697
65 |  | 77.8322 | 90.1859 | 4187 | 0.00027674 | 6.0177 | 6.018 | -5.3106 | 3613.4634 | 5865.1414 | -0.0014697
66 |  | 77.8322 | 90.1844 | 4187 | 0.00027674 | 6.018 | 6.0183 | -5.3106 | 3613.5222 | 5955.3258 | -0.0014696
67 |  | 77.8322 | 90.183 | 4187 | 0.00027673 | 6.0183 | 6.0186 | -5.3106 | 3613.5811 | 6045.5088 | -0.0014696
68 |  | 77.8322 | 90.1815 | 4187 | 0.00027673 | 6.0186 | 6.0188 | -5.3106 | 3613.64 | 6135.6903 | -0.0014696
69 |  | 77.8322 | 90.18 | 4187 | 0.00027672 | 6.0188 | 6.0191 | -5.3106 | 3613.6989 | 6225.8703 | -0.0014696
70 |  | 77.8322 | 90.1786 | 4187 | 0.00027672 | 6.0191 | 6.0194 | -5.3106 | 3613.7578 | 6316.0488 | -0.0014695
71 |  | 77.8322 | 90.1771 | 4187 | 0.00027672 | 6.0194 | 6.0197 | -5.3106 | 3613.8167 | 6406.2259 | -0.0014695
72 |  | 77.8322 | 90.1756 | 4187 | 0.00027671 | 6.0197 | 6.0199 | -5.3106 | 3613.8756 | 6496.4015 | -0.0014695
73 |  | 77.8322 | 90.1741 | 4187 | 0.00027671 | 6.0199 | 6.0202 | -5.3106 | 3613.9345 | 6586.5757 | -0.0014695
74 |  | 77.8322 | 90.1727 | 4187 | 0.0002767 | 6.0202 | 6.0205 | -5.3106 | 3613.9934 | 6676.7483 | -0.0014695
75 |  | 77.8322 | 90.1712 | 4187 | 0.0002767 | 6.0205 | 6.0208 | -5.3106 | 3614.0523 | 6766.9195 | -0.0014694
76 |  | 77.8322 | 90.1697 | 4187 | 0.00027669 | 6.0208 | 6.021 | -5.3106 | 3614.1112 | 6857.0893 | -0.0014694
77 |  | 77.8322 | 90.1683 | 4187 | 0.00027669 | 6.021 | 6.0213 | -5.3106 | 3614.17 | 6947.2575 | -0.0014694
78 |  | 77.8322 | 90.1668 | 4187 | 0.00027668 | 6.0213 | 6.0216 | -5.3106 | 3614.2289 | 7037.4243 | -0.0014694
79 |  | 77.8322 | 90.1653 | 4187 | 0.00027668 | 6.0216 | 6.0219 | -5.3106 | 3614.2878 | 7127.5897 | -0.0014693
80 |  | 77.8322 | 90.1639 | 4187 | 0.00027668 | 6.0219 | 6.0221 | -5.3106 | 3614.3467 | 7217.7535 | -0.0014693
81 |  | 77.8322 | 90.1624 | 4187 | 0.00027667 | 6.0221 | 6.0224 | -5.3106 | 3614.4056 | 7307.9159 | -0.0014693
82 |  | 77.8322 | 90.1609 | 4187 | 0.00027667 | 6.0224 | 6.0227 | -5.3106 | 3614.4645 | 7398.0768 | -0.0014693
83 |  | 77.8322 | 90.1594 | 4187 | 0.00027666 | 6.0227 | 6.023 | -5.3106 | 3614.5234 | 7488.2363 | -0.0014692
84 |  | 77.8322 | 90.158 | 4187 | 0.00027666 | 6.023 | 6.0233 | -5.3106 | 3614.5823 | 7578.3942 | -0.0014692
85 |  | 77.8322 | 90.1565 | 4187 | 0.00027665 | 6.0233 | 6.0235 | -5.3106 | 3614.6413 | 7668.5508 | -0.0014692
86 |  | 77.8322 | 90.155 | 4187 | 0.00027665 | 6.0235 | 6.0238 | -5.3106 | 3614.7002 | 7758.7058 | -0.0014692
87 |  | 77.8322 | 90.1536 | 4187 | 0.00027664 | 6.0238 | 6.0241 | -5.3106 | 3614.7591 | 7848.8594 | -0.0014691
88 |  | 77.8322 | 90.1521 | 4187 | 0.00027664 | 6.0241 | 6.0244 | -5.3106 | 3614.818 | 7939.0115 | -0.0014691
89 |  | 77.8322 | 90.1506 | 4187 | 0.00027663 | 6.0244 | 6.0246 | -5.3106 | 3614.8769 | 8029.1621 | -0.0014691
90 |  | 77.8322 | 90.1492 | 4187 | 0.00027663 | 6.0246 | 6.0249 | -5.3106 | 3614.9358 | 8119.3113 | -0.0014691
91 |  | 77.8322 | 90.1477 | 4187 | 0.00027663 | 6.0249 | 6.0252 | -5.3106 | 3614.9947 | 8209.459 | -0.001469
92 |  | 77.8322 | 90.1462 | 4187 | 0.00027662 | 6.0252 | 6.0255 | -5.3106 | 3615.0536 | 8299.6052 | -0.001469
93 |  | 77.8322 | 90.1448 | 4187 | 0.00027662 | 6.0255 | 6.0257 | -5.3106 | 3615.1125 | 8389.7499 | -0.001469
94 |  | 77.8322 | 90.1433 | 4187 | 0.00027661 | 6.0257 | 6.026 | -5.3106 | 3615.1714 | 8479.8932 | -0.001469
95 |  | 77.8322 | 90.1418 | 4187 | 0.00027661 | 6.026 | 6.0263 | -5.3106 | 3615.2303 | 8570.035 | -0.0014689
96 |  | 77.8322 | 90.1403 | 4187 | 0.0002766 | 6.0263 | 6.0266 | -5.3106 | 3615.2893 | 8660.1754 | -0.0014689
97 |  | 77.8322 | 90.1389 | 4187 | 0.0002766 | 6.0266 | 6.0269 | -5.3106 | 3615.3482 | 8750.3143 | -0.0014689
98 |  | 77.8322 | 90.1374 | 4187 | 0.00027659 | 6.0269 | 6.0271 | -5.3106 | 3615.4071 | 8840.4517 | -0.0014689
99 |  | 77.8322 | 90.1359 | 4187 | 0.00027659 | 6.0271 | 6.0274 | -5.3106 | 3615.466 | 8930.5876 | -0.0014689
100 |  | 77.8322 | 90.1345 | 4187 | 0.00027659 | 6.0274 | 6.0277 | -5.3106 | 3615.5249 | 9020.7221 | -0.0014688
101 |  | 77.8322 | 90.133 | 4187 | 0.00027658 | 6.0277 | 6.028 | -5.3106 | 3615.5838 | 9110.8551 | -0.0014688
102 |  | 77.8322 | 90.1315 | 4187 | 0.00027658 | 6.028 | 6.0282 | -5.3106 | 3615.6428 | 9200.9866 | -0.0014688
103 |  | 77.8322 | 90.1301 | 4187 | 0.00027657 | 6.0282 | 6.0285 | -5.3106 | 3615.7017 | 9291.1167 | -0.0014688
104 |  | 77.8322 | 90.1286 | 4187 | 0.00027657 | 6.0285 | 6.0288 | -5.3106 | 3615.7606 | 9381.2453 | -0.0014687
105 |  | 77.8322 | 90.1271 | 4187 | 0.00027656 | 6.0288 | 6.0291 | -5.3106 | 3615.8195 | 9471.3724 | -0.0014687
106 |  | 77.8322 | 90.1257 | 4187 | 0.00027656 | 6.0291 | 6.0293 | -5.3106 | 3615.8785 | 9561.4981 | -0.0014687
107 |  | 77.8322 | 90.1242 | 4187 | 0.00027655 | 6.0293 | 6.0296 | -5.3106 | 3615.9374 | 9651.6223 | -0.0014687
108 |  | 77.8322 | 90.1227 | 4187 | 0.00027655 | 6.0296 | 6.0299 | -5.3106 | 3615.9963 | 9741.745 | -0.0014686
109 |  | 77.8322 | 90.1213 | 4187 | 0.00027654 | 6.0299 | 6.0302 | -5.3106 | 3616.0552 | 9831.8663 | -0.0014686
110 |  | 77.8322 | 90.1198 | 4187 | 0.00027654 | 6.0302 | 6.0304 | -5.3106 | 3616.1142 | 9921.9861 | -0.0014686
111 |  | 77.8322 | 90.1183 | 4187 | 0.00027654 | 6.0304 | 6.0307 | -5.3106 | 3616.1731 | 10012.1044 | -0.0014686
112 |  | 77.8322 | 90.1168 | 4187 | 0.00027653 | 6.0307 | 6.031 | -5.3106 | 3616.232 | 10102.2212 | -0.0014685
113 |  | 77.8322 | 90.1154 | 4187 | 0.00027653 | 6.031 | 6.0313 | -5.3106 | 3616.291 | 10192.3366 | -0.0014685
114 |  | 77.8322 | 90.1139 | 4187 | 0.00027652 | 6.0313 | 6.0316 | -5.3106 | 3616.3499 | 10282.4505 | -0.0014685
115 |  | 77.8322 | 90.1124 | 4187 | 0.00027652 | 6.0316 | 6.0318 | -5.3106 | 3616.4088 | 10372.563 | -0.0014685
116 |  | 77.8322 | 90.111 | 4187 | 0.00027651 | 6.0318 | 6.0321 | -5.3106 | 3616.4678 | 10462.6739 | -0.0014684
117 |  | 77.8322 | 90.1095 | 4187 | 0.00027651 | 6.0321 | 6.0324 | -5.3106 | 3616.5267 | 10552.7835 | -0.0014684
118 |  | 77.8322 | 90.108 | 4187 | 0.0002765 | 6.0324 | 6.0327 | -5.3106 | 3616.5856 | 10642.8915 | -0.0014684
119 |  | 77.8322 | 90.1066 | 4187 | 0.0002765 | 6.0327 | 6.0329 | -5.3106 | 3616.6446 | 10732.9981 | -0.0014684
120 |  | 77.8322 | 90.1051 | 4187 | 0.00027649 | 6.0329 | 6.0332 | -5.3106 | 3616.7035 | 10823.1032 | -0.0014684
121 |  | 77.8322 | 90.1036 | 4187 | 0.00027649 | 6.0332 | 6.0335 | -5.3106 | 3616.7624 | 10913.2068 | -0.0014683
122 |  | 77.8322 | 90.1022 | 4187 | 0.00027649 | 6.0335 | 6.0338 | -5.3106 | 3616.8214 | 11003.309 | -0.0014683
123 |  | 77.8322 | 90.1007 | 4187 | 0.00027648 | 6.0338 | 6.034 | -5.3106 | 3616.8803 | 11093.4097 | -0.0014683
124 |  | 77.8322 | 90.0992 | 4187 | 0.00027648 | 6.034 | 6.0343 | -5.3106 | 3616.9393 | 11183.5089 | -0.0014683
125 |  | 77.8322 | 90.0978 | 4187 | 0.00027647 | 6.0343 | 6.0346 | -5.3106 | 3616.9982 | 11273.6067 | -0.0014682
126 |  | 77.8322 | 90.0963 | 4187 | 0.00027647 | 6.0346 | 6.0349 | -5.3106 | 3617.0571 | 11363.7029 | -0.0014682
127 |  | 77.8322 | 90.0948 | 4187 | 0.00027646 | 6.0349 | 6.0351 | -5.3106 | 3617.1161 | 11453.7978 | -0.0014682
128 |  | 77.8322 | 90.0934 | 4187 | 0.00027646 | 6.0351 | 6.0354 | -5.3106 | 3617.175 | 11543.8911 | -0.0014682
129 |  | 77.8322 | 90.0919 | 4187 | 0.00027645 | 6.0354 | 6.0357 | -5.3106 | 3617.234 | 11633.983 | -0.0014681
130 |  | 77.8322 | 90.0904 | 4187 | 0.00027645 | 6.0357 | 6.036 | -5.3106 | 3617.2929 | 11724.0734 | -0.0014681
131 |  | 77.8322 | 90.089 | 4187 | 0.00027645 | 6.036 | 6.0363 | -5.3106 | 3617.3519 | 11814.1624 | -0.0014681
132 |  | 77.8322 | 90.0875 | 4187 | 0.00027644 | 6.0363 | 6.0365 | -5.3106 | 3617.4108 | 11904.2499 | -0.0014681
133 |  | 77.8322 | 90.086 | 4187 | 0.00027644 | 6.0365 | 6.0368 | -5.3106 | 3617.4698 | 11994.3359 | -0.001468
134 |  | 77.8322 | 90.0845 | 4187 | 0.00027643 | 6.0368 | 6.0371 | -5.3106 | 3617.5287 | 12084.4204 | -0.001468
135 |  | 77.8322 | 90.0831 | 4187 | 0.00027643 | 6.0371 | 6.0374 | -5.3106 | 3617.5877 | 12174.5035 | -0.001468
136 |  | 77.8322 | 90.0816 | 4187 | 0.00027642 | 6.0374 | 6.0376 | -5.3106 | 3617.6466 | 12264.5851 | -0.001468
137 |  | 77.8322 | 90.0801 | 4187 | 0.00027642 | 6.0376 | 6.0379 | -5.3106 | 3617.7056 | 12354.6653 | -0.0014679
138 |  | 77.8322 | 90.0787 | 4187 | 0.00027641 | 6.0379 | 6.0382 | -5.3106 | 3617.7645 | 12444.7439 | -0.0014679
139 |  | 77.8322 | 90.0772 | 4187 | 0.00027641 | 6.0382 | 6.0385 | -5.3106 | 3617.8235 | 12534.8211 | -0.0014679
140 |  | 77.8322 | 90.0757 | 4187 | 0.0002764 | 6.0385 | 6.0387 | -5.3106 | 3617.8825 | 12624.8969 | -0.0014679
141 |  | 77.8322 | 90.0743 | 4187 | 0.0002764 | 6.0387 | 6.039 | -5.3106 | 3617.9414 | 12714.9712 | -0.0014678
142 |  | 77.8322 | 90.0728 | 4187 | 0.0002764 | 6.039 | 6.0393 | -5.3106 | 3618.0004 | 12805.044 | -0.0014678
143 |  | 77.8322 | 90.0713 | 4187 | 0.00027639 | 6.0393 | 6.0396 | -5.3106 | 3618.0593 | 12895.1153 | -0.0014678
144 |  | 77.8322 | 90.0699 | 4187 | 0.00027639 | 6.0396 | 6.0398 | -5.3106 | 3618.1183 | 12985.1852 | -0.0014678
145 |  | 77.8322 | 90.0684 | 4187 | 0.00027638 | 6.0398 | 6.0401 | -5.3106 | 3618.1773 | 13075.2536 | -0.0014678
146 |  | 77.8322 | 90.0669 | 4187 | 0.00027638 | 6.0401 | 6.0404 | -5.3106 | 3618.2362 | 13165.3205 | -0.0014677
147 |  | 77.8322 | 90.0655 | 4187 | 0.00027637 | 6.0404 | 6.0407 | -5.3106 | 3618.2952 | 13255.386 | -0.0014677
148 |  | 77.8322 | 90.064 | 4187 | 0.00027637 | 6.0407 | 6.041 | -5.3106 | 3618.3541 | 13345.45 | -0.0014677
149 |  | 77.8322 | 90.0625 | 4187 | 0.00027636 | 6.041 | 6.0412 | -5.3106 | 3618.4131 | 13435.5125 | -0.0014677
150 |  | 77.8322 | 90.0611 | 4187 | 0.00027636 | 6.0412 | 6.0415 | -5.3106 | 3618.4721 | 13525.5736 | -0.0014676
151 |  | 77.8322 | 90.0596 | 4187 | 0.00027636 | 6.0415 | 6.0418 | -5.3106 | 3618.531 | 13615.6331 | -0.0014676
152 |  | 77.8322 | 90.0581 | 4187 | 0.00027635 | 6.0418 | 6.0421 | -5.3106 | 3618.59 | 13705.6913 | -0.0014676
153 |  | 77.8322 | 90.0567 | 4187 | 0.00027635 | 6.0421 | 6.0423 | -5.3106 | 3618.649 | 13795.7479 | -0.0014676
154 |  | 77.8322 | 90.0552 | 4187 | 0.00027634 | 6.0423 | 6.0426 | -5.3106 | 3618.708 | 13885.8031 | -0.0014675
155 |  | 77.8322 | 90.0537 | 4187 | 0.00027634 | 6.0426 | 6.0429 | -5.3106 | 3618.7669 | 13975.8568 | -0.0014675
156 |  | 77.8322 | 90.0523 | 4187 | 0.00027633 | 6.0429 | 6.0432 | -5.3106 | 3618.8259 | 14065.9091 | -0.0014675
157 |  | 77.8322 | 90.0508 | 4187 | 0.00027633 | 6.0432 | 6.0434 | -5.3106 | 3618.8849 | 14155.9599 | -0.0014675
158 |  | 77.8322 | 90.0493 | 4187 | 0.00027632 | 6.0434 | 6.0437 | -5.3106 | 3618.9438 | 14246.0092 | -0.0014674
159 |  | 77.8322 | 90.0479 | 4187 | 0.00027632 | 6.0437 | 6.044 | -5.3106 | 3619.0028 | 14336.0571 | -0.0014674
160 |  | 77.8322 | 90.0464 | 4187 | 0.00027631 | 6.044 | 6.0443 | -5.3106 | 3619.0618 | 14426.1035 | -0.0014674
161 |  | 77.8322 | 90.0449 | 4187 | 0.00027631 | 6.0443 | 6.0445 | -5.3106 | 3619.1208 | 14516.1484 | -0.0014674
162 |  | 77.8322 | 90.0435 | 4187 | 0.00027631 | 6.0445 | 6.0448 | -5.3106 | 3619.1798 | 14606.1918 | -0.0014673
163 |  | 77.8322 | 90.042 | 4187 | 0.0002763 | 6.0448 | 6.0451 | -5.3106 | 3619.2387 | 14696.2338 | -0.0014673
164 |  | 77.8322 | 90.0405 | 4187 | 0.0002763 | 6.0451 | 6.0454 | -5.3106 | 3619.2977 | 14786.2743 | -0.0014673
165 |  | 77.8322 | 90.039 | 4187 | 0.00027629 | 6.0454 | 6.0456 | -5.3106 | 3619.3567 | 14876.3134 | -0.0014673
166 |  | 77.8322 | 90.0376 | 4187 | 0.00027629 | 6.0456 | 6.0459 | -5.3106 | 3619.4157 | 14966.351 | -0.0014673
167 |  | 77.8322 | 90.0361 | 4187 | 0.00027628 | 6.0459 | 6.0462 | -5.3106 | 3619.4747 | 15056.3871 | -0.0014672
168 |  | 77.8322 | 90.0346 | 4187 | 0.00027628 | 6.0462 | 6.0465 | -5.3106 | 3619.5336 | 15146.4217 | -0.0014672
169 |  | 77.8322 | 90.0332 | 4187 | 0.00027627 | 6.0465 | 6.0468 | -5.3106 | 3619.5926 | 15236.4549 | -0.0014672
170 |  | 77.8322 | 90.0317 | 4187 | 0.00027627 | 6.0468 | 6.047 | -5.3106 | 3619.6516 | 15326.4866 | -0.0014672
171 |  | 77.8322 | 90.0302 | 4187 | 0.00027627 | 6.047 | 6.0473 | -5.3106 | 3619.7106 | 15416.5169 | -0.0014671
172 |  | 77.8322 | 90.0288 | 4187 | 0.00027626 | 6.0473 | 6.0476 | -5.3106 | 3619.7696 | 15506.5456 | -0.0014671
173 |  | 77.8322 | 90.0273 | 4187 | 0.00027626 | 6.0476 | 6.0479 | -5.3106 | 3619.8286 | 15596.573 | -0.0014671
174 |  | 77.8322 | 90.0258 | 4187 | 0.00027625 | 6.0479 | 6.0481 | -5.3106 | 3619.8876 | 15686.5988 | -0.0014671
175 |  | 77.8322 | 90.0244 | 4187 | 0.00027625 | 6.0481 | 6.0484 | -5.3106 | 3619.9466 | 15776.6232 | -0.001467
176 |  | 77.8322 | 90.0229 | 4187 | 0.00027624 | 6.0484 | 6.0487 | -5.3106 | 3620.0055 | 15866.6461 | -0.001467
177 |  | 77.8322 | 90.0214 | 4187 | 0.00027624 | 6.0487 | 6.049 | -5.3106 | 3620.0645 | 15956.6675 | -0.001467
178 |  | 77.8322 | 90.02 | 4187 | 0.00027623 | 6.049 | 6.0492 | -5.3106 | 3620.1235 | 16046.6875 | -0.001467
179 |  | 77.8322 | 90.0185 | 4187 | 0.00027623 | 6.0492 | 6.0495 | -5.3106 | 3620.1825 | 16136.706 | -0.0014669
180 |  | 77.8322 | 90.017 | 4187 | 0.00027622 | 6.0495 | 6.0498 | -5.3106 | 3620.2415 | 16226.7231 | -0.0014669
181 |  | 77.8322 | 90.0156 | 4187 | 0.00027622 | 6.0498 | 6.0501 | -5.3106 | 3620.3005 | 16316.7386 | -0.0014669
182 |  | 77.8322 | 90.0141 | 4187 | 0.00027622 | 6.0501 | 6.0503 | -5.3106 | 3620.3595 | 16406.7528 | -0.0014669
183 |  | 77.8322 | 90.0126 | 4187 | 0.00027621 | 6.0503 | 6.0506 | -5.3106 | 3620.4185 | 16496.7654 | -0.0014668
184 |  | 77.8322 | 90.0112 | 4187 | 0.00027621 | 6.0506 | 6.0509 | -5.3106 | 3620.4775 | 16586.7766 | -0.0014668
185 |  | 77.8322 | 90.0097 | 4187 | 0.0002762 | 6.0509 | 6.0512 | -5.3106 | 3620.5365 | 16676.7863 | -0.0014668
186 |  | 77.8322 | 90.0082 | 4187 | 0.0002762 | 6.0512 | 6.0515 | -5.3106 | 3620.5955 | 16766.7945 | -0.0014668
187 |  | 77.8322 | 90.0068 | 4187 | 0.00027619 | 6.0515 | 6.0517 | -5.3106 | 3620.6545 | 16856.8013 | -0.0014667
188 |  | 77.8322 | 90.0053 | 4187 | 0.00027619 | 6.0517 | 6.052 | -5.3106 | 3620.7135 | 16946.8066 | -0.0014667
189 |  | 77.8322 | 90.0038 | 4187 | 0.00027618 | 6.052 | 6.0523 | -5.3106 | 3620.7725 | 17036.8105 | -0.0014667
190 |  | 77.8322 | 90.0024 | 4187 | 0.00027618 | 6.0523 | 6.0526 | -5.3106 | 3620.8315 | 17126.8128 | -0.0014667
191 |  | 77.8322 | 90.0009 | 4187 | 0.00027618 | 6.0526 | 6.0528 | -5.3106 | 3620.8905 | 17216.8137 | -0.0014667
192 |  | 77.8322 | 89.9994 | 4187 | 0.00027617 | 6.0528 | 6.0531 | -5.3106 | 3620.9495 | 17306.8132 | -0.0014666
193 |  | 77.8322 | 89.998 | 4187 | 0.00027617 | 6.0531 | 6.0534 | -5.3106 | 3621.0085 | 17396.8112 | -0.0014666
194 |  | 77.8322 | 89.9965 | 4187 | 0.00027616 | 6.0534 | 6.0537 | -5.3106 | 3621.0676 | 17486.8077 | -0.0014666
195 |  | 77.8322 | 89.995 | 4187 | 0.00027616 | 6.0537 | 6.0539 | -5.3106 | 3621.1266 | 17576.8027 | -0.0014666
196 |  | 77.8322 | 89.9936 | 4187 | 0.00027615 | 6.0539 | 6.0542 | -5.3106 | 3621.1856 | 17666.7963 | -0.0014665
197 |  | 77.8322 | 89.9921 | 4187 | 0.00027615 | 6.0542 | 6.0545 | -5.3106 | 3621.2446 | 17756.7884 | -0.0014665
198 |  | 77.8322 | 89.9906 | 4187 | 0.00027614 | 6.0545 | 6.0548 | -5.3106 | 3621.3036 | 17846.779 | -0.0014665
199 |  | 77.8322 | 89.9892 | 4187 | 0.00027614 | 6.0548 | 6.055 | -5.3106 | 3621.3626 | 17936.7682 | -0.0014665
200 |  | 77.8322 | 89.9877 | 4187 | 0.00027613 | 6.055 | 6.0553 | -5.3106 | 3621.4216 | 18026.7559 | -0.0014664
201 |  | 77.8322 | 89.9862 | 4187 | 0.00027613 | 6.0553 | 6.0556 | -5.3106 | 3621.4806 | 18116.7422 | -0.0014664
202 |  | 77.8322 | 89.9848 | 4187 | 0.00027613 | 6.0556 | 6.0559 | -5.3106 | 3621.5397 | 18206.7269 | -0.0014664
203 |  | 77.8322 | 89.9833 | 4187 | 0.00027612 | 6.0559 | 6.0561 | -5.3106 | 3621.5987 | 18296.7102 | -0.0014664
204 |  | 77.8322 | 89.9818 | 4187 | 0.00027612 | 6.0561 | 6.0564 | -5.3106 | 3621.6577 | 18386.6921 | -0.0014663
205 |  | 77.8322 | 89.9804 | 4187 | 0.00027611 | 6.0564 | 6.0567 | -5.3106 | 3621.7167 | 18476.6725 | -0.0014663
206 |  | 77.8322 | 89.9789 | 4187 | 0.00027611 | 6.0567 | 6.057 | -5.3106 | 3621.7757 | 18566.6514 | -0.0014663
207 |  | 77.8322 | 89.9774 | 4187 | 0.0002761 | 6.057 | 6.0572 | -5.3106 | 3621.8348 | 18656.6288 | -0.0014663
208 |  | 77.8322 | 89.976 | 4187 | 0.0002761 | 6.0572 | 6.0575 | -5.3106 | 3621.8938 | 18746.6048 | -0.0014662
209 |  | 77.8322 | 89.9745 | 4187 | 0.00027609 | 6.0575 | 6.0578 | -5.3106 | 3621.9528 | 18836.5793 | -0.0014662
210 |  | 77.8322 | 89.973 | 4187 | 0.00027609 | 6.0578 | 6.0581 | -5.3106 | 3622.0118 | 18926.5524 | -0.0014662
211 |  | 77.8322 | 89.9716 | 4187 | 0.00027609 | 6.0581 | 6.0584 | -5.3106 | 3622.0709 | 19016.5239 | -0.0014662
212 |  | 77.8322 | 89.9701 | 4187 | 0.00027608 | 6.0584 | 6.0586 | -5.3106 | 3622.1299 | 19106.4941 | -0.0014662
213 |  | 77.8322 | 89.9686 | 4187 | 0.00027608 | 6.0586 | 6.0589 | -5.3106 | 3622.1889 | 19196.4627 | -0.0014661
214 |  | 77.8322 | 89.9672 | 4187 | 0.00027607 | 6.0589 | 6.0592 | -5.3106 | 3622.2479 | 19286.4299 | -0.0014661
215 |  | 77.8322 | 89.9657 | 4187 | 0.00027607 | 6.0592 | 6.0595 | -5.3106 | 3622.307 | 19376.3956 | -0.0014661
216 |  | 77.8322 | 89.9642 | 4187 | 0.00027606 | 6.0595 | 6.0597 | -5.3106 | 3622.366 | 19466.3599 | -0.0014661
217 |  | 77.8322 | 89.9628 | 4187 | 0.00027606 | 6.0597 | 6.06 | -5.3106 | 3622.425 | 19556.3226 | -0.001466
218 |  | 77.8322 | 89.9613 | 4187 | 0.00027605 | 6.06 | 6.0603 | -5.3106 | 3622.4841 | 19646.284 | -0.001466
219 |  | 77.8322 | 89.9599 | 4187 | 0.00027605 | 6.0603 | 6.0606 | -5.3106 | 3622.5431 | 19736.2438 | -0.001466
220 |  | 77.8322 | 89.9584 | 4187 | 0.00027604 | 6.0606 | 6.0608 | -5.3106 | 3622.6021 | 19826.2022 | -0.001466
221 |  | 77.8322 | 89.9569 | 4187 | 0.00027604 | 6.0608 | 6.0611 | -5.3106 | 3622.6612 | 19916.1591 | -0.0014659
222 |  | 77.8322 | 89.9555 | 4187 | 0.00027604 | 6.0611 | 6.0614 | -5.3106 | 3622.7202 | 20006.1146 | -0.0014659
223 |  | 77.8322 | 89.954 | 4187 | 0.00027603 | 6.0614 | 6.0617 | -5.3106 | 3622.7792 | 20096.0686 | -0.0014659
224 |  | 77.8322 | 89.9525 | 4187 | 0.00027603 | 6.0617 | 6.0619 | -5.3106 | 3622.8383 | 20186.0211 | -0.0014659
225 |  | 77.8322 | 89.9511 | 4187 | 0.00027602 | 6.0619 | 6.0622 | -5.3106 | 3622.8973 | 20275.9721 | -0.0014658
226 |  | 77.8322 | 89.9496 | 4187 | 0.00027602 | 6.0622 | 6.0625 | -5.3106 | 3622.9563 | 20365.9217 | -0.0014658
227 |  | 77.8322 | 89.9481 | 4187 | 0.00027601 | 6.0625 | 6.0628 | -5.3106 | 3623.0154 | 20455.8698 | -0.0014658
228 |  | 77.8322 | 89.9467 | 4187 | 0.00027601 | 6.0628 | 6.063 | -5.3106 | 3623.0744 | 20545.8165 | -0.0014658
229 |  | 77.8322 | 89.9452 | 4187 | 0.000276 | 6.063 | 6.0633 | -5.3106 | 3623.1335 | 20635.7617 | -0.0014657
230 |  | 77.8322 | 89.9437 | 4187 | 0.000276 | 6.0633 | 6.0636 | -5.3106 | 3623.1925 | 20725.7054 | -0.0014657
231 |  | 77.8322 | 89.9423 | 4187 | 0.000276 | 6.0636 | 6.0639 | -5.3106 | 3623.2516 | 20815.6477 | -0.0014657
232 |  | 77.8322 | 89.9408 | 4187 | 0.00027599 | 6.0639 | 6.0642 | -5.3106 | 3623.3106 | 20905.5885 | -0.0014657
233 |  | 77.8322 | 89.9393 | 4187 | 0.00027599 | 6.0642 | 6.0644 | -5.3106 | 3623.3697 | 20995.5278 | -0.0014656
234 |  | 77.8322 | 89.9379 | 4187 | 0.00027598 | 6.0644 | 6.0647 | -5.3106 | 3623.4287 | 21085.4657 | -0.0014656
235 |  | 77.8322 | 89.9364 | 4187 | 0.00027598 | 6.0647 | 6.065 | -5.3106 | 3623.4877 | 21175.4021 | -0.0014656
236 |  | 77.8322 | 89.9349 | 4187 | 0.00027597 | 6.065 | 6.0653 | -5.3106 | 3623.5468 | 21265.337 | -0.0014656

## CLX400
|  |  | buis | verlies W/M | L /°C/sec
diam | wandikte |  | inhoud l/m |  | W/M
400 | 22.7 | 3.1416 | 98.7569 | 93.5214 | 4187
[8 empty] | J/sec/mtr | aantal mtr. | verlies
|  | buis | verlies W/M | L /°C/sec | verlies temp | begintemp | eindtemp | verlies | bij 1°C | totaal J/sec
|  | inhoud L |  | W/M | °C per M | °C | °C | per m°C | daling | aantal mtr
1 | 400 | 98.7569 | 93.5214 | 4187 | 0.00022617 | 6 | 6.0002 | -5.5013 | 4421.3932 | 93.5214 | -0.0012442
2 |  | 98.7569 | 93.5202 | 4187 | 0.00022617 | 6.0002 | 6.0005 | -5.5013 | 4421.452 | 187.0416 | -0.0012442
3 |  | 98.7569 | 93.5189 | 4187 | 0.00022617 | 6.0005 | 6.0007 | -5.5013 | 4421.5108 | 280.5606 | -0.0012442
4 |  | 98.7569 | 93.5177 | 4187 | 0.00022616 | 6.0007 | 6.0009 | -5.5013 | 4421.5697 | 374.0783 | -0.0012442
5 |  | 98.7569 | 93.5165 | 4187 | 0.00022616 | 6.0009 | 6.0011 | -5.5013 | 4421.6285 | 467.5947 | -0.0012442
6 |  | 98.7569 | 93.5152 | 4187 | 0.00022616 | 6.0011 | 6.0014 | -5.5013 | 4421.6873 | 561.11 | -0.0012442
7 |  | 98.7569 | 93.514 | 4187 | 0.00022616 | 6.0014 | 6.0016 | -5.5013 | 4421.7461 | 654.6239 | -0.0012441
8 |  | 98.7569 | 93.5127 | 4187 | 0.00022615 | 6.0016 | 6.0018 | -5.5013 | 4421.805 | 748.1367 | -0.0012441
9 |  | 98.7569 | 93.5115 | 4187 | 0.00022615 | 6.0018 | 6.002 | -5.5013 | 4421.8638 | 841.6481 | -0.0012441
10 |  | 98.7569 | 93.5102 | 4187 | 0.00022615 | 6.002 | 6.0023 | -5.5013 | 4421.9226 | 935.1584 | -0.0012441
11 |  | 98.7569 | 93.509 | 4187 | 0.00022614 | 6.0023 | 6.0025 | -5.5013 | 4421.9815 | 1028.6674 | -0.0012441
12 |  | 98.7569 | 93.5078 | 4187 | 0.00022614 | 6.0025 | 6.0027 | -5.5013 | 4422.0403 | 1122.1751 | -0.0012441
13 |  | 98.7569 | 93.5065 | 4187 | 0.00022614 | 6.0027 | 6.0029 | -5.5013 | 4422.0991 | 1215.6816 | -0.001244
14 |  | 98.7569 | 93.5053 | 4187 | 0.00022613 | 6.0029 | 6.0032 | -5.5013 | 4422.158 | 1309.1869 | -0.001244
15 |  | 98.7569 | 93.504 | 4187 | 0.00022613 | 6.0032 | 6.0034 | -5.5013 | 4422.2168 | 1402.6909 | -0.001244
16 |  | 98.7569 | 93.5028 | 4187 | 0.00022613 | 6.0034 | 6.0036 | -5.5013 | 4422.2756 | 1496.1937 | -0.001244
17 |  | 98.7569 | 93.5015 | 4187 | 0.00022612 | 6.0036 | 6.0038 | -5.5013 | 4422.3345 | 1589.6952 | -0.001244
18 |  | 98.7569 | 93.5003 | 4187 | 0.00022612 | 6.0038 | 6.0041 | -5.5013 | 4422.3933 | 1683.1955 | -0.001244
19 |  | 98.7569 | 93.499 | 4187 | 0.00022612 | 6.0041 | 6.0043 | -5.5013 | 4422.4521 | 1776.6945 | -0.0012439
20 |  | 98.7569 | 93.4978 | 4187 | 0.00022612 | 6.0043 | 6.0045 | -5.5013 | 4422.511 | 1870.1923 | -0.0012439
21 |  | 98.7569 | 93.4966 | 4187 | 0.00022611 | 6.0045 | 6.0047 | -5.5013 | 4422.5698 | 1963.6889 | -0.0012439
22 |  | 98.7569 | 93.4953 | 4187 | 0.00022611 | 6.0047 | 6.005 | -5.5013 | 4422.6287 | 2057.1842 | -0.0012439
23 |  | 98.7569 | 93.4941 | 4187 | 0.00022611 | 6.005 | 6.0052 | -5.5013 | 4422.6875 | 2150.6783 | -0.0012439
24 |  | 98.7569 | 93.4928 | 4187 | 0.0002261 | 6.0052 | 6.0054 | -5.5013 | 4422.7463 | 2244.1711 | -0.0012439
25 |  | 98.7569 | 93.4916 | 4187 | 0.0002261 | 6.0054 | 6.0057 | -5.5013 | 4422.8052 | 2337.6627 | -0.0012438
26 |  | 98.7569 | 93.4903 | 4187 | 0.0002261 | 6.0057 | 6.0059 | -5.5013 | 4422.864 | 2431.153 | -0.0012438
27 |  | 98.7569 | 93.4891 | 4187 | 0.00022609 | 6.0059 | 6.0061 | -5.5013 | 4422.9229 | 2524.6421 | -0.0012438
28 |  | 98.7569 | 93.4878 | 4187 | 0.00022609 | 6.0061 | 6.0063 | -5.5013 | 4422.9817 | 2618.1299 | -0.0012438
29 |  | 98.7569 | 93.4866 | 4187 | 0.00022609 | 6.0063 | 6.0066 | -5.5013 | 4423.0406 | 2711.6165 | -0.0012438
30 |  | 98.7569 | 93.4854 | 4187 | 0.00022609 | 6.0066 | 6.0068 | -5.5013 | 4423.0994 | 2805.1019 | -0.0012438
31 |  | 98.7569 | 93.4841 | 4187 | 0.00022608 | 6.0068 | 6.007 | -5.5013 | 4423.1583 | 2898.586 | -0.0012437
32 |  | 98.7569 | 93.4829 | 4187 | 0.00022608 | 6.007 | 6.0072 | -5.5013 | 4423.2171 | 2992.0689 | -0.0012437
33 |  | 98.7569 | 93.4816 | 4187 | 0.00022608 | 6.0072 | 6.0075 | -5.5013 | 4423.276 | 3085.5505 | -0.0012437
34 |  | 98.7569 | 93.4804 | 4187 | 0.00022607 | 6.0075 | 6.0077 | -5.5013 | 4423.3348 | 3179.0309 | -0.0012437
35 |  | 98.7569 | 93.4791 | 4187 | 0.00022607 | 6.0077 | 6.0079 | -5.5013 | 4423.3937 | 3272.5101 | -0.0012437
36 |  | 98.7569 | 93.4779 | 4187 | 0.00022607 | 6.0079 | 6.0081 | -5.5013 | 4423.4525 | 3365.9879 | -0.0012437
37 |  | 98.7569 | 93.4767 | 4187 | 0.00022606 | 6.0081 | 6.0084 | -5.5013 | 4423.5114 | 3459.4646 | -0.0012436
38 |  | 98.7569 | 93.4754 | 4187 | 0.00022606 | 6.0084 | 6.0086 | -5.5013 | 4423.5702 | 3552.94 | -0.0012436
39 |  | 98.7569 | 93.4742 | 4187 | 0.00022606 | 6.0086 | 6.0088 | -5.5013 | 4423.6291 | 3646.4142 | -0.0012436
40 |  | 98.7569 | 93.4729 | 4187 | 0.00022606 | 6.0088 | 6.009 | -5.5013 | 4423.6879 | 3739.8871 | -0.0012436
41 |  | 98.7569 | 93.4717 | 4187 | 0.00022605 | 6.009 | 6.0093 | -5.5013 | 4423.7468 | 3833.3588 | -0.0012436
42 |  | 98.7569 | 93.4704 | 4187 | 0.00022605 | 6.0093 | 6.0095 | -5.5013 | 4423.8056 | 3926.8292 | -0.0012436
43 |  | 98.7569 | 93.4692 | 4187 | 0.00022605 | 6.0095 | 6.0097 | -5.5013 | 4423.8645 | 4020.2984 | -0.0012435
44 |  | 98.7569 | 93.4679 | 4187 | 0.00022604 | 6.0097 | 6.0099 | -5.5013 | 4423.9233 | 4113.7664 | -0.0012435
45 |  | 98.7569 | 93.4667 | 4187 | 0.00022604 | 6.0099 | 6.0102 | -5.5013 | 4423.9822 | 4207.2331 | -0.0012435
46 |  | 98.7569 | 93.4655 | 4187 | 0.00022604 | 6.0102 | 6.0104 | -5.5013 | 4424.0411 | 4300.6985 | -0.0012435
47 |  | 98.7569 | 93.4642 | 4187 | 0.00022603 | 6.0104 | 6.0106 | -5.5013 | 4424.0999 | 4394.1627 | -0.0012435
48 |  | 98.7569 | 93.463 | 4187 | 0.00022603 | 6.0106 | 6.0109 | -5.5013 | 4424.1588 | 4487.6257 | -0.0012435
49 |  | 98.7569 | 93.4617 | 4187 | 0.00022603 | 6.0109 | 6.0111 | -5.5013 | 4424.2176 | 4581.0875 | -0.0012434
50 |  | 98.7569 | 93.4605 | 4187 | 0.00022603 | 6.0111 | 6.0113 | -5.5013 | 4424.2765 | 4674.5479 | -0.0012434
51 |  | 98.7569 | 93.4592 | 4187 | 0.00022602 | 6.0113 | 6.0115 | -5.5013 | 4424.3354 | 4768.0072 | -0.0012434
52 |  | 98.7569 | 93.458 | 4187 | 0.00022602 | 6.0115 | 6.0118 | -5.5013 | 4424.3942 | 4861.4652 | -0.0012434
53 |  | 98.7569 | 93.4568 | 4187 | 0.00022602 | 6.0118 | 6.012 | -5.5013 | 4424.4531 | 4954.9219 | -0.0012434
54 |  | 98.7569 | 93.4555 | 4187 | 0.00022601 | 6.012 | 6.0122 | -5.5013 | 4424.512 | 5048.3775 | -0.0012434
55 |  | 98.7569 | 93.4543 | 4187 | 0.00022601 | 6.0122 | 6.0124 | -5.5013 | 4424.5708 | 5141.8317 | -0.0012433
56 |  | 98.7569 | 93.453 | 4187 | 0.00022601 | 6.0124 | 6.0127 | -5.5013 | 4424.6297 | 5235.2848 | -0.0012433
57 |  | 98.7569 | 93.4518 | 4187 | 0.000226 | 6.0127 | 6.0129 | -5.5013 | 4424.6886 | 5328.7365 | -0.0012433
58 |  | 98.7569 | 93.4505 | 4187 | 0.000226 | 6.0129 | 6.0131 | -5.5013 | 4424.7474 | 5422.1871 | -0.0012433
59 |  | 98.7569 | 93.4493 | 4187 | 0.000226 | 6.0131 | 6.0133 | -5.5013 | 4424.8063 | 5515.6364 | -0.0012433
60 |  | 98.7569 | 93.4481 | 4187 | 0.000226 | 6.0133 | 6.0136 | -5.5013 | 4424.8652 | 5609.0844 | -0.0012433
61 |  | 98.7569 | 93.4468 | 4187 | 0.00022599 | 6.0136 | 6.0138 | -5.5013 | 4424.924 | 5702.5312 | -0.0012432
62 |  | 98.7569 | 93.4456 | 4187 | 0.00022599 | 6.0138 | 6.014 | -5.5013 | 4424.9829 | 5795.9768 | -0.0012432
63 |  | 98.7569 | 93.4443 | 4187 | 0.00022599 | 6.014 | 6.0142 | -5.5013 | 4425.0418 | 5889.4211 | -0.0012432
64 |  | 98.7569 | 93.4431 | 4187 | 0.00022598 | 6.0142 | 6.0145 | -5.5013 | 4425.1006 | 5982.8642 | -0.0012432
65 |  | 98.7569 | 93.4418 | 4187 | 0.00022598 | 6.0145 | 6.0147 | -5.5013 | 4425.1595 | 6076.3061 | -0.0012432
66 |  | 98.7569 | 93.4406 | 4187 | 0.00022598 | 6.0147 | 6.0149 | -5.5013 | 4425.2184 | 6169.7467 | -0.0012432
67 |  | 98.7569 | 93.4394 | 4187 | 0.00022597 | 6.0149 | 6.0151 | -5.5013 | 4425.2773 | 6263.186 | -0.0012431
68 |  | 98.7569 | 93.4381 | 4187 | 0.00022597 | 6.0151 | 6.0154 | -5.5013 | 4425.3361 | 6356.6241 | -0.0012431
69 |  | 98.7569 | 93.4369 | 4187 | 0.00022597 | 6.0154 | 6.0156 | -5.5013 | 4425.395 | 6450.061 | -0.0012431
70 |  | 98.7569 | 93.4356 | 4187 | 0.00022597 | 6.0156 | 6.0158 | -5.5013 | 4425.4539 | 6543.4966 | -0.0012431
71 |  | 98.7569 | 93.4344 | 4187 | 0.00022596 | 6.0158 | 6.0161 | -5.5013 | 4425.5128 | 6636.931 | -0.0012431
72 |  | 98.7569 | 93.4331 | 4187 | 0.00022596 | 6.0161 | 6.0163 | -5.5013 | 4425.5717 | 6730.3641 | -0.0012431
73 |  | 98.7569 | 93.4319 | 4187 | 0.00022596 | 6.0163 | 6.0165 | -5.5013 | 4425.6305 | 6823.796 | -0.001243
74 |  | 98.7569 | 93.4307 | 4187 | 0.00022595 | 6.0165 | 6.0167 | -5.5013 | 4425.6894 | 6917.2267 | -0.001243
75 |  | 98.7569 | 93.4294 | 4187 | 0.00022595 | 6.0167 | 6.017 | -5.5013 | 4425.7483 | 7010.6561 | -0.001243
76 |  | 98.7569 | 93.4282 | 4187 | 0.00022595 | 6.017 | 6.0172 | -5.5013 | 4425.8072 | 7104.0842 | -0.001243
77 |  | 98.7569 | 93.4269 | 4187 | 0.00022594 | 6.0172 | 6.0174 | -5.5013 | 4425.8661 | 7197.5112 | -0.001243
78 |  | 98.7569 | 93.4257 | 4187 | 0.00022594 | 6.0174 | 6.0176 | -5.5013 | 4425.9249 | 7290.9368 | -0.001243
79 |  | 98.7569 | 93.4244 | 4187 | 0.00022594 | 6.0176 | 6.0179 | -5.5013 | 4425.9838 | 7384.3613 | -0.0012429
80 |  | 98.7569 | 93.4232 | 4187 | 0.00022594 | 6.0179 | 6.0181 | -5.5013 | 4426.0427 | 7477.7845 | -0.0012429
81 |  | 98.7569 | 93.4219 | 4187 | 0.00022593 | 6.0181 | 6.0183 | -5.5013 | 4426.1016 | 7571.2064 | -0.0012429
82 |  | 98.7569 | 93.4207 | 4187 | 0.00022593 | 6.0183 | 6.0185 | -5.5013 | 4426.1605 | 7664.6271 | -0.0012429
83 |  | 98.7569 | 93.4195 | 4187 | 0.00022593 | 6.0185 | 6.0188 | -5.5013 | 4426.2194 | 7758.0466 | -0.0012429
84 |  | 98.7569 | 93.4182 | 4187 | 0.00022592 | 6.0188 | 6.019 | -5.5013 | 4426.2783 | 7851.4648 | -0.0012429
85 |  | 98.7569 | 93.417 | 4187 | 0.00022592 | 6.019 | 6.0192 | -5.5013 | 4426.3372 | 7944.8818 | -0.0012428
86 |  | 98.7569 | 93.4157 | 4187 | 0.00022592 | 6.0192 | 6.0194 | -5.5013 | 4426.396 | 8038.2975 | -0.0012428
87 |  | 98.7569 | 93.4145 | 4187 | 0.00022591 | 6.0194 | 6.0197 | -5.5013 | 4426.4549 | 8131.712 | -0.0012428
88 |  | 98.7569 | 93.4132 | 4187 | 0.00022591 | 6.0197 | 6.0199 | -5.5013 | 4426.5138 | 8225.1253 | -0.0012428
89 |  | 98.7569 | 93.412 | 4187 | 0.00022591 | 6.0199 | 6.0201 | -5.5013 | 4426.5727 | 8318.5373 | -0.0012428
90 |  | 98.7569 | 93.4108 | 4187 | 0.00022591 | 6.0201 | 6.0203 | -5.5013 | 4426.6316 | 8411.948 | -0.0012428
91 |  | 98.7569 | 93.4095 | 4187 | 0.0002259 | 6.0203 | 6.0206 | -5.5013 | 4426.6905 | 8505.3575 | -0.0012427
92 |  | 98.7569 | 93.4083 | 4187 | 0.0002259 | 6.0206 | 6.0208 | -5.5013 | 4426.7494 | 8598.7658 | -0.0012427
93 |  | 98.7569 | 93.407 | 4187 | 0.0002259 | 6.0208 | 6.021 | -5.5013 | 4426.8083 | 8692.1729 | -0.0012427
94 |  | 98.7569 | 93.4058 | 4187 | 0.00022589 | 6.021 | 6.0212 | -5.5013 | 4426.8672 | 8785.5787 | -0.0012427
95 |  | 98.7569 | 93.4046 | 4187 | 0.00022589 | 6.0212 | 6.0215 | -5.5013 | 4426.9261 | 8878.9832 | -0.0012427
96 |  | 98.7569 | 93.4033 | 4187 | 0.00022589 | 6.0215 | 6.0217 | -5.5013 | 4426.985 | 8972.3865 | -0.0012427
97 |  | 98.7569 | 93.4021 | 4187 | 0.00022588 | 6.0217 | 6.0219 | -5.5013 | 4427.0439 | 9065.7886 | -0.0012426
98 |  | 98.7569 | 93.4008 | 4187 | 0.00022588 | 6.0219 | 6.0222 | -5.5013 | 4427.1028 | 9159.1894 | -0.0012426
99 |  | 98.7569 | 93.3996 | 4187 | 0.00022588 | 6.0222 | 6.0224 | -5.5013 | 4427.1617 | 9252.589 | -0.0012426
100 |  | 98.7569 | 93.3983 | 4187 | 0.00022588 | 6.0224 | 6.0226 | -5.5013 | 4427.2206 | 9345.9873 | -0.0012426
101 |  | 98.7569 | 93.3971 | 4187 | 0.00022587 | 6.0226 | 6.0228 | -5.5013 | 4427.2795 | 9439.3844 | -0.0012426
102 |  | 98.7569 | 93.3959 | 4187 | 0.00022587 | 6.0228 | 6.0231 | -5.5013 | 4427.3384 | 9532.7803 | -0.0012426
103 |  | 98.7569 | 93.3946 | 4187 | 0.00022587 | 6.0231 | 6.0233 | -5.5013 | 4427.3973 | 9626.1749 | -0.0012425
104 |  | 98.7569 | 93.3934 | 4187 | 0.00022586 | 6.0233 | 6.0235 | -5.5013 | 4427.4562 | 9719.5682 | -0.0012425
105 |  | 98.7569 | 93.3921 | 4187 | 0.00022586 | 6.0235 | 6.0237 | -5.5013 | 4427.5151 | 9812.9604 | -0.0012425
106 |  | 98.7569 | 93.3909 | 4187 | 0.00022586 | 6.0237 | 6.024 | -5.5013 | 4427.574 | 9906.3512 | -0.0012425
107 |  | 98.7569 | 93.3896 | 4187 | 0.00022585 | 6.024 | 6.0242 | -5.5013 | 4427.6329 | 9999.7409 | -0.0012425
108 |  | 98.7569 | 93.3884 | 4187 | 0.00022585 | 6.0242 | 6.0244 | -5.5013 | 4427.6918 | 10093.1293 | -0.0012425
109 |  | 98.7569 | 93.3872 | 4187 | 0.00022585 | 6.0244 | 6.0246 | -5.5013 | 4427.7507 | 10186.5164 | -0.0012425
110 |  | 98.7569 | 93.3859 | 4187 | 0.00022585 | 6.0246 | 6.0249 | -5.5013 | 4427.8096 | 10279.9023 | -0.0012424
111 |  | 98.7569 | 93.3847 | 4187 | 0.00022584 | 6.0249 | 6.0251 | -5.5013 | 4427.8686 | 10373.287 | -0.0012424
112 |  | 98.7569 | 93.3834 | 4187 | 0.00022584 | 6.0251 | 6.0253 | -5.5013 | 4427.9275 | 10466.6704 | -0.0012424
113 |  | 98.7569 | 93.3822 | 4187 | 0.00022584 | 6.0253 | 6.0255 | -5.5013 | 4427.9864 | 10560.0526 | -0.0012424
114 |  | 98.7569 | 93.3809 | 4187 | 0.00022583 | 6.0255 | 6.0258 | -5.5013 | 4428.0453 | 10653.4336 | -0.0012424
115 |  | 98.7569 | 93.3797 | 4187 | 0.00022583 | 6.0258 | 6.026 | -5.5013 | 4428.1042 | 10746.8133 | -0.0012424
116 |  | 98.7569 | 93.3785 | 4187 | 0.00022583 | 6.026 | 6.0262 | -5.5013 | 4428.1631 | 10840.1917 | -0.0012423
117 |  | 98.7569 | 93.3772 | 4187 | 0.00022582 | 6.0262 | 6.0264 | -5.5013 | 4428.222 | 10933.5689 | -0.0012423
118 |  | 98.7569 | 93.376 | 4187 | 0.00022582 | 6.0264 | 6.0267 | -5.5013 | 4428.2809 | 11026.9449 | -0.0012423
119 |  | 98.7569 | 93.3747 | 4187 | 0.00022582 | 6.0267 | 6.0269 | -5.5013 | 4428.3399 | 11120.3196 | -0.0012423
120 |  | 98.7569 | 93.3735 | 4187 | 0.00022582 | 6.0269 | 6.0271 | -5.5013 | 4428.3988 | 11213.6931 | -0.0012423
121 |  | 98.7569 | 93.3722 | 4187 | 0.00022581 | 6.0271 | 6.0273 | -5.5013 | 4428.4577 | 11307.0654 | -0.0012423
122 |  | 98.7569 | 93.371 | 4187 | 0.00022581 | 6.0273 | 6.0276 | -5.5013 | 4428.5166 | 11400.4364 | -0.0012422
123 |  | 98.7569 | 93.3698 | 4187 | 0.00022581 | 6.0276 | 6.0278 | -5.5013 | 4428.5755 | 11493.8061 | -0.0012422
124 |  | 98.7569 | 93.3685 | 4187 | 0.0002258 | 6.0278 | 6.028 | -5.5013 | 4428.6345 | 11587.1747 | -0.0012422
125 |  | 98.7569 | 93.3673 | 4187 | 0.0002258 | 6.028 | 6.0282 | -5.5013 | 4428.6934 | 11680.5419 | -0.0012422
126 |  | 98.7569 | 93.366 | 4187 | 0.0002258 | 6.0282 | 6.0285 | -5.5013 | 4428.7523 | 11773.908 | -0.0012422
127 |  | 98.7569 | 93.3648 | 4187 | 0.00022579 | 6.0285 | 6.0287 | -5.5013 | 4428.8112 | 11867.2728 | -0.0012422
128 |  | 98.7569 | 93.3636 | 4187 | 0.00022579 | 6.0287 | 6.0289 | -5.5013 | 4428.8701 | 11960.6363 | -0.0012421
129 |  | 98.7569 | 93.3623 | 4187 | 0.00022579 | 6.0289 | 6.0292 | -5.5013 | 4428.9291 | 12053.9986 | -0.0012421
130 |  | 98.7569 | 93.3611 | 4187 | 0.00022579 | 6.0292 | 6.0294 | -5.5013 | 4428.988 | 12147.3597 | -0.0012421
131 |  | 98.7569 | 93.3598 | 4187 | 0.00022578 | 6.0294 | 6.0296 | -5.5013 | 4429.0469 | 12240.7195 | -0.0012421
132 |  | 98.7569 | 93.3586 | 4187 | 0.00022578 | 6.0296 | 6.0298 | -5.5013 | 4429.1058 | 12334.0781 | -0.0012421
133 |  | 98.7569 | 93.3573 | 4187 | 0.00022578 | 6.0298 | 6.0301 | -5.5013 | 4429.1648 | 12427.4354 | -0.0012421
134 |  | 98.7569 | 93.3561 | 4187 | 0.00022577 | 6.0301 | 6.0303 | -5.5013 | 4429.2237 | 12520.7915 | -0.001242
135 |  | 98.7569 | 93.3549 | 4187 | 0.00022577 | 6.0303 | 6.0305 | -5.5013 | 4429.2826 | 12614.1464 | -0.001242
136 |  | 98.7569 | 93.3536 | 4187 | 0.00022577 | 6.0305 | 6.0307 | -5.5013 | 4429.3416 | 12707.5 | -0.001242
137 |  | 98.7569 | 93.3524 | 4187 | 0.00022576 | 6.0307 | 6.031 | -5.5013 | 4429.4005 | 12800.8524 | -0.001242
138 |  | 98.7569 | 93.3511 | 4187 | 0.00022576 | 6.031 | 6.0312 | -5.5013 | 4429.4594 | 12894.2035 | -0.001242
139 |  | 98.7569 | 93.3499 | 4187 | 0.00022576 | 6.0312 | 6.0314 | -5.5013 | 4429.5183 | 12987.5534 | -0.001242
140 |  | 98.7569 | 93.3486 | 4187 | 0.00022576 | 6.0314 | 6.0316 | -5.5013 | 4429.5773 | 13080.902 | -0.0012419
141 |  | 98.7569 | 93.3474 | 4187 | 0.00022575 | 6.0316 | 6.0319 | -5.5013 | 4429.6362 | 13174.2494 | -0.0012419
142 |  | 98.7569 | 93.3462 | 4187 | 0.00022575 | 6.0319 | 6.0321 | -5.5013 | 4429.6951 | 13267.5956 | -0.0012419
143 |  | 98.7569 | 93.3449 | 4187 | 0.00022575 | 6.0321 | 6.0323 | -5.5013 | 4429.7541 | 13360.9405 | -0.0012419
144 |  | 98.7569 | 93.3437 | 4187 | 0.00022574 | 6.0323 | 6.0325 | -5.5013 | 4429.813 | 13454.2842 | -0.0012419
145 |  | 98.7569 | 93.3424 | 4187 | 0.00022574 | 6.0325 | 6.0328 | -5.5013 | 4429.872 | 13547.6266 | -0.0012419
146 |  | 98.7569 | 93.3412 | 4187 | 0.00022574 | 6.0328 | 6.033 | -5.5013 | 4429.9309 | 13640.9678 | -0.0012418
147 |  | 98.7569 | 93.34 | 4187 | 0.00022573 | 6.033 | 6.0332 | -5.5013 | 4429.9898 | 13734.3078 | -0.0012418
148 |  | 98.7569 | 93.3387 | 4187 | 0.00022573 | 6.0332 | 6.0334 | -5.5013 | 4430.0488 | 13827.6465 | -0.0012418
149 |  | 98.7569 | 93.3375 | 4187 | 0.00022573 | 6.0334 | 6.0337 | -5.5013 | 4430.1077 | 13920.984 | -0.0012418
150 |  | 98.7569 | 93.3362 | 4187 | 0.00022573 | 6.0337 | 6.0339 | -5.5013 | 4430.1666 | 14014.3202 | -0.0012418
151 |  | 98.7569 | 93.335 | 4187 | 0.00022572 | 6.0339 | 6.0341 | -5.5013 | 4430.2256 | 14107.6552 | -0.0012418
152 |  | 98.7569 | 93.3337 | 4187 | 0.00022572 | 6.0341 | 6.0343 | -5.5013 | 4430.2845 | 14200.9889 | -0.0012417
153 |  | 98.7569 | 93.3325 | 4187 | 0.00022572 | 6.0343 | 6.0346 | -5.5013 | 4430.3435 | 14294.3214 | -0.0012417
154 |  | 98.7569 | 93.3313 | 4187 | 0.00022571 | 6.0346 | 6.0348 | -5.5013 | 4430.4024 | 14387.6527 | -0.0012417
155 |  | 98.7569 | 93.33 | 4187 | 0.00022571 | 6.0348 | 6.035 | -5.5013 | 4430.4614 | 14480.9827 | -0.0012417
156 |  | 98.7569 | 93.3288 | 4187 | 0.00022571 | 6.035 | 6.0352 | -5.5013 | 4430.5203 | 14574.3115 | -0.0012417
157 |  | 98.7569 | 93.3275 | 4187 | 0.0002257 | 6.0352 | 6.0355 | -5.5013 | 4430.5792 | 14667.639 | -0.0012417
158 |  | 98.7569 | 93.3263 | 4187 | 0.0002257 | 6.0355 | 6.0357 | -5.5013 | 4430.6382 | 14760.9653 | -0.0012416
159 |  | 98.7569 | 93.3251 | 4187 | 0.0002257 | 6.0357 | 6.0359 | -5.5013 | 4430.6971 | 14854.2904 | -0.0012416
160 |  | 98.7569 | 93.3238 | 4187 | 0.0002257 | 6.0359 | 6.0361 | -5.5013 | 4430.7561 | 14947.6142 | -0.0012416
161 |  | 98.7569 | 93.3226 | 4187 | 0.00022569 | 6.0361 | 6.0364 | -5.5013 | 4430.815 | 15040.9367 | -0.0012416
162 |  | 98.7569 | 93.3213 | 4187 | 0.00022569 | 6.0364 | 6.0366 | -5.5013 | 4430.874 | 15134.2581 | -0.0012416
163 |  | 98.7569 | 93.3201 | 4187 | 0.00022569 | 6.0366 | 6.0368 | -5.5013 | 4430.9329 | 15227.5781 | -0.0012416
164 |  | 98.7569 | 93.3188 | 4187 | 0.00022568 | 6.0368 | 6.0371 | -5.5013 | 4430.9919 | 15320.897 | -0.0012415
165 |  | 98.7569 | 93.3176 | 4187 | 0.00022568 | 6.0371 | 6.0373 | -5.5013 | 4431.0508 | 15414.2146 | -0.0012415
166 |  | 98.7569 | 93.3164 | 4187 | 0.00022568 | 6.0373 | 6.0375 | -5.5013 | 4431.1098 | 15507.531 | -0.0012415
167 |  | 98.7569 | 93.3151 | 4187 | 0.00022567 | 6.0375 | 6.0377 | -5.5013 | 4431.1687 | 15600.8461 | -0.0012415
168 |  | 98.7569 | 93.3139 | 4187 | 0.00022567 | 6.0377 | 6.038 | -5.5013 | 4431.2277 | 15694.1599 | -0.0012415
169 |  | 98.7569 | 93.3126 | 4187 | 0.00022567 | 6.038 | 6.0382 | -5.5013 | 4431.2867 | 15787.4726 | -0.0012415
170 |  | 98.7569 | 93.3114 | 4187 | 0.00022567 | 6.0382 | 6.0384 | -5.5013 | 4431.3456 | 15880.784 | -0.0012414
171 |  | 98.7569 | 93.3102 | 4187 | 0.00022566 | 6.0384 | 6.0386 | -5.5013 | 4431.4046 | 15974.0941 | -0.0012414
172 |  | 98.7569 | 93.3089 | 4187 | 0.00022566 | 6.0386 | 6.0389 | -5.5013 | 4431.4635 | 16067.403 | -0.0012414
173 |  | 98.7569 | 93.3077 | 4187 | 0.00022566 | 6.0389 | 6.0391 | -5.5013 | 4431.5225 | 16160.7107 | -0.0012414
174 |  | 98.7569 | 93.3064 | 4187 | 0.00022565 | 6.0391 | 6.0393 | -5.5013 | 4431.5814 | 16254.0171 | -0.0012414
175 |  | 98.7569 | 93.3052 | 4187 | 0.00022565 | 6.0393 | 6.0395 | -5.5013 | 4431.6404 | 16347.3223 | -0.0012414
176 |  | 98.7569 | 93.3039 | 4187 | 0.00022565 | 6.0395 | 6.0398 | -5.5013 | 4431.6994 | 16440.6263 | -0.0012413
177 |  | 98.7569 | 93.3027 | 4187 | 0.00022564 | 6.0398 | 6.04 | -5.5013 | 4431.7583 | 16533.929 | -0.0012413
178 |  | 98.7569 | 93.3015 | 4187 | 0.00022564 | 6.04 | 6.0402 | -5.5013 | 4431.8173 | 16627.2304 | -0.0012413
179 |  | 98.7569 | 93.3002 | 4187 | 0.00022564 | 6.0402 | 6.0404 | -5.5013 | 4431.8763 | 16720.5307 | -0.0012413
180 |  | 98.7569 | 93.299 | 4187 | 0.00022564 | 6.0404 | 6.0407 | -5.5013 | 4431.9352 | 16813.8297 | -0.0012413
181 |  | 98.7569 | 93.2977 | 4187 | 0.00022563 | 6.0407 | 6.0409 | -5.5013 | 4431.9942 | 16907.1274 | -0.0012413
182 |  | 98.7569 | 93.2965 | 4187 | 0.00022563 | 6.0409 | 6.0411 | -5.5013 | 4432.0531 | 17000.4239 | -0.0012412
183 |  | 98.7569 | 93.2953 | 4187 | 0.00022563 | 6.0411 | 6.0413 | -5.5013 | 4432.1121 | 17093.7191 | -0.0012412
184 |  | 98.7569 | 93.294 | 4187 | 0.00022562 | 6.0413 | 6.0416 | -5.5013 | 4432.1711 | 17187.0132 | -0.0012412
185 |  | 98.7569 | 93.2928 | 4187 | 0.00022562 | 6.0416 | 6.0418 | -5.5013 | 4432.23 | 17280.3059 | -0.0012412
186 |  | 98.7569 | 93.2915 | 4187 | 0.00022562 | 6.0418 | 6.042 | -5.5013 | 4432.289 | 17373.5975 | -0.0012412
187 |  | 98.7569 | 93.2903 | 4187 | 0.00022561 | 6.042 | 6.0422 | -5.5013 | 4432.348 | 17466.8878 | -0.0012412
188 |  | 98.7569 | 93.2891 | 4187 | 0.00022561 | 6.0422 | 6.0425 | -5.5013 | 4432.407 | 17560.1768 | -0.0012411
189 |  | 98.7569 | 93.2878 | 4187 | 0.00022561 | 6.0425 | 6.0427 | -5.5013 | 4432.4659 | 17653.4646 | -0.0012411
190 |  | 98.7569 | 93.2866 | 4187 | 0.00022561 | 6.0427 | 6.0429 | -5.5013 | 4432.5249 | 17746.7512 | -0.0012411
191 |  | 98.7569 | 93.2853 | 4187 | 0.0002256 | 6.0429 | 6.0431 | -5.5013 | 4432.5839 | 17840.0365 | -0.0012411
192 |  | 98.7569 | 93.2841 | 4187 | 0.0002256 | 6.0431 | 6.0434 | -5.5013 | 4432.6428 | 17933.3206 | -0.0012411
193 |  | 98.7569 | 93.2828 | 4187 | 0.0002256 | 6.0434 | 6.0436 | -5.5013 | 4432.7018 | 18026.6035 | -0.0012411
194 |  | 98.7569 | 93.2816 | 4187 | 0.00022559 | 6.0436 | 6.0438 | -5.5013 | 4432.7608 | 18119.8851 | -0.001241
195 |  | 98.7569 | 93.2804 | 4187 | 0.00022559 | 6.0438 | 6.044 | -5.5013 | 4432.8198 | 18213.1654 | -0.001241
196 |  | 98.7569 | 93.2791 | 4187 | 0.00022559 | 6.044 | 6.0443 | -5.5013 | 4432.8787 | 18306.4445 | -0.001241
197 |  | 98.7569 | 93.2779 | 4187 | 0.00022558 | 6.0443 | 6.0445 | -5.5013 | 4432.9377 | 18399.7224 | -0.001241
198 |  | 98.7569 | 93.2766 | 4187 | 0.00022558 | 6.0445 | 6.0447 | -5.5013 | 4432.9967 | 18492.9991 | -0.001241
199 |  | 98.7569 | 93.2754 | 4187 | 0.00022558 | 6.0447 | 6.0449 | -5.5013 | 4433.0557 | 18586.2745 | -0.001241
200 |  | 98.7569 | 93.2742 | 4187 | 0.00022558 | 6.0449 | 6.0452 | -5.5013 | 4433.1147 | 18679.5486 | -0.0012409
201 |  | 98.7569 | 93.2729 | 4187 | 0.00022557 | 6.0452 | 6.0454 | -5.5013 | 4433.1736 | 18772.8215 | -0.0012409
202 |  | 98.7569 | 93.2717 | 4187 | 0.00022557 | 6.0454 | 6.0456 | -5.5013 | 4433.2326 | 18866.0932 | -0.0012409
203 |  | 98.7569 | 93.2704 | 4187 | 0.00022557 | 6.0456 | 6.0459 | -5.5013 | 4433.2916 | 18959.3637 | -0.0012409
204 |  | 98.7569 | 93.2692 | 4187 | 0.00022556 | 6.0459 | 6.0461 | -5.5013 | 4433.3506 | 19052.6329 | -0.0012409
205 |  | 98.7569 | 93.268 | 4187 | 0.00022556 | 6.0461 | 6.0463 | -5.5013 | 4433.4096 | 19145.9008 | -0.0012409
206 |  | 98.7569 | 93.2667 | 4187 | 0.00022556 | 6.0463 | 6.0465 | -5.5013 | 4433.4685 | 19239.1675 | -0.0012408
207 |  | 98.7569 | 93.2655 | 4187 | 0.00022555 | 6.0465 | 6.0468 | -5.5013 | 4433.5275 | 19332.433 | -0.0012408
208 |  | 98.7569 | 93.2642 | 4187 | 0.00022555 | 6.0468 | 6.047 | -5.5013 | 4433.5865 | 19425.6972 | -0.0012408
209 |  | 98.7569 | 93.263 | 4187 | 0.00022555 | 6.047 | 6.0472 | -5.5013 | 4433.6455 | 19518.9602 | -0.0012408
210 |  | 98.7569 | 93.2618 | 4187 | 0.00022555 | 6.0472 | 6.0474 | -5.5013 | 4433.7045 | 19612.222 | -0.0012408
211 |  | 98.7569 | 93.2605 | 4187 | 0.00022554 | 6.0474 | 6.0477 | -5.5013 | 4433.7635 | 19705.4825 | -0.0012408
212 |  | 98.7569 | 93.2593 | 4187 | 0.00022554 | 6.0477 | 6.0479 | -5.5013 | 4433.8225 | 19798.7417 | -0.0012407
213 |  | 98.7569 | 93.258 | 4187 | 0.00022554 | 6.0479 | 6.0481 | -5.5013 | 4433.8815 | 19891.9998 | -0.0012407
214 |  | 98.7569 | 93.2568 | 4187 | 0.00022553 | 6.0481 | 6.0483 | -5.5013 | 4433.9405 | 19985.2566 | -0.0012407
215 |  | 98.7569 | 93.2555 | 4187 | 0.00022553 | 6.0483 | 6.0486 | -5.5013 | 4433.9994 | 20078.5121 | -0.0012407
216 |  | 98.7569 | 93.2543 | 4187 | 0.00022553 | 6.0486 | 6.0488 | -5.5013 | 4434.0584 | 20171.7664 | -0.0012407
217 |  | 98.7569 | 93.2531 | 4187 | 0.00022552 | 6.0488 | 6.049 | -5.5013 | 4434.1174 | 20265.0195 | -0.0012407
218 |  | 98.7569 | 93.2518 | 4187 | 0.00022552 | 6.049 | 6.0492 | -5.5013 | 4434.1764 | 20358.2713 | -0.0012406
219 |  | 98.7569 | 93.2506 | 4187 | 0.00022552 | 6.0492 | 6.0495 | -5.5013 | 4434.2354 | 20451.5219 | -0.0012406
220 |  | 98.7569 | 93.2493 | 4187 | 0.00022552 | 6.0495 | 6.0497 | -5.5013 | 4434.2944 | 20544.7712 | -0.0012406
221 |  | 98.7569 | 93.2481 | 4187 | 0.00022551 | 6.0497 | 6.0499 | -5.5013 | 4434.3534 | 20638.0193 | -0.0012406
222 |  | 98.7569 | 93.2469 | 4187 | 0.00022551 | 6.0499 | 6.0501 | -5.5013 | 4434.4124 | 20731.2662 | -0.0012406
223 |  | 98.7569 | 93.2456 | 4187 | 0.00022551 | 6.0501 | 6.0504 | -5.5013 | 4434.4714 | 20824.5118 | -0.0012406
224 |  | 98.7569 | 93.2444 | 4187 | 0.0002255 | 6.0504 | 6.0506 | -5.5013 | 4434.5304 | 20917.7562 | -0.0012406
225 |  | 98.7569 | 93.2431 | 4187 | 0.0002255 | 6.0506 | 6.0508 | -5.5013 | 4434.5894 | 21010.9993 | -0.0012405
226 |  | 98.7569 | 93.2419 | 4187 | 0.0002255 | 6.0508 | 6.051 | -5.5013 | 4434.6484 | 21104.2412 | -0.0012405
227 |  | 98.7569 | 93.2407 | 4187 | 0.00022549 | 6.051 | 6.0513 | -5.5013 | 4434.7074 | 21197.4819 | -0.0012405
228 |  | 98.7569 | 93.2394 | 4187 | 0.00022549 | 6.0513 | 6.0515 | -5.5013 | 4434.7664 | 21290.7213 | -0.0012405
229 |  | 98.7569 | 93.2382 | 4187 | 0.00022549 | 6.0515 | 6.0517 | -5.5013 | 4434.8254 | 21383.9595 | -0.0012405
230 |  | 98.7569 | 93.2369 | 4187 | 0.00022549 | 6.0517 | 6.0519 | -5.5013 | 4434.8844 | 21477.1964 | -0.0012405
231 |  | 98.7569 | 93.2357 | 4187 | 0.00022548 | 6.0519 | 6.0522 | -5.5013 | 4434.9434 | 21570.4321 | -0.0012404
232 |  | 98.7569 | 93.2345 | 4187 | 0.00022548 | 6.0522 | 6.0524 | -5.5013 | 4435.0024 | 21663.6666 | -0.0012404
233 |  | 98.7569 | 93.2332 | 4187 | 0.00022548 | 6.0524 | 6.0526 | -5.5013 | 4435.0614 | 21756.8998 | -0.0012404
234 |  | 98.7569 | 93.232 | 4187 | 0.00022547 | 6.0526 | 6.0528 | -5.5013 | 4435.1204 | 21850.1318 | -0.0012404
235 |  | 98.7569 | 93.2307 | 4187 | 0.00022547 | 6.0528 | 6.0531 | -5.5013 | 4435.1794 | 21943.3625 | -0.0012404
236 |  | 98.7569 | 93.2295 | 4187 | 0.00022547 | 6.0531 | 6.0533 | -5.5013 | 4435.2384 | 22036.592 | -0.0012404

## CLX450
|  |  | buis | verlies W/M | L /°C/sec
diam | wandikte |  | inhoud l/m |  | W/M
450 | 25.5 | 3.1416 | 125.0362 | 96.8206 | 4187
[8 empty] | J/sec/mtr | aantal mtr. | verlies
|  | buis | verlies W/M | L /°C/sec | verlies temp | begintemp | eindtemp | verlies | bij 1°C | totaal J/sec
|  | inhoud L |  | W/M | °C per M | °C | °C | per m°C | daling | aantal mtr
1 | 450 | 125.0362 | 96.8206 | 4187 | 0.00018494 | 6 | 6.0002 | -5.6953 | 5407.1821 | 96.8206 | -0.0010533
2 |  | 125.0362 | 96.8195 | 4187 | 0.00018494 | 6.0002 | 6.0004 | -5.6953 | 5407.241 | 193.6401 | -0.0010533
3 |  | 125.0362 | 96.8185 | 4187 | 0.00018494 | 6.0004 | 6.0006 | -5.6953 | 5407.2998 | 290.4585 | -0.0010533
4 |  | 125.0362 | 96.8174 | 4187 | 0.00018493 | 6.0006 | 6.0007 | -5.6953 | 5407.3586 | 387.276 | -0.0010533
5 |  | 125.0362 | 96.8164 | 4187 | 0.00018493 | 6.0007 | 6.0009 | -5.6953 | 5407.4174 | 484.0923 | -0.0010532
6 |  | 125.0362 | 96.8153 | 4187 | 0.00018493 | 6.0009 | 6.0011 | -5.6953 | 5407.4763 | 580.9076 | -0.0010532
7 |  | 125.0362 | 96.8143 | 4187 | 0.00018493 | 6.0011 | 6.0013 | -5.6953 | 5407.5351 | 677.7219 | -0.0010532
8 |  | 125.0362 | 96.8132 | 4187 | 0.00018493 | 6.0013 | 6.0015 | -5.6953 | 5407.5939 | 774.5351 | -0.0010532
9 |  | 125.0362 | 96.8121 | 4187 | 0.00018492 | 6.0015 | 6.0017 | -5.6953 | 5407.6527 | 871.3472 | -0.0010532
10 |  | 125.0362 | 96.8111 | 4187 | 0.00018492 | 6.0017 | 6.0018 | -5.6953 | 5407.7116 | 968.1583 | -0.0010532
11 |  | 125.0362 | 96.81 | 4187 | 0.00018492 | 6.0018 | 6.002 | -5.6953 | 5407.7704 | 1064.9683 | -0.0010532
12 |  | 125.0362 | 96.809 | 4187 | 0.00018492 | 6.002 | 6.0022 | -5.6953 | 5407.8292 | 1161.7773 | -0.0010532
13 |  | 125.0362 | 96.8079 | 4187 | 0.00018492 | 6.0022 | 6.0024 | -5.6953 | 5407.8881 | 1258.5853 | -0.0010532
14 |  | 125.0362 | 96.8069 | 4187 | 0.00018491 | 6.0024 | 6.0026 | -5.6953 | 5407.9469 | 1355.3921 | -0.0010531
15 |  | 125.0362 | 96.8058 | 4187 | 0.00018491 | 6.0026 | 6.0028 | -5.6953 | 5408.0057 | 1452.198 | -0.0010531
16 |  | 125.0362 | 96.8048 | 4187 | 0.00018491 | 6.0028 | 6.003 | -5.6953 | 5408.0646 | 1549.0027 | -0.0010531
17 |  | 125.0362 | 96.8037 | 4187 | 0.00018491 | 6.003 | 6.0031 | -5.6953 | 5408.1234 | 1645.8064 | -0.0010531
18 |  | 125.0362 | 96.8027 | 4187 | 0.00018491 | 6.0031 | 6.0033 | -5.6953 | 5408.1822 | 1742.6091 | -0.0010531
19 |  | 125.0362 | 96.8016 | 4187 | 0.0001849 | 6.0033 | 6.0035 | -5.6953 | 5408.2411 | 1839.4107 | -0.0010531
20 |  | 125.0362 | 96.8006 | 4187 | 0.0001849 | 6.0035 | 6.0037 | -5.6953 | 5408.2999 | 1936.2113 | -0.0010531
21 |  | 125.0362 | 96.7995 | 4187 | 0.0001849 | 6.0037 | 6.0039 | -5.6953 | 5408.3587 | 2033.0108 | -0.0010531
22 |  | 125.0362 | 96.7985 | 4187 | 0.0001849 | 6.0039 | 6.0041 | -5.6953 | 5408.4176 | 2129.8092 | -0.001053
23 |  | 125.0362 | 96.7974 | 4187 | 0.00018489 | 6.0041 | 6.0043 | -5.6953 | 5408.4764 | 2226.6066 | -0.001053
24 |  | 125.0362 | 96.7963 | 4187 | 0.00018489 | 6.0043 | 6.0044 | -5.6953 | 5408.5353 | 2323.403 | -0.001053
25 |  | 125.0362 | 96.7953 | 4187 | 0.00018489 | 6.0044 | 6.0046 | -5.6953 | 5408.5941 | 2420.1983 | -0.001053
26 |  | 125.0362 | 96.7942 | 4187 | 0.00018489 | 6.0046 | 6.0048 | -5.6953 | 5408.6529 | 2516.9925 | -0.001053
27 |  | 125.0362 | 96.7932 | 4187 | 0.00018489 | 6.0048 | 6.005 | -5.6953 | 5408.7118 | 2613.7857 | -0.001053
28 |  | 125.0362 | 96.7921 | 4187 | 0.00018488 | 6.005 | 6.0052 | -5.6953 | 5408.7706 | 2710.5779 | -0.001053
29 |  | 125.0362 | 96.7911 | 4187 | 0.00018488 | 6.0052 | 6.0054 | -5.6953 | 5408.8295 | 2807.3689 | -0.001053
30 |  | 125.0362 | 96.79 | 4187 | 0.00018488 | 6.0054 | 6.0055 | -5.6953 | 5408.8883 | 2904.159 | -0.001053
31 |  | 125.0362 | 96.789 | 4187 | 0.00018488 | 6.0055 | 6.0057 | -5.6953 | 5408.9471 | 3000.9479 | -0.0010529
32 |  | 125.0362 | 96.7879 | 4187 | 0.00018488 | 6.0057 | 6.0059 | -5.6953 | 5409.006 | 3097.7359 | -0.0010529
33 |  | 125.0362 | 96.7869 | 4187 | 0.00018487 | 6.0059 | 6.0061 | -5.6953 | 5409.0648 | 3194.5227 | -0.0010529
34 |  | 125.0362 | 96.7858 | 4187 | 0.00018487 | 6.0061 | 6.0063 | -5.6953 | 5409.1237 | 3291.3086 | -0.0010529
35 |  | 125.0362 | 96.7848 | 4187 | 0.00018487 | 6.0063 | 6.0065 | -5.6953 | 5409.1825 | 3388.0933 | -0.0010529
36 |  | 125.0362 | 96.7837 | 4187 | 0.00018487 | 6.0065 | 6.0067 | -5.6953 | 5409.2414 | 3484.877 | -0.0010529
37 |  | 125.0362 | 96.7827 | 4187 | 0.00018487 | 6.0067 | 6.0068 | -5.6953 | 5409.3002 | 3581.6597 | -0.0010529
38 |  | 125.0362 | 96.7816 | 4187 | 0.00018486 | 6.0068 | 6.007 | -5.6953 | 5409.3591 | 3678.4413 | -0.0010529
39 |  | 125.0362 | 96.7806 | 4187 | 0.00018486 | 6.007 | 6.0072 | -5.6953 | 5409.4179 | 3775.2218 | -0.0010529
40 |  | 125.0362 | 96.7795 | 4187 | 0.00018486 | 6.0072 | 6.0074 | -5.6953 | 5409.4768 | 3872.0013 | -0.0010528
41 |  | 125.0362 | 96.7784 | 4187 | 0.00018486 | 6.0074 | 6.0076 | -5.6953 | 5409.5356 | 3968.7798 | -0.0010528
42 |  | 125.0362 | 96.7774 | 4187 | 0.00018486 | 6.0076 | 6.0078 | -5.6953 | 5409.5945 | 4065.5572 | -0.0010528
43 |  | 125.0362 | 96.7763 | 4187 | 0.00018485 | 6.0078 | 6.008 | -5.6953 | 5409.6533 | 4162.3335 | -0.0010528
44 |  | 125.0362 | 96.7753 | 4187 | 0.00018485 | 6.008 | 6.0081 | -5.6953 | 5409.7122 | 4259.1088 | -0.0010528
45 |  | 125.0362 | 96.7742 | 4187 | 0.00018485 | 6.0081 | 6.0083 | -5.6953 | 5409.771 | 4355.8831 | -0.0010528
46 |  | 125.0362 | 96.7732 | 4187 | 0.00018485 | 6.0083 | 6.0085 | -5.6953 | 5409.8299 | 4452.6562 | -0.0010528
47 |  | 125.0362 | 96.7721 | 4187 | 0.00018485 | 6.0085 | 6.0087 | -5.6953 | 5409.8887 | 4549.4284 | -0.0010528
48 |  | 125.0362 | 96.7711 | 4187 | 0.00018484 | 6.0087 | 6.0089 | -5.6953 | 5409.9476 | 4646.1994 | -0.0010528
49 |  | 125.0362 | 96.77 | 4187 | 0.00018484 | 6.0089 | 6.0091 | -5.6953 | 5410.0064 | 4742.9695 | -0.0010527
50 |  | 125.0362 | 96.769 | 4187 | 0.00018484 | 6.0091 | 6.0092 | -5.6953 | 5410.0653 | 4839.7384 | -0.0010527
51 |  | 125.0362 | 96.7679 | 4187 | 0.00018484 | 6.0092 | 6.0094 | -5.6953 | 5410.1241 | 4936.5064 | -0.0010527
52 |  | 125.0362 | 96.7669 | 4187 | 0.00018484 | 6.0094 | 6.0096 | -5.6953 | 5410.183 | 5033.2732 | -0.0010527
53 |  | 125.0362 | 96.7658 | 4187 | 0.00018483 | 6.0096 | 6.0098 | -5.6953 | 5410.2418 | 5130.039 | -0.0010527
54 |  | 125.0362 | 96.7648 | 4187 | 0.00018483 | 6.0098 | 6.01 | -5.6953 | 5410.3007 | 5226.8038 | -0.0010527
55 |  | 125.0362 | 96.7637 | 4187 | 0.00018483 | 6.01 | 6.0102 | -5.6953 | 5410.3596 | 5323.5675 | -0.0010527
56 |  | 125.0362 | 96.7627 | 4187 | 0.00018483 | 6.0102 | 6.0104 | -5.6953 | 5410.4184 | 5420.3302 | -0.0010527
57 |  | 125.0362 | 96.7616 | 4187 | 0.00018483 | 6.0104 | 6.0105 | -5.6953 | 5410.4773 | 5517.0918 | -0.0010526
58 |  | 125.0362 | 96.7606 | 4187 | 0.00018482 | 6.0105 | 6.0107 | -5.6953 | 5410.5361 | 5613.8523 | -0.0010526
59 |  | 125.0362 | 96.7595 | 4187 | 0.00018482 | 6.0107 | 6.0109 | -5.6953 | 5410.595 | 5710.6118 | -0.0010526
60 |  | 125.0362 | 96.7584 | 4187 | 0.00018482 | 6.0109 | 6.0111 | -5.6953 | 5410.6539 | 5807.3703 | -0.0010526
61 |  | 125.0362 | 96.7574 | 4187 | 0.00018482 | 6.0111 | 6.0113 | -5.6953 | 5410.7127 | 5904.1277 | -0.0010526
62 |  | 125.0362 | 96.7563 | 4187 | 0.00018482 | 6.0113 | 6.0115 | -5.6953 | 5410.7716 | 6000.884 | -0.0010526
63 |  | 125.0362 | 96.7553 | 4187 | 0.00018481 | 6.0115 | 6.0116 | -5.6953 | 5410.8304 | 6097.6393 | -0.0010526
64 |  | 125.0362 | 96.7542 | 4187 | 0.00018481 | 6.0116 | 6.0118 | -5.6953 | 5410.8893 | 6194.3935 | -0.0010526
65 |  | 125.0362 | 96.7532 | 4187 | 0.00018481 | 6.0118 | 6.012 | -5.6953 | 5410.9482 | 6291.1467 | -0.0010526
66 |  | 125.0362 | 96.7521 | 4187 | 0.00018481 | 6.012 | 6.0122 | -5.6953 | 5411.007 | 6387.8988 | -0.0010525
67 |  | 125.0362 | 96.7511 | 4187 | 0.00018481 | 6.0122 | 6.0124 | -5.6953 | 5411.0659 | 6484.6499 | -0.0010525
68 |  | 125.0362 | 96.75 | 4187 | 0.0001848 | 6.0124 | 6.0126 | -5.6953 | 5411.1248 | 6581.3999 | -0.0010525
69 |  | 125.0362 | 96.749 | 4187 | 0.0001848 | 6.0126 | 6.0128 | -5.6953 | 5411.1836 | 6678.1489 | -0.0010525
70 |  | 125.0362 | 96.7479 | 4187 | 0.0001848 | 6.0128 | 6.0129 | -5.6953 | 5411.2425 | 6774.8968 | -0.0010525
71 |  | 125.0362 | 96.7469 | 4187 | 0.0001848 | 6.0129 | 6.0131 | -5.6953 | 5411.3014 | 6871.6437 | -0.0010525
72 |  | 125.0362 | 96.7458 | 4187 | 0.0001848 | 6.0131 | 6.0133 | -5.6953 | 5411.3602 | 6968.3895 | -0.0010525
73 |  | 125.0362 | 96.7448 | 4187 | 0.00018479 | 6.0133 | 6.0135 | -5.6953 | 5411.4191 | 7065.1343 | -0.0010525
74 |  | 125.0362 | 96.7437 | 4187 | 0.00018479 | 6.0135 | 6.0137 | -5.6953 | 5411.478 | 7161.878 | -0.0010525
75 |  | 125.0362 | 96.7427 | 4187 | 0.00018479 | 6.0137 | 6.0139 | -5.6953 | 5411.5369 | 7258.6206 | -0.0010524
76 |  | 125.0362 | 96.7416 | 4187 | 0.00018479 | 6.0139 | 6.014 | -5.6953 | 5411.5957 | 7355.3622 | -0.0010524
77 |  | 125.0362 | 96.7406 | 4187 | 0.00018479 | 6.014 | 6.0142 | -5.6953 | 5411.6546 | 7452.1028 | -0.0010524
78 |  | 125.0362 | 96.7395 | 4187 | 0.00018478 | 6.0142 | 6.0144 | -5.6953 | 5411.7135 | 7548.8423 | -0.0010524
79 |  | 125.0362 | 96.7384 | 4187 | 0.00018478 | 6.0144 | 6.0146 | -5.6953 | 5411.7723 | 7645.5807 | -0.0010524
80 |  | 125.0362 | 96.7374 | 4187 | 0.00018478 | 6.0146 | 6.0148 | -5.6953 | 5411.8312 | 7742.3181 | -0.0010524
81 |  | 125.0362 | 96.7363 | 4187 | 0.00018478 | 6.0148 | 6.015 | -5.6953 | 5411.8901 | 7839.0545 | -0.0010524
82 |  | 125.0362 | 96.7353 | 4187 | 0.00018478 | 6.015 | 6.0152 | -5.6953 | 5411.949 | 7935.7898 | -0.0010524
83 |  | 125.0362 | 96.7342 | 4187 | 0.00018477 | 6.0152 | 6.0153 | -5.6953 | 5412.0078 | 8032.524 | -0.0010524
84 |  | 125.0362 | 96.7332 | 4187 | 0.00018477 | 6.0153 | 6.0155 | -5.6953 | 5412.0667 | 8129.2572 | -0.0010523
85 |  | 125.0362 | 96.7321 | 4187 | 0.00018477 | 6.0155 | 6.0157 | -5.6953 | 5412.1256 | 8225.9893 | -0.0010523
86 |  | 125.0362 | 96.7311 | 4187 | 0.00018477 | 6.0157 | 6.0159 | -5.6953 | 5412.1845 | 8322.7204 | -0.0010523
87 |  | 125.0362 | 96.73 | 4187 | 0.00018477 | 6.0159 | 6.0161 | -5.6953 | 5412.2434 | 8419.4504 | -0.0010523
88 |  | 125.0362 | 96.729 | 4187 | 0.00018476 | 6.0161 | 6.0163 | -5.6953 | 5412.3022 | 8516.1794 | -0.0010523
89 |  | 125.0362 | 96.7279 | 4187 | 0.00018476 | 6.0163 | 6.0165 | -5.6953 | 5412.3611 | 8612.9073 | -0.0010523
90 |  | 125.0362 | 96.7269 | 4187 | 0.00018476 | 6.0165 | 6.0166 | -5.6953 | 5412.42 | 8709.6342 | -0.0010523
91 |  | 125.0362 | 96.7258 | 4187 | 0.00018476 | 6.0166 | 6.0168 | -5.6953 | 5412.4789 | 8806.36 | -0.0010523
92 |  | 125.0362 | 96.7248 | 4187 | 0.00018476 | 6.0168 | 6.017 | -5.6953 | 5412.5378 | 8903.0848 | -0.0010522
93 |  | 125.0362 | 96.7237 | 4187 | 0.00018475 | 6.017 | 6.0172 | -5.6953 | 5412.5966 | 8999.8085 | -0.0010522
94 |  | 125.0362 | 96.7227 | 4187 | 0.00018475 | 6.0172 | 6.0174 | -5.6953 | 5412.6555 | 9096.5312 | -0.0010522
95 |  | 125.0362 | 96.7216 | 4187 | 0.00018475 | 6.0174 | 6.0176 | -5.6953 | 5412.7144 | 9193.2528 | -0.0010522
96 |  | 125.0362 | 96.7206 | 4187 | 0.00018475 | 6.0176 | 6.0177 | -5.6953 | 5412.7733 | 9289.9734 | -0.0010522
97 |  | 125.0362 | 96.7195 | 4187 | 0.00018475 | 6.0177 | 6.0179 | -5.6953 | 5412.8322 | 9386.6929 | -0.0010522
98 |  | 125.0362 | 96.7185 | 4187 | 0.00018474 | 6.0179 | 6.0181 | -5.6953 | 5412.8911 | 9483.4113 | -0.0010522
99 |  | 125.0362 | 96.7174 | 4187 | 0.00018474 | 6.0181 | 6.0183 | -5.6953 | 5412.9499 | 9580.1287 | -0.0010522
100 |  | 125.0362 | 96.7163 | 4187 | 0.00018474 | 6.0183 | 6.0185 | -5.6953 | 5413.0088 | 9676.8451 | -0.0010522
101 |  | 125.0362 | 96.7153 | 4187 | 0.00018474 | 6.0185 | 6.0187 | -5.6953 | 5413.0677 | 9773.5604 | -0.0010521
102 |  | 125.0362 | 96.7142 | 4187 | 0.00018474 | 6.0187 | 6.0189 | -5.6953 | 5413.1266 | 9870.2746 | -0.0010521
103 |  | 125.0362 | 96.7132 | 4187 | 0.00018473 | 6.0189 | 6.019 | -5.6953 | 5413.1855 | 9966.9878 | -0.0010521
104 |  | 125.0362 | 96.7121 | 4187 | 0.00018473 | 6.019 | 6.0192 | -5.6953 | 5413.2444 | 10063.6999 | -0.0010521
105 |  | 125.0362 | 96.7111 | 4187 | 0.00018473 | 6.0192 | 6.0194 | -5.6953 | 5413.3033 | 10160.411 | -0.0010521
106 |  | 125.0362 | 96.71 | 4187 | 0.00018473 | 6.0194 | 6.0196 | -5.6953 | 5413.3622 | 10257.1211 | -0.0010521
107 |  | 125.0362 | 96.709 | 4187 | 0.00018473 | 6.0196 | 6.0198 | -5.6953 | 5413.4211 | 10353.8301 | -0.0010521
108 |  | 125.0362 | 96.7079 | 4187 | 0.00018472 | 6.0198 | 6.02 | -5.6953 | 5413.48 | 10450.538 | -0.0010521
109 |  | 125.0362 | 96.7069 | 4187 | 0.00018472 | 6.02 | 6.0201 | -5.6953 | 5413.5388 | 10547.2449 | -0.0010521
110 |  | 125.0362 | 96.7058 | 4187 | 0.00018472 | 6.0201 | 6.0203 | -5.6953 | 5413.5977 | 10643.9507 | -0.001052
111 |  | 125.0362 | 96.7048 | 4187 | 0.00018472 | 6.0203 | 6.0205 | -5.6953 | 5413.6566 | 10740.6555 | -0.001052
112 |  | 125.0362 | 96.7037 | 4187 | 0.00018472 | 6.0205 | 6.0207 | -5.6953 | 5413.7155 | 10837.3592 | -0.001052
113 |  | 125.0362 | 96.7027 | 4187 | 0.00018471 | 6.0207 | 6.0209 | -5.6953 | 5413.7744 | 10934.0619 | -0.001052
114 |  | 125.0362 | 96.7016 | 4187 | 0.00018471 | 6.0209 | 6.0211 | -5.6953 | 5413.8333 | 11030.7635 | -0.001052
115 |  | 125.0362 | 96.7006 | 4187 | 0.00018471 | 6.0211 | 6.0213 | -5.6953 | 5413.8922 | 11127.4641 | -0.001052
116 |  | 125.0362 | 96.6995 | 4187 | 0.00018471 | 6.0213 | 6.0214 | -5.6953 | 5413.9511 | 11224.1636 | -0.001052
117 |  | 125.0362 | 96.6985 | 4187 | 0.00018471 | 6.0214 | 6.0216 | -5.6953 | 5414.01 | 11320.862 | -0.001052
118 |  | 125.0362 | 96.6974 | 4187 | 0.0001847 | 6.0216 | 6.0218 | -5.6953 | 5414.0689 | 11417.5595 | -0.0010519
119 |  | 125.0362 | 96.6964 | 4187 | 0.0001847 | 6.0218 | 6.022 | -5.6953 | 5414.1278 | 11514.2558 | -0.0010519
120 |  | 125.0362 | 96.6953 | 4187 | 0.0001847 | 6.022 | 6.0222 | -5.6953 | 5414.1867 | 11610.9511 | -0.0010519
121 |  | 125.0362 | 96.6943 | 4187 | 0.0001847 | 6.0222 | 6.0224 | -5.6953 | 5414.2456 | 11707.6454 | -0.0010519
122 |  | 125.0362 | 96.6932 | 4187 | 0.0001847 | 6.0224 | 6.0225 | -5.6953 | 5414.3045 | 11804.3386 | -0.0010519
123 |  | 125.0362 | 96.6922 | 4187 | 0.00018469 | 6.0225 | 6.0227 | -5.6953 | 5414.3634 | 11901.0307 | -0.0010519
124 |  | 125.0362 | 96.6911 | 4187 | 0.00018469 | 6.0227 | 6.0229 | -5.6953 | 5414.4223 | 11997.7218 | -0.0010519
125 |  | 125.0362 | 96.69 | 4187 | 0.00018469 | 6.0229 | 6.0231 | -5.6953 | 5414.4812 | 12094.4119 | -0.0010519
126 |  | 125.0362 | 96.689 | 4187 | 0.00018469 | 6.0231 | 6.0233 | -5.6953 | 5414.5401 | 12191.1009 | -0.0010519
127 |  | 125.0362 | 96.6879 | 4187 | 0.00018469 | 6.0233 | 6.0235 | -5.6953 | 5414.599 | 12287.7888 | -0.0010518
128 |  | 125.0362 | 96.6869 | 4187 | 0.00018468 | 6.0235 | 6.0237 | -5.6953 | 5414.6579 | 12384.4757 | -0.0010518
129 |  | 125.0362 | 96.6858 | 4187 | 0.00018468 | 6.0237 | 6.0238 | -5.6953 | 5414.7168 | 12481.1616 | -0.0010518
130 |  | 125.0362 | 96.6848 | 4187 | 0.00018468 | 6.0238 | 6.024 | -5.6953 | 5414.7757 | 12577.8464 | -0.0010518
131 |  | 125.0362 | 96.6837 | 4187 | 0.00018468 | 6.024 | 6.0242 | -5.6953 | 5414.8346 | 12674.5301 | -0.0010518
132 |  | 125.0362 | 96.6827 | 4187 | 0.00018468 | 6.0242 | 6.0244 | -5.6953 | 5414.8936 | 12771.2128 | -0.0010518
133 |  | 125.0362 | 96.6816 | 4187 | 0.00018467 | 6.0244 | 6.0246 | -5.6953 | 5414.9525 | 12867.8944 | -0.0010518
134 |  | 125.0362 | 96.6806 | 4187 | 0.00018467 | 6.0246 | 6.0248 | -5.6953 | 5415.0114 | 12964.575 | -0.0010518
135 |  | 125.0362 | 96.6795 | 4187 | 0.00018467 | 6.0248 | 6.0249 | -5.6953 | 5415.0703 | 13061.2545 | -0.0010518
136 |  | 125.0362 | 96.6785 | 4187 | 0.00018467 | 6.0249 | 6.0251 | -5.6953 | 5415.1292 | 13157.933 | -0.0010517
137 |  | 125.0362 | 96.6774 | 4187 | 0.00018467 | 6.0251 | 6.0253 | -5.6953 | 5415.1881 | 13254.6104 | -0.0010517
138 |  | 125.0362 | 96.6764 | 4187 | 0.00018466 | 6.0253 | 6.0255 | -5.6953 | 5415.247 | 13351.2868 | -0.0010517
139 |  | 125.0362 | 96.6753 | 4187 | 0.00018466 | 6.0255 | 6.0257 | -5.6953 | 5415.3059 | 13447.9621 | -0.0010517
140 |  | 125.0362 | 96.6743 | 4187 | 0.00018466 | 6.0257 | 6.0259 | -5.6953 | 5415.3648 | 13544.6364 | -0.0010517
141 |  | 125.0362 | 96.6732 | 4187 | 0.00018466 | 6.0259 | 6.0261 | -5.6953 | 5415.4238 | 13641.3096 | -0.0010517
142 |  | 125.0362 | 96.6722 | 4187 | 0.00018466 | 6.0261 | 6.0262 | -5.6953 | 5415.4827 | 13737.9818 | -0.0010517
143 |  | 125.0362 | 96.6711 | 4187 | 0.00018465 | 6.0262 | 6.0264 | -5.6953 | 5415.5416 | 13834.6529 | -0.0010517
144 |  | 125.0362 | 96.6701 | 4187 | 0.00018465 | 6.0264 | 6.0266 | -5.6953 | 5415.6005 | 13931.323 | -0.0010517
145 |  | 125.0362 | 96.669 | 4187 | 0.00018465 | 6.0266 | 6.0268 | -5.6953 | 5415.6594 | 14027.992 | -0.0010516
146 |  | 125.0362 | 96.668 | 4187 | 0.00018465 | 6.0268 | 6.027 | -5.6953 | 5415.7183 | 14124.66 | -0.0010516
147 |  | 125.0362 | 96.6669 | 4187 | 0.00018465 | 6.027 | 6.0272 | -5.6953 | 5415.7772 | 14221.3269 | -0.0010516
148 |  | 125.0362 | 96.6659 | 4187 | 0.00018464 | 6.0272 | 6.0273 | -5.6953 | 5415.8362 | 14317.9927 | -0.0010516
149 |  | 125.0362 | 96.6648 | 4187 | 0.00018464 | 6.0273 | 6.0275 | -5.6953 | 5415.8951 | 14414.6575 | -0.0010516
150 |  | 125.0362 | 96.6638 | 4187 | 0.00018464 | 6.0275 | 6.0277 | -5.6953 | 5415.954 | 14511.3213 | -0.0010516
151 |  | 125.0362 | 96.6627 | 4187 | 0.00018464 | 6.0277 | 6.0279 | -5.6953 | 5416.0129 | 14607.984 | -0.0010516
152 |  | 125.0362 | 96.6617 | 4187 | 0.00018464 | 6.0279 | 6.0281 | -5.6953 | 5416.0718 | 14704.6457 | -0.0010516
153 |  | 125.0362 | 96.6606 | 4187 | 0.00018463 | 6.0281 | 6.0283 | -5.6953 | 5416.1308 | 14801.3063 | -0.0010515
154 |  | 125.0362 | 96.6595 | 4187 | 0.00018463 | 6.0283 | 6.0285 | -5.6953 | 5416.1897 | 14897.9658 | -0.0010515
155 |  | 125.0362 | 96.6585 | 4187 | 0.00018463 | 6.0285 | 6.0286 | -5.6953 | 5416.2486 | 14994.6243 | -0.0010515
156 |  | 125.0362 | 96.6574 | 4187 | 0.00018463 | 6.0286 | 6.0288 | -5.6953 | 5416.3075 | 15091.2818 | -0.0010515
157 |  | 125.0362 | 96.6564 | 4187 | 0.00018463 | 6.0288 | 6.029 | -5.6953 | 5416.3664 | 15187.9381 | -0.0010515
158 |  | 125.0362 | 96.6553 | 4187 | 0.00018462 | 6.029 | 6.0292 | -5.6953 | 5416.4254 | 15284.5935 | -0.0010515
159 |  | 125.0362 | 96.6543 | 4187 | 0.00018462 | 6.0292 | 6.0294 | -5.6953 | 5416.4843 | 15381.2478 | -0.0010515
160 |  | 125.0362 | 96.6532 | 4187 | 0.00018462 | 6.0294 | 6.0296 | -5.6953 | 5416.5432 | 15477.901 | -0.0010515
161 |  | 125.0362 | 96.6522 | 4187 | 0.00018462 | 6.0296 | 6.0297 | -5.6953 | 5416.6021 | 15574.5532 | -0.0010515
162 |  | 125.0362 | 96.6511 | 4187 | 0.00018462 | 6.0297 | 6.0299 | -5.6953 | 5416.6611 | 15671.2044 | -0.0010514
163 |  | 125.0362 | 96.6501 | 4187 | 0.00018461 | 6.0299 | 6.0301 | -5.6953 | 5416.72 | 15767.8544 | -0.0010514
164 |  | 125.0362 | 96.649 | 4187 | 0.00018461 | 6.0301 | 6.0303 | -5.6953 | 5416.7789 | 15864.5035 | -0.0010514
165 |  | 125.0362 | 96.648 | 4187 | 0.00018461 | 6.0303 | 6.0305 | -5.6953 | 5416.8379 | 15961.1515 | -0.0010514
166 |  | 125.0362 | 96.6469 | 4187 | 0.00018461 | 6.0305 | 6.0307 | -5.6953 | 5416.8968 | 16057.7984 | -0.0010514
167 |  | 125.0362 | 96.6459 | 4187 | 0.00018461 | 6.0307 | 6.0309 | -5.6953 | 5416.9557 | 16154.4443 | -0.0010514
168 |  | 125.0362 | 96.6448 | 4187 | 0.0001846 | 6.0309 | 6.031 | -5.6953 | 5417.0146 | 16251.0891 | -0.0010514
169 |  | 125.0362 | 96.6438 | 4187 | 0.0001846 | 6.031 | 6.0312 | -5.6953 | 5417.0736 | 16347.7329 | -0.0010514
170 |  | 125.0362 | 96.6427 | 4187 | 0.0001846 | 6.0312 | 6.0314 | -5.6953 | 5417.1325 | 16444.3756 | -0.0010514
171 |  | 125.0362 | 96.6417 | 4187 | 0.0001846 | 6.0314 | 6.0316 | -5.6953 | 5417.1914 | 16541.0173 | -0.0010513
172 |  | 125.0362 | 96.6406 | 4187 | 0.0001846 | 6.0316 | 6.0318 | -5.6953 | 5417.2504 | 16637.6579 | -0.0010513
173 |  | 125.0362 | 96.6396 | 4187 | 0.00018459 | 6.0318 | 6.032 | -5.6953 | 5417.3093 | 16734.2975 | -0.0010513
174 |  | 125.0362 | 96.6385 | 4187 | 0.00018459 | 6.032 | 6.0321 | -5.6953 | 5417.3682 | 16830.936 | -0.0010513
175 |  | 125.0362 | 96.6375 | 4187 | 0.00018459 | 6.0321 | 6.0323 | -5.6953 | 5417.4272 | 16927.5735 | -0.0010513
176 |  | 125.0362 | 96.6364 | 4187 | 0.00018459 | 6.0323 | 6.0325 | -5.6953 | 5417.4861 | 17024.2099 | -0.0010513
177 |  | 125.0362 | 96.6354 | 4187 | 0.00018459 | 6.0325 | 6.0327 | -5.6953 | 5417.5451 | 17120.8453 | -0.0010513
178 |  | 125.0362 | 96.6343 | 4187 | 0.00018458 | 6.0327 | 6.0329 | -5.6953 | 5417.604 | 17217.4796 | -0.0010513
179 |  | 125.0362 | 96.6333 | 4187 | 0.00018458 | 6.0329 | 6.0331 | -5.6953 | 5417.6629 | 17314.1128 | -0.0010513
180 |  | 125.0362 | 96.6322 | 4187 | 0.00018458 | 6.0331 | 6.0333 | -5.6953 | 5417.7219 | 17410.745 | -0.0010512
181 |  | 125.0362 | 96.6312 | 4187 | 0.00018458 | 6.0333 | 6.0334 | -5.6953 | 5417.7808 | 17507.3762 | -0.0010512
182 |  | 125.0362 | 96.6301 | 4187 | 0.00018458 | 6.0334 | 6.0336 | -5.6953 | 5417.8397 | 17604.0063 | -0.0010512
183 |  | 125.0362 | 96.6291 | 4187 | 0.00018457 | 6.0336 | 6.0338 | -5.6953 | 5417.8987 | 17700.6354 | -0.0010512
184 |  | 125.0362 | 96.628 | 4187 | 0.00018457 | 6.0338 | 6.034 | -5.6953 | 5417.9576 | 17797.2634 | -0.0010512
185 |  | 125.0362 | 96.627 | 4187 | 0.00018457 | 6.034 | 6.0342 | -5.6953 | 5418.0166 | 17893.8903 | -0.0010512
186 |  | 125.0362 | 96.6259 | 4187 | 0.00018457 | 6.0342 | 6.0344 | -5.6953 | 5418.0755 | 17990.5163 | -0.0010512
187 |  | 125.0362 | 96.6249 | 4187 | 0.00018457 | 6.0344 | 6.0345 | -5.6953 | 5418.1345 | 18087.1411 | -0.0010512
188 |  | 125.0362 | 96.6238 | 4187 | 0.00018456 | 6.0345 | 6.0347 | -5.6953 | 5418.1934 | 18183.7649 | -0.0010511
189 |  | 125.0362 | 96.6228 | 4187 | 0.00018456 | 6.0347 | 6.0349 | -5.6953 | 5418.2523 | 18280.3877 | -0.0010511
190 |  | 125.0362 | 96.6217 | 4187 | 0.00018456 | 6.0349 | 6.0351 | -5.6953 | 5418.3113 | 18377.0094 | -0.0010511
191 |  | 125.0362 | 96.6207 | 4187 | 0.00018456 | 6.0351 | 6.0353 | -5.6953 | 5418.3702 | 18473.63 | -0.0010511
192 |  | 125.0362 | 96.6196 | 4187 | 0.00018456 | 6.0353 | 6.0355 | -5.6953 | 5418.4292 | 18570.2496 | -0.0010511
193 |  | 125.0362 | 96.6185 | 4187 | 0.00018455 | 6.0355 | 6.0357 | -5.6953 | 5418.4881 | 18666.8682 | -0.0010511
194 |  | 125.0362 | 96.6175 | 4187 | 0.00018455 | 6.0357 | 6.0358 | -5.6953 | 5418.5471 | 18763.4857 | -0.0010511
195 |  | 125.0362 | 96.6164 | 4187 | 0.00018455 | 6.0358 | 6.036 | -5.6953 | 5418.606 | 18860.1021 | -0.0010511
196 |  | 125.0362 | 96.6154 | 4187 | 0.00018455 | 6.036 | 6.0362 | -5.6953 | 5418.665 | 18956.7175 | -0.0010511
197 |  | 125.0362 | 96.6143 | 4187 | 0.00018455 | 6.0362 | 6.0364 | -5.6953 | 5418.7239 | 19053.3318 | -0.001051
198 |  | 125.0362 | 96.6133 | 4187 | 0.00018454 | 6.0364 | 6.0366 | -5.6953 | 5418.7829 | 19149.9451 | -0.001051
199 |  | 125.0362 | 96.6122 | 4187 | 0.00018454 | 6.0366 | 6.0368 | -5.6953 | 5418.8418 | 19246.5574 | -0.001051
200 |  | 125.0362 | 96.6112 | 4187 | 0.00018454 | 6.0368 | 6.0369 | -5.6953 | 5418.9008 | 19343.1686 | -0.001051
201 |  | 125.0362 | 96.6101 | 4187 | 0.00018454 | 6.0369 | 6.0371 | -5.6953 | 5418.9597 | 19439.7787 | -0.001051
202 |  | 125.0362 | 96.6091 | 4187 | 0.00018454 | 6.0371 | 6.0373 | -5.6953 | 5419.0187 | 19536.3878 | -0.001051
203 |  | 125.0362 | 96.608 | 4187 | 0.00018453 | 6.0373 | 6.0375 | -5.6953 | 5419.0776 | 19632.9958 | -0.001051
204 |  | 125.0362 | 96.607 | 4187 | 0.00018453 | 6.0375 | 6.0377 | -5.6953 | 5419.1366 | 19729.6028 | -0.001051
205 |  | 125.0362 | 96.6059 | 4187 | 0.00018453 | 6.0377 | 6.0379 | -5.6953 | 5419.1955 | 19826.2088 | -0.001051
206 |  | 125.0362 | 96.6049 | 4187 | 0.00018453 | 6.0379 | 6.0381 | -5.6953 | 5419.2545 | 19922.8136 | -0.0010509
207 |  | 125.0362 | 96.6038 | 4187 | 0.00018453 | 6.0381 | 6.0382 | -5.6953 | 5419.3134 | 20019.4175 | -0.0010509
208 |  | 125.0362 | 96.6028 | 4187 | 0.00018452 | 6.0382 | 6.0384 | -5.6953 | 5419.3724 | 20116.0203 | -0.0010509
209 |  | 125.0362 | 96.6017 | 4187 | 0.00018452 | 6.0384 | 6.0386 | -5.6953 | 5419.4314 | 20212.622 | -0.0010509
210 |  | 125.0362 | 96.6007 | 4187 | 0.00018452 | 6.0386 | 6.0388 | -5.6953 | 5419.4903 | 20309.2227 | -0.0010509
211 |  | 125.0362 | 96.5996 | 4187 | 0.00018452 | 6.0388 | 6.039 | -5.6953 | 5419.5493 | 20405.8223 | -0.0010509
212 |  | 125.0362 | 96.5986 | 4187 | 0.00018452 | 6.039 | 6.0392 | -5.6953 | 5419.6082 | 20502.4209 | -0.0010509
213 |  | 125.0362 | 96.5975 | 4187 | 0.00018451 | 6.0392 | 6.0393 | -5.6953 | 5419.6672 | 20599.0184 | -0.0010509
214 |  | 125.0362 | 96.5965 | 4187 | 0.00018451 | 6.0393 | 6.0395 | -5.6953 | 5419.7261 | 20695.6149 | -0.0010509
215 |  | 125.0362 | 96.5954 | 4187 | 0.00018451 | 6.0395 | 6.0397 | -5.6953 | 5419.7851 | 20792.2103 | -0.0010508
216 |  | 125.0362 | 96.5944 | 4187 | 0.00018451 | 6.0397 | 6.0399 | -5.6953 | 5419.8441 | 20888.8047 | -0.0010508
217 |  | 125.0362 | 96.5933 | 4187 | 0.00018451 | 6.0399 | 6.0401 | -5.6953 | 5419.903 | 20985.398 | -0.0010508
218 |  | 125.0362 | 96.5923 | 4187 | 0.0001845 | 6.0401 | 6.0403 | -5.6953 | 5419.962 | 21081.9903 | -0.0010508
219 |  | 125.0362 | 96.5912 | 4187 | 0.0001845 | 6.0403 | 6.0405 | -5.6953 | 5420.021 | 21178.5815 | -0.0010508
220 |  | 125.0362 | 96.5902 | 4187 | 0.0001845 | 6.0405 | 6.0406 | -5.6953 | 5420.0799 | 21275.1717 | -0.0010508
221 |  | 125.0362 | 96.5891 | 4187 | 0.0001845 | 6.0406 | 6.0408 | -5.6953 | 5420.1389 | 21371.7608 | -0.0010508
222 |  | 125.0362 | 96.5881 | 4187 | 0.0001845 | 6.0408 | 6.041 | -5.6953 | 5420.1978 | 21468.3489 | -0.0010508
223 |  | 125.0362 | 96.587 | 4187 | 0.00018449 | 6.041 | 6.0412 | -5.6953 | 5420.2568 | 21564.9359 | -0.0010507
224 |  | 125.0362 | 96.586 | 4187 | 0.00018449 | 6.0412 | 6.0414 | -5.6953 | 5420.3158 | 21661.5219 | -0.0010507
225 |  | 125.0362 | 96.5849 | 4187 | 0.00018449 | 6.0414 | 6.0416 | -5.6953 | 5420.3747 | 21758.1068 | -0.0010507
226 |  | 125.0362 | 96.5839 | 4187 | 0.00018449 | 6.0416 | 6.0417 | -5.6953 | 5420.4337 | 21854.6907 | -0.0010507
227 |  | 125.0362 | 96.5828 | 4187 | 0.00018449 | 6.0417 | 6.0419 | -5.6953 | 5420.4927 | 21951.2735 | -0.0010507
228 |  | 125.0362 | 96.5818 | 4187 | 0.00018448 | 6.0419 | 6.0421 | -5.6953 | 5420.5517 | 22047.8552 | -0.0010507
229 |  | 125.0362 | 96.5807 | 4187 | 0.00018448 | 6.0421 | 6.0423 | -5.6953 | 5420.6106 | 22144.436 | -0.0010507
230 |  | 125.0362 | 96.5797 | 4187 | 0.00018448 | 6.0423 | 6.0425 | -5.6953 | 5420.6696 | 22241.0156 | -0.0010507
231 |  | 125.0362 | 96.5786 | 4187 | 0.00018448 | 6.0425 | 6.0427 | -5.6953 | 5420.7286 | 22337.5942 | -0.0010507
232 |  | 125.0362 | 96.5776 | 4187 | 0.00018448 | 6.0427 | 6.0429 | -5.6953 | 5420.7875 | 22434.1718 | -0.0010506
233 |  | 125.0362 | 96.5765 | 4187 | 0.00018447 | 6.0429 | 6.043 | -5.6953 | 5420.8465 | 22530.7483 | -0.0010506
234 |  | 125.0362 | 96.5755 | 4187 | 0.00018447 | 6.043 | 6.0432 | -5.6953 | 5420.9055 | 22627.3238 | -0.0010506
235 |  | 125.0362 | 96.5744 | 4187 | 0.00018447 | 6.0432 | 6.0434 | -5.6953 | 5420.9645 | 22723.8982 | -0.0010506
236 |  | 125.0362 | 96.5734 | 4187 | 0.00018447 | 6.0434 | 6.0436 | -5.6953 | 5421.0234 | 22820.4716 | -0.0010506

## CLX500
|  |  | buis | verlies W/M | L /°C/sec
diam | wandikte |  | inhoud l/m |  | W/M
500 | 28.4 | 3.1416 | 154.2728 | 99.3534 | 4187
[8 empty] | J/sec/mtr | aantal mtr. | verlies
|  | buis | verlies W/M | L /°C/sec | verlies temp | begintemp | eindtemp | verlies | bij 1°C | totaal J/sec
|  | inhoud L |  | W/M | °C per M | °C | °C | per m°C | daling | aantal mtr
1 | 450 | 154.2728 | 99.3534 | 4187 | 0.00015381 | 6 | 6.0002 | -5.8443 | 6501.4423 | 99.3534 | -0.00089893
2 |  | 154.2728 | 99.3525 | 4187 | 0.00015381 | 6.0002 | 6.0003 | -5.8443 | 6501.5011 | 198.7059 | -0.00089892
3 |  | 154.2728 | 99.3516 | 4187 | 0.00015381 | 6.0003 | 6.0005 | -5.8443 | 6501.5599 | 298.0574 | -0.00089891
4 |  | 154.2728 | 99.3507 | 4187 | 0.00015381 | 6.0005 | 6.0006 | -5.8443 | 6501.6187 | 397.4081 | -0.0008989
5 |  | 154.2728 | 99.3498 | 4187 | 0.00015381 | 6.0006 | 6.0008 | -5.8443 | 6501.6776 | 496.7579 | -0.00089889
6 |  | 154.2728 | 99.3489 | 4187 | 0.00015381 | 6.0008 | 6.0009 | -5.8443 | 6501.7364 | 596.1068 | -0.00089889
7 |  | 154.2728 | 99.348 | 4187 | 0.0001538 | 6.0009 | 6.0011 | -5.8443 | 6501.7952 | 695.4548 | -0.00089888
8 |  | 154.2728 | 99.3471 | 4187 | 0.0001538 | 6.0011 | 6.0012 | -5.8443 | 6501.854 | 794.8019 | -0.00089887
9 |  | 154.2728 | 99.3462 | 4187 | 0.0001538 | 6.0012 | 6.0014 | -5.8443 | 6501.9129 | 894.148 | -0.00089886
10 |  | 154.2728 | 99.3453 | 4187 | 0.0001538 | 6.0014 | 6.0015 | -5.8443 | 6501.9717 | 993.4933 | -0.00089885
11 |  | 154.2728 | 99.3444 | 4187 | 0.0001538 | 6.0015 | 6.0017 | -5.8443 | 6502.0305 | 1092.8377 | -0.00089884
12 |  | 154.2728 | 99.3435 | 4187 | 0.0001538 | 6.0017 | 6.0018 | -5.8443 | 6502.0894 | 1192.1812 | -0.00089884
13 |  | 154.2728 | 99.3426 | 4187 | 0.0001538 | 6.0018 | 6.002 | -5.8443 | 6502.1482 | 1291.5238 | -0.00089883
14 |  | 154.2728 | 99.3417 | 4187 | 0.00015379 | 6.002 | 6.0022 | -5.8443 | 6502.207 | 1390.8655 | -0.00089882
15 |  | 154.2728 | 99.3408 | 4187 | 0.00015379 | 6.0022 | 6.0023 | -5.8443 | 6502.2658 | 1490.2063 | -0.00089881
16 |  | 154.2728 | 99.3399 | 4187 | 0.00015379 | 6.0023 | 6.0025 | -5.8443 | 6502.3247 | 1589.5462 | -0.0008988
17 |  | 154.2728 | 99.339 | 4187 | 0.00015379 | 6.0025 | 6.0026 | -5.8443 | 6502.3835 | 1688.8852 | -0.0008988
18 |  | 154.2728 | 99.3381 | 4187 | 0.00015379 | 6.0026 | 6.0028 | -5.8443 | 6502.4423 | 1788.2233 | -0.00089879
19 |  | 154.2728 | 99.3372 | 4187 | 0.00015379 | 6.0028 | 6.0029 | -5.8443 | 6502.5012 | 1887.5605 | -0.00089878
20 |  | 154.2728 | 99.3363 | 4187 | 0.00015379 | 6.0029 | 6.0031 | -5.8443 | 6502.56 | 1986.8968 | -0.00089877
21 |  | 154.2728 | 99.3354 | 4187 | 0.00015378 | 6.0031 | 6.0032 | -5.8443 | 6502.6188 | 2086.2322 | -0.00089876
22 |  | 154.2728 | 99.3345 | 4187 | 0.00015378 | 6.0032 | 6.0034 | -5.8443 | 6502.6777 | 2185.5667 | -0.00089876
23 |  | 154.2728 | 99.3336 | 4187 | 0.00015378 | 6.0034 | 6.0035 | -5.8443 | 6502.7365 | 2284.9003 | -0.00089875
24 |  | 154.2728 | 99.3327 | 4187 | 0.00015378 | 6.0035 | 6.0037 | -5.8443 | 6502.7953 | 2384.233 | -0.00089874
25 |  | 154.2728 | 99.3318 | 4187 | 0.00015378 | 6.0037 | 6.0038 | -5.8443 | 6502.8542 | 2483.5648 | -0.00089873
26 |  | 154.2728 | 99.3309 | 4187 | 0.00015378 | 6.0038 | 6.004 | -5.8443 | 6502.913 | 2582.8957 | -0.00089872
27 |  | 154.2728 | 99.33 | 4187 | 0.00015378 | 6.004 | 6.0042 | -5.8443 | 6502.9719 | 2682.2257 | -0.00089871
28 |  | 154.2728 | 99.3291 | 4187 | 0.00015377 | 6.0042 | 6.0043 | -5.8443 | 6503.0307 | 2781.5548 | -0.00089871
29 |  | 154.2728 | 99.3282 | 4187 | 0.00015377 | 6.0043 | 6.0045 | -5.8443 | 6503.0895 | 2880.883 | -0.0008987
30 |  | 154.2728 | 99.3273 | 4187 | 0.00015377 | 6.0045 | 6.0046 | -5.8443 | 6503.1484 | 2980.2103 | -0.00089869
31 |  | 154.2728 | 99.3264 | 4187 | 0.00015377 | 6.0046 | 6.0048 | -5.8443 | 6503.2072 | 3079.5367 | -0.00089868
32 |  | 154.2728 | 99.3255 | 4187 | 0.00015377 | 6.0048 | 6.0049 | -5.8443 | 6503.2661 | 3178.8623 | -0.00089867
33 |  | 154.2728 | 99.3246 | 4187 | 0.00015377 | 6.0049 | 6.0051 | -5.8443 | 6503.3249 | 3278.1869 | -0.00089867
34 |  | 154.2728 | 99.3237 | 4187 | 0.00015377 | 6.0051 | 6.0052 | -5.8443 | 6503.3837 | 3377.5106 | -0.00089866
35 |  | 154.2728 | 99.3228 | 4187 | 0.00015376 | 6.0052 | 6.0054 | -5.8443 | 6503.4426 | 3476.8334 | -0.00089865
36 |  | 154.2728 | 99.3219 | 4187 | 0.00015376 | 6.0054 | 6.0055 | -5.8443 | 6503.5014 | 3576.1553 | -0.00089864
37 |  | 154.2728 | 99.321 | 4187 | 0.00015376 | 6.0055 | 6.0057 | -5.8443 | 6503.5603 | 3675.4763 | -0.00089863
38 |  | 154.2728 | 99.3201 | 4187 | 0.00015376 | 6.0057 | 6.0058 | -5.8443 | 6503.6191 | 3774.7965 | -0.00089863
39 |  | 154.2728 | 99.3192 | 4187 | 0.00015376 | 6.0058 | 6.006 | -5.8443 | 6503.6779 | 3874.1157 | -0.00089862
40 |  | 154.2728 | 99.3183 | 4187 | 0.00015376 | 6.006 | 6.0062 | -5.8443 | 6503.7368 | 3973.434 | -0.00089861
41 |  | 154.2728 | 99.3174 | 4187 | 0.00015376 | 6.0062 | 6.0063 | -5.8443 | 6503.7956 | 4072.7514 | -0.0008986
42 |  | 154.2728 | 99.3165 | 4187 | 0.00015375 | 6.0063 | 6.0065 | -5.8443 | 6503.8545 | 4172.068 | -0.00089859
43 |  | 154.2728 | 99.3156 | 4187 | 0.00015375 | 6.0065 | 6.0066 | -5.8443 | 6503.9133 | 4271.3836 | -0.00089858
44 |  | 154.2728 | 99.3147 | 4187 | 0.00015375 | 6.0066 | 6.0068 | -5.8443 | 6503.9722 | 4370.6983 | -0.00089858
45 |  | 154.2728 | 99.3138 | 4187 | 0.00015375 | 6.0068 | 6.0069 | -5.8443 | 6504.031 | 4470.0122 | -0.00089857
46 |  | 154.2728 | 99.3129 | 4187 | 0.00015375 | 6.0069 | 6.0071 | -5.8443 | 6504.0899 | 4569.3251 | -0.00089856
47 |  | 154.2728 | 99.312 | 4187 | 0.00015375 | 6.0071 | 6.0072 | -5.8443 | 6504.1487 | 4668.6371 | -0.00089855
48 |  | 154.2728 | 99.3111 | 4187 | 0.00015375 | 6.0072 | 6.0074 | -5.8443 | 6504.2076 | 4767.9483 | -0.00089854
49 |  | 154.2728 | 99.3102 | 4187 | 0.00015375 | 6.0074 | 6.0075 | -5.8443 | 6504.2664 | 4867.2585 | -0.00089854
50 |  | 154.2728 | 99.3093 | 4187 | 0.00015374 | 6.0075 | 6.0077 | -5.8443 | 6504.3253 | 4966.5679 | -0.00089853
51 |  | 154.2728 | 99.3084 | 4187 | 0.00015374 | 6.0077 | 6.0078 | -5.8443 | 6504.3841 | 5065.8763 | -0.00089852
52 |  | 154.2728 | 99.3075 | 4187 | 0.00015374 | 6.0078 | 6.008 | -5.8443 | 6504.443 | 5165.1838 | -0.00089851
53 |  | 154.2728 | 99.3066 | 4187 | 0.00015374 | 6.008 | 6.0082 | -5.8443 | 6504.5018 | 5264.4905 | -0.0008985
54 |  | 154.2728 | 99.3057 | 4187 | 0.00015374 | 6.0082 | 6.0083 | -5.8443 | 6504.5607 | 5363.7962 | -0.0008985
55 |  | 154.2728 | 99.3048 | 4187 | 0.00015374 | 6.0083 | 6.0085 | -5.8443 | 6504.6195 | 5463.1011 | -0.00089849
56 |  | 154.2728 | 99.3039 | 4187 | 0.00015374 | 6.0085 | 6.0086 | -5.8443 | 6504.6784 | 5562.405 | -0.00089848
57 |  | 154.2728 | 99.3031 | 4187 | 0.00015373 | 6.0086 | 6.0088 | -5.8443 | 6504.7372 | 5661.7081 | -0.00089847
58 |  | 154.2728 | 99.3022 | 4187 | 0.00015373 | 6.0088 | 6.0089 | -5.8443 | 6504.7961 | 5761.0102 | -0.00089846
59 |  | 154.2728 | 99.3013 | 4187 | 0.00015373 | 6.0089 | 6.0091 | -5.8443 | 6504.8549 | 5860.3115 | -0.00089845
60 |  | 154.2728 | 99.3004 | 4187 | 0.00015373 | 6.0091 | 6.0092 | -5.8443 | 6504.9138 | 5959.6118 | -0.00089845
61 |  | 154.2728 | 99.2995 | 4187 | 0.00015373 | 6.0092 | 6.0094 | -5.8443 | 6504.9726 | 6058.9113 | -0.00089844
62 |  | 154.2728 | 99.2986 | 4187 | 0.00015373 | 6.0094 | 6.0095 | -5.8443 | 6505.0315 | 6158.2098 | -0.00089843
63 |  | 154.2728 | 99.2977 | 4187 | 0.00015373 | 6.0095 | 6.0097 | -5.8443 | 6505.0904 | 6257.5075 | -0.00089842
64 |  | 154.2728 | 99.2968 | 4187 | 0.00015372 | 6.0097 | 6.0098 | -5.8443 | 6505.1492 | 6356.8043 | -0.00089841
65 |  | 154.2728 | 99.2959 | 4187 | 0.00015372 | 6.0098 | 6.01 | -5.8443 | 6505.2081 | 6456.1001 | -0.00089841
66 |  | 154.2728 | 99.295 | 4187 | 0.00015372 | 6.01 | 6.0101 | -5.8443 | 6505.2669 | 6555.3951 | -0.0008984
67 |  | 154.2728 | 99.2941 | 4187 | 0.00015372 | 6.0101 | 6.0103 | -5.8443 | 6505.3258 | 6654.6892 | -0.00089839
68 |  | 154.2728 | 99.2932 | 4187 | 0.00015372 | 6.0103 | 6.0105 | -5.8443 | 6505.3847 | 6753.9823 | -0.00089838
69 |  | 154.2728 | 99.2923 | 4187 | 0.00015372 | 6.0105 | 6.0106 | -5.8443 | 6505.4435 | 6853.2746 | -0.00089837
70 |  | 154.2728 | 99.2914 | 4187 | 0.00015372 | 6.0106 | 6.0108 | -5.8443 | 6505.5024 | 6952.566 | -0.00089837
71 |  | 154.2728 | 99.2905 | 4187 | 0.00015371 | 6.0108 | 6.0109 | -5.8443 | 6505.5612 | 7051.8564 | -0.00089836
72 |  | 154.2728 | 99.2896 | 4187 | 0.00015371 | 6.0109 | 6.0111 | -5.8443 | 6505.6201 | 7151.146 | -0.00089835
73 |  | 154.2728 | 99.2887 | 4187 | 0.00015371 | 6.0111 | 6.0112 | -5.8443 | 6505.679 | 7250.4347 | -0.00089834
74 |  | 154.2728 | 99.2878 | 4187 | 0.00015371 | 6.0112 | 6.0114 | -5.8443 | 6505.7378 | 7349.7225 | -0.00089833
75 |  | 154.2728 | 99.2869 | 4187 | 0.00015371 | 6.0114 | 6.0115 | -5.8443 | 6505.7967 | 7449.0093 | -0.00089832
76 |  | 154.2728 | 99.286 | 4187 | 0.00015371 | 6.0115 | 6.0117 | -5.8443 | 6505.8555 | 7548.2953 | -0.00089832
77 |  | 154.2728 | 99.2851 | 4187 | 0.00015371 | 6.0117 | 6.0118 | -5.8443 | 6505.9144 | 7647.5804 | -0.00089831
78 |  | 154.2728 | 99.2842 | 4187 | 0.0001537 | 6.0118 | 6.012 | -5.8443 | 6505.9733 | 7746.8646 | -0.0008983
79 |  | 154.2728 | 99.2833 | 4187 | 0.0001537 | 6.012 | 6.0121 | -5.8443 | 6506.0321 | 7846.1479 | -0.00089829
80 |  | 154.2728 | 99.2824 | 4187 | 0.0001537 | 6.0121 | 6.0123 | -5.8443 | 6506.091 | 7945.4303 | -0.00089828
81 |  | 154.2728 | 99.2815 | 4187 | 0.0001537 | 6.0123 | 6.0125 | -5.8443 | 6506.1499 | 8044.7118 | -0.00089828
82 |  | 154.2728 | 99.2806 | 4187 | 0.0001537 | 6.0125 | 6.0126 | -5.8443 | 6506.2087 | 8143.9923 | -0.00089827
83 |  | 154.2728 | 99.2797 | 4187 | 0.0001537 | 6.0126 | 6.0128 | -5.8443 | 6506.2676 | 8243.272 | -0.00089826
84 |  | 154.2728 | 99.2788 | 4187 | 0.0001537 | 6.0128 | 6.0129 | -5.8443 | 6506.3265 | 8342.5508 | -0.00089825
85 |  | 154.2728 | 99.2779 | 4187 | 0.0001537 | 6.0129 | 6.0131 | -5.8443 | 6506.3853 | 8441.8287 | -0.00089824
86 |  | 154.2728 | 99.277 | 4187 | 0.00015369 | 6.0131 | 6.0132 | -5.8443 | 6506.4442 | 8541.1057 | -0.00089824
87 |  | 154.2728 | 99.2761 | 4187 | 0.00015369 | 6.0132 | 6.0134 | -5.8443 | 6506.5031 | 8640.3818 | -0.00089823
88 |  | 154.2728 | 99.2752 | 4187 | 0.00015369 | 6.0134 | 6.0135 | -5.8443 | 6506.5619 | 8739.657 | -0.00089822
89 |  | 154.2728 | 99.2743 | 4187 | 0.00015369 | 6.0135 | 6.0137 | -5.8443 | 6506.6208 | 8838.9313 | -0.00089821
90 |  | 154.2728 | 99.2734 | 4187 | 0.00015369 | 6.0137 | 6.0138 | -5.8443 | 6506.6797 | 8938.2047 | -0.0008982
91 |  | 154.2728 | 99.2725 | 4187 | 0.00015369 | 6.0138 | 6.014 | -5.8443 | 6506.7386 | 9037.4772 | -0.00089819
92 |  | 154.2728 | 99.2716 | 4187 | 0.00015369 | 6.014 | 6.0141 | -5.8443 | 6506.7974 | 9136.7489 | -0.00089819
93 |  | 154.2728 | 99.2707 | 4187 | 0.00015368 | 6.0141 | 6.0143 | -5.8443 | 6506.8563 | 9236.0196 | -0.00089818
94 |  | 154.2728 | 99.2698 | 4187 | 0.00015368 | 6.0143 | 6.0145 | -5.8443 | 6506.9152 | 9335.2894 | -0.00089817
95 |  | 154.2728 | 99.2689 | 4187 | 0.00015368 | 6.0145 | 6.0146 | -5.8443 | 6506.9741 | 9434.5583 | -0.00089816
96 |  | 154.2728 | 99.268 | 4187 | 0.00015368 | 6.0146 | 6.0148 | -5.8443 | 6507.0329 | 9533.8263 | -0.00089815
97 |  | 154.2728 | 99.2671 | 4187 | 0.00015368 | 6.0148 | 6.0149 | -5.8443 | 6507.0918 | 9633.0934 | -0.00089815
98 |  | 154.2728 | 99.2662 | 4187 | 0.00015368 | 6.0149 | 6.0151 | -5.8443 | 6507.1507 | 9732.3596 | -0.00089814
99 |  | 154.2728 | 99.2653 | 4187 | 0.00015368 | 6.0151 | 6.0152 | -5.8443 | 6507.2095 | 9831.625 | -0.00089813
100 |  | 154.2728 | 99.2644 | 4187 | 0.00015367 | 6.0152 | 6.0154 | -5.8443 | 6507.2684 | 9930.8894 | -0.00089812
101 |  | 154.2728 | 99.2635 | 4187 | 0.00015367 | 6.0154 | 6.0155 | -5.8443 | 6507.3273 | 10030.1529 | -0.00089811
102 |  | 154.2728 | 99.2626 | 4187 | 0.00015367 | 6.0155 | 6.0157 | -5.8443 | 6507.3862 | 10129.4155 | -0.00089811
103 |  | 154.2728 | 99.2617 | 4187 | 0.00015367 | 6.0157 | 6.0158 | -5.8443 | 6507.4451 | 10228.6773 | -0.0008981
104 |  | 154.2728 | 99.2608 | 4187 | 0.00015367 | 6.0158 | 6.016 | -5.8443 | 6507.5039 | 10327.9381 | -0.00089809
105 |  | 154.2728 | 99.2599 | 4187 | 0.00015367 | 6.016 | 6.0161 | -5.8443 | 6507.5628 | 10427.198 | -0.00089808
106 |  | 154.2728 | 99.259 | 4187 | 0.00015367 | 6.0161 | 6.0163 | -5.8443 | 6507.6217 | 10526.4571 | -0.00089807
107 |  | 154.2728 | 99.2581 | 4187 | 0.00015366 | 6.0163 | 6.0164 | -5.8443 | 6507.6806 | 10625.7152 | -0.00089806
108 |  | 154.2728 | 99.2572 | 4187 | 0.00015366 | 6.0164 | 6.0166 | -5.8443 | 6507.7395 | 10724.9724 | -0.00089806
109 |  | 154.2728 | 99.2563 | 4187 | 0.00015366 | 6.0166 | 6.0168 | -5.8443 | 6507.7983 | 10824.2288 | -0.00089805
110 |  | 154.2728 | 99.2554 | 4187 | 0.00015366 | 6.0168 | 6.0169 | -5.8443 | 6507.8572 | 10923.4842 | -0.00089804
111 |  | 154.2728 | 99.2545 | 4187 | 0.00015366 | 6.0169 | 6.0171 | -5.8443 | 6507.9161 | 11022.7388 | -0.00089803
112 |  | 154.2728 | 99.2536 | 4187 | 0.00015366 | 6.0171 | 6.0172 | -5.8443 | 6507.975 | 11121.9924 | -0.00089802
113 |  | 154.2728 | 99.2527 | 4187 | 0.00015366 | 6.0172 | 6.0174 | -5.8443 | 6508.0339 | 11221.2452 | -0.00089802
114 |  | 154.2728 | 99.2519 | 4187 | 0.00015365 | 6.0174 | 6.0175 | -5.8443 | 6508.0927 | 11320.497 | -0.00089801
115 |  | 154.2728 | 99.251 | 4187 | 0.00015365 | 6.0175 | 6.0177 | -5.8443 | 6508.1516 | 11419.748 | -0.000898
116 |  | 154.2728 | 99.2501 | 4187 | 0.00015365 | 6.0177 | 6.0178 | -5.8443 | 6508.2105 | 11518.998 | -0.00089799
117 |  | 154.2728 | 99.2492 | 4187 | 0.00015365 | 6.0178 | 6.018 | -5.8443 | 6508.2694 | 11618.2472 | -0.00089798
118 |  | 154.2728 | 99.2483 | 4187 | 0.00015365 | 6.018 | 6.0181 | -5.8443 | 6508.3283 | 11717.4954 | -0.00089798
119 |  | 154.2728 | 99.2474 | 4187 | 0.00015365 | 6.0181 | 6.0183 | -5.8443 | 6508.3872 | 11816.7428 | -0.00089797
120 |  | 154.2728 | 99.2465 | 4187 | 0.00015365 | 6.0183 | 6.0184 | -5.8443 | 6508.4461 | 11915.9893 | -0.00089796
121 |  | 154.2728 | 99.2456 | 4187 | 0.00015365 | 6.0184 | 6.0186 | -5.8443 | 6508.505 | 12015.2348 | -0.00089795
122 |  | 154.2728 | 99.2447 | 4187 | 0.00015364 | 6.0186 | 6.0188 | -5.8443 | 6508.5638 | 12114.4795 | -0.00089794
123 |  | 154.2728 | 99.2438 | 4187 | 0.00015364 | 6.0188 | 6.0189 | -5.8443 | 6508.6227 | 12213.7233 | -0.00089793
124 |  | 154.2728 | 99.2429 | 4187 | 0.00015364 | 6.0189 | 6.0191 | -5.8443 | 6508.6816 | 12312.9661 | -0.00089793
125 |  | 154.2728 | 99.242 | 4187 | 0.00015364 | 6.0191 | 6.0192 | -5.8443 | 6508.7405 | 12412.2081 | -0.00089792
126 |  | 154.2728 | 99.2411 | 4187 | 0.00015364 | 6.0192 | 6.0194 | -5.8443 | 6508.7994 | 12511.4492 | -0.00089791
127 |  | 154.2728 | 99.2402 | 4187 | 0.00015364 | 6.0194 | 6.0195 | -5.8443 | 6508.8583 | 12610.6894 | -0.0008979
128 |  | 154.2728 | 99.2393 | 4187 | 0.00015364 | 6.0195 | 6.0197 | -5.8443 | 6508.9172 | 12709.9286 | -0.00089789
129 |  | 154.2728 | 99.2384 | 4187 | 0.00015363 | 6.0197 | 6.0198 | -5.8443 | 6508.9761 | 12809.167 | -0.00089789
130 |  | 154.2728 | 99.2375 | 4187 | 0.00015363 | 6.0198 | 6.02 | -5.8443 | 6509.035 | 12908.4045 | -0.00089788
131 |  | 154.2728 | 99.2366 | 4187 | 0.00015363 | 6.02 | 6.0201 | -5.8443 | 6509.0939 | 13007.6411 | -0.00089787
132 |  | 154.2728 | 99.2357 | 4187 | 0.00015363 | 6.0201 | 6.0203 | -5.8443 | 6509.1527 | 13106.8768 | -0.00089786
133 |  | 154.2728 | 99.2348 | 4187 | 0.00015363 | 6.0203 | 6.0204 | -5.8443 | 6509.2116 | 13206.1116 | -0.00089785
134 |  | 154.2728 | 99.2339 | 4187 | 0.00015363 | 6.0204 | 6.0206 | -5.8443 | 6509.2705 | 13305.3455 | -0.00089785
135 |  | 154.2728 | 99.233 | 4187 | 0.00015363 | 6.0206 | 6.0208 | -5.8443 | 6509.3294 | 13404.5784 | -0.00089784
136 |  | 154.2728 | 99.2321 | 4187 | 0.00015362 | 6.0208 | 6.0209 | -5.8443 | 6509.3883 | 13503.8105 | -0.00089783
137 |  | 154.2728 | 99.2312 | 4187 | 0.00015362 | 6.0209 | 6.0211 | -5.8443 | 6509.4472 | 13603.0417 | -0.00089782
138 |  | 154.2728 | 99.2303 | 4187 | 0.00015362 | 6.0211 | 6.0212 | -5.8443 | 6509.5061 | 13702.272 | -0.00089781
139 |  | 154.2728 | 99.2294 | 4187 | 0.00015362 | 6.0212 | 6.0214 | -5.8443 | 6509.565 | 13801.5014 | -0.0008978
140 |  | 154.2728 | 99.2285 | 4187 | 0.00015362 | 6.0214 | 6.0215 | -5.8443 | 6509.6239 | 13900.7299 | -0.0008978
141 |  | 154.2728 | 99.2276 | 4187 | 0.00015362 | 6.0215 | 6.0217 | -5.8443 | 6509.6828 | 13999.9576 | -0.00089779
142 |  | 154.2728 | 99.2267 | 4187 | 0.00015362 | 6.0217 | 6.0218 | -5.8443 | 6509.7417 | 14099.1843 | -0.00089778
143 |  | 154.2728 | 99.2258 | 4187 | 0.00015361 | 6.0218 | 6.022 | -5.8443 | 6509.8006 | 14198.4101 | -0.00089777
144 |  | 154.2728 | 99.2249 | 4187 | 0.00015361 | 6.022 | 6.0221 | -5.8443 | 6509.8595 | 14297.635 | -0.00089776
145 |  | 154.2728 | 99.224 | 4187 | 0.00015361 | 6.0221 | 6.0223 | -5.8443 | 6509.9184 | 14396.859 | -0.00089776
146 |  | 154.2728 | 99.2231 | 4187 | 0.00015361 | 6.0223 | 6.0224 | -5.8443 | 6509.9773 | 14496.0821 | -0.00089775
147 |  | 154.2728 | 99.2222 | 4187 | 0.00015361 | 6.0224 | 6.0226 | -5.8443 | 6510.0362 | 14595.3043 | -0.00089774
148 |  | 154.2728 | 99.2213 | 4187 | 0.00015361 | 6.0226 | 6.0227 | -5.8443 | 6510.0951 | 14694.5257 | -0.00089773
149 |  | 154.2728 | 99.2204 | 4187 | 0.00015361 | 6.0227 | 6.0229 | -5.8443 | 6510.154 | 14793.7461 | -0.00089772
150 |  | 154.2728 | 99.2195 | 4187 | 0.0001536 | 6.0229 | 6.0231 | -5.8443 | 6510.2129 | 14892.9656 | -0.00089772
151 |  | 154.2728 | 99.2186 | 4187 | 0.0001536 | 6.0231 | 6.0232 | -5.8443 | 6510.2718 | 14992.1842 | -0.00089771
152 |  | 154.2728 | 99.2177 | 4187 | 0.0001536 | 6.0232 | 6.0234 | -5.8443 | 6510.3307 | 15091.402 | -0.0008977
153 |  | 154.2728 | 99.2168 | 4187 | 0.0001536 | 6.0234 | 6.0235 | -5.8443 | 6510.3896 | 15190.6188 | -0.00089769
154 |  | 154.2728 | 99.2159 | 4187 | 0.0001536 | 6.0235 | 6.0237 | -5.8443 | 6510.4485 | 15289.8347 | -0.00089768
155 |  | 154.2728 | 99.215 | 4187 | 0.0001536 | 6.0237 | 6.0238 | -5.8443 | 6510.5074 | 15389.0498 | -0.00089767
156 |  | 154.2728 | 99.2141 | 4187 | 0.0001536 | 6.0238 | 6.024 | -5.8443 | 6510.5663 | 15488.2639 | -0.00089767
157 |  | 154.2728 | 99.2132 | 4187 | 0.0001536 | 6.024 | 6.0241 | -5.8443 | 6510.6253 | 15587.4772 | -0.00089766
158 |  | 154.2728 | 99.2123 | 4187 | 0.00015359 | 6.0241 | 6.0243 | -5.8443 | 6510.6842 | 15686.6895 | -0.00089765
159 |  | 154.2728 | 99.2114 | 4187 | 0.00015359 | 6.0243 | 6.0244 | -5.8443 | 6510.7431 | 15785.901 | -0.00089764
160 |  | 154.2728 | 99.2106 | 4187 | 0.00015359 | 6.0244 | 6.0246 | -5.8443 | 6510.802 | 15885.1115 | -0.00089763
161 |  | 154.2728 | 99.2097 | 4187 | 0.00015359 | 6.0246 | 6.0247 | -5.8443 | 6510.8609 | 15984.3212 | -0.00089763
162 |  | 154.2728 | 99.2088 | 4187 | 0.00015359 | 6.0247 | 6.0249 | -5.8443 | 6510.9198 | 16083.5299 | -0.00089762
163 |  | 154.2728 | 99.2079 | 4187 | 0.00015359 | 6.0249 | 6.0251 | -5.8443 | 6510.9787 | 16182.7378 | -0.00089761
164 |  | 154.2728 | 99.207 | 4187 | 0.00015359 | 6.0251 | 6.0252 | -5.8443 | 6511.0376 | 16281.9447 | -0.0008976
165 |  | 154.2728 | 99.2061 | 4187 | 0.00015358 | 6.0252 | 6.0254 | -5.8443 | 6511.0965 | 16381.1508 | -0.00089759
166 |  | 154.2728 | 99.2052 | 4187 | 0.00015358 | 6.0254 | 6.0255 | -5.8443 | 6511.1554 | 16480.356 | -0.00089759
167 |  | 154.2728 | 99.2043 | 4187 | 0.00015358 | 6.0255 | 6.0257 | -5.8443 | 6511.2143 | 16579.5602 | -0.00089758
168 |  | 154.2728 | 99.2034 | 4187 | 0.00015358 | 6.0257 | 6.0258 | -5.8443 | 6511.2733 | 16678.7636 | -0.00089757
169 |  | 154.2728 | 99.2025 | 4187 | 0.00015358 | 6.0258 | 6.026 | -5.8443 | 6511.3322 | 16777.9661 | -0.00089756
170 |  | 154.2728 | 99.2016 | 4187 | 0.00015358 | 6.026 | 6.0261 | -5.8443 | 6511.3911 | 16877.1677 | -0.00089755
171 |  | 154.2728 | 99.2007 | 4187 | 0.00015358 | 6.0261 | 6.0263 | -5.8443 | 6511.45 | 16976.3683 | -0.00089754
172 |  | 154.2728 | 99.1998 | 4187 | 0.00015357 | 6.0263 | 6.0264 | -5.8443 | 6511.5089 | 17075.5681 | -0.00089754
173 |  | 154.2728 | 99.1989 | 4187 | 0.00015357 | 6.0264 | 6.0266 | -5.8443 | 6511.5678 | 17174.767 | -0.00089753
174 |  | 154.2728 | 99.198 | 4187 | 0.00015357 | 6.0266 | 6.0267 | -5.8443 | 6511.6267 | 17273.965 | -0.00089752
175 |  | 154.2728 | 99.1971 | 4187 | 0.00015357 | 6.0267 | 6.0269 | -5.8443 | 6511.6857 | 17373.1621 | -0.00089751
176 |  | 154.2728 | 99.1962 | 4187 | 0.00015357 | 6.0269 | 6.027 | -5.8443 | 6511.7446 | 17472.3582 | -0.0008975
177 |  | 154.2728 | 99.1953 | 4187 | 0.00015357 | 6.027 | 6.0272 | -5.8443 | 6511.8035 | 17571.5535 | -0.0008975
178 |  | 154.2728 | 99.1944 | 4187 | 0.00015357 | 6.0272 | 6.0274 | -5.8443 | 6511.8624 | 17670.7479 | -0.00089749
179 |  | 154.2728 | 99.1935 | 4187 | 0.00015356 | 6.0274 | 6.0275 | -5.8443 | 6511.9213 | 17769.9414 | -0.00089748
180 |  | 154.2728 | 99.1926 | 4187 | 0.00015356 | 6.0275 | 6.0277 | -5.8443 | 6511.9803 | 17869.134 | -0.00089747
181 |  | 154.2728 | 99.1917 | 4187 | 0.00015356 | 6.0277 | 6.0278 | -5.8443 | 6512.0392 | 17968.3257 | -0.00089746
182 |  | 154.2728 | 99.1908 | 4187 | 0.00015356 | 6.0278 | 6.028 | -5.8443 | 6512.0981 | 18067.5165 | -0.00089746
183 |  | 154.2728 | 99.1899 | 4187 | 0.00015356 | 6.028 | 6.0281 | -5.8443 | 6512.157 | 18166.7064 | -0.00089745
184 |  | 154.2728 | 99.189 | 4187 | 0.00015356 | 6.0281 | 6.0283 | -5.8443 | 6512.2159 | 18265.8955 | -0.00089744
185 |  | 154.2728 | 99.1881 | 4187 | 0.00015356 | 6.0283 | 6.0284 | -5.8443 | 6512.2749 | 18365.0836 | -0.00089743
186 |  | 154.2728 | 99.1872 | 4187 | 0.00015355 | 6.0284 | 6.0286 | -5.8443 | 6512.3338 | 18464.2708 | -0.00089742
187 |  | 154.2728 | 99.1863 | 4187 | 0.00015355 | 6.0286 | 6.0287 | -5.8443 | 6512.3927 | 18563.4571 | -0.00089741
188 |  | 154.2728 | 99.1854 | 4187 | 0.00015355 | 6.0287 | 6.0289 | -5.8443 | 6512.4516 | 18662.6425 | -0.00089741
189 |  | 154.2728 | 99.1845 | 4187 | 0.00015355 | 6.0289 | 6.029 | -5.8443 | 6512.5105 | 18761.827 | -0.0008974
190 |  | 154.2728 | 99.1836 | 4187 | 0.00015355 | 6.029 | 6.0292 | -5.8443 | 6512.5695 | 18861.0107 | -0.00089739
191 |  | 154.2728 | 99.1827 | 4187 | 0.00015355 | 6.0292 | 6.0294 | -5.8443 | 6512.6284 | 18960.1934 | -0.00089738
192 |  | 154.2728 | 99.1818 | 4187 | 0.00015355 | 6.0294 | 6.0295 | -5.8443 | 6512.6873 | 19059.3752 | -0.00089737
193 |  | 154.2728 | 99.1809 | 4187 | 0.00015355 | 6.0295 | 6.0297 | -5.8443 | 6512.7462 | 19158.5562 | -0.00089737
194 |  | 154.2728 | 99.18 | 4187 | 0.00015354 | 6.0297 | 6.0298 | -5.8443 | 6512.8052 | 19257.7362 | -0.00089736
195 |  | 154.2728 | 99.1791 | 4187 | 0.00015354 | 6.0298 | 6.03 | -5.8443 | 6512.8641 | 19356.9153 | -0.00089735
196 |  | 154.2728 | 99.1782 | 4187 | 0.00015354 | 6.03 | 6.0301 | -5.8443 | 6512.923 | 19456.0936 | -0.00089734
197 |  | 154.2728 | 99.1773 | 4187 | 0.00015354 | 6.0301 | 6.0303 | -5.8443 | 6512.982 | 19555.2709 | -0.00089733
198 |  | 154.2728 | 99.1764 | 4187 | 0.00015354 | 6.0303 | 6.0304 | -5.8443 | 6513.0409 | 19654.4474 | -0.00089733
199 |  | 154.2728 | 99.1755 | 4187 | 0.00015354 | 6.0304 | 6.0306 | -5.8443 | 6513.0998 | 19753.6229 | -0.00089732
200 |  | 154.2728 | 99.1747 | 4187 | 0.00015354 | 6.0306 | 6.0307 | -5.8443 | 6513.1587 | 19852.7976 | -0.00089731
201 |  | 154.2728 | 99.1738 | 4187 | 0.00015353 | 6.0307 | 6.0309 | -5.8443 | 6513.2177 | 19951.9713 | -0.0008973
202 |  | 154.2728 | 99.1729 | 4187 | 0.00015353 | 6.0309 | 6.031 | -5.8443 | 6513.2766 | 20051.1442 | -0.00089729
203 |  | 154.2728 | 99.172 | 4187 | 0.00015353 | 6.031 | 6.0312 | -5.8443 | 6513.3355 | 20150.3161 | -0.00089728
204 |  | 154.2728 | 99.1711 | 4187 | 0.00015353 | 6.0312 | 6.0313 | -5.8443 | 6513.3945 | 20249.4872 | -0.00089728
205 |  | 154.2728 | 99.1702 | 4187 | 0.00015353 | 6.0313 | 6.0315 | -5.8443 | 6513.4534 | 20348.6574 | -0.00089727
206 |  | 154.2728 | 99.1693 | 4187 | 0.00015353 | 6.0315 | 6.0317 | -5.8443 | 6513.5123 | 20447.8266 | -0.00089726
207 |  | 154.2728 | 99.1684 | 4187 | 0.00015353 | 6.0317 | 6.0318 | -5.8443 | 6513.5713 | 20546.995 | -0.00089725
208 |  | 154.2728 | 99.1675 | 4187 | 0.00015352 | 6.0318 | 6.032 | -5.8443 | 6513.6302 | 20646.1625 | -0.00089724
209 |  | 154.2728 | 99.1666 | 4187 | 0.00015352 | 6.032 | 6.0321 | -5.8443 | 6513.6891 | 20745.329 | -0.00089724
210 |  | 154.2728 | 99.1657 | 4187 | 0.00015352 | 6.0321 | 6.0323 | -5.8443 | 6513.7481 | 20844.4947 | -0.00089723
211 |  | 154.2728 | 99.1648 | 4187 | 0.00015352 | 6.0323 | 6.0324 | -5.8443 | 6513.807 | 20943.6595 | -0.00089722
212 |  | 154.2728 | 99.1639 | 4187 | 0.00015352 | 6.0324 | 6.0326 | -5.8443 | 6513.8659 | 21042.8234 | -0.00089721
213 |  | 154.2728 | 99.163 | 4187 | 0.00015352 | 6.0326 | 6.0327 | -5.8443 | 6513.9249 | 21141.9864 | -0.0008972
214 |  | 154.2728 | 99.1621 | 4187 | 0.00015352 | 6.0327 | 6.0329 | -5.8443 | 6513.9838 | 21241.1485 | -0.0008972
215 |  | 154.2728 | 99.1612 | 4187 | 0.00015351 | 6.0329 | 6.033 | -5.8443 | 6514.0427 | 21340.3097 | -0.00089719
216 |  | 154.2728 | 99.1603 | 4187 | 0.00015351 | 6.033 | 6.0332 | -5.8443 | 6514.1017 | 21439.47 | -0.00089718
217 |  | 154.2728 | 99.1594 | 4187 | 0.00015351 | 6.0332 | 6.0333 | -5.8443 | 6514.1606 | 21538.6294 | -0.00089717
218 |  | 154.2728 | 99.1585 | 4187 | 0.00015351 | 6.0333 | 6.0335 | -5.8443 | 6514.2196 | 21637.7879 | -0.00089716
219 |  | 154.2728 | 99.1576 | 4187 | 0.00015351 | 6.0335 | 6.0337 | -5.8443 | 6514.2785 | 21736.9455 | -0.00089715
220 |  | 154.2728 | 99.1567 | 4187 | 0.00015351 | 6.0337 | 6.0338 | -5.8443 | 6514.3374 | 21836.1022 | -0.00089715
221 |  | 154.2728 | 99.1558 | 4187 | 0.00015351 | 6.0338 | 6.034 | -5.8443 | 6514.3964 | 21935.258 | -0.00089714
222 |  | 154.2728 | 99.1549 | 4187 | 0.0001535 | 6.034 | 6.0341 | -5.8443 | 6514.4553 | 22034.4129 | -0.00089713
223 |  | 154.2728 | 99.154 | 4187 | 0.0001535 | 6.0341 | 6.0343 | -5.8443 | 6514.5143 | 22133.5669 | -0.00089712
224 |  | 154.2728 | 99.1531 | 4187 | 0.0001535 | 6.0343 | 6.0344 | -5.8443 | 6514.5732 | 22232.72 | -0.00089711
225 |  | 154.2728 | 99.1522 | 4187 | 0.0001535 | 6.0344 | 6.0346 | -5.8443 | 6514.6322 | 22331.8722 | -0.00089711
226 |  | 154.2728 | 99.1513 | 4187 | 0.0001535 | 6.0346 | 6.0347 | -5.8443 | 6514.6911 | 22431.0236 | -0.0008971
227 |  | 154.2728 | 99.1504 | 4187 | 0.0001535 | 6.0347 | 6.0349 | -5.8443 | 6514.75 | 22530.174 | -0.00089709
228 |  | 154.2728 | 99.1495 | 4187 | 0.0001535 | 6.0349 | 6.035 | -5.8443 | 6514.809 | 22629.3235 | -0.00089708
229 |  | 154.2728 | 99.1486 | 4187 | 0.0001535 | 6.035 | 6.0352 | -5.8443 | 6514.8679 | 22728.4722 | -0.00089707
230 |  | 154.2728 | 99.1477 | 4187 | 0.00015349 | 6.0352 | 6.0353 | -5.8443 | 6514.9269 | 22827.6199 | -0.00089707
231 |  | 154.2728 | 99.1468 | 4187 | 0.00015349 | 6.0353 | 6.0355 | -5.8443 | 6514.9858 | 22926.7667 | -0.00089706
232 |  | 154.2728 | 99.1459 | 4187 | 0.00015349 | 6.0355 | 6.0356 | -5.8443 | 6515.0448 | 23025.9127 | -0.00089705
233 |  | 154.2728 | 99.145 | 4187 | 0.00015349 | 6.0356 | 6.0358 | -5.8443 | 6515.1037 | 23125.0577 | -0.00089704
234 |  | 154.2728 | 99.1441 | 4187 | 0.00015349 | 6.0358 | 6.036 | -5.8443 | 6515.1627 | 23224.2019 | -0.00089703
235 |  | 154.2728 | 99.1433 | 4187 | 0.00015349 | 6.036 | 6.0361 | -5.8443 | 6515.2216 | 23323.3451 | -0.00089702
236 |  | 154.2728 | 99.1424 | 4187 | 0.00015349 | 6.0361 | 6.0363 | -5.8443 | 6515.2806 | 23422.4875 | -0.00089702

## CLX560
|  |  | buis | verlies W/M | L /°C/sec
diam | wandikte |  | inhoud l/m |  | W/M
560 | 31.7 | 3.1416 | 193.6883 | 102.3971 | 4187
[8 empty] | J/sec/mtr | aantal mtr. | verlies
|  | buis | verlies W/M | L /°C/sec | verlies temp | begintemp | eindtemp | verlies | bij 1°C | totaal J/sec
|  | inhoud L |  | W/M | °C per M | °C | °C | per m°C | daling | aantal mtr
1 | 450 | 193.6883 | 102.3971 | 4187 | 0.00012626 | 6 | 6.0001 | -6.0234 | 7919.8785 | 102.3971 | -0.00076054
2 |  | 193.6883 | 102.3964 | 4187 | 0.00012626 | 6.0001 | 6.0003 | -6.0234 | 7919.9373 | 204.7935 | -0.00076053
3 |  | 193.6883 | 102.3956 | 4187 | 0.00012626 | 6.0003 | 6.0004 | -6.0234 | 7919.9961 | 307.1891 | -0.00076053
4 |  | 193.6883 | 102.3948 | 4187 | 0.00012626 | 6.0004 | 6.0005 | -6.0234 | 7920.055 | 409.5839 | -0.00076052
5 |  | 193.6883 | 102.3941 | 4187 | 0.00012626 | 6.0005 | 6.0006 | -6.0234 | 7920.1138 | 511.978 | -0.00076051
6 |  | 193.6883 | 102.3933 | 4187 | 0.00012626 | 6.0006 | 6.0008 | -6.0234 | 7920.1726 | 614.3713 | -0.00076051
7 |  | 193.6883 | 102.3926 | 4187 | 0.00012626 | 6.0008 | 6.0009 | -6.0234 | 7920.2314 | 716.7639 | -0.0007605
8 |  | 193.6883 | 102.3918 | 4187 | 0.00012626 | 6.0009 | 6.001 | -6.0234 | 7920.2903 | 819.1557 | -0.0007605
9 |  | 193.6883 | 102.391 | 4187 | 0.00012626 | 6.001 | 6.0011 | -6.0234 | 7920.3491 | 921.5467 | -0.00076049
10 |  | 193.6883 | 102.3903 | 4187 | 0.00012626 | 6.0011 | 6.0013 | -6.0234 | 7920.4079 | 1023.937 | -0.00076049
11 |  | 193.6883 | 102.3895 | 4187 | 0.00012626 | 6.0013 | 6.0014 | -6.0234 | 7920.4667 | 1126.3265 | -0.00076048
12 |  | 193.6883 | 102.3888 | 4187 | 0.00012625 | 6.0014 | 6.0015 | -6.0234 | 7920.5256 | 1228.7153 | -0.00076047
13 |  | 193.6883 | 102.388 | 4187 | 0.00012625 | 6.0015 | 6.0016 | -6.0234 | 7920.5844 | 1331.1033 | -0.00076047
14 |  | 193.6883 | 102.3872 | 4187 | 0.00012625 | 6.0016 | 6.0018 | -6.0234 | 7920.6432 | 1433.4905 | -0.00076046
15 |  | 193.6883 | 102.3865 | 4187 | 0.00012625 | 6.0018 | 6.0019 | -6.0234 | 7920.7021 | 1535.877 | -0.00076046
16 |  | 193.6883 | 102.3857 | 4187 | 0.00012625 | 6.0019 | 6.002 | -6.0234 | 7920.7609 | 1638.2627 | -0.00076045
17 |  | 193.6883 | 102.385 | 4187 | 0.00012625 | 6.002 | 6.0021 | -6.0234 | 7920.8197 | 1740.6477 | -0.00076045
18 |  | 193.6883 | 102.3842 | 4187 | 0.00012625 | 6.0021 | 6.0023 | -6.0234 | 7920.8785 | 1843.0319 | -0.00076044
19 |  | 193.6883 | 102.3834 | 4187 | 0.00012625 | 6.0023 | 6.0024 | -6.0234 | 7920.9374 | 1945.4153 | -0.00076044
20 |  | 193.6883 | 102.3827 | 4187 | 0.00012625 | 6.0024 | 6.0025 | -6.0234 | 7920.9962 | 2047.798 | -0.00076043
21 |  | 193.6883 | 102.3819 | 4187 | 0.00012625 | 6.0025 | 6.0027 | -6.0234 | 7921.055 | 2150.1799 | -0.00076042
22 |  | 193.6883 | 102.3812 | 4187 | 0.00012624 | 6.0027 | 6.0028 | -6.0234 | 7921.1139 | 2252.561 | -0.00076042
23 |  | 193.6883 | 102.3804 | 4187 | 0.00012624 | 6.0028 | 6.0029 | -6.0234 | 7921.1727 | 2354.9414 | -0.00076041
24 |  | 193.6883 | 102.3796 | 4187 | 0.00012624 | 6.0029 | 6.003 | -6.0234 | 7921.2315 | 2457.3211 | -0.00076041
25 |  | 193.6883 | 102.3789 | 4187 | 0.00012624 | 6.003 | 6.0032 | -6.0234 | 7921.2904 | 2559.6999 | -0.0007604
26 |  | 193.6883 | 102.3781 | 4187 | 0.00012624 | 6.0032 | 6.0033 | -6.0234 | 7921.3492 | 2662.078 | -0.0007604
27 |  | 193.6883 | 102.3774 | 4187 | 0.00012624 | 6.0033 | 6.0034 | -6.0234 | 7921.408 | 2764.4554 | -0.00076039
28 |  | 193.6883 | 102.3766 | 4187 | 0.00012624 | 6.0034 | 6.0035 | -6.0234 | 7921.4669 | 2866.832 | -0.00076038
29 |  | 193.6883 | 102.3758 | 4187 | 0.00012624 | 6.0035 | 6.0037 | -6.0234 | 7921.5257 | 2969.2078 | -0.00076038
30 |  | 193.6883 | 102.3751 | 4187 | 0.00012624 | 6.0037 | 6.0038 | -6.0234 | 7921.5846 | 3071.5829 | -0.00076037
31 |  | 193.6883 | 102.3743 | 4187 | 0.00012624 | 6.0038 | 6.0039 | -6.0234 | 7921.6434 | 3173.9572 | -0.00076037
32 |  | 193.6883 | 102.3735 | 4187 | 0.00012624 | 6.0039 | 6.004 | -6.0234 | 7921.7022 | 3276.3307 | -0.00076036
33 |  | 193.6883 | 102.3728 | 4187 | 0.00012623 | 6.004 | 6.0042 | -6.0234 | 7921.7611 | 3378.7035 | -0.00076036
34 |  | 193.6883 | 102.372 | 4187 | 0.00012623 | 6.0042 | 6.0043 | -6.0234 | 7921.8199 | 3481.0756 | -0.00076035
35 |  | 193.6883 | 102.3713 | 4187 | 0.00012623 | 6.0043 | 6.0044 | -6.0234 | 7921.8787 | 3583.4468 | -0.00076034
36 |  | 193.6883 | 102.3705 | 4187 | 0.00012623 | 6.0044 | 6.0045 | -6.0234 | 7921.9376 | 3685.8173 | -0.00076034
37 |  | 193.6883 | 102.3697 | 4187 | 0.00012623 | 6.0045 | 6.0047 | -6.0234 | 7921.9964 | 3788.1871 | -0.00076033
38 |  | 193.6883 | 102.369 | 4187 | 0.00012623 | 6.0047 | 6.0048 | -6.0234 | 7922.0553 | 3890.5561 | -0.00076033
39 |  | 193.6883 | 102.3682 | 4187 | 0.00012623 | 6.0048 | 6.0049 | -6.0234 | 7922.1141 | 3992.9243 | -0.00076032
40 |  | 193.6883 | 102.3675 | 4187 | 0.00012623 | 6.0049 | 6.005 | -6.0234 | 7922.1729 | 4095.2918 | -0.00076032
41 |  | 193.6883 | 102.3667 | 4187 | 0.00012623 | 6.005 | 6.0052 | -6.0234 | 7922.2318 | 4197.6585 | -0.00076031
42 |  | 193.6883 | 102.3659 | 4187 | 0.00012623 | 6.0052 | 6.0053 | -6.0234 | 7922.2906 | 4300.0244 | -0.00076031
43 |  | 193.6883 | 102.3652 | 4187 | 0.00012623 | 6.0053 | 6.0054 | -6.0234 | 7922.3495 | 4402.3896 | -0.0007603
44 |  | 193.6883 | 102.3644 | 4187 | 0.00012622 | 6.0054 | 6.0056 | -6.0234 | 7922.4083 | 4504.754 | -0.00076029
45 |  | 193.6883 | 102.3637 | 4187 | 0.00012622 | 6.0056 | 6.0057 | -6.0234 | 7922.4671 | 4607.1177 | -0.00076029
46 |  | 193.6883 | 102.3629 | 4187 | 0.00012622 | 6.0057 | 6.0058 | -6.0234 | 7922.526 | 4709.4806 | -0.00076028
47 |  | 193.6883 | 102.3621 | 4187 | 0.00012622 | 6.0058 | 6.0059 | -6.0234 | 7922.5848 | 4811.8427 | -0.00076028
48 |  | 193.6883 | 102.3614 | 4187 | 0.00012622 | 6.0059 | 6.0061 | -6.0234 | 7922.6437 | 4914.2041 | -0.00076027
49 |  | 193.6883 | 102.3606 | 4187 | 0.00012622 | 6.0061 | 6.0062 | -6.0234 | 7922.7025 | 5016.5647 | -0.00076027
50 |  | 193.6883 | 102.3599 | 4187 | 0.00012622 | 6.0062 | 6.0063 | -6.0234 | 7922.7614 | 5118.9246 | -0.00076026
51 |  | 193.6883 | 102.3591 | 4187 | 0.00012622 | 6.0063 | 6.0064 | -6.0234 | 7922.8202 | 5221.2837 | -0.00076025
52 |  | 193.6883 | 102.3583 | 4187 | 0.00012622 | 6.0064 | 6.0066 | -6.0234 | 7922.8791 | 5323.6421 | -0.00076025
53 |  | 193.6883 | 102.3576 | 4187 | 0.00012622 | 6.0066 | 6.0067 | -6.0234 | 7922.9379 | 5425.9996 | -0.00076024
54 |  | 193.6883 | 102.3568 | 4187 | 0.00012621 | 6.0067 | 6.0068 | -6.0234 | 7922.9968 | 5528.3565 | -0.00076024
55 |  | 193.6883 | 102.3561 | 4187 | 0.00012621 | 6.0068 | 6.0069 | -6.0234 | 7923.0556 | 5630.7125 | -0.00076023
56 |  | 193.6883 | 102.3553 | 4187 | 0.00012621 | 6.0069 | 6.0071 | -6.0234 | 7923.1144 | 5733.0678 | -0.00076023
57 |  | 193.6883 | 102.3545 | 4187 | 0.00012621 | 6.0071 | 6.0072 | -6.0234 | 7923.1733 | 5835.4224 | -0.00076022
58 |  | 193.6883 | 102.3538 | 4187 | 0.00012621 | 6.0072 | 6.0073 | -6.0234 | 7923.2321 | 5937.7761 | -0.00076022
59 |  | 193.6883 | 102.353 | 4187 | 0.00012621 | 6.0073 | 6.0074 | -6.0234 | 7923.291 | 6040.1292 | -0.00076021
60 |  | 193.6883 | 102.3523 | 4187 | 0.00012621 | 6.0074 | 6.0076 | -6.0234 | 7923.3498 | 6142.4814 | -0.0007602
61 |  | 193.6883 | 102.3515 | 4187 | 0.00012621 | 6.0076 | 6.0077 | -6.0234 | 7923.4087 | 6244.8329 | -0.0007602
62 |  | 193.6883 | 102.3507 | 4187 | 0.00012621 | 6.0077 | 6.0078 | -6.0234 | 7923.4675 | 6347.1837 | -0.00076019
63 |  | 193.6883 | 102.35 | 4187 | 0.00012621 | 6.0078 | 6.008 | -6.0234 | 7923.5264 | 6449.5336 | -0.00076019
64 |  | 193.6883 | 102.3492 | 4187 | 0.00012621 | 6.008 | 6.0081 | -6.0234 | 7923.5852 | 6551.8829 | -0.00076018
65 |  | 193.6883 | 102.3485 | 4187 | 0.0001262 | 6.0081 | 6.0082 | -6.0234 | 7923.6441 | 6654.2313 | -0.00076018
66 |  | 193.6883 | 102.3477 | 4187 | 0.0001262 | 6.0082 | 6.0083 | -6.0234 | 7923.7029 | 6756.579 | -0.00076017
67 |  | 193.6883 | 102.3469 | 4187 | 0.0001262 | 6.0083 | 6.0085 | -6.0234 | 7923.7618 | 6858.926 | -0.00076016
68 |  | 193.6883 | 102.3462 | 4187 | 0.0001262 | 6.0085 | 6.0086 | -6.0234 | 7923.8207 | 6961.2721 | -0.00076016
69 |  | 193.6883 | 102.3454 | 4187 | 0.0001262 | 6.0086 | 6.0087 | -6.0234 | 7923.8795 | 7063.6176 | -0.00076015
70 |  | 193.6883 | 102.3447 | 4187 | 0.0001262 | 6.0087 | 6.0088 | -6.0234 | 7923.9384 | 7165.9622 | -0.00076015
71 |  | 193.6883 | 102.3439 | 4187 | 0.0001262 | 6.0088 | 6.009 | -6.0234 | 7923.9972 | 7268.3061 | -0.00076014
72 |  | 193.6883 | 102.3431 | 4187 | 0.0001262 | 6.009 | 6.0091 | -6.0234 | 7924.0561 | 7370.6493 | -0.00076014
73 |  | 193.6883 | 102.3424 | 4187 | 0.0001262 | 6.0091 | 6.0092 | -6.0234 | 7924.1149 | 7472.9916 | -0.00076013
74 |  | 193.6883 | 102.3416 | 4187 | 0.0001262 | 6.0092 | 6.0093 | -6.0234 | 7924.1738 | 7575.3333 | -0.00076012
75 |  | 193.6883 | 102.3409 | 4187 | 0.0001262 | 6.0093 | 6.0095 | -6.0234 | 7924.2326 | 7677.6741 | -0.00076012
76 |  | 193.6883 | 102.3401 | 4187 | 0.00012619 | 6.0095 | 6.0096 | -6.0234 | 7924.2915 | 7780.0142 | -0.00076011
77 |  | 193.6883 | 102.3393 | 4187 | 0.00012619 | 6.0096 | 6.0097 | -6.0234 | 7924.3503 | 7882.3536 | -0.00076011
78 |  | 193.6883 | 102.3386 | 4187 | 0.00012619 | 6.0097 | 6.0098 | -6.0234 | 7924.4092 | 7984.6921 | -0.0007601
79 |  | 193.6883 | 102.3378 | 4187 | 0.00012619 | 6.0098 | 6.01 | -6.0234 | 7924.4681 | 8087.03 | -0.0007601
80 |  | 193.6883 | 102.3371 | 4187 | 0.00012619 | 6.01 | 6.0101 | -6.0234 | 7924.5269 | 8189.367 | -0.00076009
81 |  | 193.6883 | 102.3363 | 4187 | 0.00012619 | 6.0101 | 6.0102 | -6.0234 | 7924.5858 | 8291.7033 | -0.00076009
82 |  | 193.6883 | 102.3355 | 4187 | 0.00012619 | 6.0102 | 6.0104 | -6.0234 | 7924.6446 | 8394.0388 | -0.00076008
83 |  | 193.6883 | 102.3348 | 4187 | 0.00012619 | 6.0104 | 6.0105 | -6.0234 | 7924.7035 | 8496.3736 | -0.00076007
84 |  | 193.6883 | 102.334 | 4187 | 0.00012619 | 6.0105 | 6.0106 | -6.0234 | 7924.7624 | 8598.7076 | -0.00076007
85 |  | 193.6883 | 102.3333 | 4187 | 0.00012619 | 6.0106 | 6.0107 | -6.0234 | 7924.8212 | 8701.0409 | -0.00076006
86 |  | 193.6883 | 102.3325 | 4187 | 0.00012618 | 6.0107 | 6.0109 | -6.0234 | 7924.8801 | 8803.3734 | -0.00076006
87 |  | 193.6883 | 102.3317 | 4187 | 0.00012618 | 6.0109 | 6.011 | -6.0234 | 7924.9389 | 8905.7051 | -0.00076005
88 |  | 193.6883 | 102.331 | 4187 | 0.00012618 | 6.011 | 6.0111 | -6.0234 | 7924.9978 | 9008.0361 | -0.00076005
89 |  | 193.6883 | 102.3302 | 4187 | 0.00012618 | 6.0111 | 6.0112 | -6.0234 | 7925.0567 | 9110.3663 | -0.00076004
90 |  | 193.6883 | 102.3295 | 4187 | 0.00012618 | 6.0112 | 6.0114 | -6.0234 | 7925.1155 | 9212.6958 | -0.00076003
91 |  | 193.6883 | 102.3287 | 4187 | 0.00012618 | 6.0114 | 6.0115 | -6.0234 | 7925.1744 | 9315.0245 | -0.00076003
92 |  | 193.6883 | 102.3279 | 4187 | 0.00012618 | 6.0115 | 6.0116 | -6.0234 | 7925.2332 | 9417.3524 | -0.00076002
93 |  | 193.6883 | 102.3272 | 4187 | 0.00012618 | 6.0116 | 6.0117 | -6.0234 | 7925.2921 | 9519.6796 | -0.00076002
94 |  | 193.6883 | 102.3264 | 4187 | 0.00012618 | 6.0117 | 6.0119 | -6.0234 | 7925.351 | 9622.006 | -0.00076001
95 |  | 193.6883 | 102.3257 | 4187 | 0.00012618 | 6.0119 | 6.012 | -6.0234 | 7925.4098 | 9724.3317 | -0.00076001
96 |  | 193.6883 | 102.3249 | 4187 | 0.00012618 | 6.012 | 6.0121 | -6.0234 | 7925.4687 | 9826.6566 | -0.00076
97 |  | 193.6883 | 102.3241 | 4187 | 0.00012617 | 6.0121 | 6.0122 | -6.0234 | 7925.5276 | 9928.9807 | -0.00075999
98 |  | 193.6883 | 102.3234 | 4187 | 0.00012617 | 6.0122 | 6.0124 | -6.0234 | 7925.5864 | 10031.3041 | -0.00075999
99 |  | 193.6883 | 102.3226 | 4187 | 0.00012617 | 6.0124 | 6.0125 | -6.0234 | 7925.6453 | 10133.6267 | -0.00075998
100 |  | 193.6883 | 102.3219 | 4187 | 0.00012617 | 6.0125 | 6.0126 | -6.0234 | 7925.7042 | 10235.9486 | -0.00075998
101 |  | 193.6883 | 102.3211 | 4187 | 0.00012617 | 6.0126 | 6.0127 | -6.0234 | 7925.763 | 10338.2697 | -0.00075997
102 |  | 193.6883 | 102.3203 | 4187 | 0.00012617 | 6.0127 | 6.0129 | -6.0234 | 7925.8219 | 10440.59 | -0.00075997
103 |  | 193.6883 | 102.3196 | 4187 | 0.00012617 | 6.0129 | 6.013 | -6.0234 | 7925.8808 | 10542.9096 | -0.00075996
104 |  | 193.6883 | 102.3188 | 4187 | 0.00012617 | 6.013 | 6.0131 | -6.0234 | 7925.9396 | 10645.2284 | -0.00075996
105 |  | 193.6883 | 102.3181 | 4187 | 0.00012617 | 6.0131 | 6.0133 | -6.0234 | 7925.9985 | 10747.5464 | -0.00075995
106 |  | 193.6883 | 102.3173 | 4187 | 0.00012617 | 6.0133 | 6.0134 | -6.0234 | 7926.0574 | 10849.8637 | -0.00075994
107 |  | 193.6883 | 102.3165 | 4187 | 0.00012617 | 6.0134 | 6.0135 | -6.0234 | 7926.1163 | 10952.1803 | -0.00075994
108 |  | 193.6883 | 102.3158 | 4187 | 0.00012616 | 6.0135 | 6.0136 | -6.0234 | 7926.1751 | 11054.4961 | -0.00075993
109 |  | 193.6883 | 102.315 | 4187 | 0.00012616 | 6.0136 | 6.0138 | -6.0234 | 7926.234 | 11156.8111 | -0.00075993
110 |  | 193.6883 | 102.3143 | 4187 | 0.00012616 | 6.0138 | 6.0139 | -6.0234 | 7926.2929 | 11259.1253 | -0.00075992
111 |  | 193.6883 | 102.3135 | 4187 | 0.00012616 | 6.0139 | 6.014 | -6.0234 | 7926.3517 | 11361.4388 | -0.00075992
112 |  | 193.6883 | 102.3127 | 4187 | 0.00012616 | 6.014 | 6.0141 | -6.0234 | 7926.4106 | 11463.7516 | -0.00075991
113 |  | 193.6883 | 102.312 | 4187 | 0.00012616 | 6.0141 | 6.0143 | -6.0234 | 7926.4695 | 11566.0635 | -0.0007599
114 |  | 193.6883 | 102.3112 | 4187 | 0.00012616 | 6.0143 | 6.0144 | -6.0234 | 7926.5284 | 11668.3748 | -0.0007599
115 |  | 193.6883 | 102.3105 | 4187 | 0.00012616 | 6.0144 | 6.0145 | -6.0234 | 7926.5872 | 11770.6852 | -0.00075989
116 |  | 193.6883 | 102.3097 | 4187 | 0.00012616 | 6.0145 | 6.0146 | -6.0234 | 7926.6461 | 11872.9949 | -0.00075989
117 |  | 193.6883 | 102.3089 | 4187 | 0.00012616 | 6.0146 | 6.0148 | -6.0234 | 7926.705 | 11975.3039 | -0.00075988
118 |  | 193.6883 | 102.3082 | 4187 | 0.00012615 | 6.0148 | 6.0149 | -6.0234 | 7926.7638 | 12077.612 | -0.00075988
119 |  | 193.6883 | 102.3074 | 4187 | 0.00012615 | 6.0149 | 6.015 | -6.0234 | 7926.8227 | 12179.9195 | -0.00075987
120 |  | 193.6883 | 102.3067 | 4187 | 0.00012615 | 6.015 | 6.0151 | -6.0234 | 7926.8816 | 12282.2261 | -0.00075987
121 |  | 193.6883 | 102.3059 | 4187 | 0.00012615 | 6.0151 | 6.0153 | -6.0234 | 7926.9405 | 12384.532 | -0.00075986
122 |  | 193.6883 | 102.3051 | 4187 | 0.00012615 | 6.0153 | 6.0154 | -6.0234 | 7926.9994 | 12486.8372 | -0.00075985
123 |  | 193.6883 | 102.3044 | 4187 | 0.00012615 | 6.0154 | 6.0155 | -6.0234 | 7927.0582 | 12589.1415 | -0.00075985
124 |  | 193.6883 | 102.3036 | 4187 | 0.00012615 | 6.0155 | 6.0156 | -6.0234 | 7927.1171 | 12691.4452 | -0.00075984
125 |  | 193.6883 | 102.3029 | 4187 | 0.00012615 | 6.0156 | 6.0158 | -6.0234 | 7927.176 | 12793.748 | -0.00075984
126 |  | 193.6883 | 102.3021 | 4187 | 0.00012615 | 6.0158 | 6.0159 | -6.0234 | 7927.2349 | 12896.0501 | -0.00075983
127 |  | 193.6883 | 102.3013 | 4187 | 0.00012615 | 6.0159 | 6.016 | -6.0234 | 7927.2937 | 12998.3515 | -0.00075983
128 |  | 193.6883 | 102.3006 | 4187 | 0.00012615 | 6.016 | 6.0162 | -6.0234 | 7927.3526 | 13100.652 | -0.00075982
129 |  | 193.6883 | 102.2998 | 4187 | 0.00012614 | 6.0162 | 6.0163 | -6.0234 | 7927.4115 | 13202.9519 | -0.00075981
130 |  | 193.6883 | 102.2991 | 4187 | 0.00012614 | 6.0163 | 6.0164 | -6.0234 | 7927.4704 | 13305.2509 | -0.00075981
131 |  | 193.6883 | 102.2983 | 4187 | 0.00012614 | 6.0164 | 6.0165 | -6.0234 | 7927.5293 | 13407.5492 | -0.0007598
132 |  | 193.6883 | 102.2975 | 4187 | 0.00012614 | 6.0165 | 6.0167 | -6.0234 | 7927.5881 | 13509.8468 | -0.0007598
133 |  | 193.6883 | 102.2968 | 4187 | 0.00012614 | 6.0167 | 6.0168 | -6.0234 | 7927.647 | 13612.1435 | -0.00075979
134 |  | 193.6883 | 102.296 | 4187 | 0.00012614 | 6.0168 | 6.0169 | -6.0234 | 7927.7059 | 13714.4396 | -0.00075979
135 |  | 193.6883 | 102.2953 | 4187 | 0.00012614 | 6.0169 | 6.017 | -6.0234 | 7927.7648 | 13816.7348 | -0.00075978
136 |  | 193.6883 | 102.2945 | 4187 | 0.00012614 | 6.017 | 6.0172 | -6.0234 | 7927.8237 | 13919.0293 | -0.00075977
137 |  | 193.6883 | 102.2937 | 4187 | 0.00012614 | 6.0172 | 6.0173 | -6.0234 | 7927.8826 | 14021.3231 | -0.00075977
138 |  | 193.6883 | 102.293 | 4187 | 0.00012614 | 6.0173 | 6.0174 | -6.0234 | 7927.9414 | 14123.616 | -0.00075976
139 |  | 193.6883 | 102.2922 | 4187 | 0.00012614 | 6.0174 | 6.0175 | -6.0234 | 7928.0003 | 14225.9083 | -0.00075976
140 |  | 193.6883 | 102.2915 | 4187 | 0.00012613 | 6.0175 | 6.0177 | -6.0234 | 7928.0592 | 14328.1997 | -0.00075975
141 |  | 193.6883 | 102.2907 | 4187 | 0.00012613 | 6.0177 | 6.0178 | -6.0234 | 7928.1181 | 14430.4904 | -0.00075975
142 |  | 193.6883 | 102.2899 | 4187 | 0.00012613 | 6.0178 | 6.0179 | -6.0234 | 7928.177 | 14532.7804 | -0.00075974
143 |  | 193.6883 | 102.2892 | 4187 | 0.00012613 | 6.0179 | 6.018 | -6.0234 | 7928.2359 | 14635.0696 | -0.00075974
144 |  | 193.6883 | 102.2884 | 4187 | 0.00012613 | 6.018 | 6.0182 | -6.0234 | 7928.2947 | 14737.358 | -0.00075973
145 |  | 193.6883 | 102.2877 | 4187 | 0.00012613 | 6.0182 | 6.0183 | -6.0234 | 7928.3536 | 14839.6456 | -0.00075972
146 |  | 193.6883 | 102.2869 | 4187 | 0.00012613 | 6.0183 | 6.0184 | -6.0234 | 7928.4125 | 14941.9325 | -0.00075972
147 |  | 193.6883 | 102.2861 | 4187 | 0.00012613 | 6.0184 | 6.0186 | -6.0234 | 7928.4714 | 15044.2187 | -0.00075971
148 |  | 193.6883 | 102.2854 | 4187 | 0.00012613 | 6.0186 | 6.0187 | -6.0234 | 7928.5303 | 15146.5041 | -0.00075971
149 |  | 193.6883 | 102.2846 | 4187 | 0.00012613 | 6.0187 | 6.0188 | -6.0234 | 7928.5892 | 15248.7887 | -0.0007597
150 |  | 193.6883 | 102.2839 | 4187 | 0.00012612 | 6.0188 | 6.0189 | -6.0234 | 7928.6481 | 15351.0726 | -0.0007597
151 |  | 193.6883 | 102.2831 | 4187 | 0.00012612 | 6.0189 | 6.0191 | -6.0234 | 7928.707 | 15453.3557 | -0.00075969
152 |  | 193.6883 | 102.2823 | 4187 | 0.00012612 | 6.0191 | 6.0192 | -6.0234 | 7928.7658 | 15555.638 | -0.00075968
153 |  | 193.6883 | 102.2816 | 4187 | 0.00012612 | 6.0192 | 6.0193 | -6.0234 | 7928.8247 | 15657.9196 | -0.00075968
154 |  | 193.6883 | 102.2808 | 4187 | 0.00012612 | 6.0193 | 6.0194 | -6.0234 | 7928.8836 | 15760.2004 | -0.00075967
155 |  | 193.6883 | 102.2801 | 4187 | 0.00012612 | 6.0194 | 6.0196 | -6.0234 | 7928.9425 | 15862.4805 | -0.00075967
156 |  | 193.6883 | 102.2793 | 4187 | 0.00012612 | 6.0196 | 6.0197 | -6.0234 | 7929.0014 | 15964.7598 | -0.00075966
157 |  | 193.6883 | 102.2785 | 4187 | 0.00012612 | 6.0197 | 6.0198 | -6.0234 | 7929.0603 | 16067.0384 | -0.00075966
158 |  | 193.6883 | 102.2778 | 4187 | 0.00012612 | 6.0198 | 6.0199 | -6.0234 | 7929.1192 | 16169.3161 | -0.00075965
159 |  | 193.6883 | 102.277 | 4187 | 0.00012612 | 6.0199 | 6.0201 | -6.0234 | 7929.1781 | 16271.5932 | -0.00075964
160 |  | 193.6883 | 102.2763 | 4187 | 0.00012612 | 6.0201 | 6.0202 | -6.0234 | 7929.237 | 16373.8694 | -0.00075964
161 |  | 193.6883 | 102.2755 | 4187 | 0.00012611 | 6.0202 | 6.0203 | -6.0234 | 7929.2959 | 16476.1449 | -0.00075963
162 |  | 193.6883 | 102.2747 | 4187 | 0.00012611 | 6.0203 | 6.0204 | -6.0234 | 7929.3548 | 16578.4197 | -0.00075963
163 |  | 193.6883 | 102.274 | 4187 | 0.00012611 | 6.0204 | 6.0206 | -6.0234 | 7929.4137 | 16680.6937 | -0.00075962
164 |  | 193.6883 | 102.2732 | 4187 | 0.00012611 | 6.0206 | 6.0207 | -6.0234 | 7929.4726 | 16782.9669 | -0.00075962
165 |  | 193.6883 | 102.2725 | 4187 | 0.00012611 | 6.0207 | 6.0208 | -6.0234 | 7929.5315 | 16885.2394 | -0.00075961
166 |  | 193.6883 | 102.2717 | 4187 | 0.00012611 | 6.0208 | 6.0209 | -6.0234 | 7929.5903 | 16987.5111 | -0.00075961
167 |  | 193.6883 | 102.271 | 4187 | 0.00012611 | 6.0209 | 6.0211 | -6.0234 | 7929.6492 | 17089.782 | -0.0007596
168 |  | 193.6883 | 102.2702 | 4187 | 0.00012611 | 6.0211 | 6.0212 | -6.0234 | 7929.7081 | 17192.0522 | -0.00075959
169 |  | 193.6883 | 102.2694 | 4187 | 0.00012611 | 6.0212 | 6.0213 | -6.0234 | 7929.767 | 17294.3217 | -0.00075959
170 |  | 193.6883 | 102.2687 | 4187 | 0.00012611 | 6.0213 | 6.0215 | -6.0234 | 7929.8259 | 17396.5903 | -0.00075958
171 |  | 193.6883 | 102.2679 | 4187 | 0.00012611 | 6.0215 | 6.0216 | -6.0234 | 7929.8848 | 17498.8583 | -0.00075958
172 |  | 193.6883 | 102.2672 | 4187 | 0.0001261 | 6.0216 | 6.0217 | -6.0234 | 7929.9437 | 17601.1254 | -0.00075957
173 |  | 193.6883 | 102.2664 | 4187 | 0.0001261 | 6.0217 | 6.0218 | -6.0234 | 7930.0026 | 17703.3918 | -0.00075957
174 |  | 193.6883 | 102.2656 | 4187 | 0.0001261 | 6.0218 | 6.022 | -6.0234 | 7930.0615 | 17805.6574 | -0.00075956
175 |  | 193.6883 | 102.2649 | 4187 | 0.0001261 | 6.022 | 6.0221 | -6.0234 | 7930.1204 | 17907.9223 | -0.00075955
176 |  | 193.6883 | 102.2641 | 4187 | 0.0001261 | 6.0221 | 6.0222 | -6.0234 | 7930.1793 | 18010.1864 | -0.00075955
177 |  | 193.6883 | 102.2634 | 4187 | 0.0001261 | 6.0222 | 6.0223 | -6.0234 | 7930.2382 | 18112.4498 | -0.00075954
178 |  | 193.6883 | 102.2626 | 4187 | 0.0001261 | 6.0223 | 6.0225 | -6.0234 | 7930.2971 | 18214.7124 | -0.00075954
179 |  | 193.6883 | 102.2618 | 4187 | 0.0001261 | 6.0225 | 6.0226 | -6.0234 | 7930.356 | 18316.9742 | -0.00075953
180 |  | 193.6883 | 102.2611 | 4187 | 0.0001261 | 6.0226 | 6.0227 | -6.0234 | 7930.4149 | 18419.2353 | -0.00075953
181 |  | 193.6883 | 102.2603 | 4187 | 0.0001261 | 6.0227 | 6.0228 | -6.0234 | 7930.4738 | 18521.4956 | -0.00075952
182 |  | 193.6883 | 102.2596 | 4187 | 0.00012609 | 6.0228 | 6.023 | -6.0234 | 7930.5327 | 18623.7552 | -0.00075952
183 |  | 193.6883 | 102.2588 | 4187 | 0.00012609 | 6.023 | 6.0231 | -6.0234 | 7930.5916 | 18726.014 | -0.00075951
184 |  | 193.6883 | 102.258 | 4187 | 0.00012609 | 6.0231 | 6.0232 | -6.0234 | 7930.6505 | 18828.272 | -0.0007595
185 |  | 193.6883 | 102.2573 | 4187 | 0.00012609 | 6.0232 | 6.0233 | -6.0234 | 7930.7094 | 18930.5293 | -0.0007595
186 |  | 193.6883 | 102.2565 | 4187 | 0.00012609 | 6.0233 | 6.0235 | -6.0234 | 7930.7684 | 19032.7858 | -0.00075949
187 |  | 193.6883 | 102.2558 | 4187 | 0.00012609 | 6.0235 | 6.0236 | -6.0234 | 7930.8273 | 19135.0416 | -0.00075949
188 |  | 193.6883 | 102.255 | 4187 | 0.00012609 | 6.0236 | 6.0237 | -6.0234 | 7930.8862 | 19237.2966 | -0.00075948
189 |  | 193.6883 | 102.2542 | 4187 | 0.00012609 | 6.0237 | 6.0238 | -6.0234 | 7930.9451 | 19339.5508 | -0.00075948
190 |  | 193.6883 | 102.2535 | 4187 | 0.00012609 | 6.0238 | 6.024 | -6.0234 | 7931.004 | 19441.8043 | -0.00075947
191 |  | 193.6883 | 102.2527 | 4187 | 0.00012609 | 6.024 | 6.0241 | -6.0234 | 7931.0629 | 19544.057 | -0.00075946
192 |  | 193.6883 | 102.252 | 4187 | 0.00012609 | 6.0241 | 6.0242 | -6.0234 | 7931.1218 | 19646.309 | -0.00075946
193 |  | 193.6883 | 102.2512 | 4187 | 0.00012608 | 6.0242 | 6.0244 | -6.0234 | 7931.1807 | 19748.5602 | -0.00075945
194 |  | 193.6883 | 102.2504 | 4187 | 0.00012608 | 6.0244 | 6.0245 | -6.0234 | 7931.2396 | 19850.8106 | -0.00075945
195 |  | 193.6883 | 102.2497 | 4187 | 0.00012608 | 6.0245 | 6.0246 | -6.0234 | 7931.2985 | 19953.0603 | -0.00075944
196 |  | 193.6883 | 102.2489 | 4187 | 0.00012608 | 6.0246 | 6.0247 | -6.0234 | 7931.3574 | 20055.3092 | -0.00075944
197 |  | 193.6883 | 102.2482 | 4187 | 0.00012608 | 6.0247 | 6.0249 | -6.0234 | 7931.4163 | 20157.5574 | -0.00075943
198 |  | 193.6883 | 102.2474 | 4187 | 0.00012608 | 6.0249 | 6.025 | -6.0234 | 7931.4752 | 20259.8048 | -0.00075942
199 |  | 193.6883 | 102.2466 | 4187 | 0.00012608 | 6.025 | 6.0251 | -6.0234 | 7931.5341 | 20362.0514 | -0.00075942
200 |  | 193.6883 | 102.2459 | 4187 | 0.00012608 | 6.0251 | 6.0252 | -6.0234 | 7931.5931 | 20464.2973 | -0.00075941
201 |  | 193.6883 | 102.2451 | 4187 | 0.00012608 | 6.0252 | 6.0254 | -6.0234 | 7931.652 | 20566.5425 | -0.00075941
202 |  | 193.6883 | 102.2444 | 4187 | 0.00012608 | 6.0254 | 6.0255 | -6.0234 | 7931.7109 | 20668.7868 | -0.0007594
203 |  | 193.6883 | 102.2436 | 4187 | 0.00012608 | 6.0255 | 6.0256 | -6.0234 | 7931.7698 | 20771.0304 | -0.0007594
204 |  | 193.6883 | 102.2428 | 4187 | 0.00012607 | 6.0256 | 6.0257 | -6.0234 | 7931.8287 | 20873.2733 | -0.00075939
205 |  | 193.6883 | 102.2421 | 4187 | 0.00012607 | 6.0257 | 6.0259 | -6.0234 | 7931.8876 | 20975.5154 | -0.00075939
206 |  | 193.6883 | 102.2413 | 4187 | 0.00012607 | 6.0259 | 6.026 | -6.0234 | 7931.9465 | 21077.7567 | -0.00075938
207 |  | 193.6883 | 102.2406 | 4187 | 0.00012607 | 6.026 | 6.0261 | -6.0234 | 7932.0054 | 21179.9973 | -0.00075937
208 |  | 193.6883 | 102.2398 | 4187 | 0.00012607 | 6.0261 | 6.0262 | -6.0234 | 7932.0644 | 21282.2371 | -0.00075937
209 |  | 193.6883 | 102.2391 | 4187 | 0.00012607 | 6.0262 | 6.0264 | -6.0234 | 7932.1233 | 21384.4762 | -0.00075936
210 |  | 193.6883 | 102.2383 | 4187 | 0.00012607 | 6.0264 | 6.0265 | -6.0234 | 7932.1822 | 21486.7144 | -0.00075936
211 |  | 193.6883 | 102.2375 | 4187 | 0.00012607 | 6.0265 | 6.0266 | -6.0234 | 7932.2411 | 21588.952 | -0.00075935
212 |  | 193.6883 | 102.2368 | 4187 | 0.00012607 | 6.0266 | 6.0267 | -6.0234 | 7932.3 | 21691.1888 | -0.00075935
213 |  | 193.6883 | 102.236 | 4187 | 0.00012607 | 6.0267 | 6.0269 | -6.0234 | 7932.3589 | 21793.4248 | -0.00075934
214 |  | 193.6883 | 102.2353 | 4187 | 0.00012606 | 6.0269 | 6.027 | -6.0234 | 7932.4179 | 21895.66 | -0.00075933
215 |  | 193.6883 | 102.2345 | 4187 | 0.00012606 | 6.027 | 6.0271 | -6.0234 | 7932.4768 | 21997.8945 | -0.00075933
216 |  | 193.6883 | 102.2337 | 4187 | 0.00012606 | 6.0271 | 6.0273 | -6.0234 | 7932.5357 | 22100.1283 | -0.00075932
217 |  | 193.6883 | 102.233 | 4187 | 0.00012606 | 6.0273 | 6.0274 | -6.0234 | 7932.5946 | 22202.3612 | -0.00075932
218 |  | 193.6883 | 102.2322 | 4187 | 0.00012606 | 6.0274 | 6.0275 | -6.0234 | 7932.6535 | 22304.5935 | -0.00075931
219 |  | 193.6883 | 102.2315 | 4187 | 0.00012606 | 6.0275 | 6.0276 | -6.0234 | 7932.7124 | 22406.8249 | -0.00075931
220 |  | 193.6883 | 102.2307 | 4187 | 0.00012606 | 6.0276 | 6.0278 | -6.0234 | 7932.7714 | 22509.0556 | -0.0007593
221 |  | 193.6883 | 102.2299 | 4187 | 0.00012606 | 6.0278 | 6.0279 | -6.0234 | 7932.8303 | 22611.2856 | -0.0007593
222 |  | 193.6883 | 102.2292 | 4187 | 0.00012606 | 6.0279 | 6.028 | -6.0234 | 7932.8892 | 22713.5147 | -0.00075929
223 |  | 193.6883 | 102.2284 | 4187 | 0.00012606 | 6.028 | 6.0281 | -6.0234 | 7932.9481 | 22815.7432 | -0.00075928
224 |  | 193.6883 | 102.2277 | 4187 | 0.00012606 | 6.0281 | 6.0283 | -6.0234 | 7933.007 | 22917.9708 | -0.00075928
225 |  | 193.6883 | 102.2269 | 4187 | 0.00012605 | 6.0283 | 6.0284 | -6.0234 | 7933.066 | 23020.1977 | -0.00075927
226 |  | 193.6883 | 102.2261 | 4187 | 0.00012605 | 6.0284 | 6.0285 | -6.0234 | 7933.1249 | 23122.4239 | -0.00075927
227 |  | 193.6883 | 102.2254 | 4187 | 0.00012605 | 6.0285 | 6.0286 | -6.0234 | 7933.1838 | 23224.6493 | -0.00075926
228 |  | 193.6883 | 102.2246 | 4187 | 0.00012605 | 6.0286 | 6.0288 | -6.0234 | 7933.2427 | 23326.8739 | -0.00075926
229 |  | 193.6883 | 102.2239 | 4187 | 0.00012605 | 6.0288 | 6.0289 | -6.0234 | 7933.3017 | 23429.0977 | -0.00075925
230 |  | 193.6883 | 102.2231 | 4187 | 0.00012605 | 6.0289 | 6.029 | -6.0234 | 7933.3606 | 23531.3209 | -0.00075924
231 |  | 193.6883 | 102.2223 | 4187 | 0.00012605 | 6.029 | 6.0291 | -6.0234 | 7933.4195 | 23633.5432 | -0.00075924
232 |  | 193.6883 | 102.2216 | 4187 | 0.00012605 | 6.0291 | 6.0293 | -6.0234 | 7933.4784 | 23735.7648 | -0.00075923
233 |  | 193.6883 | 102.2208 | 4187 | 0.00012605 | 6.0293 | 6.0294 | -6.0234 | 7933.5374 | 23837.9856 | -0.00075923
234 |  | 193.6883 | 102.2201 | 4187 | 0.00012605 | 6.0294 | 6.0295 | -6.0234 | 7933.5963 | 23940.2057 | -0.00075922
235 |  | 193.6883 | 102.2193 | 4187 | 0.00012605 | 6.0295 | 6.0296 | -6.0234 | 7933.6552 | 24042.425 | -0.00075922
236 |  | 193.6883 | 102.2186 | 4187 | 0.00012604 | 6.0296 | 6.0298 | -6.0234 | 7933.7141 | 24144.6436 | -0.00075921

## CLX630
|  |  | buis | verlies W/M | L /°C/sec
diam | wandikte |  | inhoud l/m |  | W/M
630 | 35.7 | 3.1416 | 245.0709 | 105.0153 | 4187
[8 empty] | J/sec/mtr | aantal mtr. | verlies
|  | buis | verlies W/M | L /°C/sec | verlies temp | begintemp | eindtemp | verlies | bij 1°C | totaal J/sec
|  | inhoud L |  | W/M | °C per M | °C | °C | per m°C | daling | aantal mtr
1 | 450 | 245.0709 | 105.0153 | 4187 | 0.00010234 | 6 | 6.0001 | -6.1774 | 9771.0683 | 105.0153 | -0.00063221
2 |  | 245.0709 | 105.0147 | 4187 | 0.00010234 | 6.0001 | 6.0002 | -6.1774 | 9771.1271 | 210.03 | -0.00063221
3 |  | 245.0709 | 105.0141 | 4187 | 0.00010234 | 6.0002 | 6.0003 | -6.1774 | 9771.1859 | 315.0441 | -0.0006322
4 |  | 245.0709 | 105.0134 | 4187 | 0.00010234 | 6.0003 | 6.0004 | -6.1774 | 9771.2447 | 420.0575 | -0.0006322
5 |  | 245.0709 | 105.0128 | 4187 | 0.00010234 | 6.0004 | 6.0005 | -6.1774 | 9771.3036 | 525.0703 | -0.0006322
6 |  | 245.0709 | 105.0122 | 4187 | 0.00010234 | 6.0005 | 6.0006 | -6.1774 | 9771.3624 | 630.0824 | -0.00063219
7 |  | 245.0709 | 105.0115 | 4187 | 0.00010234 | 6.0006 | 6.0007 | -6.1774 | 9771.4212 | 735.094 | -0.00063219
8 |  | 245.0709 | 105.0109 | 4187 | 0.00010234 | 6.0007 | 6.0008 | -6.1774 | 9771.48 | 840.1049 | -0.00063218
9 |  | 245.0709 | 105.0103 | 4187 | 0.00010234 | 6.0008 | 6.0009 | -6.1774 | 9771.5389 | 945.1151 | -0.00063218
10 |  | 245.0709 | 105.0096 | 4187 | 0.00010234 | 6.0009 | 6.001 | -6.1774 | 9771.5977 | 1050.1247 | -0.00063218
11 |  | 245.0709 | 105.009 | 4187 | 0.00010234 | 6.001 | 6.0011 | -6.1774 | 9771.6565 | 1155.1337 | -0.00063217
12 |  | 245.0709 | 105.0084 | 4187 | 0.00010234 | 6.0011 | 6.0012 | -6.1774 | 9771.7153 | 1260.1421 | -0.00063217
13 |  | 245.0709 | 105.0077 | 4187 | 0.00010234 | 6.0012 | 6.0013 | -6.1774 | 9771.7742 | 1365.1498 | -0.00063216
14 |  | 245.0709 | 105.0071 | 4187 | 0.00010233 | 6.0013 | 6.0014 | -6.1774 | 9771.833 | 1470.1569 | -0.00063216
15 |  | 245.0709 | 105.0065 | 4187 | 0.00010233 | 6.0014 | 6.0015 | -6.1774 | 9771.8918 | 1575.1634 | -0.00063216
16 |  | 245.0709 | 105.0058 | 4187 | 0.00010233 | 6.0015 | 6.0016 | -6.1774 | 9771.9507 | 1680.1692 | -0.00063215
17 |  | 245.0709 | 105.0052 | 4187 | 0.00010233 | 6.0016 | 6.0017 | -6.1774 | 9772.0095 | 1785.1745 | -0.00063215
18 |  | 245.0709 | 105.0046 | 4187 | 0.00010233 | 6.0017 | 6.0018 | -6.1774 | 9772.0683 | 1890.179 | -0.00063215
19 |  | 245.0709 | 105.0039 | 4187 | 0.00010233 | 6.0018 | 6.0019 | -6.1774 | 9772.1271 | 1995.183 | -0.00063214
20 |  | 245.0709 | 105.0033 | 4187 | 0.00010233 | 6.0019 | 6.002 | -6.1774 | 9772.186 | 2100.1863 | -0.00063214
21 |  | 245.0709 | 105.0027 | 4187 | 0.00010233 | 6.002 | 6.0021 | -6.1774 | 9772.2448 | 2205.1889 | -0.00063213
22 |  | 245.0709 | 105.002 | 4187 | 0.00010233 | 6.0021 | 6.0023 | -6.1774 | 9772.3036 | 2310.191 | -0.00063213
23 |  | 245.0709 | 105.0014 | 4187 | 0.00010233 | 6.0023 | 6.0024 | -6.1774 | 9772.3625 | 2415.1924 | -0.00063213
24 |  | 245.0709 | 105.0008 | 4187 | 0.00010233 | 6.0024 | 6.0025 | -6.1774 | 9772.4213 | 2520.1932 | -0.00063212
25 |  | 245.0709 | 105.0001 | 4187 | 0.00010233 | 6.0025 | 6.0026 | -6.1774 | 9772.4801 | 2625.1933 | -0.00063212
26 |  | 245.0709 | 104.9995 | 4187 | 0.00010233 | 6.0026 | 6.0027 | -6.1774 | 9772.539 | 2730.1928 | -0.00063212
27 |  | 245.0709 | 104.9989 | 4187 | 0.00010233 | 6.0027 | 6.0028 | -6.1774 | 9772.5978 | 2835.1917 | -0.00063211
28 |  | 245.0709 | 104.9983 | 4187 | 0.00010233 | 6.0028 | 6.0029 | -6.1774 | 9772.6566 | 2940.19 | -0.00063211
29 |  | 245.0709 | 104.9976 | 4187 | 0.00010233 | 6.0029 | 6.003 | -6.1774 | 9772.7155 | 3045.1876 | -0.0006321
30 |  | 245.0709 | 104.997 | 4187 | 0.00010233 | 6.003 | 6.0031 | -6.1774 | 9772.7743 | 3150.1846 | -0.0006321
31 |  | 245.0709 | 104.9964 | 4187 | 0.00010232 | 6.0031 | 6.0032 | -6.1774 | 9772.8331 | 3255.1809 | -0.0006321
32 |  | 245.0709 | 104.9957 | 4187 | 0.00010232 | 6.0032 | 6.0033 | -6.1774 | 9772.892 | 3360.1767 | -0.00063209
33 |  | 245.0709 | 104.9951 | 4187 | 0.00010232 | 6.0033 | 6.0034 | -6.1774 | 9772.9508 | 3465.1718 | -0.00063209
34 |  | 245.0709 | 104.9945 | 4187 | 0.00010232 | 6.0034 | 6.0035 | -6.1774 | 9773.0096 | 3570.1662 | -0.00063208
35 |  | 245.0709 | 104.9938 | 4187 | 0.00010232 | 6.0035 | 6.0036 | -6.1774 | 9773.0685 | 3675.16 | -0.00063208
36 |  | 245.0709 | 104.9932 | 4187 | 0.00010232 | 6.0036 | 6.0037 | -6.1774 | 9773.1273 | 3780.1532 | -0.00063208
37 |  | 245.0709 | 104.9926 | 4187 | 0.00010232 | 6.0037 | 6.0038 | -6.1774 | 9773.1861 | 3885.1458 | -0.00063207
38 |  | 245.0709 | 104.9919 | 4187 | 0.00010232 | 6.0038 | 6.0039 | -6.1774 | 9773.245 | 3990.1377 | -0.00063207
39 |  | 245.0709 | 104.9913 | 4187 | 0.00010232 | 6.0039 | 6.004 | -6.1774 | 9773.3038 | 4095.129 | -0.00063207
40 |  | 245.0709 | 104.9907 | 4187 | 0.00010232 | 6.004 | 6.0041 | -6.1774 | 9773.3627 | 4200.1197 | -0.00063206
41 |  | 245.0709 | 104.99 | 4187 | 0.00010232 | 6.0041 | 6.0042 | -6.1774 | 9773.4215 | 4305.1097 | -0.00063206
42 |  | 245.0709 | 104.9894 | 4187 | 0.00010232 | 6.0042 | 6.0043 | -6.1774 | 9773.4803 | 4410.0991 | -0.00063205
43 |  | 245.0709 | 104.9888 | 4187 | 0.00010232 | 6.0043 | 6.0044 | -6.1774 | 9773.5392 | 4515.0879 | -0.00063205
44 |  | 245.0709 | 104.9881 | 4187 | 0.00010232 | 6.0044 | 6.0045 | -6.1774 | 9773.598 | 4620.076 | -0.00063205
45 |  | 245.0709 | 104.9875 | 4187 | 0.00010232 | 6.0045 | 6.0046 | -6.1774 | 9773.6568 | 4725.0635 | -0.00063204
46 |  | 245.0709 | 104.9869 | 4187 | 0.00010232 | 6.0046 | 6.0047 | -6.1774 | 9773.7157 | 4830.0504 | -0.00063204
47 |  | 245.0709 | 104.9862 | 4187 | 0.00010231 | 6.0047 | 6.0048 | -6.1774 | 9773.7745 | 4935.0367 | -0.00063204
48 |  | 245.0709 | 104.9856 | 4187 | 0.00010231 | 6.0048 | 6.0049 | -6.1774 | 9773.8334 | 5040.0223 | -0.00063203
49 |  | 245.0709 | 104.985 | 4187 | 0.00010231 | 6.0049 | 6.005 | -6.1774 | 9773.8922 | 5145.0072 | -0.00063203
50 |  | 245.0709 | 104.9843 | 4187 | 0.00010231 | 6.005 | 6.0051 | -6.1774 | 9773.951 | 5249.9916 | -0.00063202
51 |  | 245.0709 | 104.9837 | 4187 | 0.00010231 | 6.0051 | 6.0052 | -6.1774 | 9774.0099 | 5354.9753 | -0.00063202
52 |  | 245.0709 | 104.9831 | 4187 | 0.00010231 | 6.0052 | 6.0053 | -6.1774 | 9774.0687 | 5459.9584 | -0.00063202
53 |  | 245.0709 | 104.9824 | 4187 | 0.00010231 | 6.0053 | 6.0054 | -6.1774 | 9774.1276 | 5564.9408 | -0.00063201
54 |  | 245.0709 | 104.9818 | 4187 | 0.00010231 | 6.0054 | 6.0055 | -6.1774 | 9774.1864 | 5669.9226 | -0.00063201
55 |  | 245.0709 | 104.9812 | 4187 | 0.00010231 | 6.0055 | 6.0056 | -6.1774 | 9774.2453 | 5774.9038 | -0.000632
56 |  | 245.0709 | 104.9806 | 4187 | 0.00010231 | 6.0056 | 6.0057 | -6.1774 | 9774.3041 | 5879.8844 | -0.000632
57 |  | 245.0709 | 104.9799 | 4187 | 0.00010231 | 6.0057 | 6.0058 | -6.1774 | 9774.3629 | 5984.8643 | -0.000632
58 |  | 245.0709 | 104.9793 | 4187 | 0.00010231 | 6.0058 | 6.0059 | -6.1774 | 9774.4218 | 6089.8436 | -0.00063199
59 |  | 245.0709 | 104.9787 | 4187 | 0.00010231 | 6.0059 | 6.006 | -6.1774 | 9774.4806 | 6194.8223 | -0.00063199
60 |  | 245.0709 | 104.978 | 4187 | 0.00010231 | 6.006 | 6.0061 | -6.1774 | 9774.5395 | 6299.8003 | -0.00063199
61 |  | 245.0709 | 104.9774 | 4187 | 0.00010231 | 6.0061 | 6.0062 | -6.1774 | 9774.5983 | 6404.7777 | -0.00063198
62 |  | 245.0709 | 104.9768 | 4187 | 0.00010231 | 6.0062 | 6.0063 | -6.1774 | 9774.6572 | 6509.7544 | -0.00063198
63 |  | 245.0709 | 104.9761 | 4187 | 0.0001023 | 6.0063 | 6.0064 | -6.1774 | 9774.716 | 6614.7306 | -0.00063197
64 |  | 245.0709 | 104.9755 | 4187 | 0.0001023 | 6.0064 | 6.0065 | -6.1774 | 9774.7749 | 6719.7061 | -0.00063197
65 |  | 245.0709 | 104.9749 | 4187 | 0.0001023 | 6.0065 | 6.0067 | -6.1774 | 9774.8337 | 6824.6809 | -0.00063197
66 |  | 245.0709 | 104.9742 | 4187 | 0.0001023 | 6.0067 | 6.0068 | -6.1774 | 9774.8926 | 6929.6552 | -0.00063196
67 |  | 245.0709 | 104.9736 | 4187 | 0.0001023 | 6.0068 | 6.0069 | -6.1774 | 9774.9514 | 7034.6288 | -0.00063196
68 |  | 245.0709 | 104.973 | 4187 | 0.0001023 | 6.0069 | 6.007 | -6.1774 | 9775.0102 | 7139.6017 | -0.00063196
69 |  | 245.0709 | 104.9723 | 4187 | 0.0001023 | 6.007 | 6.0071 | -6.1774 | 9775.0691 | 7244.5741 | -0.00063195
70 |  | 245.0709 | 104.9717 | 4187 | 0.0001023 | 6.0071 | 6.0072 | -6.1774 | 9775.1279 | 7349.5458 | -0.00063195
71 |  | 245.0709 | 104.9711 | 4187 | 0.0001023 | 6.0072 | 6.0073 | -6.1774 | 9775.1868 | 7454.5169 | -0.00063194
72 |  | 245.0709 | 104.9704 | 4187 | 0.0001023 | 6.0073 | 6.0074 | -6.1774 | 9775.2456 | 7559.4873 | -0.00063194
73 |  | 245.0709 | 104.9698 | 4187 | 0.0001023 | 6.0074 | 6.0075 | -6.1774 | 9775.3045 | 7664.4571 | -0.00063194
74 |  | 245.0709 | 104.9692 | 4187 | 0.0001023 | 6.0075 | 6.0076 | -6.1774 | 9775.3633 | 7769.4263 | -0.00063193
75 |  | 245.0709 | 104.9685 | 4187 | 0.0001023 | 6.0076 | 6.0077 | -6.1774 | 9775.4222 | 7874.3948 | -0.00063193
76 |  | 245.0709 | 104.9679 | 4187 | 0.0001023 | 6.0077 | 6.0078 | -6.1774 | 9775.481 | 7979.3627 | -0.00063193
77 |  | 245.0709 | 104.9673 | 4187 | 0.0001023 | 6.0078 | 6.0079 | -6.1774 | 9775.5399 | 8084.33 | -0.00063192
78 |  | 245.0709 | 104.9667 | 4187 | 0.0001023 | 6.0079 | 6.008 | -6.1774 | 9775.5987 | 8189.2967 | -0.00063192
79 |  | 245.0709 | 104.966 | 4187 | 0.00010229 | 6.008 | 6.0081 | -6.1774 | 9775.6576 | 8294.2627 | -0.00063191
80 |  | 245.0709 | 104.9654 | 4187 | 0.00010229 | 6.0081 | 6.0082 | -6.1774 | 9775.7164 | 8399.2281 | -0.00063191
81 |  | 245.0709 | 104.9648 | 4187 | 0.00010229 | 6.0082 | 6.0083 | -6.1774 | 9775.7753 | 8504.1928 | -0.00063191
82 |  | 245.0709 | 104.9641 | 4187 | 0.00010229 | 6.0083 | 6.0084 | -6.1774 | 9775.8341 | 8609.157 | -0.0006319
83 |  | 245.0709 | 104.9635 | 4187 | 0.00010229 | 6.0084 | 6.0085 | -6.1774 | 9775.893 | 8714.1204 | -0.0006319
84 |  | 245.0709 | 104.9629 | 4187 | 0.00010229 | 6.0085 | 6.0086 | -6.1774 | 9775.9518 | 8819.0833 | -0.00063189
85 |  | 245.0709 | 104.9622 | 4187 | 0.00010229 | 6.0086 | 6.0087 | -6.1774 | 9776.0107 | 8924.0455 | -0.00063189
86 |  | 245.0709 | 104.9616 | 4187 | 0.00010229 | 6.0087 | 6.0088 | -6.1774 | 9776.0696 | 9029.0071 | -0.00063189
87 |  | 245.0709 | 104.961 | 4187 | 0.00010229 | 6.0088 | 6.0089 | -6.1774 | 9776.1284 | 9133.9681 | -0.00063188
88 |  | 245.0709 | 104.9603 | 4187 | 0.00010229 | 6.0089 | 6.009 | -6.1774 | 9776.1873 | 9238.9284 | -0.00063188
89 |  | 245.0709 | 104.9597 | 4187 | 0.00010229 | 6.009 | 6.0091 | -6.1774 | 9776.2461 | 9343.8881 | -0.00063188
90 |  | 245.0709 | 104.9591 | 4187 | 0.00010229 | 6.0091 | 6.0092 | -6.1774 | 9776.305 | 9448.8472 | -0.00063187
91 |  | 245.0709 | 104.9584 | 4187 | 0.00010229 | 6.0092 | 6.0093 | -6.1774 | 9776.3638 | 9553.8056 | -0.00063187
92 |  | 245.0709 | 104.9578 | 4187 | 0.00010229 | 6.0093 | 6.0094 | -6.1774 | 9776.4227 | 9658.7634 | -0.00063186
93 |  | 245.0709 | 104.9572 | 4187 | 0.00010229 | 6.0094 | 6.0095 | -6.1774 | 9776.4815 | 9763.7206 | -0.00063186
94 |  | 245.0709 | 104.9565 | 4187 | 0.00010229 | 6.0095 | 6.0096 | -6.1774 | 9776.5404 | 9868.6771 | -0.00063186
95 |  | 245.0709 | 104.9559 | 4187 | 0.00010229 | 6.0096 | 6.0097 | -6.1774 | 9776.5993 | 9973.6331 | -0.00063185
96 |  | 245.0709 | 104.9553 | 4187 | 0.00010228 | 6.0097 | 6.0098 | -6.1774 | 9776.6581 | 10078.5883 | -0.00063185
97 |  | 245.0709 | 104.9546 | 4187 | 0.00010228 | 6.0098 | 6.0099 | -6.1774 | 9776.717 | 10183.543 | -0.00063185
98 |  | 245.0709 | 104.954 | 4187 | 0.00010228 | 6.0099 | 6.01 | -6.1774 | 9776.7758 | 10288.497 | -0.00063184
99 |  | 245.0709 | 104.9534 | 4187 | 0.00010228 | 6.01 | 6.0101 | -6.1774 | 9776.8347 | 10393.4504 | -0.00063184
100 |  | 245.0709 | 104.9527 | 4187 | 0.00010228 | 6.0101 | 6.0102 | -6.1774 | 9776.8935 | 10498.4031 | -0.00063183
101 |  | 245.0709 | 104.9521 | 4187 | 0.00010228 | 6.0102 | 6.0103 | -6.1774 | 9776.9524 | 10603.3552 | -0.00063183
102 |  | 245.0709 | 104.9515 | 4187 | 0.00010228 | 6.0103 | 6.0104 | -6.1774 | 9777.0113 | 10708.3067 | -0.00063183
103 |  | 245.0709 | 104.9509 | 4187 | 0.00010228 | 6.0104 | 6.0105 | -6.1774 | 9777.0701 | 10813.2576 | -0.00063182
104 |  | 245.0709 | 104.9502 | 4187 | 0.00010228 | 6.0105 | 6.0106 | -6.1774 | 9777.129 | 10918.2078 | -0.00063182
105 |  | 245.0709 | 104.9496 | 4187 | 0.00010228 | 6.0106 | 6.0107 | -6.1774 | 9777.1878 | 11023.1574 | -0.00063181
106 |  | 245.0709 | 104.949 | 4187 | 0.00010228 | 6.0107 | 6.0108 | -6.1774 | 9777.2467 | 11128.1063 | -0.00063181
107 |  | 245.0709 | 104.9483 | 4187 | 0.00010228 | 6.0108 | 6.0109 | -6.1774 | 9777.3056 | 11233.0547 | -0.00063181
108 |  | 245.0709 | 104.9477 | 4187 | 0.00010228 | 6.0109 | 6.011 | -6.1774 | 9777.3644 | 11338.0024 | -0.0006318
109 |  | 245.0709 | 104.9471 | 4187 | 0.00010228 | 6.011 | 6.0112 | -6.1774 | 9777.4233 | 11442.9494 | -0.0006318
110 |  | 245.0709 | 104.9464 | 4187 | 0.00010228 | 6.0112 | 6.0113 | -6.1774 | 9777.4821 | 11547.8959 | -0.0006318
111 |  | 245.0709 | 104.9458 | 4187 | 0.00010228 | 6.0113 | 6.0114 | -6.1774 | 9777.541 | 11652.8417 | -0.00063179
112 |  | 245.0709 | 104.9452 | 4187 | 0.00010227 | 6.0114 | 6.0115 | -6.1774 | 9777.5999 | 11757.7868 | -0.00063179
113 |  | 245.0709 | 104.9445 | 4187 | 0.00010227 | 6.0115 | 6.0116 | -6.1774 | 9777.6587 | 11862.7314 | -0.00063178
114 |  | 245.0709 | 104.9439 | 4187 | 0.00010227 | 6.0116 | 6.0117 | -6.1774 | 9777.7176 | 11967.6753 | -0.00063178
115 |  | 245.0709 | 104.9433 | 4187 | 0.00010227 | 6.0117 | 6.0118 | -6.1774 | 9777.7765 | 12072.6185 | -0.00063178
116 |  | 245.0709 | 104.9426 | 4187 | 0.00010227 | 6.0118 | 6.0119 | -6.1774 | 9777.8353 | 12177.5612 | -0.00063177
117 |  | 245.0709 | 104.942 | 4187 | 0.00010227 | 6.0119 | 6.012 | -6.1774 | 9777.8942 | 12282.5032 | -0.00063177
118 |  | 245.0709 | 104.9414 | 4187 | 0.00010227 | 6.012 | 6.0121 | -6.1774 | 9777.9531 | 12387.4446 | -0.00063177
119 |  | 245.0709 | 104.9407 | 4187 | 0.00010227 | 6.0121 | 6.0122 | -6.1774 | 9778.0119 | 12492.3853 | -0.00063176
120 |  | 245.0709 | 104.9401 | 4187 | 0.00010227 | 6.0122 | 6.0123 | -6.1774 | 9778.0708 | 12597.3254 | -0.00063176
121 |  | 245.0709 | 104.9395 | 4187 | 0.00010227 | 6.0123 | 6.0124 | -6.1774 | 9778.1297 | 12702.2649 | -0.00063175
122 |  | 245.0709 | 104.9388 | 4187 | 0.00010227 | 6.0124 | 6.0125 | -6.1774 | 9778.1885 | 12807.2037 | -0.00063175
123 |  | 245.0709 | 104.9382 | 4187 | 0.00010227 | 6.0125 | 6.0126 | -6.1774 | 9778.2474 | 12912.142 | -0.00063175
124 |  | 245.0709 | 104.9376 | 4187 | 0.00010227 | 6.0126 | 6.0127 | -6.1774 | 9778.3063 | 13017.0796 | -0.00063174
125 |  | 245.0709 | 104.937 | 4187 | 0.00010227 | 6.0127 | 6.0128 | -6.1774 | 9778.3651 | 13122.0165 | -0.00063174
126 |  | 245.0709 | 104.9363 | 4187 | 0.00010227 | 6.0128 | 6.0129 | -6.1774 | 9778.424 | 13226.9528 | -0.00063173
127 |  | 245.0709 | 104.9357 | 4187 | 0.00010227 | 6.0129 | 6.013 | -6.1774 | 9778.4829 | 13331.8885 | -0.00063173
128 |  | 245.0709 | 104.9351 | 4187 | 0.00010226 | 6.013 | 6.0131 | -6.1774 | 9778.5417 | 13436.8236 | -0.00063173
129 |  | 245.0709 | 104.9344 | 4187 | 0.00010226 | 6.0131 | 6.0132 | -6.1774 | 9778.6006 | 13541.758 | -0.00063172
130 |  | 245.0709 | 104.9338 | 4187 | 0.00010226 | 6.0132 | 6.0133 | -6.1774 | 9778.6595 | 13646.6918 | -0.00063172
131 |  | 245.0709 | 104.9332 | 4187 | 0.00010226 | 6.0133 | 6.0134 | -6.1774 | 9778.7183 | 13751.625 | -0.00063172
132 |  | 245.0709 | 104.9325 | 4187 | 0.00010226 | 6.0134 | 6.0135 | -6.1774 | 9778.7772 | 13856.5575 | -0.00063171
133 |  | 245.0709 | 104.9319 | 4187 | 0.00010226 | 6.0135 | 6.0136 | -6.1774 | 9778.8361 | 13961.4894 | -0.00063171
134 |  | 245.0709 | 104.9313 | 4187 | 0.00010226 | 6.0136 | 6.0137 | -6.1774 | 9778.8949 | 14066.4207 | -0.0006317
135 |  | 245.0709 | 104.9306 | 4187 | 0.00010226 | 6.0137 | 6.0138 | -6.1774 | 9778.9538 | 14171.3513 | -0.0006317
136 |  | 245.0709 | 104.93 | 4187 | 0.00010226 | 6.0138 | 6.0139 | -6.1774 | 9779.0127 | 14276.2813 | -0.0006317
137 |  | 245.0709 | 104.9294 | 4187 | 0.00010226 | 6.0139 | 6.014 | -6.1774 | 9779.0716 | 14381.2107 | -0.00063169
138 |  | 245.0709 | 104.9287 | 4187 | 0.00010226 | 6.014 | 6.0141 | -6.1774 | 9779.1304 | 14486.1394 | -0.00063169
139 |  | 245.0709 | 104.9281 | 4187 | 0.00010226 | 6.0141 | 6.0142 | -6.1774 | 9779.1893 | 14591.0675 | -0.00063169
140 |  | 245.0709 | 104.9275 | 4187 | 0.00010226 | 6.0142 | 6.0143 | -6.1774 | 9779.2482 | 14695.995 | -0.00063168
141 |  | 245.0709 | 104.9268 | 4187 | 0.00010226 | 6.0143 | 6.0144 | -6.1774 | 9779.3071 | 14800.9219 | -0.00063168
142 |  | 245.0709 | 104.9262 | 4187 | 0.00010226 | 6.0144 | 6.0145 | -6.1774 | 9779.3659 | 14905.8481 | -0.00063167
143 |  | 245.0709 | 104.9256 | 4187 | 0.00010226 | 6.0145 | 6.0146 | -6.1774 | 9779.4248 | 15010.7737 | -0.00063167
144 |  | 245.0709 | 104.925 | 4187 | 0.00010225 | 6.0146 | 6.0147 | -6.1774 | 9779.4837 | 15115.6986 | -0.00063167
145 |  | 245.0709 | 104.9243 | 4187 | 0.00010225 | 6.0147 | 6.0148 | -6.1774 | 9779.5425 | 15220.6229 | -0.00063166
146 |  | 245.0709 | 104.9237 | 4187 | 0.00010225 | 6.0148 | 6.0149 | -6.1774 | 9779.6014 | 15325.5466 | -0.00063166
147 |  | 245.0709 | 104.9231 | 4187 | 0.00010225 | 6.0149 | 6.015 | -6.1774 | 9779.6603 | 15430.4697 | -0.00063166
148 |  | 245.0709 | 104.9224 | 4187 | 0.00010225 | 6.015 | 6.0151 | -6.1774 | 9779.7192 | 15535.3921 | -0.00063165
149 |  | 245.0709 | 104.9218 | 4187 | 0.00010225 | 6.0151 | 6.0152 | -6.1774 | 9779.778 | 15640.3139 | -0.00063165
150 |  | 245.0709 | 104.9212 | 4187 | 0.00010225 | 6.0152 | 6.0153 | -6.1774 | 9779.8369 | 15745.2351 | -0.00063164
151 |  | 245.0709 | 104.9205 | 4187 | 0.00010225 | 6.0153 | 6.0154 | -6.1774 | 9779.8958 | 15850.1556 | -0.00063164
152 |  | 245.0709 | 104.9199 | 4187 | 0.00010225 | 6.0154 | 6.0155 | -6.1774 | 9779.9547 | 15955.0755 | -0.00063164
153 |  | 245.0709 | 104.9193 | 4187 | 0.00010225 | 6.0155 | 6.0157 | -6.1774 | 9780.0136 | 16059.9948 | -0.00063163
154 |  | 245.0709 | 104.9186 | 4187 | 0.00010225 | 6.0157 | 6.0158 | -6.1774 | 9780.0724 | 16164.9134 | -0.00063163
155 |  | 245.0709 | 104.918 | 4187 | 0.00010225 | 6.0158 | 6.0159 | -6.1774 | 9780.1313 | 16269.8314 | -0.00063162
156 |  | 245.0709 | 104.9174 | 4187 | 0.00010225 | 6.0159 | 6.016 | -6.1774 | 9780.1902 | 16374.7488 | -0.00063162
157 |  | 245.0709 | 104.9167 | 4187 | 0.00010225 | 6.016 | 6.0161 | -6.1774 | 9780.2491 | 16479.6655 | -0.00063162
158 |  | 245.0709 | 104.9161 | 4187 | 0.00010225 | 6.0161 | 6.0162 | -6.1774 | 9780.3079 | 16584.5816 | -0.00063161
159 |  | 245.0709 | 104.9155 | 4187 | 0.00010225 | 6.0162 | 6.0163 | -6.1774 | 9780.3668 | 16689.4971 | -0.00063161
160 |  | 245.0709 | 104.9148 | 4187 | 0.00010225 | 6.0163 | 6.0164 | -6.1774 | 9780.4257 | 16794.4119 | -0.00063161
161 |  | 245.0709 | 104.9142 | 4187 | 0.00010224 | 6.0164 | 6.0165 | -6.1774 | 9780.4846 | 16899.3262 | -0.0006316
162 |  | 245.0709 | 104.9136 | 4187 | 0.00010224 | 6.0165 | 6.0166 | -6.1774 | 9780.5435 | 17004.2397 | -0.0006316
163 |  | 245.0709 | 104.913 | 4187 | 0.00010224 | 6.0166 | 6.0167 | -6.1774 | 9780.6024 | 17109.1527 | -0.00063159
164 |  | 245.0709 | 104.9123 | 4187 | 0.00010224 | 6.0167 | 6.0168 | -6.1774 | 9780.6612 | 17214.065 | -0.00063159
165 |  | 245.0709 | 104.9117 | 4187 | 0.00010224 | 6.0168 | 6.0169 | -6.1774 | 9780.7201 | 17318.9767 | -0.00063159
166 |  | 245.0709 | 104.9111 | 4187 | 0.00010224 | 6.0169 | 6.017 | -6.1774 | 9780.779 | 17423.8877 | -0.00063158
167 |  | 245.0709 | 104.9104 | 4187 | 0.00010224 | 6.017 | 6.0171 | -6.1774 | 9780.8379 | 17528.7982 | -0.00063158
168 |  | 245.0709 | 104.9098 | 4187 | 0.00010224 | 6.0171 | 6.0172 | -6.1774 | 9780.8968 | 17633.708 | -0.00063158
169 |  | 245.0709 | 104.9092 | 4187 | 0.00010224 | 6.0172 | 6.0173 | -6.1774 | 9780.9556 | 17738.6171 | -0.00063157
170 |  | 245.0709 | 104.9085 | 4187 | 0.00010224 | 6.0173 | 6.0174 | -6.1774 | 9781.0145 | 17843.5257 | -0.00063157
171 |  | 245.0709 | 104.9079 | 4187 | 0.00010224 | 6.0174 | 6.0175 | -6.1774 | 9781.0734 | 17948.4336 | -0.00063156
172 |  | 245.0709 | 104.9073 | 4187 | 0.00010224 | 6.0175 | 6.0176 | -6.1774 | 9781.1323 | 18053.3408 | -0.00063156
173 |  | 245.0709 | 104.9066 | 4187 | 0.00010224 | 6.0176 | 6.0177 | -6.1774 | 9781.1912 | 18158.2475 | -0.00063156
174 |  | 245.0709 | 104.906 | 4187 | 0.00010224 | 6.0177 | 6.0178 | -6.1774 | 9781.2501 | 18263.1535 | -0.00063155
175 |  | 245.0709 | 104.9054 | 4187 | 0.00010224 | 6.0178 | 6.0179 | -6.1774 | 9781.3089 | 18368.0588 | -0.00063155
176 |  | 245.0709 | 104.9047 | 4187 | 0.00010224 | 6.0179 | 6.018 | -6.1774 | 9781.3678 | 18472.9636 | -0.00063154
177 |  | 245.0709 | 104.9041 | 4187 | 0.00010223 | 6.018 | 6.0181 | -6.1774 | 9781.4267 | 18577.8677 | -0.00063154
178 |  | 245.0709 | 104.9035 | 4187 | 0.00010223 | 6.0181 | 6.0182 | -6.1774 | 9781.4856 | 18682.7712 | -0.00063154
179 |  | 245.0709 | 104.9028 | 4187 | 0.00010223 | 6.0182 | 6.0183 | -6.1774 | 9781.5445 | 18787.674 | -0.00063153
180 |  | 245.0709 | 104.9022 | 4187 | 0.00010223 | 6.0183 | 6.0184 | -6.1774 | 9781.6034 | 18892.5762 | -0.00063153
181 |  | 245.0709 | 104.9016 | 4187 | 0.00010223 | 6.0184 | 6.0185 | -6.1774 | 9781.6623 | 18997.4778 | -0.00063153
182 |  | 245.0709 | 104.901 | 4187 | 0.00010223 | 6.0185 | 6.0186 | -6.1774 | 9781.7212 | 19102.3788 | -0.00063152
183 |  | 245.0709 | 104.9003 | 4187 | 0.00010223 | 6.0186 | 6.0187 | -6.1774 | 9781.78 | 19207.2791 | -0.00063152
184 |  | 245.0709 | 104.8997 | 4187 | 0.00010223 | 6.0187 | 6.0188 | -6.1774 | 9781.8389 | 19312.1788 | -0.00063151
185 |  | 245.0709 | 104.8991 | 4187 | 0.00010223 | 6.0188 | 6.0189 | -6.1774 | 9781.8978 | 19417.0778 | -0.00063151
186 |  | 245.0709 | 104.8984 | 4187 | 0.00010223 | 6.0189 | 6.019 | -6.1774 | 9781.9567 | 19521.9762 | -0.00063151
187 |  | 245.0709 | 104.8978 | 4187 | 0.00010223 | 6.019 | 6.0191 | -6.1774 | 9782.0156 | 19626.874 | -0.0006315
188 |  | 245.0709 | 104.8972 | 4187 | 0.00010223 | 6.0191 | 6.0192 | -6.1774 | 9782.0745 | 19731.7712 | -0.0006315
189 |  | 245.0709 | 104.8965 | 4187 | 0.00010223 | 6.0192 | 6.0193 | -6.1774 | 9782.1334 | 19836.6677 | -0.0006315
190 |  | 245.0709 | 104.8959 | 4187 | 0.00010223 | 6.0193 | 6.0194 | -6.1774 | 9782.1923 | 19941.5636 | -0.00063149
191 |  | 245.0709 | 104.8953 | 4187 | 0.00010223 | 6.0194 | 6.0195 | -6.1774 | 9782.2512 | 20046.4589 | -0.00063149
192 |  | 245.0709 | 104.8946 | 4187 | 0.00010223 | 6.0195 | 6.0196 | -6.1774 | 9782.3101 | 20151.3535 | -0.00063148
193 |  | 245.0709 | 104.894 | 4187 | 0.00010222 | 6.0196 | 6.0197 | -6.1774 | 9782.3689 | 20256.2475 | -0.00063148
194 |  | 245.0709 | 104.8934 | 4187 | 0.00010222 | 6.0197 | 6.0198 | -6.1774 | 9782.4278 | 20361.1409 | -0.00063148
195 |  | 245.0709 | 104.8927 | 4187 | 0.00010222 | 6.0198 | 6.0199 | -6.1774 | 9782.4867 | 20466.0337 | -0.00063147
196 |  | 245.0709 | 104.8921 | 4187 | 0.00010222 | 6.0199 | 6.02 | -6.1774 | 9782.5456 | 20570.9258 | -0.00063147
197 |  | 245.0709 | 104.8915 | 4187 | 0.00010222 | 6.02 | 6.0201 | -6.1774 | 9782.6045 | 20675.8172 | -0.00063146
198 |  | 245.0709 | 104.8908 | 4187 | 0.00010222 | 6.0201 | 6.0203 | -6.1774 | 9782.6634 | 20780.7081 | -0.00063146
199 |  | 245.0709 | 104.8902 | 4187 | 0.00010222 | 6.0203 | 6.0204 | -6.1774 | 9782.7223 | 20885.5983 | -0.00063146
200 |  | 245.0709 | 104.8896 | 4187 | 0.00010222 | 6.0204 | 6.0205 | -6.1774 | 9782.7812 | 20990.4879 | -0.00063145
201 |  | 245.0709 | 104.889 | 4187 | 0.00010222 | 6.0205 | 6.0206 | -6.1774 | 9782.8401 | 21095.3768 | -0.00063145
202 |  | 245.0709 | 104.8883 | 4187 | 0.00010222 | 6.0206 | 6.0207 | -6.1774 | 9782.899 | 21200.2652 | -0.00063145
203 |  | 245.0709 | 104.8877 | 4187 | 0.00010222 | 6.0207 | 6.0208 | -6.1774 | 9782.9579 | 21305.1529 | -0.00063144
204 |  | 245.0709 | 104.8871 | 4187 | 0.00010222 | 6.0208 | 6.0209 | -6.1774 | 9783.0168 | 21410.0399 | -0.00063144
205 |  | 245.0709 | 104.8864 | 4187 | 0.00010222 | 6.0209 | 6.021 | -6.1774 | 9783.0757 | 21514.9263 | -0.00063143
206 |  | 245.0709 | 104.8858 | 4187 | 0.00010222 | 6.021 | 6.0211 | -6.1774 | 9783.1346 | 21619.8121 | -0.00063143
207 |  | 245.0709 | 104.8852 | 4187 | 0.00010222 | 6.0211 | 6.0212 | -6.1774 | 9783.1935 | 21724.6973 | -0.00063143
208 |  | 245.0709 | 104.8845 | 4187 | 0.00010222 | 6.0212 | 6.0213 | -6.1774 | 9783.2524 | 21829.5818 | -0.00063142
209 |  | 245.0709 | 104.8839 | 4187 | 0.00010221 | 6.0213 | 6.0214 | -6.1774 | 9783.3113 | 21934.4657 | -0.00063142
210 |  | 245.0709 | 104.8833 | 4187 | 0.00010221 | 6.0214 | 6.0215 | -6.1774 | 9783.3702 | 22039.349 | -0.00063142
211 |  | 245.0709 | 104.8826 | 4187 | 0.00010221 | 6.0215 | 6.0216 | -6.1774 | 9783.4291 | 22144.2316 | -0.00063141
212 |  | 245.0709 | 104.882 | 4187 | 0.00010221 | 6.0216 | 6.0217 | -6.1774 | 9783.4879 | 22249.1137 | -0.00063141
213 |  | 245.0709 | 104.8814 | 4187 | 0.00010221 | 6.0217 | 6.0218 | -6.1774 | 9783.5468 | 22353.995 | -0.0006314
214 |  | 245.0709 | 104.8807 | 4187 | 0.00010221 | 6.0218 | 6.0219 | -6.1774 | 9783.6057 | 22458.8758 | -0.0006314
215 |  | 245.0709 | 104.8801 | 4187 | 0.00010221 | 6.0219 | 6.022 | -6.1774 | 9783.6646 | 22563.7559 | -0.0006314
216 |  | 245.0709 | 104.8795 | 4187 | 0.00010221 | 6.022 | 6.0221 | -6.1774 | 9783.7235 | 22668.6354 | -0.00063139
217 |  | 245.0709 | 104.8789 | 4187 | 0.00010221 | 6.0221 | 6.0222 | -6.1774 | 9783.7824 | 22773.5142 | -0.00063139
218 |  | 245.0709 | 104.8782 | 4187 | 0.00010221 | 6.0222 | 6.0223 | -6.1774 | 9783.8413 | 22878.3924 | -0.00063139
219 |  | 245.0709 | 104.8776 | 4187 | 0.00010221 | 6.0223 | 6.0224 | -6.1774 | 9783.9002 | 22983.27 | -0.00063138
220 |  | 245.0709 | 104.877 | 4187 | 0.00010221 | 6.0224 | 6.0225 | -6.1774 | 9783.9591 | 23088.147 | -0.00063138
221 |  | 245.0709 | 104.8763 | 4187 | 0.00010221 | 6.0225 | 6.0226 | -6.1774 | 9784.0181 | 23193.0233 | -0.00063137
222 |  | 245.0709 | 104.8757 | 4187 | 0.00010221 | 6.0226 | 6.0227 | -6.1774 | 9784.077 | 23297.899 | -0.00063137
223 |  | 245.0709 | 104.8751 | 4187 | 0.00010221 | 6.0227 | 6.0228 | -6.1774 | 9784.1359 | 23402.7741 | -0.00063137
224 |  | 245.0709 | 104.8744 | 4187 | 0.00010221 | 6.0228 | 6.0229 | -6.1774 | 9784.1948 | 23507.6485 | -0.00063136
225 |  | 245.0709 | 104.8738 | 4187 | 0.00010221 | 6.0229 | 6.023 | -6.1774 | 9784.2537 | 23612.5223 | -0.00063136
226 |  | 245.0709 | 104.8732 | 4187 | 0.0001022 | 6.023 | 6.0231 | -6.1774 | 9784.3126 | 23717.3955 | -0.00063135
227 |  | 245.0709 | 104.8725 | 4187 | 0.0001022 | 6.0231 | 6.0232 | -6.1774 | 9784.3715 | 23822.268 | -0.00063135
228 |  | 245.0709 | 104.8719 | 4187 | 0.0001022 | 6.0232 | 6.0233 | -6.1774 | 9784.4304 | 23927.1399 | -0.00063135
229 |  | 245.0709 | 104.8713 | 4187 | 0.0001022 | 6.0233 | 6.0234 | -6.1774 | 9784.4893 | 24032.0112 | -0.00063134
230 |  | 245.0709 | 104.8706 | 4187 | 0.0001022 | 6.0234 | 6.0235 | -6.1774 | 9784.5482 | 24136.8818 | -0.00063134
231 |  | 245.0709 | 104.87 | 4187 | 0.0001022 | 6.0235 | 6.0236 | -6.1774 | 9784.6071 | 24241.7518 | -0.00063134
232 |  | 245.0709 | 104.8694 | 4187 | 0.0001022 | 6.0236 | 6.0237 | -6.1774 | 9784.666 | 24346.6212 | -0.00063133
233 |  | 245.0709 | 104.8687 | 4187 | 0.0001022 | 6.0237 | 6.0238 | -6.1774 | 9784.7249 | 24451.49 | -0.00063133
234 |  | 245.0709 | 104.8681 | 4187 | 0.0001022 | 6.0238 | 6.0239 | -6.1774 | 9784.7838 | 24556.3581 | -0.00063132
235 |  | 245.0709 | 104.8675 | 4187 | 0.0001022 | 6.0239 | 6.024 | -6.1774 | 9784.8427 | 24661.2256 | -0.00063132
236 |  | 245.0709 | 104.8669 | 4187 | 0.0001022 | 6.024 | 6.0241 | -6.1774 | 9784.9016 | 24766.0924 | -0.00063132

## St21
|  |  | buis | verlies W/M | L /°C/sec
diam | wandikte |  | inhoud l/m |  | W/M
21.3 | 2 | 3.1416 | 0.23506 | 16.7432 | 4187
[8 empty] | J/sec/mtr | aantal mtr. | verlies
|  | buis | verlies W/M | L /°C/sec | verlies temp | begintemp | eindtemp | verlies | bij 1°C | totaal J/sec
|  | inhoud L |  | W/M | °C per M | °C | °C | per m°C | daling | aantal mtr
1 | 21.3 | 0.23506 | 16.7432 | 4187 | 0.017012 | 6 | 6.017 | -0.98489 | 58.7823 | 16.7432 | -0.016755
2 |  | 0.23506 | 16.7264 | 4187 | 0.016995 | 6.017 | 6.034 | -0.98489 | 58.8412 | 33.4696 | -0.016738
3 |  | 0.23506 | 16.7097 | 4187 | 0.016978 | 6.034 | 6.051 | -0.98489 | 58.9001 | 50.1794 | -0.016721
4 |  | 0.23506 | 16.693 | 4187 | 0.016961 | 6.051 | 6.0679 | -0.98489 | 58.9591 | 66.8723 | -0.016705
5 |  | 0.23506 | 16.6763 | 4187 | 0.016944 | 6.0679 | 6.0849 | -0.98489 | 59.0182 | 83.5486 | -0.016688
6 |  | 0.23506 | 16.6596 | 4187 | 0.016927 | 6.0849 | 6.1018 | -0.98489 | 59.0773 | 100.2082 | -0.016671
7 |  | 0.23506 | 16.6429 | 4187 | 0.01691 | 6.1018 | 6.1187 | -0.98489 | 59.1365 | 116.8511 | -0.016655
8 |  | 0.23506 | 16.6263 | 4187 | 0.016893 | 6.1187 | 6.1356 | -0.98489 | 59.1957 | 133.4774 | -0.016638
9 |  | 0.23506 | 16.6096 | 4187 | 0.016876 | 6.1356 | 6.1525 | -0.98489 | 59.255 | 150.087 | -0.016621
10 |  | 0.23506 | 16.593 | 4187 | 0.016859 | 6.1525 | 6.1694 | -0.98489 | 59.3144 | 166.6801 | -0.016605
11 |  | 0.23506 | 16.5764 | 4187 | 0.016842 | 6.1694 | 6.1862 | -0.98489 | 59.3738 | 183.2565 | -0.016588
12 |  | 0.23506 | 16.5598 | 4187 | 0.016826 | 6.1862 | 6.203 | -0.98489 | 59.4333 | 199.8163 | -0.016571
13 |  | 0.23506 | 16.5432 | 4187 | 0.016809 | 6.203 | 6.2198 | -0.98489 | 59.4928 | 216.3595 | -0.016555
14 |  | 0.23506 | 16.5267 | 4187 | 0.016792 | 6.2198 | 6.2366 | -0.98489 | 59.5524 | 232.8862 | -0.016538
15 |  | 0.23506 | 16.5102 | 4187 | 0.016775 | 6.2366 | 6.2534 | -0.98489 | 59.612 | 249.3964 | -0.016522
16 |  | 0.23506 | 16.4936 | 4187 | 0.016758 | 6.2534 | 6.2702 | -0.98489 | 59.6718 | 265.89 | -0.016505
17 |  | 0.23506 | 16.4771 | 4187 | 0.016742 | 6.2702 | 6.2869 | -0.98489 | 59.7315 | 282.3671 | -0.016489
18 |  | 0.23506 | 16.4606 | 4187 | 0.016725 | 6.2869 | 6.3036 | -0.98489 | 59.7914 | 298.8278 | -0.016472
19 |  | 0.23506 | 16.4442 | 4187 | 0.016708 | 6.3036 | 6.3203 | -0.98489 | 59.8513 | 315.2719 | -0.016456
20 |  | 0.23506 | 16.4277 | 4187 | 0.016691 | 6.3203 | 6.337 | -0.98489 | 59.9112 | 331.6996 | -0.016439
21 |  | 0.23506 | 16.4113 | 4187 | 0.016675 | 6.337 | 6.3537 | -0.98489 | 59.9712 | 348.1109 | -0.016423
22 |  | 0.23506 | 16.3948 | 4187 | 0.016658 | 6.3537 | 6.3704 | -0.98489 | 60.0313 | 364.5058 | -0.016406
23 |  | 0.23506 | 16.3784 | 4187 | 0.016641 | 6.3704 | 6.387 | -0.98489 | 60.0914 | 380.8842 | -0.01639
24 |  | 0.23506 | 16.3621 | 4187 | 0.016625 | 6.387 | 6.4036 | -0.98489 | 60.1516 | 397.2462 | -0.016374
25 |  | 0.23506 | 16.3457 | 4187 | 0.016608 | 6.4036 | 6.4202 | -0.98489 | 60.2119 | 413.5919 | -0.016357
26 |  | 0.23506 | 16.3293 | 4187 | 0.016591 | 6.4202 | 6.4368 | -0.98489 | 60.2722 | 429.9212 | -0.016341
27 |  | 0.23506 | 16.313 | 4187 | 0.016575 | 6.4368 | 6.4534 | -0.98489 | 60.3326 | 446.2342 | -0.016324
28 |  | 0.23506 | 16.2967 | 4187 | 0.016558 | 6.4534 | 6.47 | -0.98489 | 60.393 | 462.5309 | -0.016308
29 |  | 0.23506 | 16.2803 | 4187 | 0.016542 | 6.47 | 6.4865 | -0.98489 | 60.4535 | 478.8112 | -0.016292
30 |  | 0.23506 | 16.2641 | 4187 | 0.016525 | 6.4865 | 6.503 | -0.98489 | 60.514 | 495.0753 | -0.016275
31 |  | 0.23506 | 16.2478 | 4187 | 0.016509 | 6.503 | 6.5195 | -0.98489 | 60.5747 | 511.3231 | -0.016259
32 |  | 0.23506 | 16.2315 | 4187 | 0.016492 | 6.5195 | 6.536 | -0.98489 | 60.6353 | 527.5546 | -0.016243
33 |  | 0.23506 | 16.2153 | 4187 | 0.016476 | 6.536 | 6.5525 | -0.98489 | 60.6961 | 543.7699 | -0.016227
34 |  | 0.23506 | 16.1991 | 4187 | 0.016459 | 6.5525 | 6.569 | -0.98489 | 60.7569 | 559.9689 | -0.01621
35 |  | 0.23506 | 16.1828 | 4187 | 0.016443 | 6.569 | 6.5854 | -0.98489 | 60.8177 | 576.1517 | -0.016194
36 |  | 0.23506 | 16.1666 | 4187 | 0.016426 | 6.5854 | 6.6018 | -0.98489 | 60.8787 | 592.3184 | -0.016178
37 |  | 0.23506 | 16.1505 | 4187 | 0.01641 | 6.6018 | 6.6182 | -0.98489 | 60.9396 | 608.4689 | -0.016162
38 |  | 0.23506 | 16.1343 | 4187 | 0.016393 | 6.6182 | 6.6346 | -0.98489 | 61.0007 | 624.6032 | -0.016146
39 |  | 0.23506 | 16.1182 | 4187 | 0.016377 | 6.6346 | 6.651 | -0.98489 | 61.0618 | 640.7213 | -0.016129
40 |  | 0.23506 | 16.102 | 4187 | 0.01636 | 6.651 | 6.6674 | -0.98489 | 61.123 | 656.8234 | -0.016113
41 |  | 0.23506 | 16.0859 | 4187 | 0.016344 | 6.6674 | 6.6837 | -0.98489 | 61.1842 | 672.9093 | -0.016097
42 |  | 0.23506 | 16.0698 | 4187 | 0.016328 | 6.6837 | 6.7 | -0.98489 | 61.2455 | 688.9791 | -0.016081
43 |  | 0.23506 | 16.0537 | 4187 | 0.016311 | 6.7 | 6.7163 | -0.98489 | 61.3068 | 705.0328 | -0.016065
44 |  | 0.23506 | 16.0377 | 4187 | 0.016295 | 6.7163 | 6.7326 | -0.98489 | 61.3682 | 721.0705 | -0.016049
45 |  | 0.23506 | 16.0216 | 4187 | 0.016279 | 6.7326 | 6.7489 | -0.98489 | 61.4297 | 737.0921 | -0.016033
46 |  | 0.23506 | 16.0056 | 4187 | 0.016262 | 6.7489 | 6.7652 | -0.98489 | 61.4912 | 753.0977 | -0.016017
47 |  | 0.23506 | 15.9896 | 4187 | 0.016246 | 6.7652 | 6.7814 | -0.98489 | 61.5528 | 769.0873 | -0.016001
48 |  | 0.23506 | 15.9736 | 4187 | 0.01623 | 6.7814 | 6.7977 | -0.98489 | 61.6145 | 785.0609 | -0.015985
49 |  | 0.23506 | 15.9576 | 4187 | 0.016214 | 6.7977 | 6.8139 | -0.98489 | 61.6762 | 801.0185 | -0.015969
50 |  | 0.23506 | 15.9416 | 4187 | 0.016197 | 6.8139 | 6.8301 | -0.98489 | 61.738 | 816.9601 | -0.015953
51 |  | 0.23506 | 15.9257 | 4187 | 0.016181 | 6.8301 | 6.8463 | -0.98489 | 61.7998 | 832.8858 | -0.015937
52 |  | 0.23506 | 15.9097 | 4187 | 0.016165 | 6.8463 | 6.8624 | -0.98489 | 61.8617 | 848.7955 | -0.015921
53 |  | 0.23506 | 15.8938 | 4187 | 0.016149 | 6.8624 | 6.8786 | -0.98489 | 61.9237 | 864.6893 | -0.015905
54 |  | 0.23506 | 15.8779 | 4187 | 0.016133 | 6.8786 | 6.8947 | -0.98489 | 61.9857 | 880.5672 | -0.015889
55 |  | 0.23506 | 15.862 | 4187 | 0.016117 | 6.8947 | 6.9108 | -0.98489 | 62.0478 | 896.4292 | -0.015873
56 |  | 0.23506 | 15.8461 | 4187 | 0.0161 | 6.9108 | 6.9269 | -0.98489 | 62.11 | 912.2754 | -0.015857
57 |  | 0.23506 | 15.8303 | 4187 | 0.016084 | 6.9269 | 6.943 | -0.98489 | 62.1722 | 928.1057 | -0.015841
58 |  | 0.23506 | 15.8144 | 4187 | 0.016068 | 6.943 | 6.9591 | -0.98489 | 62.2345 | 943.9201 | -0.015826
59 |  | 0.23506 | 15.7986 | 4187 | 0.016052 | 6.9591 | 6.9751 | -0.98489 | 62.2968 | 959.7187 | -0.01581
60 |  | 0.23506 | 15.7828 | 4187 | 0.016036 | 6.9751 | 6.9912 | -0.98489 | 62.3592 | 975.5015 | -0.015794
61 |  | 0.23506 | 15.767 | 4187 | 0.01602 | 6.9912 | 7.0072 | -0.98489 | 62.4217 | 991.2686 | -0.015778
62 |  | 0.23506 | 15.7512 | 4187 | 0.016004 | 7.0072 | 7.0232 | -0.98489 | 62.4842 | 1007.0198 | -0.015762
63 |  | 0.23506 | 15.7355 | 4187 | 0.015988 | 7.0232 | 7.0392 | -0.98489 | 62.5468 | 1022.7553 | -0.015747
64 |  | 0.23506 | 15.7197 | 4187 | 0.015972 | 7.0392 | 7.0551 | -0.98489 | 62.6095 | 1038.475 | -0.015731
65 |  | 0.23506 | 15.704 | 4187 | 0.015956 | 7.0551 | 7.0711 | -0.98489 | 62.6722 | 1054.179 | -0.015715
66 |  | 0.23506 | 15.6883 | 4187 | 0.01594 | 7.0711 | 7.087 | -0.98489 | 62.735 | 1069.8673 | -0.015699
67 |  | 0.23506 | 15.6726 | 4187 | 0.015924 | 7.087 | 7.103 | -0.98489 | 62.7978 | 1085.5399 | -0.015684
68 |  | 0.23506 | 15.6569 | 4187 | 0.015908 | 7.103 | 7.1189 | -0.98489 | 62.8607 | 1101.1968 | -0.015668
69 |  | 0.23506 | 15.6412 | 4187 | 0.015892 | 7.1189 | 7.1348 | -0.98489 | 62.9237 | 1116.838 | -0.015652
70 |  | 0.23506 | 15.6256 | 4187 | 0.015876 | 7.1348 | 7.1506 | -0.98489 | 62.9867 | 1132.4636 | -0.015637
71 |  | 0.23506 | 15.6099 | 4187 | 0.01586 | 7.1506 | 7.1665 | -0.98489 | 63.0498 | 1148.0735 | -0.015621
72 |  | 0.23506 | 15.5943 | 4187 | 0.015845 | 7.1665 | 7.1823 | -0.98489 | 63.113 | 1163.6679 | -0.015605
73 |  | 0.23506 | 15.5787 | 4187 | 0.015829 | 7.1823 | 7.1982 | -0.98489 | 63.1762 | 1179.2466 | -0.01559
74 |  | 0.23506 | 15.5631 | 4187 | 0.015813 | 7.1982 | 7.214 | -0.98489 | 63.2395 | 1194.8097 | -0.015574
75 |  | 0.23506 | 15.5476 | 4187 | 0.015797 | 7.214 | 7.2298 | -0.98489 | 63.3028 | 1210.3573 | -0.015558
76 |  | 0.23506 | 15.532 | 4187 | 0.015781 | 7.2298 | 7.2456 | -0.98489 | 63.3662 | 1225.8892 | -0.015543
77 |  | 0.23506 | 15.5165 | 4187 | 0.015765 | 7.2456 | 7.2613 | -0.98489 | 63.4297 | 1241.4057 | -0.015527
78 |  | 0.23506 | 15.5009 | 4187 | 0.01575 | 7.2613 | 7.2771 | -0.98489 | 63.4932 | 1256.9066 | -0.015512
79 |  | 0.23506 | 15.4854 | 4187 | 0.015734 | 7.2771 | 7.2928 | -0.98489 | 63.5568 | 1272.392 | -0.015496
80 |  | 0.23506 | 15.4699 | 4187 | 0.015718 | 7.2928 | 7.3085 | -0.98489 | 63.6205 | 1287.862 | -0.015481
81 |  | 0.23506 | 15.4544 | 4187 | 0.015702 | 7.3085 | 7.3242 | -0.98489 | 63.6842 | 1303.3164 | -0.015465
82 |  | 0.23506 | 15.439 | 4187 | 0.015687 | 7.3242 | 7.3399 | -0.98489 | 63.748 | 1318.7554 | -0.01545
83 |  | 0.23506 | 15.4235 | 4187 | 0.015671 | 7.3399 | 7.3556 | -0.98489 | 63.8119 | 1334.1789 | -0.015434
84 |  | 0.23506 | 15.4081 | 4187 | 0.015655 | 7.3556 | 7.3712 | -0.98489 | 63.8758 | 1349.587 | -0.015419
85 |  | 0.23506 | 15.3927 | 4187 | 0.01564 | 7.3712 | 7.3869 | -0.98489 | 63.9398 | 1364.9796 | -0.015403
86 |  | 0.23506 | 15.3773 | 4187 | 0.015624 | 7.3869 | 7.4025 | -0.98489 | 64.0038 | 1380.3569 | -0.015388
87 |  | 0.23506 | 15.3619 | 4187 | 0.015608 | 7.4025 | 7.4181 | -0.98489 | 64.0679 | 1395.7188 | -0.015373
88 |  | 0.23506 | 15.3465 | 4187 | 0.015593 | 7.4181 | 7.4337 | -0.98489 | 64.1321 | 1411.0653 | -0.015357
89 |  | 0.23506 | 15.3311 | 4187 | 0.015577 | 7.4337 | 7.4493 | -0.98489 | 64.1964 | 1426.3964 | -0.015342
90 |  | 0.23506 | 15.3158 | 4187 | 0.015562 | 7.4493 | 7.4649 | -0.98489 | 64.2607 | 1441.7122 | -0.015327
91 |  | 0.23506 | 15.3005 | 4187 | 0.015546 | 7.4649 | 7.4804 | -0.98489 | 64.325 | 1457.0127 | -0.015311
92 |  | 0.23506 | 15.2852 | 4187 | 0.01553 | 7.4804 | 7.4959 | -0.98489 | 64.3895 | 1472.2979 | -0.015296
93 |  | 0.23506 | 15.2699 | 4187 | 0.015515 | 7.4959 | 7.5114 | -0.98489 | 64.454 | 1487.5678 | -0.015281
94 |  | 0.23506 | 15.2546 | 4187 | 0.015499 | 7.5114 | 7.5269 | -0.98489 | 64.5185 | 1502.8224 | -0.015265
95 |  | 0.23506 | 15.2393 | 4187 | 0.015484 | 7.5269 | 7.5424 | -0.98489 | 64.5832 | 1518.0617 | -0.01525
96 |  | 0.23506 | 15.2241 | 4187 | 0.015468 | 7.5424 | 7.5579 | -0.98489 | 64.6479 | 1533.2858 | -0.015235
97 |  | 0.23506 | 15.2088 | 4187 | 0.015453 | 7.5579 | 7.5733 | -0.98489 | 64.7126 | 1548.4946 | -0.01522
98 |  | 0.23506 | 15.1936 | 4187 | 0.015437 | 7.5733 | 7.5888 | -0.98489 | 64.7774 | 1563.6882 | -0.015204
99 |  | 0.23506 | 15.1784 | 4187 | 0.015422 | 7.5888 | 7.6042 | -0.98489 | 64.8423 | 1578.8666 | -0.015189
100 |  | 0.23506 | 15.1632 | 4187 | 0.015407 | 7.6042 | 7.6196 | -0.98489 | 64.9073 | 1594.0299 | -0.015174
101 |  | 0.23506 | 15.1481 | 4187 | 0.015391 | 7.6196 | 7.635 | -0.98489 | 64.9723 | 1609.1779 | -0.015159
102 |  | 0.23506 | 15.1329 | 4187 | 0.015376 | 7.635 | 7.6504 | -0.98489 | 65.0374 | 1624.3108 | -0.015144
103 |  | 0.23506 | 15.1178 | 4187 | 0.01536 | 7.6504 | 7.6657 | -0.98489 | 65.1025 | 1639.4286 | -0.015128
104 |  | 0.23506 | 15.1026 | 4187 | 0.015345 | 7.6657 | 7.6811 | -0.98489 | 65.1677 | 1654.5312 | -0.015113
105 |  | 0.23506 | 15.0875 | 4187 | 0.01533 | 7.6811 | 7.6964 | -0.98489 | 65.233 | 1669.6187 | -0.015098
106 |  | 0.23506 | 15.0724 | 4187 | 0.015314 | 7.6964 | 7.7117 | -0.98489 | 65.2984 | 1684.6911 | -0.015083
107 |  | 0.23506 | 15.0573 | 4187 | 0.015299 | 7.7117 | 7.727 | -0.98489 | 65.3638 | 1699.7484 | -0.015068
108 |  | 0.23506 | 15.0423 | 4187 | 0.015284 | 7.727 | 7.7423 | -0.98489 | 65.4292 | 1714.7907 | -0.015053
109 |  | 0.23506 | 15.0272 | 4187 | 0.015268 | 7.7423 | 7.7576 | -0.98489 | 65.4948 | 1729.8179 | -0.015038
110 |  | 0.23506 | 15.0122 | 4187 | 0.015253 | 7.7576 | 7.7728 | -0.98489 | 65.5604 | 1744.8301 | -0.015023
111 |  | 0.23506 | 14.9971 | 4187 | 0.015238 | 7.7728 | 7.7881 | -0.98489 | 65.6261 | 1759.8272 | -0.015008
112 |  | 0.23506 | 14.9821 | 4187 | 0.015223 | 7.7881 | 7.8033 | -0.98489 | 65.6918 | 1774.8094 | -0.014993
113 |  | 0.23506 | 14.9671 | 4187 | 0.015207 | 7.8033 | 7.8185 | -0.98489 | 65.7576 | 1789.7765 | -0.014978
114 |  | 0.23506 | 14.9522 | 4187 | 0.015192 | 7.8185 | 7.8337 | -0.98489 | 65.8235 | 1804.7287 | -0.014963
115 |  | 0.23506 | 14.9372 | 4187 | 0.015177 | 7.8337 | 7.8489 | -0.98489 | 65.8894 | 1819.6659 | -0.014948
116 |  | 0.23506 | 14.9223 | 4187 | 0.015162 | 7.8489 | 7.864 | -0.98489 | 65.9554 | 1834.5882 | -0.014933
117 |  | 0.23506 | 14.9073 | 4187 | 0.015147 | 7.864 | 7.8792 | -0.98489 | 66.0215 | 1849.4955 | -0.014918
118 |  | 0.23506 | 14.8924 | 4187 | 0.015131 | 7.8792 | 7.8943 | -0.98489 | 66.0876 | 1864.3879 | -0.014903
119 |  | 0.23506 | 14.8775 | 4187 | 0.015116 | 7.8943 | 7.9094 | -0.98489 | 66.1538 | 1879.2654 | -0.014888
120 |  | 0.23506 | 14.8626 | 4187 | 0.015101 | 7.9094 | 7.9245 | -0.98489 | 66.2201 | 1894.128 | -0.014873
121 |  | 0.23506 | 14.8477 | 4187 | 0.015086 | 7.9245 | 7.9396 | -0.98489 | 66.2864 | 1908.9758 | -0.014858
122 |  | 0.23506 | 14.8329 | 4187 | 0.015071 | 7.9396 | 7.9547 | -0.98489 | 66.3528 | 1923.8086 | -0.014843
123 |  | 0.23506 | 14.818 | 4187 | 0.015056 | 7.9547 | 7.9697 | -0.98489 | 66.4193 | 1938.6267 | -0.014828
124 |  | 0.23506 | 14.8032 | 4187 | 0.015041 | 7.9697 | 7.9848 | -0.98489 | 66.4858 | 1953.4299 | -0.014814
125 |  | 0.23506 | 14.7884 | 4187 | 0.015026 | 7.9848 | 7.9998 | -0.98489 | 66.5524 | 1968.2183 | -0.014799
126 |  | 0.23506 | 14.7736 | 4187 | 0.015011 | 7.9998 | 8.0148 | -0.98489 | 66.6191 | 1982.9919 | -0.014784
127 |  | 0.23506 | 14.7588 | 4187 | 0.014996 | 8.0148 | 8.0298 | -0.98489 | 66.6858 | 1997.7507 | -0.014769
128 |  | 0.23506 | 14.7441 | 4187 | 0.014981 | 8.0298 | 8.0448 | -0.98489 | 66.7526 | 2012.4948 | -0.014754
129 |  | 0.23506 | 14.7293 | 4187 | 0.014966 | 8.0448 | 8.0598 | -0.98489 | 66.8195 | 2027.2241 | -0.01474
130 |  | 0.23506 | 14.7146 | 4187 | 0.014951 | 8.0598 | 8.0747 | -0.98489 | 66.8864 | 2041.9386 | -0.014725
131 |  | 0.23506 | 14.6998 | 4187 | 0.014936 | 8.0747 | 8.0896 | -0.98489 | 66.9534 | 2056.6385 | -0.01471
132 |  | 0.23506 | 14.6851 | 4187 | 0.014921 | 8.0896 | 8.1046 | -0.98489 | 67.0205 | 2071.3236 | -0.014695
133 |  | 0.23506 | 14.6704 | 4187 | 0.014906 | 8.1046 | 8.1195 | -0.98489 | 67.0876 | 2085.994 | -0.014681
134 |  | 0.23506 | 14.6557 | 4187 | 0.014891 | 8.1195 | 8.1344 | -0.98489 | 67.1548 | 2100.6498 | -0.014666
135 |  | 0.23506 | 14.6411 | 4187 | 0.014876 | 8.1344 | 8.1492 | -0.98489 | 67.2221 | 2115.2908 | -0.014651
136 |  | 0.23506 | 14.6264 | 4187 | 0.014861 | 8.1492 | 8.1641 | -0.98489 | 67.2894 | 2129.9173 | -0.014637
137 |  | 0.23506 | 14.6118 | 4187 | 0.014846 | 8.1641 | 8.1789 | -0.98489 | 67.3568 | 2144.5291 | -0.014622
138 |  | 0.23506 | 14.5972 | 4187 | 0.014831 | 8.1789 | 8.1938 | -0.98489 | 67.4243 | 2159.1262 | -0.014607
139 |  | 0.23506 | 14.5826 | 4187 | 0.014817 | 8.1938 | 8.2086 | -0.98489 | 67.4918 | 2173.7088 | -0.014593
140 |  | 0.23506 | 14.568 | 4187 | 0.014802 | 8.2086 | 8.2234 | -0.98489 | 67.5594 | 2188.2768 | -0.014578
141 |  | 0.23506 | 14.5534 | 4187 | 0.014787 | 8.2234 | 8.2382 | -0.98489 | 67.6271 | 2202.8301 | -0.014564
142 |  | 0.23506 | 14.5388 | 4187 | 0.014772 | 8.2382 | 8.253 | -0.98489 | 67.6949 | 2217.369 | -0.014549
143 |  | 0.23506 | 14.5243 | 4187 | 0.014757 | 8.253 | 8.2677 | -0.98489 | 67.7627 | 2231.8932 | -0.014534
144 |  | 0.23506 | 14.5097 | 4187 | 0.014743 | 8.2677 | 8.2825 | -0.98489 | 67.8305 | 2246.403 | -0.01452
145 |  | 0.23506 | 14.4952 | 4187 | 0.014728 | 8.2825 | 8.2972 | -0.98489 | 67.8985 | 2260.8982 | -0.014505
146 |  | 0.23506 | 14.4807 | 4187 | 0.014713 | 8.2972 | 8.3119 | -0.98489 | 67.9665 | 2275.3789 | -0.014491
147 |  | 0.23506 | 14.4662 | 4187 | 0.014698 | 8.3119 | 8.3266 | -0.98489 | 68.0346 | 2289.8452 | -0.014476
148 |  | 0.23506 | 14.4518 | 4187 | 0.014684 | 8.3266 | 8.3413 | -0.98489 | 68.1027 | 2304.2969 | -0.014462
149 |  | 0.23506 | 14.4373 | 4187 | 0.014669 | 8.3413 | 8.3559 | -0.98489 | 68.171 | 2318.7342 | -0.014447
150 |  | 0.23506 | 14.4228 | 4187 | 0.014654 | 8.3559 | 8.3706 | -0.98489 | 68.2392 | 2333.157 | -0.014433
151 |  | 0.23506 | 14.4084 | 4187 | 0.01464 | 8.3706 | 8.3852 | -0.98489 | 68.3076 | 2347.5654 | -0.014419
152 |  | 0.23506 | 14.394 | 4187 | 0.014625 | 8.3852 | 8.3999 | -0.98489 | 68.376 | 2361.9594 | -0.014404
153 |  | 0.23506 | 14.3796 | 4187 | 0.01461 | 8.3999 | 8.4145 | -0.98489 | 68.4445 | 2376.339 | -0.01439
154 |  | 0.23506 | 14.3652 | 4187 | 0.014596 | 8.4145 | 8.4291 | -0.98489 | 68.5131 | 2390.7042 | -0.014375
155 |  | 0.23506 | 14.3508 | 4187 | 0.014581 | 8.4291 | 8.4437 | -0.98489 | 68.5817 | 2405.055 | -0.014361
156 |  | 0.23506 | 14.3365 | 4187 | 0.014567 | 8.4437 | 8.4582 | -0.98489 | 68.6504 | 2419.3915 | -0.014347
157 |  | 0.23506 | 14.3221 | 4187 | 0.014552 | 8.4582 | 8.4728 | -0.98489 | 68.7192 | 2433.7136 | -0.014332
158 |  | 0.23506 | 14.3078 | 4187 | 0.014537 | 8.4728 | 8.4873 | -0.98489 | 68.788 | 2448.0214 | -0.014318
159 |  | 0.23506 | 14.2935 | 4187 | 0.014523 | 8.4873 | 8.5018 | -0.98489 | 68.8569 | 2462.3149 | -0.014303
160 |  | 0.23506 | 14.2792 | 4187 | 0.014508 | 8.5018 | 8.5163 | -0.98489 | 68.9259 | 2476.594 | -0.014289
161 |  | 0.23506 | 14.2649 | 4187 | 0.014494 | 8.5163 | 8.5308 | -0.98489 | 68.9949 | 2490.8589 | -0.014275
162 |  | 0.23506 | 14.2506 | 4187 | 0.014479 | 8.5308 | 8.5453 | -0.98489 | 69.064 | 2505.1095 | -0.014261
163 |  | 0.23506 | 14.2363 | 4187 | 0.014465 | 8.5453 | 8.5598 | -0.98489 | 69.1332 | 2519.3458 | -0.014246
164 |  | 0.23506 | 14.2221 | 4187 | 0.01445 | 8.5598 | 8.5742 | -0.98489 | 69.2025 | 2533.5679 | -0.014232
165 |  | 0.23506 | 14.2079 | 4187 | 0.014436 | 8.5742 | 8.5887 | -0.98489 | 69.2718 | 2547.7758 | -0.014218
166 |  | 0.23506 | 14.1936 | 4187 | 0.014421 | 8.5887 | 8.6031 | -0.98489 | 69.3412 | 2561.9694 | -0.014204
167 |  | 0.23506 | 14.1794 | 4187 | 0.014407 | 8.6031 | 8.6175 | -0.98489 | 69.4106 | 2576.1488 | -0.014189
168 |  | 0.23506 | 14.1652 | 4187 | 0.014393 | 8.6175 | 8.6319 | -0.98489 | 69.4802 | 2590.3141 | -0.014175
169 |  | 0.23506 | 14.1511 | 4187 | 0.014378 | 8.6319 | 8.6463 | -0.98489 | 69.5498 | 2604.4652 | -0.014161
170 |  | 0.23506 | 14.1369 | 4187 | 0.014364 | 8.6463 | 8.6606 | -0.98489 | 69.6194 | 2618.6021 | -0.014147
171 |  | 0.23506 | 14.1228 | 4187 | 0.014349 | 8.6606 | 8.675 | -0.98489 | 69.6892 | 2632.7248 | -0.014133
172 |  | 0.23506 | 14.1086 | 4187 | 0.014335 | 8.675 | 8.6893 | -0.98489 | 69.759 | 2646.8335 | -0.014119
173 |  | 0.23506 | 14.0945 | 4187 | 0.014321 | 8.6893 | 8.7036 | -0.98489 | 69.8289 | 2660.928 | -0.014104
174 |  | 0.23506 | 14.0804 | 4187 | 0.014306 | 8.7036 | 8.7179 | -0.98489 | 69.8988 | 2675.0084 | -0.01409
175 |  | 0.23506 | 14.0663 | 4187 | 0.014292 | 8.7179 | 8.7322 | -0.98489 | 69.9688 | 2689.0747 | -0.014076
176 |  | 0.23506 | 14.0522 | 4187 | 0.014278 | 8.7322 | 8.7465 | -0.98489 | 70.0389 | 2703.1269 | -0.014062
177 |  | 0.23506 | 14.0382 | 4187 | 0.014263 | 8.7465 | 8.7608 | -0.98489 | 70.1091 | 2717.1651 | -0.014048
178 |  | 0.23506 | 14.0241 | 4187 | 0.014249 | 8.7608 | 8.775 | -0.98489 | 70.1793 | 2731.1893 | -0.014034
179 |  | 0.23506 | 14.0101 | 4187 | 0.014235 | 8.775 | 8.7893 | -0.98489 | 70.2496 | 2745.1994 | -0.01402
180 |  | 0.23506 | 13.9961 | 4187 | 0.014221 | 8.7893 | 8.8035 | -0.98489 | 70.32 | 2759.1954 | -0.014006
181 |  | 0.23506 | 13.9821 | 4187 | 0.014206 | 8.8035 | 8.8177 | -0.98489 | 70.3904 | 2773.1775 | -0.013992
182 |  | 0.23506 | 13.9681 | 4187 | 0.014192 | 8.8177 | 8.8319 | -0.98489 | 70.4609 | 2787.1456 | -0.013978
183 |  | 0.23506 | 13.9541 | 4187 | 0.014178 | 8.8319 | 8.8461 | -0.98489 | 70.5315 | 2801.0997 | -0.013964
184 |  | 0.23506 | 13.9401 | 4187 | 0.014164 | 8.8461 | 8.8602 | -0.98489 | 70.6022 | 2815.0398 | -0.01395
185 |  | 0.23506 | 13.9262 | 4187 | 0.01415 | 8.8602 | 8.8744 | -0.98489 | 70.6729 | 2828.966 | -0.013936
186 |  | 0.23506 | 13.9123 | 4187 | 0.014136 | 8.8744 | 8.8885 | -0.98489 | 70.7437 | 2842.8783 | -0.013922
187 |  | 0.23506 | 13.8983 | 4187 | 0.014121 | 8.8885 | 8.9026 | -0.98489 | 70.8145 | 2856.7766 | -0.013908
188 |  | 0.23506 | 13.8844 | 4187 | 0.014107 | 8.9026 | 8.9167 | -0.98489 | 70.8855 | 2870.661 | -0.013894
189 |  | 0.23506 | 13.8705 | 4187 | 0.014093 | 8.9167 | 8.9308 | -0.98489 | 70.9565 | 2884.5315 | -0.01388
190 |  | 0.23506 | 13.8566 | 4187 | 0.014079 | 8.9308 | 8.9449 | -0.98489 | 71.0276 | 2898.3882 | -0.013866
191 |  | 0.23506 | 13.8428 | 4187 | 0.014065 | 8.9449 | 8.959 | -0.98489 | 71.0987 | 2912.231 | -0.013852
192 |  | 0.23506 | 13.8289 | 4187 | 0.014051 | 8.959 | 8.973 | -0.98489 | 71.1699 | 2926.0599 | -0.013839
193 |  | 0.23506 | 13.8151 | 4187 | 0.014037 | 8.973 | 8.9871 | -0.98489 | 71.2412 | 2939.875 | -0.013825
194 |  | 0.23506 | 13.8013 | 4187 | 0.014023 | 8.9871 | 9.0011 | -0.98489 | 71.3126 | 2953.6762 | -0.013811
195 |  | 0.23506 | 13.7875 | 4187 | 0.014009 | 9.0011 | 9.0151 | -0.98489 | 71.384 | 2967.4637 | -0.013797
196 |  | 0.23506 | 13.7737 | 4187 | 0.013995 | 9.0151 | 9.0291 | -0.98489 | 71.4555 | 2981.2374 | -0.013783
197 |  | 0.23506 | 13.7599 | 4187 | 0.013981 | 9.0291 | 9.0431 | -0.98489 | 71.5271 | 2994.9972 | -0.01377
198 |  | 0.23506 | 13.7461 | 4187 | 0.013967 | 9.0431 | 9.057 | -0.98489 | 71.5987 | 3008.7433 | -0.013756
199 |  | 0.23506 | 13.7323 | 4187 | 0.013953 | 9.057 | 9.071 | -0.98489 | 71.6705 | 3022.4757 | -0.013742
200 |  | 0.23506 | 13.7186 | 4187 | 0.013939 | 9.071 | 9.0849 | -0.98489 | 71.7423 | 3036.1943 | -0.013728
201 |  | 0.23506 | 13.7049 | 4187 | 0.013925 | 9.0849 | 9.0988 | -0.98489 | 71.8141 | 3049.8992 | -0.013714
202 |  | 0.23506 | 13.6912 | 4187 | 0.013911 | 9.0988 | 9.1128 | -0.98489 | 71.8861 | 3063.5903 | -0.013701
203 |  | 0.23506 | 13.6775 | 4187 | 0.013897 | 9.1128 | 9.1267 | -0.98489 | 71.9581 | 3077.2678 | -0.013687
204 |  | 0.23506 | 13.6638 | 4187 | 0.013883 | 9.1267 | 9.1405 | -0.98489 | 72.0302 | 3090.9316 | -0.013673
205 |  | 0.23506 | 13.6501 | 4187 | 0.013869 | 9.1405 | 9.1544 | -0.98489 | 72.1023 | 3104.5817 | -0.01366
206 |  | 0.23506 | 13.6364 | 4187 | 0.013855 | 9.1544 | 9.1683 | -0.98489 | 72.1745 | 3118.2181 | -0.013646
207 |  | 0.23506 | 13.6228 | 4187 | 0.013841 | 9.1683 | 9.1821 | -0.98489 | 72.2468 | 3131.8409 | -0.013632
208 |  | 0.23506 | 13.6092 | 4187 | 0.013828 | 9.1821 | 9.1959 | -0.98489 | 72.3192 | 3145.4501 | -0.013619
209 |  | 0.23506 | 13.5955 | 4187 | 0.013814 | 9.1959 | 9.2097 | -0.98489 | 72.3916 | 3159.0456 | -0.013605
210 |  | 0.23506 | 13.5819 | 4187 | 0.0138 | 9.2097 | 9.2235 | -0.98489 | 72.4642 | 3172.6276 | -0.013591
211 |  | 0.23506 | 13.5683 | 4187 | 0.013786 | 9.2235 | 9.2373 | -0.98489 | 72.5367 | 3186.1959 | -0.013578
212 |  | 0.23506 | 13.5548 | 4187 | 0.013772 | 9.2373 | 9.2511 | -0.98489 | 72.6094 | 3199.7507 | -0.013564
213 |  | 0.23506 | 13.5412 | 4187 | 0.013759 | 9.2511 | 9.2649 | -0.98489 | 72.6821 | 3213.2919 | -0.013551
214 |  | 0.23506 | 13.5277 | 4187 | 0.013745 | 9.2649 | 9.2786 | -0.98489 | 72.7549 | 3226.8195 | -0.013537
215 |  | 0.23506 | 13.5141 | 4187 | 0.013731 | 9.2786 | 9.2923 | -0.98489 | 72.8278 | 3240.3337 | -0.013524
216 |  | 0.23506 | 13.5006 | 4187 | 0.013717 | 9.2923 | 9.3061 | -0.98489 | 72.9008 | 3253.8343 | -0.01351
217 |  | 0.23506 | 13.4871 | 4187 | 0.013704 | 9.3061 | 9.3198 | -0.98489 | 72.9738 | 3267.3213 | -0.013497
218 |  | 0.23506 | 13.4736 | 4187 | 0.01369 | 9.3198 | 9.3335 | -0.98489 | 73.0469 | 3280.7949 | -0.013483
219 |  | 0.23506 | 13.4601 | 4187 | 0.013676 | 9.3335 | 9.3471 | -0.98489 | 73.1201 | 3294.255 | -0.01347
220 |  | 0.23506 | 13.4466 | 4187 | 0.013662 | 9.3471 | 9.3608 | -0.98489 | 73.1933 | 3307.7017 | -0.013456
221 |  | 0.23506 | 13.4332 | 4187 | 0.013649 | 9.3608 | 9.3744 | -0.98489 | 73.2666 | 3321.1349 | -0.013443
222 |  | 0.23506 | 13.4197 | 4187 | 0.013635 | 9.3744 | 9.3881 | -0.98489 | 73.34 | 3334.5546 | -0.013429
223 |  | 0.23506 | 13.4063 | 4187 | 0.013621 | 9.3881 | 9.4017 | -0.98489 | 73.4135 | 3347.9609 | -0.013416
224 |  | 0.23506 | 13.3929 | 4187 | 0.013608 | 9.4017 | 9.4153 | -0.98489 | 73.487 | 3361.3538 | -0.013402
225 |  | 0.23506 | 13.3795 | 4187 | 0.013594 | 9.4153 | 9.4289 | -0.98489 | 73.5606 | 3374.7333 | -0.013389
226 |  | 0.23506 | 13.3661 | 4187 | 0.013581 | 9.4289 | 9.4425 | -0.98489 | 73.6343 | 3388.0994 | -0.013375
227 |  | 0.23506 | 13.3527 | 4187 | 0.013567 | 9.4425 | 9.456 | -0.98489 | 73.7081 | 3401.4521 | -0.013362
228 |  | 0.23506 | 13.3394 | 4187 | 0.013553 | 9.456 | 9.4696 | -0.98489 | 73.7819 | 3414.7915 | -0.013349
229 |  | 0.23506 | 13.326 | 4187 | 0.01354 | 9.4696 | 9.4831 | -0.98489 | 73.8558 | 3428.1175 | -0.013335
230 |  | 0.23506 | 13.3127 | 4187 | 0.013526 | 9.4831 | 9.4967 | -0.98489 | 73.9298 | 3441.4302 | -0.013322
231 |  | 0.23506 | 13.2994 | 4187 | 0.013513 | 9.4967 | 9.5102 | -0.98489 | 74.0039 | 3454.7295 | -0.013309
232 |  | 0.23506 | 13.286 | 4187 | 0.013499 | 9.5102 | 9.5237 | -0.98489 | 74.078 | 3468.0156 | -0.013295
233 |  | 0.23506 | 13.2728 | 4187 | 0.013486 | 9.5237 | 9.5372 | -0.98489 | 74.1522 | 3481.2883 | -0.013282
234 |  | 0.23506 | 13.2595 | 4187 | 0.013472 | 9.5372 | 9.5506 | -0.98489 | 74.2265 | 3494.5478 | -0.013269
235 |  | 0.23506 | 13.2462 | 4187 | 0.013459 | 9.5506 | 9.5641 | -0.98489 | 74.3008 | 3507.794 | -0.013255
236 |  | 0.23506 | 13.2329 | 4187 | 0.013445 | 9.5641 | 9.5775 | -0.98489 | 74.3753 | 3521.027 | -0.013242

## St26
|  |  | buis | verlies W/M | L /°C/sec
diam | wandikte |  | inhoud l/m |  | W/M
26.9 | 2.3 | 3.1416 | 0.39057 | 21.151 | 4187
[8 empty] | J/sec/mtr | aantal mtr. | verlies
|  | buis | verlies W/M | L /°C/sec | verlies temp | begintemp | eindtemp | verlies | bij 1°C | totaal J/sec
|  | inhoud L |  | W/M | °C per M | °C | °C | per m°C | daling | aantal mtr
1 | 26.9 | 0.39057 | 21.151 | 4187 | 0.012934 | 6 | 6.0129 | -1.2442 | 77.3163 | 21.151 | -0.016092
2 |  | 0.39057 | 21.1349 | 4187 | 0.012924 | 6.0129 | 6.0259 | -1.2442 | 77.3752 | 42.2859 | -0.01608
3 |  | 0.39057 | 21.1188 | 4187 | 0.012914 | 6.0259 | 6.0388 | -1.2442 | 77.4341 | 63.4048 | -0.016068
4 |  | 0.39057 | 21.1028 | 4187 | 0.012904 | 6.0388 | 6.0517 | -1.2442 | 77.4931 | 84.5076 | -0.016055
5 |  | 0.39057 | 21.0867 | 4187 | 0.012895 | 6.0517 | 6.0646 | -1.2442 | 77.5521 | 105.5943 | -0.016043
6 |  | 0.39057 | 21.0707 | 4187 | 0.012885 | 6.0646 | 6.0775 | -1.2442 | 77.6111 | 126.665 | -0.016031
7 |  | 0.39057 | 21.0547 | 4187 | 0.012875 | 6.0775 | 6.0903 | -1.2442 | 77.6702 | 147.7196 | -0.016019
8 |  | 0.39057 | 21.0386 | 4187 | 0.012865 | 6.0903 | 6.1032 | -1.2442 | 77.7294 | 168.7583 | -0.016007
9 |  | 0.39057 | 21.0226 | 4187 | 0.012855 | 6.1032 | 6.1161 | -1.2442 | 77.7885 | 189.7809 | -0.015994
10 |  | 0.39057 | 21.0066 | 4187 | 0.012846 | 6.1161 | 6.1289 | -1.2442 | 77.8478 | 210.7875 | -0.015982
11 |  | 0.39057 | 20.9907 | 4187 | 0.012836 | 6.1289 | 6.1417 | -1.2442 | 77.907 | 231.7782 | -0.01597
12 |  | 0.39057 | 20.9747 | 4187 | 0.012826 | 6.1417 | 6.1546 | -1.2442 | 77.9664 | 252.7529 | -0.015958
13 |  | 0.39057 | 20.9587 | 4187 | 0.012816 | 6.1546 | 6.1674 | -1.2442 | 78.0257 | 273.7116 | -0.015946
14 |  | 0.39057 | 20.9428 | 4187 | 0.012807 | 6.1674 | 6.1802 | -1.2442 | 78.0851 | 294.6544 | -0.015934
15 |  | 0.39057 | 20.9268 | 4187 | 0.012797 | 6.1802 | 6.193 | -1.2442 | 78.1446 | 315.5812 | -0.015921
16 |  | 0.39057 | 20.9109 | 4187 | 0.012787 | 6.193 | 6.2058 | -1.2442 | 78.2041 | 336.4921 | -0.015909
17 |  | 0.39057 | 20.895 | 4187 | 0.012777 | 6.2058 | 6.2185 | -1.2442 | 78.2636 | 357.3871 | -0.015897
18 |  | 0.39057 | 20.8791 | 4187 | 0.012768 | 6.2185 | 6.2313 | -1.2442 | 78.3232 | 378.2663 | -0.015885
19 |  | 0.39057 | 20.8632 | 4187 | 0.012758 | 6.2313 | 6.2441 | -1.2442 | 78.3828 | 399.1295 | -0.015873
20 |  | 0.39057 | 20.8474 | 4187 | 0.012748 | 6.2441 | 6.2568 | -1.2442 | 78.4425 | 419.9768 | -0.015861
21 |  | 0.39057 | 20.8315 | 4187 | 0.012738 | 6.2568 | 6.2696 | -1.2442 | 78.5023 | 440.8083 | -0.015849
22 |  | 0.39057 | 20.8156 | 4187 | 0.012729 | 6.2696 | 6.2823 | -1.2442 | 78.562 | 461.624 | -0.015837
23 |  | 0.39057 | 20.7998 | 4187 | 0.012719 | 6.2823 | 6.295 | -1.2442 | 78.6218 | 482.4238 | -0.015825
24 |  | 0.39057 | 20.784 | 4187 | 0.012709 | 6.295 | 6.3077 | -1.2442 | 78.6817 | 503.2078 | -0.015813
25 |  | 0.39057 | 20.7682 | 4187 | 0.0127 | 6.3077 | 6.3204 | -1.2442 | 78.7416 | 523.976 | -0.015801
26 |  | 0.39057 | 20.7524 | 4187 | 0.01269 | 6.3204 | 6.3331 | -1.2442 | 78.8016 | 544.7283 | -0.015789
27 |  | 0.39057 | 20.7366 | 4187 | 0.01268 | 6.3331 | 6.3458 | -1.2442 | 78.8616 | 565.4649 | -0.015777
28 |  | 0.39057 | 20.7208 | 4187 | 0.012671 | 6.3458 | 6.3585 | -1.2442 | 78.9216 | 586.1857 | -0.015765
29 |  | 0.39057 | 20.705 | 4187 | 0.012661 | 6.3585 | 6.3711 | -1.2442 | 78.9817 | 606.8908 | -0.015753
30 |  | 0.39057 | 20.6893 | 4187 | 0.012652 | 6.3711 | 6.3838 | -1.2442 | 79.0418 | 627.58 | -0.015741
31 |  | 0.39057 | 20.6735 | 4187 | 0.012642 | 6.3838 | 6.3964 | -1.2442 | 79.102 | 648.2536 | -0.015729
32 |  | 0.39057 | 20.6578 | 4187 | 0.012632 | 6.3964 | 6.409 | -1.2442 | 79.1622 | 668.9114 | -0.015717
33 |  | 0.39057 | 20.6421 | 4187 | 0.012623 | 6.409 | 6.4217 | -1.2442 | 79.2225 | 689.5535 | -0.015705
34 |  | 0.39057 | 20.6264 | 4187 | 0.012613 | 6.4217 | 6.4343 | -1.2442 | 79.2828 | 710.1799 | -0.015693
35 |  | 0.39057 | 20.6107 | 4187 | 0.012603 | 6.4343 | 6.4469 | -1.2442 | 79.3432 | 730.7906 | -0.015681
36 |  | 0.39057 | 20.595 | 4187 | 0.012594 | 6.4469 | 6.4595 | -1.2442 | 79.4036 | 751.3856 | -0.015669
37 |  | 0.39057 | 20.5794 | 4187 | 0.012584 | 6.4595 | 6.4721 | -1.2442 | 79.4641 | 771.965 | -0.015657
38 |  | 0.39057 | 20.5637 | 4187 | 0.012575 | 6.4721 | 6.4846 | -1.2442 | 79.5246 | 792.5287 | -0.015645
39 |  | 0.39057 | 20.5481 | 4187 | 0.012565 | 6.4846 | 6.4972 | -1.2442 | 79.5851 | 813.0767 | -0.015633
40 |  | 0.39057 | 20.5324 | 4187 | 0.012556 | 6.4972 | 6.5098 | -1.2442 | 79.6457 | 833.6092 | -0.015621
41 |  | 0.39057 | 20.5168 | 4187 | 0.012546 | 6.5098 | 6.5223 | -1.2442 | 79.7064 | 854.126 | -0.01561
42 |  | 0.39057 | 20.5012 | 4187 | 0.012537 | 6.5223 | 6.5348 | -1.2442 | 79.7671 | 874.6271 | -0.015598
43 |  | 0.39057 | 20.4856 | 4187 | 0.012527 | 6.5348 | 6.5474 | -1.2442 | 79.8278 | 895.1127 | -0.015586
44 |  | 0.39057 | 20.47 | 4187 | 0.012517 | 6.5474 | 6.5599 | -1.2442 | 79.8886 | 915.5827 | -0.015574
45 |  | 0.39057 | 20.4544 | 4187 | 0.012508 | 6.5599 | 6.5724 | -1.2442 | 79.9494 | 936.0372 | -0.015562
46 |  | 0.39057 | 20.4389 | 4187 | 0.012498 | 6.5724 | 6.5849 | -1.2442 | 80.0103 | 956.476 | -0.01555
47 |  | 0.39057 | 20.4233 | 4187 | 0.012489 | 6.5849 | 6.5974 | -1.2442 | 80.0712 | 976.8994 | -0.015538
48 |  | 0.39057 | 20.4078 | 4187 | 0.012479 | 6.5974 | 6.6099 | -1.2442 | 80.1322 | 997.3071 | -0.015527
49 |  | 0.39057 | 20.3923 | 4187 | 0.01247 | 6.6099 | 6.6223 | -1.2442 | 80.1932 | 1017.6994 | -0.015515
50 |  | 0.39057 | 20.3767 | 4187 | 0.01246 | 6.6223 | 6.6348 | -1.2442 | 80.2542 | 1038.0761 | -0.015503
51 |  | 0.39057 | 20.3612 | 4187 | 0.012451 | 6.6348 | 6.6472 | -1.2442 | 80.3153 | 1058.4374 | -0.015491
52 |  | 0.39057 | 20.3457 | 4187 | 0.012441 | 6.6472 | 6.6597 | -1.2442 | 80.3765 | 1078.7831 | -0.015479
53 |  | 0.39057 | 20.3303 | 4187 | 0.012432 | 6.6597 | 6.6721 | -1.2442 | 80.4377 | 1099.1134 | -0.015468
54 |  | 0.39057 | 20.3148 | 4187 | 0.012423 | 6.6721 | 6.6845 | -1.2442 | 80.4989 | 1119.4282 | -0.015456
55 |  | 0.39057 | 20.2993 | 4187 | 0.012413 | 6.6845 | 6.6969 | -1.2442 | 80.5602 | 1139.7275 | -0.015444
56 |  | 0.39057 | 20.2839 | 4187 | 0.012404 | 6.6969 | 6.7093 | -1.2442 | 80.6216 | 1160.0114 | -0.015432
57 |  | 0.39057 | 20.2685 | 4187 | 0.012394 | 6.7093 | 6.7217 | -1.2442 | 80.6829 | 1180.2799 | -0.015421
58 |  | 0.39057 | 20.253 | 4187 | 0.012385 | 6.7217 | 6.7341 | -1.2442 | 80.7444 | 1200.5329 | -0.015409
59 |  | 0.39057 | 20.2376 | 4187 | 0.012375 | 6.7341 | 6.7465 | -1.2442 | 80.8058 | 1220.7706 | -0.015397
60 |  | 0.39057 | 20.2222 | 4187 | 0.012366 | 6.7465 | 6.7589 | -1.2442 | 80.8674 | 1240.9928 | -0.015385
61 |  | 0.39057 | 20.2069 | 4187 | 0.012357 | 6.7589 | 6.7712 | -1.2442 | 80.9289 | 1261.1997 | -0.015374
62 |  | 0.39057 | 20.1915 | 4187 | 0.012347 | 6.7712 | 6.7836 | -1.2442 | 80.9906 | 1281.3911 | -0.015362
63 |  | 0.39057 | 20.1761 | 4187 | 0.012338 | 6.7836 | 6.7959 | -1.2442 | 81.0522 | 1301.5672 | -0.01535
64 |  | 0.39057 | 20.1608 | 4187 | 0.012328 | 6.7959 | 6.8082 | -1.2442 | 81.1139 | 1321.728 | -0.015339
65 |  | 0.39057 | 20.1454 | 4187 | 0.012319 | 6.8082 | 6.8206 | -1.2442 | 81.1757 | 1341.8734 | -0.015327
66 |  | 0.39057 | 20.1301 | 4187 | 0.01231 | 6.8206 | 6.8329 | -1.2442 | 81.2375 | 1362.0035 | -0.015315
67 |  | 0.39057 | 20.1148 | 4187 | 0.0123 | 6.8329 | 6.8452 | -1.2442 | 81.2994 | 1382.1183 | -0.015304
68 |  | 0.39057 | 20.0995 | 4187 | 0.012291 | 6.8452 | 6.8575 | -1.2442 | 81.3613 | 1402.2178 | -0.015292
69 |  | 0.39057 | 20.0842 | 4187 | 0.012282 | 6.8575 | 6.8697 | -1.2442 | 81.4232 | 1422.302 | -0.01528
70 |  | 0.39057 | 20.0689 | 4187 | 0.012272 | 6.8697 | 6.882 | -1.2442 | 81.4852 | 1442.3709 | -0.015269
71 |  | 0.39057 | 20.0536 | 4187 | 0.012263 | 6.882 | 6.8943 | -1.2442 | 81.5472 | 1462.4246 | -0.015257
72 |  | 0.39057 | 20.0384 | 4187 | 0.012253 | 6.8943 | 6.9065 | -1.2442 | 81.6093 | 1482.4629 | -0.015246
73 |  | 0.39057 | 20.0231 | 4187 | 0.012244 | 6.9065 | 6.9188 | -1.2442 | 81.6715 | 1502.4861 | -0.015234
74 |  | 0.39057 | 20.0079 | 4187 | 0.012235 | 6.9188 | 6.931 | -1.2442 | 81.7337 | 1522.494 | -0.015222
75 |  | 0.39057 | 19.9927 | 4187 | 0.012226 | 6.931 | 6.9432 | -1.2442 | 81.7959 | 1542.4867 | -0.015211
76 |  | 0.39057 | 19.9775 | 4187 | 0.012216 | 6.9432 | 6.9554 | -1.2442 | 81.8582 | 1562.4641 | -0.015199
77 |  | 0.39057 | 19.9623 | 4187 | 0.012207 | 6.9554 | 6.9677 | -1.2442 | 81.9205 | 1582.4264 | -0.015188
78 |  | 0.39057 | 19.9471 | 4187 | 0.012198 | 6.9677 | 6.9799 | -1.2442 | 81.9829 | 1602.3735 | -0.015176
79 |  | 0.39057 | 19.9319 | 4187 | 0.012188 | 6.9799 | 6.992 | -1.2442 | 82.0453 | 1622.3054 | -0.015165
80 |  | 0.39057 | 19.9167 | 4187 | 0.012179 | 6.992 | 7.0042 | -1.2442 | 82.1078 | 1642.2222 | -0.015153
81 |  | 0.39057 | 19.9016 | 4187 | 0.01217 | 7.0042 | 7.0164 | -1.2442 | 82.1703 | 1662.1237 | -0.015141
82 |  | 0.39057 | 19.8865 | 4187 | 0.012161 | 7.0164 | 7.0286 | -1.2442 | 82.2328 | 1682.0102 | -0.01513
83 |  | 0.39057 | 19.8713 | 4187 | 0.012151 | 7.0286 | 7.0407 | -1.2442 | 82.2955 | 1701.8815 | -0.015118
84 |  | 0.39057 | 19.8562 | 4187 | 0.012142 | 7.0407 | 7.0528 | -1.2442 | 82.3581 | 1721.7377 | -0.015107
85 |  | 0.39057 | 19.8411 | 4187 | 0.012133 | 7.0528 | 7.065 | -1.2442 | 82.4208 | 1741.5788 | -0.015095
86 |  | 0.39057 | 19.826 | 4187 | 0.012124 | 7.065 | 7.0771 | -1.2442 | 82.4836 | 1761.4048 | -0.015084
87 |  | 0.39057 | 19.8109 | 4187 | 0.012114 | 7.0771 | 7.0892 | -1.2442 | 82.5464 | 1781.2157 | -0.015072
88 |  | 0.39057 | 19.7958 | 4187 | 0.012105 | 7.0892 | 7.1013 | -1.2442 | 82.6092 | 1801.0116 | -0.015061
89 |  | 0.39057 | 19.7808 | 4187 | 0.012096 | 7.1013 | 7.1134 | -1.2442 | 82.6721 | 1820.7923 | -0.01505
90 |  | 0.39057 | 19.7657 | 4187 | 0.012087 | 7.1134 | 7.1255 | -1.2442 | 82.7351 | 1840.5581 | -0.015038
91 |  | 0.39057 | 19.7507 | 4187 | 0.012078 | 7.1255 | 7.1376 | -1.2442 | 82.7981 | 1860.3088 | -0.015027
92 |  | 0.39057 | 19.7357 | 4187 | 0.012068 | 7.1376 | 7.1496 | -1.2442 | 82.8611 | 1880.0444 | -0.015015
93 |  | 0.39057 | 19.7207 | 4187 | 0.012059 | 7.1496 | 7.1617 | -1.2442 | 82.9242 | 1899.7651 | -0.015004
94 |  | 0.39057 | 19.7056 | 4187 | 0.01205 | 7.1617 | 7.1738 | -1.2442 | 82.9873 | 1919.4707 | -0.014992
95 |  | 0.39057 | 19.6907 | 4187 | 0.012041 | 7.1738 | 7.1858 | -1.2442 | 83.0505 | 1939.1614 | -0.014981
96 |  | 0.39057 | 19.6757 | 4187 | 0.012032 | 7.1858 | 7.1978 | -1.2442 | 83.1138 | 1958.8371 | -0.01497
97 |  | 0.39057 | 19.6607 | 4187 | 0.012023 | 7.1978 | 7.2099 | -1.2442 | 83.177 | 1978.4978 | -0.014958
98 |  | 0.39057 | 19.6457 | 4187 | 0.012013 | 7.2099 | 7.2219 | -1.2442 | 83.2404 | 1998.1435 | -0.014947
99 |  | 0.39057 | 19.6308 | 4187 | 0.012004 | 7.2219 | 7.2339 | -1.2442 | 83.3038 | 2017.7743 | -0.014935
100 |  | 0.39057 | 19.6159 | 4187 | 0.011995 | 7.2339 | 7.2459 | -1.2442 | 83.3672 | 2037.3902 | -0.014924
101 |  | 0.39057 | 19.6009 | 4187 | 0.011986 | 7.2459 | 7.2579 | -1.2442 | 83.4307 | 2056.9911 | -0.014913
102 |  | 0.39057 | 19.586 | 4187 | 0.011977 | 7.2579 | 7.2698 | -1.2442 | 83.4942 | 2076.5772 | -0.014901
103 |  | 0.39057 | 19.5711 | 4187 | 0.011968 | 7.2698 | 7.2818 | -1.2442 | 83.5577 | 2096.1483 | -0.01489
104 |  | 0.39057 | 19.5562 | 4187 | 0.011959 | 7.2818 | 7.2938 | -1.2442 | 83.6214 | 2115.7045 | -0.014879
105 |  | 0.39057 | 19.5414 | 4187 | 0.01195 | 7.2938 | 7.3057 | -1.2442 | 83.685 | 2135.2459 | -0.014867
106 |  | 0.39057 | 19.5265 | 4187 | 0.01194 | 7.3057 | 7.3176 | -1.2442 | 83.7488 | 2154.7724 | -0.014856
107 |  | 0.39057 | 19.5116 | 4187 | 0.011931 | 7.3176 | 7.3296 | -1.2442 | 83.8125 | 2174.284 | -0.014845
108 |  | 0.39057 | 19.4968 | 4187 | 0.011922 | 7.3296 | 7.3415 | -1.2442 | 83.8763 | 2193.7808 | -0.014833
109 |  | 0.39057 | 19.482 | 4187 | 0.011913 | 7.3415 | 7.3534 | -1.2442 | 83.9402 | 2213.2628 | -0.014822
110 |  | 0.39057 | 19.4671 | 4187 | 0.011904 | 7.3534 | 7.3653 | -1.2442 | 84.0041 | 2232.7299 | -0.014811
111 |  | 0.39057 | 19.4523 | 4187 | 0.011895 | 7.3653 | 7.3772 | -1.2442 | 84.0681 | 2252.1822 | -0.0148
112 |  | 0.39057 | 19.4375 | 4187 | 0.011886 | 7.3772 | 7.3891 | -1.2442 | 84.1321 | 2271.6197 | -0.014788
113 |  | 0.39057 | 19.4227 | 4187 | 0.011877 | 7.3891 | 7.401 | -1.2442 | 84.1961 | 2291.0425 | -0.014777
114 |  | 0.39057 | 19.408 | 4187 | 0.011868 | 7.401 | 7.4128 | -1.2442 | 84.2602 | 2310.4504 | -0.014766
115 |  | 0.39057 | 19.3932 | 4187 | 0.011859 | 7.4128 | 7.4247 | -1.2442 | 84.3244 | 2329.8436 | -0.014755
116 |  | 0.39057 | 19.3784 | 4187 | 0.01185 | 7.4247 | 7.4366 | -1.2442 | 84.3886 | 2349.2221 | -0.014743
117 |  | 0.39057 | 19.3637 | 4187 | 0.011841 | 7.4366 | 7.4484 | -1.2442 | 84.4529 | 2368.5858 | -0.014732
118 |  | 0.39057 | 19.349 | 4187 | 0.011832 | 7.4484 | 7.4602 | -1.2442 | 84.5172 | 2387.9347 | -0.014721
119 |  | 0.39057 | 19.3342 | 4187 | 0.011823 | 7.4602 | 7.472 | -1.2442 | 84.5815 | 2407.269 | -0.01471
120 |  | 0.39057 | 19.3195 | 4187 | 0.011814 | 7.472 | 7.4839 | -1.2442 | 84.6459 | 2426.5885 | -0.014699
121 |  | 0.39057 | 19.3048 | 4187 | 0.011805 | 7.4839 | 7.4957 | -1.2442 | 84.7104 | 2445.8933 | -0.014687
122 |  | 0.39057 | 19.2901 | 4187 | 0.011796 | 7.4957 | 7.5075 | -1.2442 | 84.7749 | 2465.1835 | -0.014676
123 |  | 0.39057 | 19.2755 | 4187 | 0.011787 | 7.5075 | 7.5193 | -1.2442 | 84.8394 | 2484.4589 | -0.014665
124 |  | 0.39057 | 19.2608 | 4187 | 0.011778 | 7.5193 | 7.531 | -1.2442 | 84.904 | 2503.7197 | -0.014654
125 |  | 0.39057 | 19.2462 | 4187 | 0.011769 | 7.531 | 7.5428 | -1.2442 | 84.9686 | 2522.9659 | -0.014643
126 |  | 0.39057 | 19.2315 | 4187 | 0.01176 | 7.5428 | 7.5546 | -1.2442 | 85.0333 | 2542.1974 | -0.014632
127 |  | 0.39057 | 19.2169 | 4187 | 0.011751 | 7.5546 | 7.5663 | -1.2442 | 85.0981 | 2561.4143 | -0.014621
128 |  | 0.39057 | 19.2023 | 4187 | 0.011742 | 7.5663 | 7.5781 | -1.2442 | 85.1629 | 2580.6165 | -0.014609
129 |  | 0.39057 | 19.1876 | 4187 | 0.011733 | 7.5781 | 7.5898 | -1.2442 | 85.2277 | 2599.8042 | -0.014598
130 |  | 0.39057 | 19.173 | 4187 | 0.011724 | 7.5898 | 7.6015 | -1.2442 | 85.2926 | 2618.9772 | -0.014587
131 |  | 0.39057 | 19.1585 | 4187 | 0.011715 | 7.6015 | 7.6132 | -1.2442 | 85.3576 | 2638.1357 | -0.014576
132 |  | 0.39057 | 19.1439 | 4187 | 0.011707 | 7.6132 | 7.6249 | -1.2442 | 85.4225 | 2657.2796 | -0.014565
133 |  | 0.39057 | 19.1293 | 4187 | 0.011698 | 7.6249 | 7.6366 | -1.2442 | 85.4876 | 2676.4089 | -0.014554
134 |  | 0.39057 | 19.1148 | 4187 | 0.011689 | 7.6366 | 7.6483 | -1.2442 | 85.5527 | 2695.5237 | -0.014543
135 |  | 0.39057 | 19.1002 | 4187 | 0.01168 | 7.6483 | 7.66 | -1.2442 | 85.6178 | 2714.6239 | -0.014532
136 |  | 0.39057 | 19.0857 | 4187 | 0.011671 | 7.66 | 7.6717 | -1.2442 | 85.683 | 2733.7096 | -0.014521
137 |  | 0.39057 | 19.0712 | 4187 | 0.011662 | 7.6717 | 7.6833 | -1.2442 | 85.7482 | 2752.7807 | -0.01451
138 |  | 0.39057 | 19.0567 | 4187 | 0.011653 | 7.6833 | 7.695 | -1.2442 | 85.8135 | 2771.8374 | -0.014499
139 |  | 0.39057 | 19.0422 | 4187 | 0.011644 | 7.695 | 7.7066 | -1.2442 | 85.8789 | 2790.8796 | -0.014488
140 |  | 0.39057 | 19.0277 | 4187 | 0.011635 | 7.7066 | 7.7183 | -1.2442 | 85.9443 | 2809.9072 | -0.014477
141 |  | 0.39057 | 19.0132 | 4187 | 0.011627 | 7.7183 | 7.7299 | -1.2442 | 86.0097 | 2828.9204 | -0.014466
142 |  | 0.39057 | 18.9987 | 4187 | 0.011618 | 7.7299 | 7.7415 | -1.2442 | 86.0752 | 2847.9192 | -0.014455
143 |  | 0.39057 | 18.9843 | 4187 | 0.011609 | 7.7415 | 7.7531 | -1.2442 | 86.1407 | 2866.9034 | -0.014444
144 |  | 0.39057 | 18.9698 | 4187 | 0.0116 | 7.7531 | 7.7647 | -1.2442 | 86.2063 | 2885.8733 | -0.014433
145 |  | 0.39057 | 18.9554 | 4187 | 0.011591 | 7.7647 | 7.7763 | -1.2442 | 86.2719 | 2904.8287 | -0.014422
146 |  | 0.39057 | 18.941 | 4187 | 0.011582 | 7.7763 | 7.7879 | -1.2442 | 86.3376 | 2923.7697 | -0.014411
147 |  | 0.39057 | 18.9266 | 4187 | 0.011574 | 7.7879 | 7.7995 | -1.2442 | 86.4034 | 2942.6962 | -0.0144
148 |  | 0.39057 | 18.9122 | 4187 | 0.011565 | 7.7995 | 7.811 | -1.2442 | 86.4692 | 2961.6084 | -0.014389
149 |  | 0.39057 | 18.8978 | 4187 | 0.011556 | 7.811 | 7.8226 | -1.2442 | 86.535 | 2980.5062 | -0.014378
150 |  | 0.39057 | 18.8834 | 4187 | 0.011547 | 7.8226 | 7.8341 | -1.2442 | 86.6009 | 2999.3896 | -0.014367
151 |  | 0.39057 | 18.869 | 4187 | 0.011538 | 7.8341 | 7.8457 | -1.2442 | 86.6668 | 3018.2586 | -0.014356
152 |  | 0.39057 | 18.8547 | 4187 | 0.01153 | 7.8457 | 7.8572 | -1.2442 | 86.7328 | 3037.1133 | -0.014345
153 |  | 0.39057 | 18.8403 | 4187 | 0.011521 | 7.8572 | 7.8687 | -1.2442 | 86.7988 | 3055.9536 | -0.014334
154 |  | 0.39057 | 18.826 | 4187 | 0.011512 | 7.8687 | 7.8802 | -1.2442 | 86.8649 | 3074.7796 | -0.014323
155 |  | 0.39057 | 18.8117 | 4187 | 0.011503 | 7.8802 | 7.8917 | -1.2442 | 86.9311 | 3093.5913 | -0.014312
156 |  | 0.39057 | 18.7974 | 4187 | 0.011495 | 7.8917 | 7.9032 | -1.2442 | 86.9973 | 3112.3887 | -0.014301
157 |  | 0.39057 | 18.7831 | 4187 | 0.011486 | 7.9032 | 7.9147 | -1.2442 | 87.0635 | 3131.1717 | -0.01429
158 |  | 0.39057 | 18.7688 | 4187 | 0.011477 | 7.9147 | 7.9262 | -1.2442 | 87.1298 | 3149.9405 | -0.01428
159 |  | 0.39057 | 18.7545 | 4187 | 0.011468 | 7.9262 | 7.9377 | -1.2442 | 87.1961 | 3168.695 | -0.014269
160 |  | 0.39057 | 18.7402 | 4187 | 0.01146 | 7.9377 | 7.9491 | -1.2442 | 87.2625 | 3187.4352 | -0.014258
161 |  | 0.39057 | 18.726 | 4187 | 0.011451 | 7.9491 | 7.9606 | -1.2442 | 87.329 | 3206.1612 | -0.014247
162 |  | 0.39057 | 18.7117 | 4187 | 0.011442 | 7.9606 | 7.972 | -1.2442 | 87.3955 | 3224.8729 | -0.014236
163 |  | 0.39057 | 18.6975 | 4187 | 0.011434 | 7.972 | 7.9834 | -1.2442 | 87.462 | 3243.5704 | -0.014225
164 |  | 0.39057 | 18.6833 | 4187 | 0.011425 | 7.9834 | 7.9949 | -1.2442 | 87.5286 | 3262.2537 | -0.014215
165 |  | 0.39057 | 18.669 | 4187 | 0.011416 | 7.9949 | 8.0063 | -1.2442 | 87.5952 | 3280.9227 | -0.014204
166 |  | 0.39057 | 18.6548 | 4187 | 0.011407 | 8.0063 | 8.0177 | -1.2442 | 87.6619 | 3299.5776 | -0.014193
167 |  | 0.39057 | 18.6406 | 4187 | 0.011399 | 8.0177 | 8.0291 | -1.2442 | 87.7287 | 3318.2182 | -0.014182
168 |  | 0.39057 | 18.6265 | 4187 | 0.01139 | 8.0291 | 8.0405 | -1.2442 | 87.7955 | 3336.8447 | -0.014171
169 |  | 0.39057 | 18.6123 | 4187 | 0.011381 | 8.0405 | 8.0519 | -1.2442 | 87.8623 | 3355.457 | -0.014161
170 |  | 0.39057 | 18.5981 | 4187 | 0.011373 | 8.0519 | 8.0632 | -1.2442 | 87.9292 | 3374.0551 | -0.01415
171 |  | 0.39057 | 18.584 | 4187 | 0.011364 | 8.0632 | 8.0746 | -1.2442 | 87.9962 | 3392.6391 | -0.014139
172 |  | 0.39057 | 18.5698 | 4187 | 0.011355 | 8.0746 | 8.086 | -1.2442 | 88.0632 | 3411.2089 | -0.014128
173 |  | 0.39057 | 18.5557 | 4187 | 0.011347 | 8.086 | 8.0973 | -1.2442 | 88.1302 | 3429.7646 | -0.014117
174 |  | 0.39057 | 18.5416 | 4187 | 0.011338 | 8.0973 | 8.1086 | -1.2442 | 88.1973 | 3448.3062 | -0.014107
175 |  | 0.39057 | 18.5275 | 4187 | 0.01133 | 8.1086 | 8.12 | -1.2442 | 88.2645 | 3466.8337 | -0.014096
176 |  | 0.39057 | 18.5134 | 4187 | 0.011321 | 8.12 | 8.1313 | -1.2442 | 88.3317 | 3485.3471 | -0.014085
177 |  | 0.39057 | 18.4993 | 4187 | 0.011312 | 8.1313 | 8.1426 | -1.2442 | 88.3989 | 3503.8465 | -0.014075
178 |  | 0.39057 | 18.4852 | 4187 | 0.011304 | 8.1426 | 8.1539 | -1.2442 | 88.4662 | 3522.3317 | -0.014064
179 |  | 0.39057 | 18.4712 | 4187 | 0.011295 | 8.1539 | 8.1652 | -1.2442 | 88.5336 | 3540.8029 | -0.014053
180 |  | 0.39057 | 18.4571 | 4187 | 0.011287 | 8.1652 | 8.1765 | -1.2442 | 88.601 | 3559.26 | -0.014042
181 |  | 0.39057 | 18.4431 | 4187 | 0.011278 | 8.1765 | 8.1878 | -1.2442 | 88.6685 | 3577.7031 | -0.014032
182 |  | 0.39057 | 18.429 | 4187 | 0.011269 | 8.1878 | 8.199 | -1.2442 | 88.736 | 3596.1321 | -0.014021
183 |  | 0.39057 | 18.415 | 4187 | 0.011261 | 8.199 | 8.2103 | -1.2442 | 88.8035 | 3614.5471 | -0.01401
184 |  | 0.39057 | 18.401 | 4187 | 0.011252 | 8.2103 | 8.2216 | -1.2442 | 88.8712 | 3632.9481 | -0.014
185 |  | 0.39057 | 18.387 | 4187 | 0.011244 | 8.2216 | 8.2328 | -1.2442 | 88.9388 | 3651.3352 | -0.013989
186 |  | 0.39057 | 18.373 | 4187 | 0.011235 | 8.2328 | 8.244 | -1.2442 | 89.0065 | 3669.7082 | -0.013978
187 |  | 0.39057 | 18.359 | 4187 | 0.011227 | 8.244 | 8.2553 | -1.2442 | 89.0743 | 3688.0672 | -0.013968
188 |  | 0.39057 | 18.3451 | 4187 | 0.011218 | 8.2553 | 8.2665 | -1.2442 | 89.1421 | 3706.4123 | -0.013957
189 |  | 0.39057 | 18.3311 | 4187 | 0.01121 | 8.2665 | 8.2777 | -1.2442 | 89.21 | 3724.7434 | -0.013947
190 |  | 0.39057 | 18.3172 | 4187 | 0.011201 | 8.2777 | 8.2889 | -1.2442 | 89.2779 | 3743.0606 | -0.013936
191 |  | 0.39057 | 18.3032 | 4187 | 0.011192 | 8.2889 | 8.3001 | -1.2442 | 89.3459 | 3761.3638 | -0.013925
192 |  | 0.39057 | 18.2893 | 4187 | 0.011184 | 8.3001 | 8.3113 | -1.2442 | 89.4139 | 3779.6532 | -0.013915
193 |  | 0.39057 | 18.2754 | 4187 | 0.011175 | 8.3113 | 8.3224 | -1.2442 | 89.482 | 3797.9286 | -0.013904
194 |  | 0.39057 | 18.2615 | 4187 | 0.011167 | 8.3224 | 8.3336 | -1.2442 | 89.5501 | 3816.1901 | -0.013894
195 |  | 0.39057 | 18.2476 | 4187 | 0.011158 | 8.3336 | 8.3448 | -1.2442 | 89.6183 | 3834.4377 | -0.013883
196 |  | 0.39057 | 18.2337 | 4187 | 0.01115 | 8.3448 | 8.3559 | -1.2442 | 89.6866 | 3852.6714 | -0.013873
197 |  | 0.39057 | 18.2198 | 4187 | 0.011141 | 8.3559 | 8.3671 | -1.2442 | 89.7548 | 3870.8912 | -0.013862
198 |  | 0.39057 | 18.206 | 4187 | 0.011133 | 8.3671 | 8.3782 | -1.2442 | 89.8232 | 3889.0972 | -0.013851
199 |  | 0.39057 | 18.1921 | 4187 | 0.011125 | 8.3782 | 8.3893 | -1.2442 | 89.8916 | 3907.2893 | -0.013841
200 |  | 0.39057 | 18.1783 | 4187 | 0.011116 | 8.3893 | 8.4004 | -1.2442 | 89.96 | 3925.4676 | -0.01383
201 |  | 0.39057 | 18.1645 | 4187 | 0.011108 | 8.4004 | 8.4115 | -1.2442 | 90.0285 | 3943.6321 | -0.01382
202 |  | 0.39057 | 18.1506 | 4187 | 0.011099 | 8.4115 | 8.4226 | -1.2442 | 90.0971 | 3961.7827 | -0.013809
203 |  | 0.39057 | 18.1368 | 4187 | 0.011091 | 8.4226 | 8.4337 | -1.2442 | 90.1657 | 3979.9196 | -0.013799
204 |  | 0.39057 | 18.123 | 4187 | 0.011082 | 8.4337 | 8.4448 | -1.2442 | 90.2343 | 3998.0426 | -0.013788
205 |  | 0.39057 | 18.1092 | 4187 | 0.011074 | 8.4448 | 8.4559 | -1.2442 | 90.303 | 4016.1518 | -0.013778
206 |  | 0.39057 | 18.0955 | 4187 | 0.011065 | 8.4559 | 8.4669 | -1.2442 | 90.3718 | 4034.2473 | -0.013767
207 |  | 0.39057 | 18.0817 | 4187 | 0.011057 | 8.4669 | 8.478 | -1.2442 | 90.4406 | 4052.329 | -0.013757
208 |  | 0.39057 | 18.0679 | 4187 | 0.011049 | 8.478 | 8.4891 | -1.2442 | 90.5094 | 4070.3969 | -0.013746
209 |  | 0.39057 | 18.0542 | 4187 | 0.01104 | 8.4891 | 8.5001 | -1.2442 | 90.5784 | 4088.4511 | -0.013736
210 |  | 0.39057 | 18.0405 | 4187 | 0.011032 | 8.5001 | 8.5111 | -1.2442 | 90.6473 | 4106.4916 | -0.013725
211 |  | 0.39057 | 18.0267 | 4187 | 0.011023 | 8.5111 | 8.5221 | -1.2442 | 90.7163 | 4124.5183 | -0.013715
212 |  | 0.39057 | 18.013 | 4187 | 0.011015 | 8.5221 | 8.5332 | -1.2442 | 90.7854 | 4142.5314 | -0.013705
213 |  | 0.39057 | 17.9993 | 4187 | 0.011007 | 8.5332 | 8.5442 | -1.2442 | 90.8545 | 4160.5307 | -0.013694
214 |  | 0.39057 | 17.9856 | 4187 | 0.010998 | 8.5442 | 8.5552 | -1.2442 | 90.9237 | 4178.5163 | -0.013684
215 |  | 0.39057 | 17.9719 | 4187 | 0.01099 | 8.5552 | 8.5662 | -1.2442 | 90.9929 | 4196.4882 | -0.013673
216 |  | 0.39057 | 17.9583 | 4187 | 0.010982 | 8.5662 | 8.5771 | -1.2442 | 91.0622 | 4214.4465 | -0.013663
217 |  | 0.39057 | 17.9446 | 4187 | 0.010973 | 8.5771 | 8.5881 | -1.2442 | 91.1316 | 4232.3911 | -0.013653
218 |  | 0.39057 | 17.9309 | 4187 | 0.010965 | 8.5881 | 8.5991 | -1.2442 | 91.2009 | 4250.322 | -0.013642
219 |  | 0.39057 | 17.9173 | 4187 | 0.010956 | 8.5991 | 8.61 | -1.2442 | 91.2704 | 4268.2394 | -0.013632
220 |  | 0.39057 | 17.9037 | 4187 | 0.010948 | 8.61 | 8.621 | -1.2442 | 91.3399 | 4286.143 | -0.013621
221 |  | 0.39057 | 17.8901 | 4187 | 0.01094 | 8.621 | 8.6319 | -1.2442 | 91.4094 | 4304.0331 | -0.013611
222 |  | 0.39057 | 17.8764 | 4187 | 0.010931 | 8.6319 | 8.6429 | -1.2442 | 91.479 | 4321.9095 | -0.013601
223 |  | 0.39057 | 17.8628 | 4187 | 0.010923 | 8.6429 | 8.6538 | -1.2442 | 91.5487 | 4339.7724 | -0.01359
224 |  | 0.39057 | 17.8493 | 4187 | 0.010915 | 8.6538 | 8.6647 | -1.2442 | 91.6184 | 4357.6216 | -0.01358
225 |  | 0.39057 | 17.8357 | 4187 | 0.010907 | 8.6647 | 8.6756 | -1.2442 | 91.6881 | 4375.4573 | -0.01357
226 |  | 0.39057 | 17.8221 | 4187 | 0.010898 | 8.6756 | 8.6865 | -1.2442 | 91.7579 | 4393.2794 | -0.013559
227 |  | 0.39057 | 17.8085 | 4187 | 0.01089 | 8.6865 | 8.6974 | -1.2442 | 91.8278 | 4411.0879 | -0.013549
228 |  | 0.39057 | 17.795 | 4187 | 0.010882 | 8.6974 | 8.7083 | -1.2442 | 91.8977 | 4428.8829 | -0.013539
229 |  | 0.39057 | 17.7815 | 4187 | 0.010873 | 8.7083 | 8.7191 | -1.2442 | 91.9677 | 4446.6644 | -0.013528
230 |  | 0.39057 | 17.7679 | 4187 | 0.010865 | 8.7191 | 8.73 | -1.2442 | 92.0377 | 4464.4323 | -0.013518
231 |  | 0.39057 | 17.7544 | 4187 | 0.010857 | 8.73 | 8.7409 | -1.2442 | 92.1078 | 4482.1867 | -0.013508
232 |  | 0.39057 | 17.7409 | 4187 | 0.010849 | 8.7409 | 8.7517 | -1.2442 | 92.1779 | 4499.9276 | -0.013498
233 |  | 0.39057 | 17.7274 | 4187 | 0.01084 | 8.7517 | 8.7626 | -1.2442 | 92.2481 | 4517.655 | -0.013487
234 |  | 0.39057 | 17.7139 | 4187 | 0.010832 | 8.7626 | 8.7734 | -1.2442 | 92.3183 | 4535.3689 | -0.013477
235 |  | 0.39057 | 17.7004 | 4187 | 0.010824 | 8.7734 | 8.7842 | -1.2442 | 92.3886 | 4553.0694 | -0.013467
236 |  | 0.39057 | 17.687 | 4187 | 0.010816 | 8.7842 | 8.795 | -1.2442 | 92.459 | 4570.7563 | -0.013457

## St33
|  |  | buis | verlies W/M | L /°C/sec
diam | wandikte |  | inhoud l/m |  | W/M
33.7 | 2.6 | 3.1416 | 0.63794 | 26.5047 | 4187
[8 empty] | J/sec/mtr | aantal mtr. | verlies
|  | buis | verlies W/M | L /°C/sec | verlies temp | begintemp | eindtemp | verlies | bij 1°C | totaal J/sec
|  | inhoud L |  | W/M | °C per M | °C | °C | per m°C | daling | aantal mtr
1 | 33.7 | 0.63794 | 26.5047 | 4187 | 0.0099229 | 6 | 6.0099 | -1.5591 | 100.7766 | 26.5047 | -0.015471
2 |  | 0.63794 | 26.4892 | 4187 | 0.0099171 | 6.0099 | 6.0198 | -1.5591 | 100.8355 | 52.9939 | -0.015462
3 |  | 0.63794 | 26.4738 | 4187 | 0.0099114 | 6.0198 | 6.0298 | -1.5591 | 100.8944 | 79.4677 | -0.015453
4 |  | 0.63794 | 26.4583 | 4187 | 0.0099056 | 6.0298 | 6.0397 | -1.5591 | 100.9533 | 105.926 | -0.015444
5 |  | 0.63794 | 26.4429 | 4187 | 0.0098998 | 6.0397 | 6.0496 | -1.5591 | 101.0123 | 132.3688 | -0.015435
6 |  | 0.63794 | 26.4274 | 4187 | 0.009894 | 6.0496 | 6.0595 | -1.5591 | 101.0713 | 158.7963 | -0.015426
7 |  | 0.63794 | 26.412 | 4187 | 0.0098882 | 6.0595 | 6.0693 | -1.5591 | 101.1303 | 185.2083 | -0.015417
8 |  | 0.63794 | 26.3966 | 4187 | 0.0098825 | 6.0693 | 6.0792 | -1.5591 | 101.1894 | 211.6048 | -0.015408
9 |  | 0.63794 | 26.3812 | 4187 | 0.0098767 | 6.0792 | 6.0891 | -1.5591 | 101.2485 | 237.986 | -0.015399
10 |  | 0.63794 | 26.3658 | 4187 | 0.0098709 | 6.0891 | 6.099 | -1.5591 | 101.3076 | 264.3518 | -0.01539
11 |  | 0.63794 | 26.3504 | 4187 | 0.0098652 | 6.099 | 6.1088 | -1.5591 | 101.3668 | 290.7022 | -0.015381
12 |  | 0.63794 | 26.335 | 4187 | 0.0098594 | 6.1088 | 6.1187 | -1.5591 | 101.426 | 317.0372 | -0.015372
13 |  | 0.63794 | 26.3196 | 4187 | 0.0098537 | 6.1187 | 6.1285 | -1.5591 | 101.4852 | 343.3568 | -0.015363
14 |  | 0.63794 | 26.3043 | 4187 | 0.0098479 | 6.1285 | 6.1384 | -1.5591 | 101.5445 | 369.6611 | -0.015354
15 |  | 0.63794 | 26.2889 | 4187 | 0.0098422 | 6.1384 | 6.1482 | -1.5591 | 101.6038 | 395.95 | -0.015345
16 |  | 0.63794 | 26.2736 | 4187 | 0.0098364 | 6.1482 | 6.1581 | -1.5591 | 101.6631 | 422.2236 | -0.015336
17 |  | 0.63794 | 26.2582 | 4187 | 0.0098307 | 6.1581 | 6.1679 | -1.5591 | 101.7225 | 448.4818 | -0.015327
18 |  | 0.63794 | 26.2429 | 4187 | 0.0098249 | 6.1679 | 6.1777 | -1.5591 | 101.7819 | 474.7247 | -0.015318
19 |  | 0.63794 | 26.2276 | 4187 | 0.0098192 | 6.1777 | 6.1875 | -1.5591 | 101.8413 | 500.9523 | -0.015309
20 |  | 0.63794 | 26.2123 | 4187 | 0.0098135 | 6.1875 | 6.1974 | -1.5591 | 101.9008 | 527.1646 | -0.0153
21 |  | 0.63794 | 26.197 | 4187 | 0.0098077 | 6.1974 | 6.2072 | -1.5591 | 101.9603 | 553.3616 | -0.015291
22 |  | 0.63794 | 26.1817 | 4187 | 0.009802 | 6.2072 | 6.217 | -1.5591 | 102.0199 | 579.5433 | -0.015282
23 |  | 0.63794 | 26.1664 | 4187 | 0.0097963 | 6.217 | 6.2268 | -1.5591 | 102.0795 | 605.7097 | -0.015273
24 |  | 0.63794 | 26.1511 | 4187 | 0.0097906 | 6.2268 | 6.2366 | -1.5591 | 102.1391 | 631.8608 | -0.015264
25 |  | 0.63794 | 26.1359 | 4187 | 0.0097849 | 6.2366 | 6.2463 | -1.5591 | 102.1987 | 657.9967 | -0.015256
26 |  | 0.63794 | 26.1206 | 4187 | 0.0097791 | 6.2463 | 6.2561 | -1.5591 | 102.2584 | 684.1173 | -0.015247
27 |  | 0.63794 | 26.1054 | 4187 | 0.0097734 | 6.2561 | 6.2659 | -1.5591 | 102.3182 | 710.2227 | -0.015238
28 |  | 0.63794 | 26.0901 | 4187 | 0.0097677 | 6.2659 | 6.2757 | -1.5591 | 102.3779 | 736.3128 | -0.015229
29 |  | 0.63794 | 26.0749 | 4187 | 0.009762 | 6.2757 | 6.2854 | -1.5591 | 102.4377 | 762.3877 | -0.01522
30 |  | 0.63794 | 26.0597 | 4187 | 0.0097563 | 6.2854 | 6.2952 | -1.5591 | 102.4975 | 788.4474 | -0.015211
31 |  | 0.63794 | 26.0445 | 4187 | 0.0097506 | 6.2952 | 6.3049 | -1.5591 | 102.5574 | 814.4919 | -0.015202
32 |  | 0.63794 | 26.0293 | 4187 | 0.0097449 | 6.3049 | 6.3147 | -1.5591 | 102.6173 | 840.5211 | -0.015193
33 |  | 0.63794 | 26.0141 | 4187 | 0.0097393 | 6.3147 | 6.3244 | -1.5591 | 102.6772 | 866.5352 | -0.015184
34 |  | 0.63794 | 25.9989 | 4187 | 0.0097336 | 6.3244 | 6.3342 | -1.5591 | 102.7372 | 892.5341 | -0.015176
35 |  | 0.63794 | 25.9837 | 4187 | 0.0097279 | 6.3342 | 6.3439 | -1.5591 | 102.7972 | 918.5178 | -0.015167
36 |  | 0.63794 | 25.9685 | 4187 | 0.0097222 | 6.3439 | 6.3536 | -1.5591 | 102.8572 | 944.4864 | -0.015158
37 |  | 0.63794 | 25.9534 | 4187 | 0.0097165 | 6.3536 | 6.3633 | -1.5591 | 102.9173 | 970.4398 | -0.015149
38 |  | 0.63794 | 25.9382 | 4187 | 0.0097109 | 6.3633 | 6.373 | -1.5591 | 102.9774 | 996.378 | -0.01514
39 |  | 0.63794 | 25.9231 | 4187 | 0.0097052 | 6.373 | 6.3827 | -1.5591 | 103.0376 | 1022.3011 | -0.015131
40 |  | 0.63794 | 25.908 | 4187 | 0.0096995 | 6.3827 | 6.3924 | -1.5591 | 103.0977 | 1048.2091 | -0.015123
41 |  | 0.63794 | 25.8928 | 4187 | 0.0096939 | 6.3924 | 6.4021 | -1.5591 | 103.158 | 1074.1019 | -0.015114
42 |  | 0.63794 | 25.8777 | 4187 | 0.0096882 | 6.4021 | 6.4118 | -1.5591 | 103.2182 | 1099.9797 | -0.015105
43 |  | 0.63794 | 25.8626 | 4187 | 0.0096826 | 6.4118 | 6.4215 | -1.5591 | 103.2785 | 1125.8423 | -0.015096
44 |  | 0.63794 | 25.8475 | 4187 | 0.0096769 | 6.4215 | 6.4312 | -1.5591 | 103.3388 | 1151.6898 | -0.015087
45 |  | 0.63794 | 25.8324 | 4187 | 0.0096713 | 6.4312 | 6.4408 | -1.5591 | 103.3992 | 1177.5223 | -0.015078
46 |  | 0.63794 | 25.8174 | 4187 | 0.0096656 | 6.4408 | 6.4505 | -1.5591 | 103.4596 | 1203.3396 | -0.01507
47 |  | 0.63794 | 25.8023 | 4187 | 0.00966 | 6.4505 | 6.4602 | -1.5591 | 103.52 | 1229.1419 | -0.015061
48 |  | 0.63794 | 25.7872 | 4187 | 0.0096543 | 6.4602 | 6.4698 | -1.5591 | 103.5804 | 1254.9292 | -0.015052
49 |  | 0.63794 | 25.7722 | 4187 | 0.0096487 | 6.4698 | 6.4795 | -1.5591 | 103.6409 | 1280.7014 | -0.015043
50 |  | 0.63794 | 25.7571 | 4187 | 0.0096431 | 6.4795 | 6.4891 | -1.5591 | 103.7015 | 1306.4585 | -0.015034
51 |  | 0.63794 | 25.7421 | 4187 | 0.0096374 | 6.4891 | 6.4988 | -1.5591 | 103.762 | 1332.2006 | -0.015026
52 |  | 0.63794 | 25.7271 | 4187 | 0.0096318 | 6.4988 | 6.5084 | -1.5591 | 103.8226 | 1357.9277 | -0.015017
53 |  | 0.63794 | 25.7121 | 4187 | 0.0096262 | 6.5084 | 6.518 | -1.5591 | 103.8833 | 1383.6397 | -0.015008
54 |  | 0.63794 | 25.6971 | 4187 | 0.0096206 | 6.518 | 6.5276 | -1.5591 | 103.9439 | 1409.3368 | -0.014999
55 |  | 0.63794 | 25.6821 | 4187 | 0.009615 | 6.5276 | 6.5372 | -1.5591 | 104.0047 | 1435.0189 | -0.014991
56 |  | 0.63794 | 25.6671 | 4187 | 0.0096093 | 6.5372 | 6.5469 | -1.5591 | 104.0654 | 1460.6859 | -0.014982
57 |  | 0.63794 | 25.6521 | 4187 | 0.0096037 | 6.5469 | 6.5565 | -1.5591 | 104.1262 | 1486.338 | -0.014973
58 |  | 0.63794 | 25.6371 | 4187 | 0.0095981 | 6.5565 | 6.5661 | -1.5591 | 104.187 | 1511.9751 | -0.014964
59 |  | 0.63794 | 25.6221 | 4187 | 0.0095925 | 6.5661 | 6.5757 | -1.5591 | 104.2478 | 1537.5973 | -0.014956
60 |  | 0.63794 | 25.6072 | 4187 | 0.0095869 | 6.5757 | 6.5852 | -1.5591 | 104.3087 | 1563.2045 | -0.014947
61 |  | 0.63794 | 25.5922 | 4187 | 0.0095813 | 6.5852 | 6.5948 | -1.5591 | 104.3696 | 1588.7967 | -0.014938
62 |  | 0.63794 | 25.5773 | 4187 | 0.0095757 | 6.5948 | 6.6044 | -1.5591 | 104.4306 | 1614.374 | -0.01493
63 |  | 0.63794 | 25.5624 | 4187 | 0.0095701 | 6.6044 | 6.614 | -1.5591 | 104.4916 | 1639.9364 | -0.014921
64 |  | 0.63794 | 25.5475 | 4187 | 0.0095646 | 6.614 | 6.6235 | -1.5591 | 104.5526 | 1665.4838 | -0.014912
65 |  | 0.63794 | 25.5325 | 4187 | 0.009559 | 6.6235 | 6.6331 | -1.5591 | 104.6137 | 1691.0164 | -0.014903
66 |  | 0.63794 | 25.5176 | 4187 | 0.0095534 | 6.6331 | 6.6426 | -1.5591 | 104.6748 | 1716.534 | -0.014895
67 |  | 0.63794 | 25.5027 | 4187 | 0.0095478 | 6.6426 | 6.6522 | -1.5591 | 104.7359 | 1742.0368 | -0.014886
68 |  | 0.63794 | 25.4879 | 4187 | 0.0095423 | 6.6522 | 6.6617 | -1.5591 | 104.7971 | 1767.5246 | -0.014877
69 |  | 0.63794 | 25.473 | 4187 | 0.0095367 | 6.6617 | 6.6713 | -1.5591 | 104.8583 | 1792.9976 | -0.014869
70 |  | 0.63794 | 25.4581 | 4187 | 0.0095311 | 6.6713 | 6.6808 | -1.5591 | 104.9195 | 1818.4557 | -0.01486
71 |  | 0.63794 | 25.4433 | 4187 | 0.0095256 | 6.6808 | 6.6903 | -1.5591 | 104.9808 | 1843.899 | -0.014851
72 |  | 0.63794 | 25.4284 | 4187 | 0.00952 | 6.6903 | 6.6998 | -1.5591 | 105.0421 | 1869.3274 | -0.014843
73 |  | 0.63794 | 25.4136 | 4187 | 0.0095144 | 6.6998 | 6.7094 | -1.5591 | 105.1035 | 1894.7409 | -0.014834
74 |  | 0.63794 | 25.3987 | 4187 | 0.0095089 | 6.7094 | 6.7189 | -1.5591 | 105.1649 | 1920.1397 | -0.014825
75 |  | 0.63794 | 25.3839 | 4187 | 0.0095033 | 6.7189 | 6.7284 | -1.5591 | 105.2263 | 1945.5236 | -0.014817
76 |  | 0.63794 | 25.3691 | 4187 | 0.0094978 | 6.7284 | 6.7379 | -1.5591 | 105.2877 | 1970.8926 | -0.014808
77 |  | 0.63794 | 25.3543 | 4187 | 0.0094922 | 6.7379 | 6.7474 | -1.5591 | 105.3492 | 1996.2469 | -0.014799
78 |  | 0.63794 | 25.3395 | 4187 | 0.0094867 | 6.7474 | 6.7568 | -1.5591 | 105.4108 | 2021.5864 | -0.014791
79 |  | 0.63794 | 25.3247 | 4187 | 0.0094812 | 6.7568 | 6.7663 | -1.5591 | 105.4723 | 2046.9111 | -0.014782
80 |  | 0.63794 | 25.3099 | 4187 | 0.0094756 | 6.7663 | 6.7758 | -1.5591 | 105.5339 | 2072.221 | -0.014773
81 |  | 0.63794 | 25.2951 | 4187 | 0.0094701 | 6.7758 | 6.7853 | -1.5591 | 105.5956 | 2097.5161 | -0.014765
82 |  | 0.63794 | 25.2804 | 4187 | 0.0094646 | 6.7853 | 6.7947 | -1.5591 | 105.6572 | 2122.7965 | -0.014756
83 |  | 0.63794 | 25.2656 | 4187 | 0.009459 | 6.7947 | 6.8042 | -1.5591 | 105.7189 | 2148.0621 | -0.014748
84 |  | 0.63794 | 25.2509 | 4187 | 0.0094535 | 6.8042 | 6.8137 | -1.5591 | 105.7807 | 2173.313 | -0.014739
85 |  | 0.63794 | 25.2361 | 4187 | 0.009448 | 6.8137 | 6.8231 | -1.5591 | 105.8425 | 2198.5491 | -0.01473
86 |  | 0.63794 | 25.2214 | 4187 | 0.0094425 | 6.8231 | 6.8325 | -1.5591 | 105.9043 | 2223.7705 | -0.014722
87 |  | 0.63794 | 25.2067 | 4187 | 0.009437 | 6.8325 | 6.842 | -1.5591 | 105.9661 | 2248.9771 | -0.014713
88 |  | 0.63794 | 25.192 | 4187 | 0.0094315 | 6.842 | 6.8514 | -1.5591 | 106.028 | 2274.1691 | -0.014705
89 |  | 0.63794 | 25.1773 | 4187 | 0.009426 | 6.8514 | 6.8608 | -1.5591 | 106.0899 | 2299.3463 | -0.014696
90 |  | 0.63794 | 25.1626 | 4187 | 0.0094205 | 6.8608 | 6.8703 | -1.5591 | 106.1519 | 2324.5089 | -0.014687
91 |  | 0.63794 | 25.1479 | 4187 | 0.009415 | 6.8703 | 6.8797 | -1.5591 | 106.2139 | 2349.6568 | -0.014679
92 |  | 0.63794 | 25.1332 | 4187 | 0.0094095 | 6.8797 | 6.8891 | -1.5591 | 106.2759 | 2374.79 | -0.01467
93 |  | 0.63794 | 25.1185 | 4187 | 0.009404 | 6.8891 | 6.8985 | -1.5591 | 106.338 | 2399.9085 | -0.014662
94 |  | 0.63794 | 25.1039 | 4187 | 0.0093985 | 6.8985 | 6.9079 | -1.5591 | 106.4001 | 2425.0123 | -0.014653
95 |  | 0.63794 | 25.0892 | 4187 | 0.009393 | 6.9079 | 6.9173 | -1.5591 | 106.4623 | 2450.1015 | -0.014645
96 |  | 0.63794 | 25.0746 | 4187 | 0.0093875 | 6.9173 | 6.9267 | -1.5591 | 106.5244 | 2475.1761 | -0.014636
97 |  | 0.63794 | 25.0599 | 4187 | 0.009382 | 6.9267 | 6.936 | -1.5591 | 106.5866 | 2500.236 | -0.014628
98 |  | 0.63794 | 25.0453 | 4187 | 0.0093766 | 6.936 | 6.9454 | -1.5591 | 106.6489 | 2525.2813 | -0.014619
99 |  | 0.63794 | 25.0307 | 4187 | 0.0093711 | 6.9454 | 6.9548 | -1.5591 | 106.7112 | 2550.312 | -0.01461
100 |  | 0.63794 | 25.0161 | 4187 | 0.0093656 | 6.9548 | 6.9642 | -1.5591 | 106.7735 | 2575.3281 | -0.014602
101 |  | 0.63794 | 25.0015 | 4187 | 0.0093602 | 6.9642 | 6.9735 | -1.5591 | 106.8359 | 2600.3295 | -0.014593
102 |  | 0.63794 | 24.9869 | 4187 | 0.0093547 | 6.9735 | 6.9829 | -1.5591 | 106.8983 | 2625.3164 | -0.014585
103 |  | 0.63794 | 24.9723 | 4187 | 0.0093492 | 6.9829 | 6.9922 | -1.5591 | 106.9607 | 2650.2887 | -0.014576
104 |  | 0.63794 | 24.9577 | 4187 | 0.0093438 | 6.9922 | 7.0016 | -1.5591 | 107.0232 | 2675.2464 | -0.014568
105 |  | 0.63794 | 24.9431 | 4187 | 0.0093383 | 7.0016 | 7.0109 | -1.5591 | 107.0857 | 2700.1896 | -0.014559
106 |  | 0.63794 | 24.9286 | 4187 | 0.0093329 | 7.0109 | 7.0202 | -1.5591 | 107.1482 | 2725.1181 | -0.014551
107 |  | 0.63794 | 24.914 | 4187 | 0.0093274 | 7.0202 | 7.0296 | -1.5591 | 107.2108 | 2750.0322 | -0.014542
108 |  | 0.63794 | 24.8995 | 4187 | 0.009322 | 7.0296 | 7.0389 | -1.5591 | 107.2734 | 2774.9317 | -0.014534
109 |  | 0.63794 | 24.885 | 4187 | 0.0093165 | 7.0389 | 7.0482 | -1.5591 | 107.3361 | 2799.8166 | -0.014525
110 |  | 0.63794 | 24.8704 | 4187 | 0.0093111 | 7.0482 | 7.0575 | -1.5591 | 107.3988 | 2824.687 | -0.014517
111 |  | 0.63794 | 24.8559 | 4187 | 0.0093057 | 7.0575 | 7.0668 | -1.5591 | 107.4615 | 2849.543 | -0.014508
112 |  | 0.63794 | 24.8414 | 4187 | 0.0093002 | 7.0668 | 7.0761 | -1.5591 | 107.5242 | 2874.3844 | -0.0145
113 |  | 0.63794 | 24.8269 | 4187 | 0.0092948 | 7.0761 | 7.0854 | -1.5591 | 107.587 | 2899.2113 | -0.014492
114 |  | 0.63794 | 24.8124 | 4187 | 0.0092894 | 7.0854 | 7.0947 | -1.5591 | 107.6499 | 2924.0237 | -0.014483
115 |  | 0.63794 | 24.7979 | 4187 | 0.009284 | 7.0947 | 7.104 | -1.5591 | 107.7128 | 2948.8216 | -0.014475
116 |  | 0.63794 | 24.7835 | 4187 | 0.0092785 | 7.104 | 7.1133 | -1.5591 | 107.7757 | 2973.6051 | -0.014466
117 |  | 0.63794 | 24.769 | 4187 | 0.0092731 | 7.1133 | 7.1225 | -1.5591 | 107.8386 | 2998.3741 | -0.014458
118 |  | 0.63794 | 24.7545 | 4187 | 0.0092677 | 7.1225 | 7.1318 | -1.5591 | 107.9016 | 3023.1286 | -0.014449
119 |  | 0.63794 | 24.7401 | 4187 | 0.0092623 | 7.1318 | 7.1411 | -1.5591 | 107.9646 | 3047.8687 | -0.014441
120 |  | 0.63794 | 24.7256 | 4187 | 0.0092569 | 7.1411 | 7.1503 | -1.5591 | 108.0277 | 3072.5943 | -0.014432
121 |  | 0.63794 | 24.7112 | 4187 | 0.0092515 | 7.1503 | 7.1596 | -1.5591 | 108.0908 | 3097.3055 | -0.014424
122 |  | 0.63794 | 24.6968 | 4187 | 0.0092461 | 7.1596 | 7.1688 | -1.5591 | 108.1539 | 3122.0023 | -0.014416
123 |  | 0.63794 | 24.6824 | 4187 | 0.0092407 | 7.1688 | 7.1781 | -1.5591 | 108.2171 | 3146.6847 | -0.014407
124 |  | 0.63794 | 24.668 | 4187 | 0.0092353 | 7.1781 | 7.1873 | -1.5591 | 108.2803 | 3171.3527 | -0.014399
125 |  | 0.63794 | 24.6536 | 4187 | 0.0092299 | 7.1873 | 7.1965 | -1.5591 | 108.3435 | 3196.0062 | -0.01439
126 |  | 0.63794 | 24.6392 | 4187 | 0.0092245 | 7.1965 | 7.2058 | -1.5591 | 108.4068 | 3220.6454 | -0.014382
127 |  | 0.63794 | 24.6248 | 4187 | 0.0092191 | 7.2058 | 7.215 | -1.5591 | 108.4701 | 3245.2702 | -0.014374
128 |  | 0.63794 | 24.6104 | 4187 | 0.0092138 | 7.215 | 7.2242 | -1.5591 | 108.5334 | 3269.8806 | -0.014365
129 |  | 0.63794 | 24.5961 | 4187 | 0.0092084 | 7.2242 | 7.2334 | -1.5591 | 108.5968 | 3294.4767 | -0.014357
130 |  | 0.63794 | 24.5817 | 4187 | 0.009203 | 7.2334 | 7.2426 | -1.5591 | 108.6603 | 3319.0584 | -0.014348
131 |  | 0.63794 | 24.5673 | 4187 | 0.0091976 | 7.2426 | 7.2518 | -1.5591 | 108.7237 | 3343.6257 | -0.01434
132 |  | 0.63794 | 24.553 | 4187 | 0.0091923 | 7.2518 | 7.261 | -1.5591 | 108.7872 | 3368.1787 | -0.014332
133 |  | 0.63794 | 24.5387 | 4187 | 0.0091869 | 7.261 | 7.2702 | -1.5591 | 108.8507 | 3392.7174 | -0.014323
134 |  | 0.63794 | 24.5244 | 4187 | 0.0091815 | 7.2702 | 7.2794 | -1.5591 | 108.9143 | 3417.2417 | -0.014315
135 |  | 0.63794 | 24.51 | 4187 | 0.0091762 | 7.2794 | 7.2885 | -1.5591 | 108.9779 | 3441.7518 | -0.014307
136 |  | 0.63794 | 24.4957 | 4187 | 0.0091708 | 7.2885 | 7.2977 | -1.5591 | 109.0416 | 3466.2475 | -0.014298
137 |  | 0.63794 | 24.4814 | 4187 | 0.0091655 | 7.2977 | 7.3069 | -1.5591 | 109.1053 | 3490.7289 | -0.01429
138 |  | 0.63794 | 24.4671 | 4187 | 0.0091601 | 7.3069 | 7.316 | -1.5591 | 109.169 | 3515.1961 | -0.014282
139 |  | 0.63794 | 24.4529 | 4187 | 0.0091548 | 7.316 | 7.3252 | -1.5591 | 109.2327 | 3539.649 | -0.014273
140 |  | 0.63794 | 24.4386 | 4187 | 0.0091494 | 7.3252 | 7.3343 | -1.5591 | 109.2965 | 3564.0875 | -0.014265
141 |  | 0.63794 | 24.4243 | 4187 | 0.0091441 | 7.3343 | 7.3435 | -1.5591 | 109.3604 | 3588.5119 | -0.014257
142 |  | 0.63794 | 24.4101 | 4187 | 0.0091387 | 7.3435 | 7.3526 | -1.5591 | 109.4242 | 3612.9219 | -0.014248
143 |  | 0.63794 | 24.3958 | 4187 | 0.0091334 | 7.3526 | 7.3618 | -1.5591 | 109.4882 | 3637.3178 | -0.01424
144 |  | 0.63794 | 24.3816 | 4187 | 0.0091281 | 7.3618 | 7.3709 | -1.5591 | 109.5521 | 3661.6993 | -0.014232
145 |  | 0.63794 | 24.3673 | 4187 | 0.0091227 | 7.3709 | 7.38 | -1.5591 | 109.6161 | 3686.0667 | -0.014223
146 |  | 0.63794 | 24.3531 | 4187 | 0.0091174 | 7.38 | 7.3891 | -1.5591 | 109.6801 | 3710.4198 | -0.014215
147 |  | 0.63794 | 24.3389 | 4187 | 0.0091121 | 7.3891 | 7.3982 | -1.5591 | 109.7442 | 3734.7587 | -0.014207
148 |  | 0.63794 | 24.3247 | 4187 | 0.0091068 | 7.3982 | 7.4073 | -1.5591 | 109.8083 | 3759.0834 | -0.014198
149 |  | 0.63794 | 24.3105 | 4187 | 0.0091015 | 7.4073 | 7.4164 | -1.5591 | 109.8724 | 3783.3939 | -0.01419
150 |  | 0.63794 | 24.2963 | 4187 | 0.0090962 | 7.4164 | 7.4255 | -1.5591 | 109.9366 | 3807.6902 | -0.014182
151 |  | 0.63794 | 24.2821 | 4187 | 0.0090908 | 7.4255 | 7.4346 | -1.5591 | 110.0008 | 3831.9724 | -0.014174
152 |  | 0.63794 | 24.268 | 4187 | 0.0090855 | 7.4346 | 7.4437 | -1.5591 | 110.065 | 3856.2403 | -0.014165
153 |  | 0.63794 | 24.2538 | 4187 | 0.0090802 | 7.4437 | 7.4528 | -1.5591 | 110.1293 | 3880.4941 | -0.014157
154 |  | 0.63794 | 24.2396 | 4187 | 0.0090749 | 7.4528 | 7.4619 | -1.5591 | 110.1936 | 3904.7338 | -0.014149
155 |  | 0.63794 | 24.2255 | 4187 | 0.0090696 | 7.4619 | 7.4709 | -1.5591 | 110.258 | 3928.9593 | -0.01414
156 |  | 0.63794 | 24.2113 | 4187 | 0.0090643 | 7.4709 | 7.48 | -1.5591 | 110.3224 | 3953.1706 | -0.014132
157 |  | 0.63794 | 24.1972 | 4187 | 0.0090591 | 7.48 | 7.4891 | -1.5591 | 110.3868 | 3977.3678 | -0.014124
158 |  | 0.63794 | 24.1831 | 4187 | 0.0090538 | 7.4891 | 7.4981 | -1.5591 | 110.4513 | 4001.5509 | -0.014116
159 |  | 0.63794 | 24.169 | 4187 | 0.0090485 | 7.4981 | 7.5072 | -1.5591 | 110.5158 | 4025.7199 | -0.014107
160 |  | 0.63794 | 24.1549 | 4187 | 0.0090432 | 7.5072 | 7.5162 | -1.5591 | 110.5803 | 4049.8748 | -0.014099
161 |  | 0.63794 | 24.1408 | 4187 | 0.0090379 | 7.5162 | 7.5252 | -1.5591 | 110.6449 | 4074.0155 | -0.014091
162 |  | 0.63794 | 24.1267 | 4187 | 0.0090326 | 7.5252 | 7.5343 | -1.5591 | 110.7095 | 4098.1422 | -0.014083
163 |  | 0.63794 | 24.1126 | 4187 | 0.0090274 | 7.5343 | 7.5433 | -1.5591 | 110.7742 | 4122.2548 | -0.014075
164 |  | 0.63794 | 24.0985 | 4187 | 0.0090221 | 7.5433 | 7.5523 | -1.5591 | 110.8389 | 4146.3533 | -0.014066
165 |  | 0.63794 | 24.0845 | 4187 | 0.0090168 | 7.5523 | 7.5613 | -1.5591 | 110.9036 | 4170.4378 | -0.014058
166 |  | 0.63794 | 24.0704 | 4187 | 0.0090116 | 7.5613 | 7.5704 | -1.5591 | 110.9684 | 4194.5082 | -0.01405
167 |  | 0.63794 | 24.0563 | 4187 | 0.0090063 | 7.5704 | 7.5794 | -1.5591 | 111.0332 | 4218.5645 | -0.014042
168 |  | 0.63794 | 24.0423 | 4187 | 0.0090011 | 7.5794 | 7.5884 | -1.5591 | 111.0981 | 4242.6068 | -0.014034
169 |  | 0.63794 | 24.0283 | 4187 | 0.0089958 | 7.5884 | 7.5974 | -1.5591 | 111.1629 | 4266.6351 | -0.014025
170 |  | 0.63794 | 24.0142 | 4187 | 0.0089906 | 7.5974 | 7.6064 | -1.5591 | 111.2279 | 4290.6493 | -0.014017
171 |  | 0.63794 | 24.0002 | 4187 | 0.0089853 | 7.6064 | 7.6153 | -1.5591 | 111.2928 | 4314.6496 | -0.014009
172 |  | 0.63794 | 23.9862 | 4187 | 0.0089801 | 7.6153 | 7.6243 | -1.5591 | 111.3578 | 4338.6358 | -0.014001
173 |  | 0.63794 | 23.9722 | 4187 | 0.0089748 | 7.6243 | 7.6333 | -1.5591 | 111.4229 | 4362.608 | -0.013993
174 |  | 0.63794 | 23.9582 | 4187 | 0.0089696 | 7.6333 | 7.6423 | -1.5591 | 111.4879 | 4386.5662 | -0.013984
175 |  | 0.63794 | 23.9442 | 4187 | 0.0089643 | 7.6423 | 7.6512 | -1.5591 | 111.5531 | 4410.5105 | -0.013976
176 |  | 0.63794 | 23.9303 | 4187 | 0.0089591 | 7.6512 | 7.6602 | -1.5591 | 111.6182 | 4434.4407 | -0.013968
177 |  | 0.63794 | 23.9163 | 4187 | 0.0089539 | 7.6602 | 7.6691 | -1.5591 | 111.6834 | 4458.357 | -0.01396
178 |  | 0.63794 | 23.9023 | 4187 | 0.0089487 | 7.6691 | 7.6781 | -1.5591 | 111.7486 | 4482.2594 | -0.013952
179 |  | 0.63794 | 23.8884 | 4187 | 0.0089434 | 7.6781 | 7.687 | -1.5591 | 111.8139 | 4506.1478 | -0.013944
180 |  | 0.63794 | 23.8744 | 4187 | 0.0089382 | 7.687 | 7.696 | -1.5591 | 111.8792 | 4530.0222 | -0.013936
181 |  | 0.63794 | 23.8605 | 4187 | 0.008933 | 7.696 | 7.7049 | -1.5591 | 111.9445 | 4553.8827 | -0.013927
182 |  | 0.63794 | 23.8466 | 4187 | 0.0089278 | 7.7049 | 7.7138 | -1.5591 | 112.0099 | 4577.7293 | -0.013919
183 |  | 0.63794 | 23.8327 | 4187 | 0.0089226 | 7.7138 | 7.7228 | -1.5591 | 112.0753 | 4601.5619 | -0.013911
184 |  | 0.63794 | 23.8187 | 4187 | 0.0089174 | 7.7228 | 7.7317 | -1.5591 | 112.1408 | 4625.3807 | -0.013903
185 |  | 0.63794 | 23.8048 | 4187 | 0.0089122 | 7.7317 | 7.7406 | -1.5591 | 112.2063 | 4649.1855 | -0.013895
186 |  | 0.63794 | 23.791 | 4187 | 0.008907 | 7.7406 | 7.7495 | -1.5591 | 112.2718 | 4672.9765 | -0.013887
187 |  | 0.63794 | 23.7771 | 4187 | 0.0089018 | 7.7495 | 7.7584 | -1.5591 | 112.3374 | 4696.7536 | -0.013879
188 |  | 0.63794 | 23.7632 | 4187 | 0.0088966 | 7.7584 | 7.7673 | -1.5591 | 112.403 | 4720.5167 | -0.013871
189 |  | 0.63794 | 23.7493 | 4187 | 0.0088914 | 7.7673 | 7.7762 | -1.5591 | 112.4687 | 4744.2661 | -0.013863
190 |  | 0.63794 | 23.7355 | 4187 | 0.0088862 | 7.7762 | 7.7851 | -1.5591 | 112.5343 | 4768.0015 | -0.013854
191 |  | 0.63794 | 23.7216 | 4187 | 0.008881 | 7.7851 | 7.7939 | -1.5591 | 112.6001 | 4791.7231 | -0.013846
192 |  | 0.63794 | 23.7078 | 4187 | 0.0088758 | 7.7939 | 7.8028 | -1.5591 | 112.6658 | 4815.4309 | -0.013838
193 |  | 0.63794 | 23.6939 | 4187 | 0.0088706 | 7.8028 | 7.8117 | -1.5591 | 112.7316 | 4839.1248 | -0.01383
194 |  | 0.63794 | 23.6801 | 4187 | 0.0088654 | 7.8117 | 7.8206 | -1.5591 | 112.7975 | 4862.8048 | -0.013822
195 |  | 0.63794 | 23.6663 | 4187 | 0.0088603 | 7.8206 | 7.8294 | -1.5591 | 112.8633 | 4886.4711 | -0.013814
196 |  | 0.63794 | 23.6524 | 4187 | 0.0088551 | 7.8294 | 7.8383 | -1.5591 | 112.9293 | 4910.1236 | -0.013806
197 |  | 0.63794 | 23.6386 | 4187 | 0.0088499 | 7.8383 | 7.8471 | -1.5591 | 112.9952 | 4933.7622 | -0.013798
198 |  | 0.63794 | 23.6248 | 4187 | 0.0088448 | 7.8471 | 7.856 | -1.5591 | 113.0612 | 4957.387 | -0.01379
199 |  | 0.63794 | 23.6111 | 4187 | 0.0088396 | 7.856 | 7.8648 | -1.5591 | 113.1272 | 4980.9981 | -0.013782
200 |  | 0.63794 | 23.5973 | 4187 | 0.0088344 | 7.8648 | 7.8736 | -1.5591 | 113.1933 | 5004.5954 | -0.013774
201 |  | 0.63794 | 23.5835 | 4187 | 0.0088293 | 7.8736 | 7.8825 | -1.5591 | 113.2594 | 5028.1789 | -0.013766
202 |  | 0.63794 | 23.5697 | 4187 | 0.0088241 | 7.8825 | 7.8913 | -1.5591 | 113.3256 | 5051.7486 | -0.013758
203 |  | 0.63794 | 23.556 | 4187 | 0.008819 | 7.8913 | 7.9001 | -1.5591 | 113.3918 | 5075.3046 | -0.01375
204 |  | 0.63794 | 23.5422 | 4187 | 0.0088138 | 7.9001 | 7.9089 | -1.5591 | 113.458 | 5098.8468 | -0.013742
205 |  | 0.63794 | 23.5285 | 4187 | 0.0088087 | 7.9089 | 7.9177 | -1.5591 | 113.5243 | 5122.3753 | -0.013734
206 |  | 0.63794 | 23.5147 | 4187 | 0.0088035 | 7.9177 | 7.9265 | -1.5591 | 113.5906 | 5145.89 | -0.013726
207 |  | 0.63794 | 23.501 | 4187 | 0.0087984 | 7.9265 | 7.9353 | -1.5591 | 113.6569 | 5169.391 | -0.013718
208 |  | 0.63794 | 23.4873 | 4187 | 0.0087933 | 7.9353 | 7.9441 | -1.5591 | 113.7233 | 5192.8783 | -0.01371
209 |  | 0.63794 | 23.4736 | 4187 | 0.0087881 | 7.9441 | 7.9529 | -1.5591 | 113.7897 | 5216.3519 | -0.013702
210 |  | 0.63794 | 23.4599 | 4187 | 0.008783 | 7.9529 | 7.9617 | -1.5591 | 113.8562 | 5239.8118 | -0.013694
211 |  | 0.63794 | 23.4462 | 4187 | 0.0087779 | 7.9617 | 7.9705 | -1.5591 | 113.9227 | 5263.258 | -0.013686
212 |  | 0.63794 | 23.4325 | 4187 | 0.0087728 | 7.9705 | 7.9793 | -1.5591 | 113.9892 | 5286.6906 | -0.013678
213 |  | 0.63794 | 23.4188 | 4187 | 0.0087676 | 7.9793 | 7.988 | -1.5591 | 114.0558 | 5310.1094 | -0.01367
214 |  | 0.63794 | 23.4052 | 4187 | 0.0087625 | 7.988 | 7.9968 | -1.5591 | 114.1224 | 5333.5146 | -0.013662
215 |  | 0.63794 | 23.3915 | 4187 | 0.0087574 | 7.9968 | 8.0055 | -1.5591 | 114.189 | 5356.9061 | -0.013654
216 |  | 0.63794 | 23.3779 | 4187 | 0.0087523 | 8.0055 | 8.0143 | -1.5591 | 114.2557 | 5380.2839 | -0.013646
217 |  | 0.63794 | 23.3642 | 4187 | 0.0087472 | 8.0143 | 8.023 | -1.5591 | 114.3224 | 5403.6481 | -0.013638
218 |  | 0.63794 | 23.3506 | 4187 | 0.0087421 | 8.023 | 8.0318 | -1.5591 | 114.3892 | 5426.9987 | -0.01363
219 |  | 0.63794 | 23.3369 | 4187 | 0.008737 | 8.0318 | 8.0405 | -1.5591 | 114.456 | 5450.3356 | -0.013622
220 |  | 0.63794 | 23.3233 | 4187 | 0.0087319 | 8.0405 | 8.0493 | -1.5591 | 114.5229 | 5473.6589 | -0.013614
221 |  | 0.63794 | 23.3097 | 4187 | 0.0087268 | 8.0493 | 8.058 | -1.5591 | 114.5898 | 5496.9687 | -0.013606
222 |  | 0.63794 | 23.2961 | 4187 | 0.0087217 | 8.058 | 8.0667 | -1.5591 | 114.6567 | 5520.2648 | -0.013598
223 |  | 0.63794 | 23.2825 | 4187 | 0.0087166 | 8.0667 | 8.0754 | -1.5591 | 114.7236 | 5543.5473 | -0.01359
224 |  | 0.63794 | 23.2689 | 4187 | 0.0087115 | 8.0754 | 8.0841 | -1.5591 | 114.7907 | 5566.8162 | -0.013582
225 |  | 0.63794 | 23.2553 | 4187 | 0.0087064 | 8.0841 | 8.0928 | -1.5591 | 114.8577 | 5590.0715 | -0.013574
226 |  | 0.63794 | 23.2418 | 4187 | 0.0087013 | 8.0928 | 8.1015 | -1.5591 | 114.9248 | 5613.3132 | -0.013566
227 |  | 0.63794 | 23.2282 | 4187 | 0.0086963 | 8.1015 | 8.1102 | -1.5591 | 114.9919 | 5636.5414 | -0.013558
228 |  | 0.63794 | 23.2146 | 4187 | 0.0086912 | 8.1102 | 8.1189 | -1.5591 | 115.0591 | 5659.7561 | -0.01355
229 |  | 0.63794 | 23.2011 | 4187 | 0.0086861 | 8.1189 | 8.1276 | -1.5591 | 115.1263 | 5682.9571 | -0.013543
230 |  | 0.63794 | 23.1875 | 4187 | 0.008681 | 8.1276 | 8.1363 | -1.5591 | 115.1935 | 5706.1447 | -0.013535
231 |  | 0.63794 | 23.174 | 4187 | 0.008676 | 8.1363 | 8.145 | -1.5591 | 115.2608 | 5729.3187 | -0.013527
232 |  | 0.63794 | 23.1605 | 4187 | 0.0086709 | 8.145 | 8.1536 | -1.5591 | 115.3281 | 5752.4791 | -0.013519
233 |  | 0.63794 | 23.147 | 4187 | 0.0086659 | 8.1536 | 8.1623 | -1.5591 | 115.3954 | 5775.6261 | -0.013511
234 |  | 0.63794 | 23.1334 | 4187 | 0.0086608 | 8.1623 | 8.171 | -1.5591 | 115.4628 | 5798.7595 | -0.013503
235 |  | 0.63794 | 23.1199 | 4187 | 0.0086557 | 8.171 | 8.1796 | -1.5591 | 115.5303 | 5821.8795 | -0.013495
236 |  | 0.63794 | 23.1064 | 4187 | 0.0086507 | 8.1796 | 8.1883 | -1.5591 | 115.5978 | 5844.9859 | -0.013487

## St42
|  |  | buis | verlies W/M | L /°C/sec
diam | wandikte |  | inhoud l/m |  | W/M
42.4 | 2.6 | 3.1416 | 1.0869 | 33.3686 | 4187
[8 empty] | J/sec/mtr | aantal mtr. | verlies
|  | buis | verlies W/M | L /°C/sec | verlies temp | begintemp | eindtemp | verlies | bij 1°C | totaal J/sec
|  | inhoud L |  | W/M | °C per M | °C | °C | per m°C | daling | aantal mtr
1 | 42.4 | 1.0869 | 33.3686 | 4187 | 0.0073326 | 6 | 6.0073 | -1.9629 | 136.3768 | 33.3686 | -0.014393
2 |  | 1.0869 | 33.3542 | 4187 | 0.0073295 | 6.0073 | 6.0147 | -1.9629 | 136.4357 | 66.7228 | -0.014387
3 |  | 1.0869 | 33.3398 | 4187 | 0.0073263 | 6.0147 | 6.022 | -1.9629 | 136.4946 | 100.0627 | -0.01438
4 |  | 1.0869 | 33.3254 | 4187 | 0.0073231 | 6.022 | 6.0293 | -1.9629 | 136.5535 | 133.3881 | -0.014374
5 |  | 1.0869 | 33.3111 | 4187 | 0.00732 | 6.0293 | 6.0366 | -1.9629 | 136.6124 | 166.6992 | -0.014368
6 |  | 1.0869 | 33.2967 | 4187 | 0.0073168 | 6.0366 | 6.0439 | -1.9629 | 136.6713 | 199.9959 | -0.014362
7 |  | 1.0869 | 33.2823 | 4187 | 0.0073137 | 6.0439 | 6.0513 | -1.9629 | 136.7303 | 233.2782 | -0.014356
8 |  | 1.0869 | 33.268 | 4187 | 0.0073105 | 6.0513 | 6.0586 | -1.9629 | 136.7893 | 266.5462 | -0.01435
9 |  | 1.0869 | 33.2536 | 4187 | 0.0073074 | 6.0586 | 6.0659 | -1.9629 | 136.8483 | 299.7999 | -0.014343
10 |  | 1.0869 | 33.2393 | 4187 | 0.0073042 | 6.0659 | 6.0732 | -1.9629 | 136.9074 | 333.0391 | -0.014337
11 |  | 1.0869 | 33.225 | 4187 | 0.0073011 | 6.0732 | 6.0805 | -1.9629 | 136.9665 | 366.2641 | -0.014331
12 |  | 1.0869 | 33.2106 | 4187 | 0.0072979 | 6.0805 | 6.0878 | -1.9629 | 137.0256 | 399.4747 | -0.014325
13 |  | 1.0869 | 33.1963 | 4187 | 0.0072948 | 6.0878 | 6.0951 | -1.9629 | 137.0847 | 432.671 | -0.014319
14 |  | 1.0869 | 33.182 | 4187 | 0.0072916 | 6.0951 | 6.1024 | -1.9629 | 137.1439 | 465.853 | -0.014312
15 |  | 1.0869 | 33.1677 | 4187 | 0.0072885 | 6.1024 | 6.1097 | -1.9629 | 137.203 | 499.0207 | -0.014306
16 |  | 1.0869 | 33.1534 | 4187 | 0.0072853 | 6.1097 | 6.1169 | -1.9629 | 137.2622 | 532.1741 | -0.0143
17 |  | 1.0869 | 33.1391 | 4187 | 0.0072822 | 6.1169 | 6.1242 | -1.9629 | 137.3215 | 565.3131 | -0.014294
18 |  | 1.0869 | 33.1248 | 4187 | 0.007279 | 6.1242 | 6.1315 | -1.9629 | 137.3807 | 598.4379 | -0.014288
19 |  | 1.0869 | 33.1105 | 4187 | 0.0072759 | 6.1315 | 6.1388 | -1.9629 | 137.44 | 631.5484 | -0.014282
20 |  | 1.0869 | 33.0962 | 4187 | 0.0072728 | 6.1388 | 6.1461 | -1.9629 | 137.4993 | 664.6446 | -0.014275
21 |  | 1.0869 | 33.0819 | 4187 | 0.0072696 | 6.1461 | 6.1533 | -1.9629 | 137.5587 | 697.7265 | -0.014269
22 |  | 1.0869 | 33.0677 | 4187 | 0.0072665 | 6.1533 | 6.1606 | -1.9629 | 137.618 | 730.7942 | -0.014263
23 |  | 1.0869 | 33.0534 | 4187 | 0.0072634 | 6.1606 | 6.1679 | -1.9629 | 137.6774 | 763.8476 | -0.014257
24 |  | 1.0869 | 33.0391 | 4187 | 0.0072602 | 6.1679 | 6.1751 | -1.9629 | 137.7368 | 796.8867 | -0.014251
25 |  | 1.0869 | 33.0249 | 4187 | 0.0072571 | 6.1751 | 6.1824 | -1.9629 | 137.7962 | 829.9116 | -0.014245
26 |  | 1.0869 | 33.0106 | 4187 | 0.007254 | 6.1824 | 6.1896 | -1.9629 | 137.8557 | 862.9222 | -0.014239
27 |  | 1.0869 | 32.9964 | 4187 | 0.0072508 | 6.1896 | 6.1969 | -1.9629 | 137.9152 | 895.9186 | -0.014232
28 |  | 1.0869 | 32.9822 | 4187 | 0.0072477 | 6.1969 | 6.2041 | -1.9629 | 137.9747 | 928.9008 | -0.014226
29 |  | 1.0869 | 32.9679 | 4187 | 0.0072446 | 6.2041 | 6.2114 | -1.9629 | 138.0342 | 961.8687 | -0.01422
30 |  | 1.0869 | 32.9537 | 4187 | 0.0072415 | 6.2114 | 6.2186 | -1.9629 | 138.0938 | 994.8225 | -0.014214
31 |  | 1.0869 | 32.9395 | 4187 | 0.0072383 | 6.2186 | 6.2258 | -1.9629 | 138.1534 | 1027.762 | -0.014208
32 |  | 1.0869 | 32.9253 | 4187 | 0.0072352 | 6.2258 | 6.2331 | -1.9629 | 138.213 | 1060.6873 | -0.014202
33 |  | 1.0869 | 32.9111 | 4187 | 0.0072321 | 6.2331 | 6.2403 | -1.9629 | 138.2727 | 1093.5984 | -0.014196
34 |  | 1.0869 | 32.8969 | 4187 | 0.007229 | 6.2403 | 6.2475 | -1.9629 | 138.3323 | 1126.4953 | -0.014189
35 |  | 1.0869 | 32.8827 | 4187 | 0.0072259 | 6.2475 | 6.2548 | -1.9629 | 138.392 | 1159.378 | -0.014183
36 |  | 1.0869 | 32.8685 | 4187 | 0.0072227 | 6.2548 | 6.262 | -1.9629 | 138.4517 | 1192.2465 | -0.014177
37 |  | 1.0869 | 32.8544 | 4187 | 0.0072196 | 6.262 | 6.2692 | -1.9629 | 138.5115 | 1225.1009 | -0.014171
38 |  | 1.0869 | 32.8402 | 4187 | 0.0072165 | 6.2692 | 6.2764 | -1.9629 | 138.5712 | 1257.9411 | -0.014165
39 |  | 1.0869 | 32.826 | 4187 | 0.0072134 | 6.2764 | 6.2836 | -1.9629 | 138.631 | 1290.7671 | -0.014159
40 |  | 1.0869 | 32.8119 | 4187 | 0.0072103 | 6.2836 | 6.2909 | -1.9629 | 138.6909 | 1323.579 | -0.014153
41 |  | 1.0869 | 32.7977 | 4187 | 0.0072072 | 6.2909 | 6.2981 | -1.9629 | 138.7507 | 1356.3767 | -0.014147
42 |  | 1.0869 | 32.7836 | 4187 | 0.0072041 | 6.2981 | 6.3053 | -1.9629 | 138.8106 | 1389.1602 | -0.014141
43 |  | 1.0869 | 32.7694 | 4187 | 0.007201 | 6.3053 | 6.3125 | -1.9629 | 138.8705 | 1421.9296 | -0.014134
44 |  | 1.0869 | 32.7553 | 4187 | 0.0071978 | 6.3125 | 6.3197 | -1.9629 | 138.9304 | 1454.6849 | -0.014128
45 |  | 1.0869 | 32.7412 | 4187 | 0.0071947 | 6.3197 | 6.3269 | -1.9629 | 138.9904 | 1487.4261 | -0.014122
46 |  | 1.0869 | 32.727 | 4187 | 0.0071916 | 6.3269 | 6.334 | -1.9629 | 139.0503 | 1520.1531 | -0.014116
47 |  | 1.0869 | 32.7129 | 4187 | 0.0071885 | 6.334 | 6.3412 | -1.9629 | 139.1103 | 1552.866 | -0.01411
48 |  | 1.0869 | 32.6988 | 4187 | 0.0071854 | 6.3412 | 6.3484 | -1.9629 | 139.1704 | 1585.5648 | -0.014104
49 |  | 1.0869 | 32.6847 | 4187 | 0.0071823 | 6.3484 | 6.3556 | -1.9629 | 139.2304 | 1618.2496 | -0.014098
50 |  | 1.0869 | 32.6706 | 4187 | 0.0071792 | 6.3556 | 6.3628 | -1.9629 | 139.2905 | 1650.9202 | -0.014092
51 |  | 1.0869 | 32.6565 | 4187 | 0.0071761 | 6.3628 | 6.37 | -1.9629 | 139.3506 | 1683.5767 | -0.014086
52 |  | 1.0869 | 32.6424 | 4187 | 0.007173 | 6.37 | 6.3771 | -1.9629 | 139.4107 | 1716.2191 | -0.01408
53 |  | 1.0869 | 32.6284 | 4187 | 0.00717 | 6.3771 | 6.3843 | -1.9629 | 139.4709 | 1748.8475 | -0.014074
54 |  | 1.0869 | 32.6143 | 4187 | 0.0071669 | 6.3843 | 6.3915 | -1.9629 | 139.5311 | 1781.4617 | -0.014068
55 |  | 1.0869 | 32.6002 | 4187 | 0.0071638 | 6.3915 | 6.3986 | -1.9629 | 139.5913 | 1814.0619 | -0.014061
56 |  | 1.0869 | 32.5861 | 4187 | 0.0071607 | 6.3986 | 6.4058 | -1.9629 | 139.6515 | 1846.6481 | -0.014055
57 |  | 1.0869 | 32.5721 | 4187 | 0.0071576 | 6.4058 | 6.413 | -1.9629 | 139.7118 | 1879.2202 | -0.014049
58 |  | 1.0869 | 32.558 | 4187 | 0.0071545 | 6.413 | 6.4201 | -1.9629 | 139.7721 | 1911.7782 | -0.014043
59 |  | 1.0869 | 32.544 | 4187 | 0.0071514 | 6.4201 | 6.4273 | -1.9629 | 139.8324 | 1944.3222 | -0.014037
60 |  | 1.0869 | 32.53 | 4187 | 0.0071483 | 6.4273 | 6.4344 | -1.9629 | 139.8927 | 1976.8522 | -0.014031
61 |  | 1.0869 | 32.5159 | 4187 | 0.0071453 | 6.4344 | 6.4416 | -1.9629 | 139.9531 | 2009.3681 | -0.014025
62 |  | 1.0869 | 32.5019 | 4187 | 0.0071422 | 6.4416 | 6.4487 | -1.9629 | 140.0135 | 2041.87 | -0.014019
63 |  | 1.0869 | 32.4879 | 4187 | 0.0071391 | 6.4487 | 6.4558 | -1.9629 | 140.0739 | 2074.3579 | -0.014013
64 |  | 1.0869 | 32.4739 | 4187 | 0.007136 | 6.4558 | 6.463 | -1.9629 | 140.1344 | 2106.8318 | -0.014007
65 |  | 1.0869 | 32.4599 | 4187 | 0.0071329 | 6.463 | 6.4701 | -1.9629 | 140.1948 | 2139.2916 | -0.014001
66 |  | 1.0869 | 32.4459 | 4187 | 0.0071299 | 6.4701 | 6.4772 | -1.9629 | 140.2553 | 2171.7375 | -0.013995
67 |  | 1.0869 | 32.4319 | 4187 | 0.0071268 | 6.4772 | 6.4844 | -1.9629 | 140.3158 | 2204.1694 | -0.013989
68 |  | 1.0869 | 32.4179 | 4187 | 0.0071237 | 6.4844 | 6.4915 | -1.9629 | 140.3764 | 2236.5873 | -0.013983
69 |  | 1.0869 | 32.4039 | 4187 | 0.0071206 | 6.4915 | 6.4986 | -1.9629 | 140.437 | 2268.9912 | -0.013977
70 |  | 1.0869 | 32.3899 | 4187 | 0.0071176 | 6.4986 | 6.5057 | -1.9629 | 140.4976 | 2301.3811 | -0.013971
71 |  | 1.0869 | 32.376 | 4187 | 0.0071145 | 6.5057 | 6.5128 | -1.9629 | 140.5582 | 2333.757 | -0.013965
72 |  | 1.0869 | 32.362 | 4187 | 0.0071114 | 6.5128 | 6.5199 | -1.9629 | 140.6189 | 2366.119 | -0.013959
73 |  | 1.0869 | 32.348 | 4187 | 0.0071084 | 6.5199 | 6.5271 | -1.9629 | 140.6795 | 2398.4671 | -0.013953
74 |  | 1.0869 | 32.3341 | 4187 | 0.0071053 | 6.5271 | 6.5342 | -1.9629 | 140.7402 | 2430.8011 | -0.013947
75 |  | 1.0869 | 32.3201 | 4187 | 0.0071022 | 6.5342 | 6.5413 | -1.9629 | 140.801 | 2463.1213 | -0.013941
76 |  | 1.0869 | 32.3062 | 4187 | 0.0070992 | 6.5413 | 6.5484 | -1.9629 | 140.8617 | 2495.4274 | -0.013935
77 |  | 1.0869 | 32.2923 | 4187 | 0.0070961 | 6.5484 | 6.5555 | -1.9629 | 140.9225 | 2527.7197 | -0.013929
78 |  | 1.0869 | 32.2783 | 4187 | 0.007093 | 6.5555 | 6.5625 | -1.9629 | 140.9833 | 2559.998 | -0.013923
79 |  | 1.0869 | 32.2644 | 4187 | 0.00709 | 6.5625 | 6.5696 | -1.9629 | 141.0442 | 2592.2624 | -0.013917
80 |  | 1.0869 | 32.2505 | 4187 | 0.0070869 | 6.5696 | 6.5767 | -1.9629 | 141.105 | 2624.5129 | -0.013911
81 |  | 1.0869 | 32.2366 | 4187 | 0.0070839 | 6.5767 | 6.5838 | -1.9629 | 141.1659 | 2656.7495 | -0.013905
82 |  | 1.0869 | 32.2227 | 4187 | 0.0070808 | 6.5838 | 6.5909 | -1.9629 | 141.2268 | 2688.9722 | -0.013899
83 |  | 1.0869 | 32.2088 | 4187 | 0.0070778 | 6.5909 | 6.598 | -1.9629 | 141.2878 | 2721.1809 | -0.013893
84 |  | 1.0869 | 32.1949 | 4187 | 0.0070747 | 6.598 | 6.605 | -1.9629 | 141.3487 | 2753.3758 | -0.013887
85 |  | 1.0869 | 32.181 | 4187 | 0.0070716 | 6.605 | 6.6121 | -1.9629 | 141.4097 | 2785.5568 | -0.013881
86 |  | 1.0869 | 32.1671 | 4187 | 0.0070686 | 6.6121 | 6.6192 | -1.9629 | 141.4707 | 2817.7239 | -0.013875
87 |  | 1.0869 | 32.1532 | 4187 | 0.0070656 | 6.6192 | 6.6262 | -1.9629 | 141.5318 | 2849.8772 | -0.013869
88 |  | 1.0869 | 32.1394 | 4187 | 0.0070625 | 6.6262 | 6.6333 | -1.9629 | 141.5929 | 2882.0165 | -0.013863
89 |  | 1.0869 | 32.1255 | 4187 | 0.0070595 | 6.6333 | 6.6404 | -1.9629 | 141.654 | 2914.142 | -0.013857
90 |  | 1.0869 | 32.1116 | 4187 | 0.0070564 | 6.6404 | 6.6474 | -1.9629 | 141.7151 | 2946.2537 | -0.013851
91 |  | 1.0869 | 32.0978 | 4187 | 0.0070534 | 6.6474 | 6.6545 | -1.9629 | 141.7762 | 2978.3515 | -0.013845
92 |  | 1.0869 | 32.084 | 4187 | 0.0070503 | 6.6545 | 6.6615 | -1.9629 | 141.8374 | 3010.4354 | -0.013839
93 |  | 1.0869 | 32.0701 | 4187 | 0.0070473 | 6.6615 | 6.6686 | -1.9629 | 141.8986 | 3042.5055 | -0.013833
94 |  | 1.0869 | 32.0563 | 4187 | 0.0070442 | 6.6686 | 6.6756 | -1.9629 | 141.9599 | 3074.5618 | -0.013827
95 |  | 1.0869 | 32.0425 | 4187 | 0.0070412 | 6.6756 | 6.6827 | -1.9629 | 142.0211 | 3106.6043 | -0.013821
96 |  | 1.0869 | 32.0286 | 4187 | 0.0070382 | 6.6827 | 6.6897 | -1.9629 | 142.0824 | 3138.6329 | -0.013815
97 |  | 1.0869 | 32.0148 | 4187 | 0.0070351 | 6.6897 | 6.6967 | -1.9629 | 142.1437 | 3170.6477 | -0.013809
98 |  | 1.0869 | 32.001 | 4187 | 0.0070321 | 6.6967 | 6.7038 | -1.9629 | 142.2051 | 3202.6487 | -0.013803
99 |  | 1.0869 | 31.9872 | 4187 | 0.0070291 | 6.7038 | 6.7108 | -1.9629 | 142.2664 | 3234.636 | -0.013797
100 |  | 1.0869 | 31.9734 | 4187 | 0.007026 | 6.7108 | 6.7178 | -1.9629 | 142.3278 | 3266.6094 | -0.013791
101 |  | 1.0869 | 31.9596 | 4187 | 0.007023 | 6.7178 | 6.7248 | -1.9629 | 142.3892 | 3298.569 | -0.013785
102 |  | 1.0869 | 31.9458 | 4187 | 0.00702 | 6.7248 | 6.7319 | -1.9629 | 142.4507 | 3330.5148 | -0.013779
103 |  | 1.0869 | 31.9321 | 4187 | 0.0070169 | 6.7319 | 6.7389 | -1.9629 | 142.5121 | 3362.4469 | -0.013773
104 |  | 1.0869 | 31.9183 | 4187 | 0.0070139 | 6.7389 | 6.7459 | -1.9629 | 142.5736 | 3394.3651 | -0.013767
105 |  | 1.0869 | 31.9045 | 4187 | 0.0070109 | 6.7459 | 6.7529 | -1.9629 | 142.6352 | 3426.2697 | -0.013761
106 |  | 1.0869 | 31.8908 | 4187 | 0.0070079 | 6.7529 | 6.7599 | -1.9629 | 142.6967 | 3458.1604 | -0.013755
107 |  | 1.0869 | 31.877 | 4187 | 0.0070048 | 6.7599 | 6.7669 | -1.9629 | 142.7583 | 3490.0374 | -0.01375
108 |  | 1.0869 | 31.8632 | 4187 | 0.0070018 | 6.7669 | 6.7739 | -1.9629 | 142.8199 | 3521.9007 | -0.013744
109 |  | 1.0869 | 31.8495 | 4187 | 0.0069988 | 6.7739 | 6.7809 | -1.9629 | 142.8815 | 3553.7502 | -0.013738
110 |  | 1.0869 | 31.8358 | 4187 | 0.0069958 | 6.7809 | 6.7879 | -1.9629 | 142.9432 | 3585.5859 | -0.013732
111 |  | 1.0869 | 31.822 | 4187 | 0.0069928 | 6.7879 | 6.7949 | -1.9629 | 143.0049 | 3617.408 | -0.013726
112 |  | 1.0869 | 31.8083 | 4187 | 0.0069898 | 6.7949 | 6.8019 | -1.9629 | 143.0666 | 3649.2163 | -0.01372
113 |  | 1.0869 | 31.7946 | 4187 | 0.0069867 | 6.8019 | 6.8089 | -1.9629 | 143.1283 | 3681.0109 | -0.013714
114 |  | 1.0869 | 31.7809 | 4187 | 0.0069837 | 6.8089 | 6.8159 | -1.9629 | 143.1901 | 3712.7917 | -0.013708
115 |  | 1.0869 | 31.7672 | 4187 | 0.0069807 | 6.8159 | 6.8229 | -1.9629 | 143.2518 | 3744.5589 | -0.013702
116 |  | 1.0869 | 31.7535 | 4187 | 0.0069777 | 6.8229 | 6.8298 | -1.9629 | 143.3137 | 3776.3124 | -0.013696
117 |  | 1.0869 | 31.7398 | 4187 | 0.0069747 | 6.8298 | 6.8368 | -1.9629 | 143.3755 | 3808.0521 | -0.01369
118 |  | 1.0869 | 31.7261 | 4187 | 0.0069717 | 6.8368 | 6.8438 | -1.9629 | 143.4374 | 3839.7782 | -0.013684
119 |  | 1.0869 | 31.7124 | 4187 | 0.0069687 | 6.8438 | 6.8507 | -1.9629 | 143.4993 | 3871.4906 | -0.013679
120 |  | 1.0869 | 31.6987 | 4187 | 0.0069657 | 6.8507 | 6.8577 | -1.9629 | 143.5612 | 3903.1893 | -0.013673
121 |  | 1.0869 | 31.685 | 4187 | 0.0069627 | 6.8577 | 6.8647 | -1.9629 | 143.6231 | 3934.8744 | -0.013667
122 |  | 1.0869 | 31.6714 | 4187 | 0.0069597 | 6.8647 | 6.8716 | -1.9629 | 143.6851 | 3966.5457 | -0.013661
123 |  | 1.0869 | 31.6577 | 4187 | 0.0069567 | 6.8716 | 6.8786 | -1.9629 | 143.7471 | 3998.2035 | -0.013655
124 |  | 1.0869 | 31.6441 | 4187 | 0.0069537 | 6.8786 | 6.8855 | -1.9629 | 143.8092 | 4029.8475 | -0.013649
125 |  | 1.0869 | 31.6304 | 4187 | 0.0069507 | 6.8855 | 6.8925 | -1.9629 | 143.8712 | 4061.4779 | -0.013643
126 |  | 1.0869 | 31.6168 | 4187 | 0.0069477 | 6.8925 | 6.8994 | -1.9629 | 143.9333 | 4093.0947 | -0.013637
127 |  | 1.0869 | 31.6031 | 4187 | 0.0069447 | 6.8994 | 6.9064 | -1.9629 | 143.9954 | 4124.6978 | -0.013631
128 |  | 1.0869 | 31.5895 | 4187 | 0.0069417 | 6.9064 | 6.9133 | -1.9629 | 144.0575 | 4156.2873 | -0.013626
129 |  | 1.0869 | 31.5759 | 4187 | 0.0069387 | 6.9133 | 6.9203 | -1.9629 | 144.1197 | 4187.8632 | -0.01362
130 |  | 1.0869 | 31.5623 | 4187 | 0.0069357 | 6.9203 | 6.9272 | -1.9629 | 144.1819 | 4219.4255 | -0.013614
131 |  | 1.0869 | 31.5486 | 4187 | 0.0069327 | 6.9272 | 6.9341 | -1.9629 | 144.2441 | 4250.9741 | -0.013608
132 |  | 1.0869 | 31.535 | 4187 | 0.0069297 | 6.9341 | 6.9411 | -1.9629 | 144.3064 | 4282.5091 | -0.013602
133 |  | 1.0869 | 31.5214 | 4187 | 0.0069267 | 6.9411 | 6.948 | -1.9629 | 144.3686 | 4314.0306 | -0.013596
134 |  | 1.0869 | 31.5078 | 4187 | 0.0069237 | 6.948 | 6.9549 | -1.9629 | 144.4309 | 4345.5384 | -0.01359
135 |  | 1.0869 | 31.4942 | 4187 | 0.0069207 | 6.9549 | 6.9618 | -1.9629 | 144.4932 | 4377.0326 | -0.013584
136 |  | 1.0869 | 31.4807 | 4187 | 0.0069178 | 6.9618 | 6.9688 | -1.9629 | 144.5556 | 4408.5133 | -0.013579
137 |  | 1.0869 | 31.4671 | 4187 | 0.0069148 | 6.9688 | 6.9757 | -1.9629 | 144.618 | 4439.9804 | -0.013573
138 |  | 1.0869 | 31.4535 | 4187 | 0.0069118 | 6.9757 | 6.9826 | -1.9629 | 144.6804 | 4471.4339 | -0.013567
139 |  | 1.0869 | 31.4399 | 4187 | 0.0069088 | 6.9826 | 6.9895 | -1.9629 | 144.7428 | 4502.8738 | -0.013561
140 |  | 1.0869 | 31.4264 | 4187 | 0.0069058 | 6.9895 | 6.9964 | -1.9629 | 144.8053 | 4534.3002 | -0.013555
141 |  | 1.0869 | 31.4128 | 4187 | 0.0069028 | 6.9964 | 7.0033 | -1.9629 | 144.8678 | 4565.713 | -0.013549
142 |  | 1.0869 | 31.3993 | 4187 | 0.0068999 | 7.0033 | 7.0102 | -1.9629 | 144.9303 | 4597.1123 | -0.013543
143 |  | 1.0869 | 31.3857 | 4187 | 0.0068969 | 7.0102 | 7.0171 | -1.9629 | 144.9928 | 4628.498 | -0.013538
144 |  | 1.0869 | 31.3722 | 4187 | 0.0068939 | 7.0171 | 7.024 | -1.9629 | 145.0554 | 4659.8702 | -0.013532
145 |  | 1.0869 | 31.3587 | 4187 | 0.0068909 | 7.024 | 7.0309 | -1.9629 | 145.118 | 4691.2289 | -0.013526
146 |  | 1.0869 | 31.3451 | 4187 | 0.006888 | 7.0309 | 7.0378 | -1.9629 | 145.1806 | 4722.574 | -0.01352
147 |  | 1.0869 | 31.3316 | 4187 | 0.006885 | 7.0378 | 7.0447 | -1.9629 | 145.2432 | 4753.9056 | -0.013514
148 |  | 1.0869 | 31.3181 | 4187 | 0.006882 | 7.0447 | 7.0515 | -1.9629 | 145.3059 | 4785.2237 | -0.013508
149 |  | 1.0869 | 31.3046 | 4187 | 0.0068791 | 7.0515 | 7.0584 | -1.9629 | 145.3686 | 4816.5283 | -0.013503
150 |  | 1.0869 | 31.2911 | 4187 | 0.0068761 | 7.0584 | 7.0653 | -1.9629 | 145.4313 | 4847.8194 | -0.013497
151 |  | 1.0869 | 31.2776 | 4187 | 0.0068731 | 7.0653 | 7.0722 | -1.9629 | 145.4941 | 4879.097 | -0.013491
152 |  | 1.0869 | 31.2641 | 4187 | 0.0068702 | 7.0722 | 7.079 | -1.9629 | 145.5569 | 4910.3611 | -0.013485
153 |  | 1.0869 | 31.2506 | 4187 | 0.0068672 | 7.079 | 7.0859 | -1.9629 | 145.6197 | 4941.6118 | -0.013479
154 |  | 1.0869 | 31.2371 | 4187 | 0.0068642 | 7.0859 | 7.0928 | -1.9629 | 145.6825 | 4972.8489 | -0.013474
155 |  | 1.0869 | 31.2237 | 4187 | 0.0068613 | 7.0928 | 7.0996 | -1.9629 | 145.7454 | 5004.0726 | -0.013468
156 |  | 1.0869 | 31.2102 | 4187 | 0.0068583 | 7.0996 | 7.1065 | -1.9629 | 145.8083 | 5035.2828 | -0.013462
157 |  | 1.0869 | 31.1967 | 4187 | 0.0068554 | 7.1065 | 7.1133 | -1.9629 | 145.8712 | 5066.4795 | -0.013456
158 |  | 1.0869 | 31.1833 | 4187 | 0.0068524 | 7.1133 | 7.1202 | -1.9629 | 145.9341 | 5097.6628 | -0.01345
159 |  | 1.0869 | 31.1698 | 4187 | 0.0068495 | 7.1202 | 7.127 | -1.9629 | 145.9971 | 5128.8326 | -0.013445
160 |  | 1.0869 | 31.1564 | 4187 | 0.0068465 | 7.127 | 7.1339 | -1.9629 | 146.0601 | 5159.989 | -0.013439
161 |  | 1.0869 | 31.1429 | 4187 | 0.0068435 | 7.1339 | 7.1407 | -1.9629 | 146.1232 | 5191.1319 | -0.013433
162 |  | 1.0869 | 31.1295 | 4187 | 0.0068406 | 7.1407 | 7.1476 | -1.9629 | 146.1862 | 5222.2614 | -0.013427
163 |  | 1.0869 | 31.1161 | 4187 | 0.0068376 | 7.1476 | 7.1544 | -1.9629 | 146.2493 | 5253.3775 | -0.013421
164 |  | 1.0869 | 31.1027 | 4187 | 0.0068347 | 7.1544 | 7.1612 | -1.9629 | 146.3124 | 5284.4802 | -0.013416
165 |  | 1.0869 | 31.0892 | 4187 | 0.0068317 | 7.1612 | 7.1681 | -1.9629 | 146.3755 | 5315.5694 | -0.01341
166 |  | 1.0869 | 31.0758 | 4187 | 0.0068288 | 7.1681 | 7.1749 | -1.9629 | 146.4387 | 5346.6453 | -0.013404
167 |  | 1.0869 | 31.0624 | 4187 | 0.0068259 | 7.1749 | 7.1817 | -1.9629 | 146.5019 | 5377.7077 | -0.013398
168 |  | 1.0869 | 31.049 | 4187 | 0.0068229 | 7.1817 | 7.1886 | -1.9629 | 146.5651 | 5408.7568 | -0.013392
169 |  | 1.0869 | 31.0356 | 4187 | 0.00682 | 7.1886 | 7.1954 | -1.9629 | 146.6284 | 5439.7924 | -0.013387
170 |  | 1.0869 | 31.0223 | 4187 | 0.006817 | 7.1954 | 7.2022 | -1.9629 | 146.6916 | 5470.8147 | -0.013381
171 |  | 1.0869 | 31.0089 | 4187 | 0.0068141 | 7.2022 | 7.209 | -1.9629 | 146.7549 | 5501.8235 | -0.013375
172 |  | 1.0869 | 30.9955 | 4187 | 0.0068111 | 7.209 | 7.2158 | -1.9629 | 146.8182 | 5532.819 | -0.013369
173 |  | 1.0869 | 30.9821 | 4187 | 0.0068082 | 7.2158 | 7.2226 | -1.9629 | 146.8816 | 5563.8012 | -0.013364
174 |  | 1.0869 | 30.9688 | 4187 | 0.0068053 | 7.2226 | 7.2294 | -1.9629 | 146.945 | 5594.7699 | -0.013358
175 |  | 1.0869 | 30.9554 | 4187 | 0.0068023 | 7.2294 | 7.2362 | -1.9629 | 147.0084 | 5625.7254 | -0.013352
176 |  | 1.0869 | 30.9421 | 4187 | 0.0067994 | 7.2362 | 7.243 | -1.9629 | 147.0718 | 5656.6674 | -0.013346
177 |  | 1.0869 | 30.9287 | 4187 | 0.0067965 | 7.243 | 7.2498 | -1.9629 | 147.1353 | 5687.5961 | -0.013341
178 |  | 1.0869 | 30.9154 | 4187 | 0.0067935 | 7.2498 | 7.2566 | -1.9629 | 147.1988 | 5718.5115 | -0.013335
179 |  | 1.0869 | 30.902 | 4187 | 0.0067906 | 7.2566 | 7.2634 | -1.9629 | 147.2623 | 5749.4135 | -0.013329
180 |  | 1.0869 | 30.8887 | 4187 | 0.0067877 | 7.2634 | 7.2702 | -1.9629 | 147.3259 | 5780.3022 | -0.013323
181 |  | 1.0869 | 30.8754 | 4187 | 0.0067847 | 7.2702 | 7.277 | -1.9629 | 147.3894 | 5811.1776 | -0.013318
182 |  | 1.0869 | 30.8621 | 4187 | 0.0067818 | 7.277 | 7.2838 | -1.9629 | 147.453 | 5842.0397 | -0.013312
183 |  | 1.0869 | 30.8488 | 4187 | 0.0067789 | 7.2838 | 7.2905 | -1.9629 | 147.5167 | 5872.8885 | -0.013306
184 |  | 1.0869 | 30.8355 | 4187 | 0.006776 | 7.2905 | 7.2973 | -1.9629 | 147.5803 | 5903.7239 | -0.0133
185 |  | 1.0869 | 30.8222 | 4187 | 0.006773 | 7.2973 | 7.3041 | -1.9629 | 147.644 | 5934.5461 | -0.013295
186 |  | 1.0869 | 30.8089 | 4187 | 0.0067701 | 7.3041 | 7.3109 | -1.9629 | 147.7077 | 5965.3549 | -0.013289
187 |  | 1.0869 | 30.7956 | 4187 | 0.0067672 | 7.3109 | 7.3176 | -1.9629 | 147.7714 | 5996.1505 | -0.013283
188 |  | 1.0869 | 30.7823 | 4187 | 0.0067643 | 7.3176 | 7.3244 | -1.9629 | 147.8352 | 6026.9328 | -0.013277
189 |  | 1.0869 | 30.769 | 4187 | 0.0067614 | 7.3244 | 7.3312 | -1.9629 | 147.899 | 6057.7018 | -0.013272
190 |  | 1.0869 | 30.7557 | 4187 | 0.0067585 | 7.3312 | 7.3379 | -1.9629 | 147.9628 | 6088.4575 | -0.013266
191 |  | 1.0869 | 30.7425 | 4187 | 0.0067555 | 7.3379 | 7.3447 | -1.9629 | 148.0267 | 6119.2 | -0.01326
192 |  | 1.0869 | 30.7292 | 4187 | 0.0067526 | 7.3447 | 7.3514 | -1.9629 | 148.0905 | 6149.9292 | -0.013254
193 |  | 1.0869 | 30.716 | 4187 | 0.0067497 | 7.3514 | 7.3582 | -1.9629 | 148.1545 | 6180.6451 | -0.013249
194 |  | 1.0869 | 30.7027 | 4187 | 0.0067468 | 7.3582 | 7.3649 | -1.9629 | 148.2184 | 6211.3478 | -0.013243
195 |  | 1.0869 | 30.6895 | 4187 | 0.0067439 | 7.3649 | 7.3717 | -1.9629 | 148.2823 | 6242.0373 | -0.013237
196 |  | 1.0869 | 30.6762 | 4187 | 0.006741 | 7.3717 | 7.3784 | -1.9629 | 148.3463 | 6272.7135 | -0.013232
197 |  | 1.0869 | 30.663 | 4187 | 0.0067381 | 7.3784 | 7.3851 | -1.9629 | 148.4103 | 6303.3765 | -0.013226
198 |  | 1.0869 | 30.6498 | 4187 | 0.0067352 | 7.3851 | 7.3919 | -1.9629 | 148.4744 | 6334.0263 | -0.01322
199 |  | 1.0869 | 30.6365 | 4187 | 0.0067323 | 7.3919 | 7.3986 | -1.9629 | 148.5385 | 6364.6628 | -0.013214
200 |  | 1.0869 | 30.6233 | 4187 | 0.0067294 | 7.3986 | 7.4053 | -1.9629 | 148.6026 | 6395.2862 | -0.013209
201 |  | 1.0869 | 30.6101 | 4187 | 0.0067265 | 7.4053 | 7.4121 | -1.9629 | 148.6667 | 6425.8963 | -0.013203
202 |  | 1.0869 | 30.5969 | 4187 | 0.0067236 | 7.4121 | 7.4188 | -1.9629 | 148.7308 | 6456.4932 | -0.013197
203 |  | 1.0869 | 30.5837 | 4187 | 0.0067207 | 7.4188 | 7.4255 | -1.9629 | 148.795 | 6487.0769 | -0.013192
204 |  | 1.0869 | 30.5705 | 4187 | 0.0067178 | 7.4255 | 7.4322 | -1.9629 | 148.8592 | 6517.6475 | -0.013186
205 |  | 1.0869 | 30.5573 | 4187 | 0.0067149 | 7.4322 | 7.4389 | -1.9629 | 148.9234 | 6548.2048 | -0.01318
206 |  | 1.0869 | 30.5442 | 4187 | 0.006712 | 7.4389 | 7.4457 | -1.9629 | 148.9877 | 6578.749 | -0.013175
207 |  | 1.0869 | 30.531 | 4187 | 0.0067091 | 7.4457 | 7.4524 | -1.9629 | 149.052 | 6609.28 | -0.013169
208 |  | 1.0869 | 30.5178 | 4187 | 0.0067062 | 7.4524 | 7.4591 | -1.9629 | 149.1163 | 6639.7978 | -0.013163
209 |  | 1.0869 | 30.5047 | 4187 | 0.0067033 | 7.4591 | 7.4658 | -1.9629 | 149.1807 | 6670.3025 | -0.013158
210 |  | 1.0869 | 30.4915 | 4187 | 0.0067004 | 7.4658 | 7.4725 | -1.9629 | 149.245 | 6700.794 | -0.013152
211 |  | 1.0869 | 30.4783 | 4187 | 0.0066975 | 7.4725 | 7.4792 | -1.9629 | 149.3094 | 6731.2723 | -0.013146
212 |  | 1.0869 | 30.4652 | 4187 | 0.0066946 | 7.4792 | 7.4859 | -1.9629 | 149.3739 | 6761.7375 | -0.013141
213 |  | 1.0869 | 30.4521 | 4187 | 0.0066917 | 7.4859 | 7.4926 | -1.9629 | 149.4383 | 6792.1896 | -0.013135
214 |  | 1.0869 | 30.4389 | 4187 | 0.0066888 | 7.4926 | 7.4992 | -1.9629 | 149.5028 | 6822.6285 | -0.013129
215 |  | 1.0869 | 30.4258 | 4187 | 0.006686 | 7.4992 | 7.5059 | -1.9629 | 149.5673 | 6853.0543 | -0.013124
216 |  | 1.0869 | 30.4127 | 4187 | 0.0066831 | 7.5059 | 7.5126 | -1.9629 | 149.6319 | 6883.467 | -0.013118
217 |  | 1.0869 | 30.3996 | 4187 | 0.0066802 | 7.5126 | 7.5193 | -1.9629 | 149.6964 | 6913.8665 | -0.013112
218 |  | 1.0869 | 30.3864 | 4187 | 0.0066773 | 7.5193 | 7.526 | -1.9629 | 149.761 | 6944.253 | -0.013107
219 |  | 1.0869 | 30.3733 | 4187 | 0.0066744 | 7.526 | 7.5326 | -1.9629 | 149.8257 | 6974.6263 | -0.013101
220 |  | 1.0869 | 30.3602 | 4187 | 0.0066715 | 7.5326 | 7.5393 | -1.9629 | 149.8903 | 7004.9866 | -0.013095
221 |  | 1.0869 | 30.3471 | 4187 | 0.0066687 | 7.5393 | 7.546 | -1.9629 | 149.955 | 7035.3337 | -0.01309
222 |  | 1.0869 | 30.3341 | 4187 | 0.0066658 | 7.546 | 7.5527 | -1.9629 | 150.0197 | 7065.6677 | -0.013084
223 |  | 1.0869 | 30.321 | 4187 | 0.0066629 | 7.5527 | 7.5593 | -1.9629 | 150.0844 | 7095.9887 | -0.013078
224 |  | 1.0869 | 30.3079 | 4187 | 0.00666 | 7.5593 | 7.566 | -1.9629 | 150.1492 | 7126.2966 | -0.013073
225 |  | 1.0869 | 30.2948 | 4187 | 0.0066572 | 7.566 | 7.5726 | -1.9629 | 150.214 | 7156.5914 | -0.013067
226 |  | 1.0869 | 30.2818 | 4187 | 0.0066543 | 7.5726 | 7.5793 | -1.9629 | 150.2788 | 7186.8732 | -0.013061
227 |  | 1.0869 | 30.2687 | 4187 | 0.0066514 | 7.5793 | 7.5859 | -1.9629 | 150.3437 | 7217.1419 | -0.013056
228 |  | 1.0869 | 30.2556 | 4187 | 0.0066486 | 7.5859 | 7.5926 | -1.9629 | 150.4085 | 7247.3975 | -0.01305
229 |  | 1.0869 | 30.2426 | 4187 | 0.0066457 | 7.5926 | 7.5992 | -1.9629 | 150.4734 | 7277.6401 | -0.013045
230 |  | 1.0869 | 30.2295 | 4187 | 0.0066428 | 7.5992 | 7.6059 | -1.9629 | 150.5384 | 7307.8696 | -0.013039
231 |  | 1.0869 | 30.2165 | 4187 | 0.00664 | 7.6059 | 7.6125 | -1.9629 | 150.6033 | 7338.0861 | -0.013033
232 |  | 1.0869 | 30.2035 | 4187 | 0.0066371 | 7.6125 | 7.6192 | -1.9629 | 150.6683 | 7368.2896 | -0.013028
233 |  | 1.0869 | 30.1904 | 4187 | 0.0066342 | 7.6192 | 7.6258 | -1.9629 | 150.7333 | 7398.48 | -0.013022
234 |  | 1.0869 | 30.1774 | 4187 | 0.0066314 | 7.6258 | 7.6324 | -1.9629 | 150.7984 | 7428.6574 | -0.013016
235 |  | 1.0869 | 30.1644 | 4187 | 0.0066285 | 7.6324 | 7.639 | -1.9629 | 150.8635 | 7458.8218 | -0.013011
236 |  | 1.0869 | 30.1514 | 4187 | 0.0066257 | 7.639 | 7.6457 | -1.9629 | 150.9286 | 7488.9732 | -0.013005

## St48
|  |  | buis | verlies W/M | L /°C/sec
diam | wandikte |  | inhoud l/m |  | W/M
48.3 | 2.6 | 3.1416 | 1.459 | 38.0229 | 4187
[8 empty] | J/sec/mtr | aantal mtr. | verlies
|  | buis | verlies W/M | L /°C/sec | verlies temp | begintemp | eindtemp | verlies | bij 1°C | totaal J/sec
|  | inhoud L |  | W/M | °C per M | °C | °C | per m°C | daling | aantal mtr
1 | 48.3 | 1.459 | 38.0229 | 4187 | 0.0062244 | 6 | 6.0062 | -2.2366 | 160.6581 | 38.0229 | -0.013922
2 |  | 1.459 | 38.0089 | 4187 | 0.0062221 | 6.0062 | 6.0124 | -2.2366 | 160.7169 | 76.0318 | -0.013917
3 |  | 1.459 | 37.995 | 4187 | 0.0062198 | 6.0124 | 6.0187 | -2.2366 | 160.7758 | 114.0268 | -0.013912
4 |  | 1.459 | 37.9811 | 4187 | 0.0062176 | 6.0187 | 6.0249 | -2.2366 | 160.8347 | 152.0079 | -0.013906
5 |  | 1.459 | 37.9672 | 4187 | 0.0062153 | 6.0249 | 6.0311 | -2.2366 | 160.8936 | 189.9751 | -0.013901
6 |  | 1.459 | 37.9533 | 4187 | 0.006213 | 6.0311 | 6.0373 | -2.2366 | 160.9525 | 227.9284 | -0.013896
7 |  | 1.459 | 37.9394 | 4187 | 0.0062107 | 6.0373 | 6.0435 | -2.2366 | 161.0115 | 265.8678 | -0.013891
8 |  | 1.459 | 37.9255 | 4187 | 0.0062085 | 6.0435 | 6.0497 | -2.2366 | 161.0705 | 303.7934 | -0.013886
9 |  | 1.459 | 37.9116 | 4187 | 0.0062062 | 6.0497 | 6.0559 | -2.2366 | 161.1295 | 341.705 | -0.013881
10 |  | 1.459 | 37.8977 | 4187 | 0.0062039 | 6.0559 | 6.0621 | -2.2366 | 161.1885 | 379.6027 | -0.013876
11 |  | 1.459 | 37.8839 | 4187 | 0.0062016 | 6.0621 | 6.0683 | -2.2366 | 161.2475 | 417.4866 | -0.013871
12 |  | 1.459 | 37.87 | 4187 | 0.0061994 | 6.0683 | 6.0745 | -2.2366 | 161.3066 | 455.3566 | -0.013866
13 |  | 1.459 | 37.8561 | 4187 | 0.0061971 | 6.0745 | 6.0807 | -2.2366 | 161.3657 | 493.2127 | -0.013861
14 |  | 1.459 | 37.8423 | 4187 | 0.0061948 | 6.0807 | 6.0869 | -2.2366 | 161.4248 | 531.055 | -0.013856
15 |  | 1.459 | 37.8284 | 4187 | 0.0061926 | 6.0869 | 6.0931 | -2.2366 | 161.4839 | 568.8834 | -0.013851
16 |  | 1.459 | 37.8146 | 4187 | 0.0061903 | 6.0931 | 6.0993 | -2.2366 | 161.543 | 606.698 | -0.013845
17 |  | 1.459 | 37.8007 | 4187 | 0.006188 | 6.0993 | 6.1055 | -2.2366 | 161.6022 | 644.4987 | -0.01384
18 |  | 1.459 | 37.7869 | 4187 | 0.0061858 | 6.1055 | 6.1117 | -2.2366 | 161.6614 | 682.2856 | -0.013835
19 |  | 1.459 | 37.773 | 4187 | 0.0061835 | 6.1117 | 6.1179 | -2.2366 | 161.7206 | 720.0586 | -0.01383
20 |  | 1.459 | 37.7592 | 4187 | 0.0061812 | 6.1179 | 6.1241 | -2.2366 | 161.7798 | 757.8179 | -0.013825
21 |  | 1.459 | 37.7454 | 4187 | 0.006179 | 6.1241 | 6.1302 | -2.2366 | 161.8391 | 795.5633 | -0.01382
22 |  | 1.459 | 37.7316 | 4187 | 0.0061767 | 6.1302 | 6.1364 | -2.2366 | 161.8984 | 833.2948 | -0.013815
23 |  | 1.459 | 37.7178 | 4187 | 0.0061745 | 6.1364 | 6.1426 | -2.2366 | 161.9577 | 871.0126 | -0.01381
24 |  | 1.459 | 37.7039 | 4187 | 0.0061722 | 6.1426 | 6.1488 | -2.2366 | 162.017 | 908.7165 | -0.013805
25 |  | 1.459 | 37.6901 | 4187 | 0.0061699 | 6.1488 | 6.1549 | -2.2366 | 162.0763 | 946.4067 | -0.0138
26 |  | 1.459 | 37.6763 | 4187 | 0.0061677 | 6.1549 | 6.1611 | -2.2366 | 162.1357 | 984.083 | -0.013795
27 |  | 1.459 | 37.6625 | 4187 | 0.0061654 | 6.1611 | 6.1673 | -2.2366 | 162.1951 | 1021.7456 | -0.01379
28 |  | 1.459 | 37.6488 | 4187 | 0.0061632 | 6.1673 | 6.1734 | -2.2366 | 162.2545 | 1059.3943 | -0.013785
29 |  | 1.459 | 37.635 | 4187 | 0.0061609 | 6.1734 | 6.1796 | -2.2366 | 162.3139 | 1097.0293 | -0.01378
30 |  | 1.459 | 37.6212 | 4187 | 0.0061586 | 6.1796 | 6.1857 | -2.2366 | 162.3734 | 1134.6505 | -0.013775
31 |  | 1.459 | 37.6074 | 4187 | 0.0061564 | 6.1857 | 6.1919 | -2.2366 | 162.4329 | 1172.2579 | -0.01377
32 |  | 1.459 | 37.5936 | 4187 | 0.0061541 | 6.1919 | 6.1981 | -2.2366 | 162.4923 | 1209.8515 | -0.013765
33 |  | 1.459 | 37.5799 | 4187 | 0.0061519 | 6.1981 | 6.2042 | -2.2366 | 162.5519 | 1247.4314 | -0.01376
34 |  | 1.459 | 37.5661 | 4187 | 0.0061496 | 6.2042 | 6.2104 | -2.2366 | 162.6114 | 1284.9976 | -0.013755
35 |  | 1.459 | 37.5524 | 4187 | 0.0061474 | 6.2104 | 6.2165 | -2.2366 | 162.671 | 1322.5499 | -0.013749
36 |  | 1.459 | 37.5386 | 4187 | 0.0061451 | 6.2165 | 6.2226 | -2.2366 | 162.7305 | 1360.0885 | -0.013744
37 |  | 1.459 | 37.5249 | 4187 | 0.0061429 | 6.2226 | 6.2288 | -2.2366 | 162.7902 | 1397.6134 | -0.013739
38 |  | 1.459 | 37.5111 | 4187 | 0.0061406 | 6.2288 | 6.2349 | -2.2366 | 162.8498 | 1435.1246 | -0.013734
39 |  | 1.459 | 37.4974 | 4187 | 0.0061384 | 6.2349 | 6.2411 | -2.2366 | 162.9094 | 1472.622 | -0.013729
40 |  | 1.459 | 37.4837 | 4187 | 0.0061361 | 6.2411 | 6.2472 | -2.2366 | 162.9691 | 1510.1056 | -0.013724
41 |  | 1.459 | 37.4699 | 4187 | 0.0061339 | 6.2472 | 6.2533 | -2.2366 | 163.0288 | 1547.5756 | -0.013719
42 |  | 1.459 | 37.4562 | 4187 | 0.0061316 | 6.2533 | 6.2595 | -2.2366 | 163.0885 | 1585.0318 | -0.013714
43 |  | 1.459 | 37.4425 | 4187 | 0.0061294 | 6.2595 | 6.2656 | -2.2366 | 163.1482 | 1622.4743 | -0.013709
44 |  | 1.459 | 37.4288 | 4187 | 0.0061272 | 6.2656 | 6.2717 | -2.2366 | 163.208 | 1659.9031 | -0.013704
45 |  | 1.459 | 37.4151 | 4187 | 0.0061249 | 6.2717 | 6.2779 | -2.2366 | 163.2678 | 1697.3182 | -0.013699
46 |  | 1.459 | 37.4014 | 4187 | 0.0061227 | 6.2779 | 6.284 | -2.2366 | 163.3276 | 1734.7196 | -0.013694
47 |  | 1.459 | 37.3877 | 4187 | 0.0061204 | 6.284 | 6.2901 | -2.2366 | 163.3874 | 1772.1073 | -0.013689
48 |  | 1.459 | 37.374 | 4187 | 0.0061182 | 6.2901 | 6.2962 | -2.2366 | 163.4472 | 1809.4814 | -0.013684
49 |  | 1.459 | 37.3603 | 4187 | 0.0061159 | 6.2962 | 6.3023 | -2.2366 | 163.5071 | 1846.8417 | -0.013679
50 |  | 1.459 | 37.3467 | 4187 | 0.0061137 | 6.3023 | 6.3084 | -2.2366 | 163.567 | 1884.1883 | -0.013674
51 |  | 1.459 | 37.333 | 4187 | 0.0061115 | 6.3084 | 6.3146 | -2.2366 | 163.6269 | 1921.5213 | -0.013669
52 |  | 1.459 | 37.3193 | 4187 | 0.0061092 | 6.3146 | 6.3207 | -2.2366 | 163.6868 | 1958.8406 | -0.013664
53 |  | 1.459 | 37.3056 | 4187 | 0.006107 | 6.3207 | 6.3268 | -2.2366 | 163.7468 | 1996.1463 | -0.013659
54 |  | 1.459 | 37.292 | 4187 | 0.0061048 | 6.3268 | 6.3329 | -2.2366 | 163.8068 | 2033.4383 | -0.013654
55 |  | 1.459 | 37.2783 | 4187 | 0.0061025 | 6.3329 | 6.339 | -2.2366 | 163.8668 | 2070.7166 | -0.013649
56 |  | 1.459 | 37.2647 | 4187 | 0.0061003 | 6.339 | 6.3451 | -2.2366 | 163.9268 | 2107.9813 | -0.013644
57 |  | 1.459 | 37.251 | 4187 | 0.0060981 | 6.3451 | 6.3512 | -2.2366 | 163.9868 | 2145.2323 | -0.013639
58 |  | 1.459 | 37.2374 | 4187 | 0.0060958 | 6.3512 | 6.3573 | -2.2366 | 164.0469 | 2182.4697 | -0.013634
59 |  | 1.459 | 37.2238 | 4187 | 0.0060936 | 6.3573 | 6.3634 | -2.2366 | 164.107 | 2219.6935 | -0.013629
60 |  | 1.459 | 37.2101 | 4187 | 0.0060914 | 6.3634 | 6.3695 | -2.2366 | 164.1671 | 2256.9036 | -0.013624
61 |  | 1.459 | 37.1965 | 4187 | 0.0060891 | 6.3695 | 6.3755 | -2.2366 | 164.2272 | 2294.1002 | -0.013619
62 |  | 1.459 | 37.1829 | 4187 | 0.0060869 | 6.3755 | 6.3816 | -2.2366 | 164.2874 | 2331.283 | -0.013614
63 |  | 1.459 | 37.1693 | 4187 | 0.0060847 | 6.3816 | 6.3877 | -2.2366 | 164.3475 | 2368.4523 | -0.013609
64 |  | 1.459 | 37.1557 | 4187 | 0.0060824 | 6.3877 | 6.3938 | -2.2366 | 164.4077 | 2405.608 | -0.013604
65 |  | 1.459 | 37.1421 | 4187 | 0.0060802 | 6.3938 | 6.3999 | -2.2366 | 164.468 | 2442.7501 | -0.013599
66 |  | 1.459 | 37.1285 | 4187 | 0.006078 | 6.3999 | 6.406 | -2.2366 | 164.5282 | 2479.8785 | -0.013594
67 |  | 1.459 | 37.1149 | 4187 | 0.0060758 | 6.406 | 6.412 | -2.2366 | 164.5885 | 2516.9934 | -0.013589
68 |  | 1.459 | 37.1013 | 4187 | 0.0060735 | 6.412 | 6.4181 | -2.2366 | 164.6487 | 2554.0947 | -0.013584
69 |  | 1.459 | 37.0877 | 4187 | 0.0060713 | 6.4181 | 6.4242 | -2.2366 | 164.7091 | 2591.1824 | -0.013579
70 |  | 1.459 | 37.0741 | 4187 | 0.0060691 | 6.4242 | 6.4302 | -2.2366 | 164.7694 | 2628.2565 | -0.013574
71 |  | 1.459 | 37.0605 | 4187 | 0.0060669 | 6.4302 | 6.4363 | -2.2366 | 164.8297 | 2665.3171 | -0.013569
72 |  | 1.459 | 37.047 | 4187 | 0.0060646 | 6.4363 | 6.4424 | -2.2366 | 164.8901 | 2702.364 | -0.013564
73 |  | 1.459 | 37.0334 | 4187 | 0.0060624 | 6.4424 | 6.4484 | -2.2366 | 164.9505 | 2739.3975 | -0.013559
74 |  | 1.459 | 37.0199 | 4187 | 0.0060602 | 6.4484 | 6.4545 | -2.2366 | 165.0109 | 2776.4173 | -0.013554
75 |  | 1.459 | 37.0063 | 4187 | 0.006058 | 6.4545 | 6.4606 | -2.2366 | 165.0714 | 2813.4236 | -0.01355
76 |  | 1.459 | 36.9927 | 4187 | 0.0060558 | 6.4606 | 6.4666 | -2.2366 | 165.1318 | 2850.4164 | -0.013545
77 |  | 1.459 | 36.9792 | 4187 | 0.0060536 | 6.4666 | 6.4727 | -2.2366 | 165.1923 | 2887.3956 | -0.01354
78 |  | 1.459 | 36.9657 | 4187 | 0.0060513 | 6.4727 | 6.4787 | -2.2366 | 165.2528 | 2924.3612 | -0.013535
79 |  | 1.459 | 36.9521 | 4187 | 0.0060491 | 6.4787 | 6.4848 | -2.2366 | 165.3133 | 2961.3134 | -0.01353
80 |  | 1.459 | 36.9386 | 4187 | 0.0060469 | 6.4848 | 6.4908 | -2.2366 | 165.3739 | 2998.252 | -0.013525
81 |  | 1.459 | 36.9251 | 4187 | 0.0060447 | 6.4908 | 6.4969 | -2.2366 | 165.4345 | 3035.177 | -0.01352
82 |  | 1.459 | 36.9116 | 4187 | 0.0060425 | 6.4969 | 6.5029 | -2.2366 | 165.4951 | 3072.0886 | -0.013515
83 |  | 1.459 | 36.898 | 4187 | 0.0060403 | 6.5029 | 6.5089 | -2.2366 | 165.5557 | 3108.9866 | -0.01351
84 |  | 1.459 | 36.8845 | 4187 | 0.0060381 | 6.5089 | 6.515 | -2.2366 | 165.6163 | 3145.8712 | -0.013505
85 |  | 1.459 | 36.871 | 4187 | 0.0060358 | 6.515 | 6.521 | -2.2366 | 165.677 | 3182.7422 | -0.0135
86 |  | 1.459 | 36.8575 | 4187 | 0.0060336 | 6.521 | 6.5271 | -2.2366 | 165.7377 | 3219.5997 | -0.013495
87 |  | 1.459 | 36.844 | 4187 | 0.0060314 | 6.5271 | 6.5331 | -2.2366 | 165.7984 | 3256.4438 | -0.01349
88 |  | 1.459 | 36.8305 | 4187 | 0.0060292 | 6.5331 | 6.5391 | -2.2366 | 165.8591 | 3293.2743 | -0.013485
89 |  | 1.459 | 36.8171 | 4187 | 0.006027 | 6.5391 | 6.5451 | -2.2366 | 165.9198 | 3330.0914 | -0.01348
90 |  | 1.459 | 36.8036 | 4187 | 0.0060248 | 6.5451 | 6.5512 | -2.2366 | 165.9806 | 3366.8949 | -0.013475
91 |  | 1.459 | 36.7901 | 4187 | 0.0060226 | 6.5512 | 6.5572 | -2.2366 | 166.0414 | 3403.685 | -0.01347
92 |  | 1.459 | 36.7766 | 4187 | 0.0060204 | 6.5572 | 6.5632 | -2.2366 | 166.1022 | 3440.4617 | -0.013465
93 |  | 1.459 | 36.7632 | 4187 | 0.0060182 | 6.5632 | 6.5692 | -2.2366 | 166.1631 | 3477.2248 | -0.013461
94 |  | 1.459 | 36.7497 | 4187 | 0.006016 | 6.5692 | 6.5752 | -2.2366 | 166.2239 | 3513.9745 | -0.013456
95 |  | 1.459 | 36.7362 | 4187 | 0.0060138 | 6.5752 | 6.5813 | -2.2366 | 166.2848 | 3550.7108 | -0.013451
96 |  | 1.459 | 36.7228 | 4187 | 0.0060116 | 6.5813 | 6.5873 | -2.2366 | 166.3457 | 3587.4336 | -0.013446
97 |  | 1.459 | 36.7094 | 4187 | 0.0060094 | 6.5873 | 6.5933 | -2.2366 | 166.4066 | 3624.1429 | -0.013441
98 |  | 1.459 | 36.6959 | 4187 | 0.0060072 | 6.5933 | 6.5993 | -2.2366 | 166.4676 | 3660.8388 | -0.013436
99 |  | 1.459 | 36.6825 | 4187 | 0.006005 | 6.5993 | 6.6053 | -2.2366 | 166.5286 | 3697.5213 | -0.013431
100 |  | 1.459 | 36.669 | 4187 | 0.0060028 | 6.6053 | 6.6113 | -2.2366 | 166.5896 | 3734.1904 | -0.013426
101 |  | 1.459 | 36.6556 | 4187 | 0.0060006 | 6.6113 | 6.6173 | -2.2366 | 166.6506 | 3770.846 | -0.013421
102 |  | 1.459 | 36.6422 | 4187 | 0.0059984 | 6.6173 | 6.6233 | -2.2366 | 166.7116 | 3807.4882 | -0.013416
103 |  | 1.459 | 36.6288 | 4187 | 0.0059962 | 6.6233 | 6.6293 | -2.2366 | 166.7727 | 3844.117 | -0.013411
104 |  | 1.459 | 36.6154 | 4187 | 0.005994 | 6.6293 | 6.6353 | -2.2366 | 166.8338 | 3880.7323 | -0.013406
105 |  | 1.459 | 36.602 | 4187 | 0.0059918 | 6.6353 | 6.6413 | -2.2366 | 166.8949 | 3917.3343 | -0.013401
106 |  | 1.459 | 36.5886 | 4187 | 0.0059896 | 6.6413 | 6.6473 | -2.2366 | 166.956 | 3953.9229 | -0.013397
107 |  | 1.459 | 36.5752 | 4187 | 0.0059874 | 6.6473 | 6.6533 | -2.2366 | 167.0172 | 3990.498 | -0.013392
108 |  | 1.459 | 36.5618 | 4187 | 0.0059852 | 6.6533 | 6.6592 | -2.2366 | 167.0783 | 4027.0598 | -0.013387
109 |  | 1.459 | 36.5484 | 4187 | 0.005983 | 6.6592 | 6.6652 | -2.2366 | 167.1395 | 4063.6082 | -0.013382
110 |  | 1.459 | 36.535 | 4187 | 0.0059808 | 6.6652 | 6.6712 | -2.2366 | 167.2007 | 4100.1432 | -0.013377
111 |  | 1.459 | 36.5216 | 4187 | 0.0059786 | 6.6712 | 6.6772 | -2.2366 | 167.262 | 4136.6648 | -0.013372
112 |  | 1.459 | 36.5083 | 4187 | 0.0059765 | 6.6772 | 6.6832 | -2.2366 | 167.3232 | 4173.1731 | -0.013367
113 |  | 1.459 | 36.4949 | 4187 | 0.0059743 | 6.6832 | 6.6891 | -2.2366 | 167.3845 | 4209.668 | -0.013362
114 |  | 1.459 | 36.4815 | 4187 | 0.0059721 | 6.6891 | 6.6951 | -2.2366 | 167.4458 | 4246.1495 | -0.013357
115 |  | 1.459 | 36.4682 | 4187 | 0.0059699 | 6.6951 | 6.7011 | -2.2366 | 167.5072 | 4282.6177 | -0.013352
116 |  | 1.459 | 36.4548 | 4187 | 0.0059677 | 6.7011 | 6.707 | -2.2366 | 167.5685 | 4319.0725 | -0.013348
117 |  | 1.459 | 36.4415 | 4187 | 0.0059655 | 6.707 | 6.713 | -2.2366 | 167.6299 | 4355.514 | -0.013343
118 |  | 1.459 | 36.4281 | 4187 | 0.0059633 | 6.713 | 6.719 | -2.2366 | 167.6913 | 4391.9421 | -0.013338
119 |  | 1.459 | 36.4148 | 4187 | 0.0059612 | 6.719 | 6.7249 | -2.2366 | 167.7527 | 4428.3569 | -0.013333
120 |  | 1.459 | 36.4015 | 4187 | 0.005959 | 6.7249 | 6.7309 | -2.2366 | 167.8142 | 4464.7583 | -0.013328
121 |  | 1.459 | 36.3881 | 4187 | 0.0059568 | 6.7309 | 6.7368 | -2.2366 | 167.8756 | 4501.1465 | -0.013323
122 |  | 1.459 | 36.3748 | 4187 | 0.0059546 | 6.7368 | 6.7428 | -2.2366 | 167.9371 | 4537.5213 | -0.013318
123 |  | 1.459 | 36.3615 | 4187 | 0.0059524 | 6.7428 | 6.7488 | -2.2366 | 167.9986 | 4573.8827 | -0.013313
124 |  | 1.459 | 36.3482 | 4187 | 0.0059502 | 6.7488 | 6.7547 | -2.2366 | 168.0602 | 4610.2309 | -0.013309
125 |  | 1.459 | 36.3349 | 4187 | 0.0059481 | 6.7547 | 6.7606 | -2.2366 | 168.1217 | 4646.5658 | -0.013304
126 |  | 1.459 | 36.3216 | 4187 | 0.0059459 | 6.7606 | 6.7666 | -2.2366 | 168.1833 | 4682.8873 | -0.013299
127 |  | 1.459 | 36.3083 | 4187 | 0.0059437 | 6.7666 | 6.7725 | -2.2366 | 168.2449 | 4719.1956 | -0.013294
128 |  | 1.459 | 36.295 | 4187 | 0.0059415 | 6.7725 | 6.7785 | -2.2366 | 168.3065 | 4755.4906 | -0.013289
129 |  | 1.459 | 36.2817 | 4187 | 0.0059394 | 6.7785 | 6.7844 | -2.2366 | 168.3682 | 4791.7723 | -0.013284
130 |  | 1.459 | 36.2684 | 4187 | 0.0059372 | 6.7844 | 6.7904 | -2.2366 | 168.4298 | 4828.0406 | -0.013279
131 |  | 1.459 | 36.2551 | 4187 | 0.005935 | 6.7904 | 6.7963 | -2.2366 | 168.4915 | 4864.2958 | -0.013274
132 |  | 1.459 | 36.2418 | 4187 | 0.0059328 | 6.7963 | 6.8022 | -2.2366 | 168.5533 | 4900.5376 | -0.01327
133 |  | 1.459 | 36.2286 | 4187 | 0.0059307 | 6.8022 | 6.8082 | -2.2366 | 168.615 | 4936.7662 | -0.013265
134 |  | 1.459 | 36.2153 | 4187 | 0.0059285 | 6.8082 | 6.8141 | -2.2366 | 168.6767 | 4972.9815 | -0.01326
135 |  | 1.459 | 36.202 | 4187 | 0.0059263 | 6.8141 | 6.82 | -2.2366 | 168.7385 | 5009.1835 | -0.013255
136 |  | 1.459 | 36.1888 | 4187 | 0.0059242 | 6.82 | 6.8259 | -2.2366 | 168.8003 | 5045.3723 | -0.01325
137 |  | 1.459 | 36.1755 | 4187 | 0.005922 | 6.8259 | 6.8319 | -2.2366 | 168.8622 | 5081.5479 | -0.013245
138 |  | 1.459 | 36.1623 | 4187 | 0.0059198 | 6.8319 | 6.8378 | -2.2366 | 168.924 | 5117.7102 | -0.013241
139 |  | 1.459 | 36.1491 | 4187 | 0.0059177 | 6.8378 | 6.8437 | -2.2366 | 168.9859 | 5153.8592 | -0.013236
140 |  | 1.459 | 36.1358 | 4187 | 0.0059155 | 6.8437 | 6.8496 | -2.2366 | 169.0478 | 5189.995 | -0.013231
141 |  | 1.459 | 36.1226 | 4187 | 0.0059133 | 6.8496 | 6.8555 | -2.2366 | 169.1097 | 5226.1176 | -0.013226
142 |  | 1.459 | 36.1094 | 4187 | 0.0059112 | 6.8555 | 6.8614 | -2.2366 | 169.1716 | 5262.227 | -0.013221
143 |  | 1.459 | 36.0961 | 4187 | 0.005909 | 6.8614 | 6.8673 | -2.2366 | 169.2336 | 5298.3231 | -0.013216
144 |  | 1.459 | 36.0829 | 4187 | 0.0059068 | 6.8673 | 6.8733 | -2.2366 | 169.2956 | 5334.4061 | -0.013211
145 |  | 1.459 | 36.0697 | 4187 | 0.0059047 | 6.8733 | 6.8792 | -2.2366 | 169.3576 | 5370.4758 | -0.013207
146 |  | 1.459 | 36.0565 | 4187 | 0.0059025 | 6.8792 | 6.8851 | -2.2366 | 169.4196 | 5406.5323 | -0.013202
147 |  | 1.459 | 36.0433 | 4187 | 0.0059003 | 6.8851 | 6.891 | -2.2366 | 169.4817 | 5442.5756 | -0.013197
148 |  | 1.459 | 36.0301 | 4187 | 0.0058982 | 6.891 | 6.8969 | -2.2366 | 169.5438 | 5478.6057 | -0.013192
149 |  | 1.459 | 36.0169 | 4187 | 0.005896 | 6.8969 | 6.9028 | -2.2366 | 169.6059 | 5514.6226 | -0.013187
150 |  | 1.459 | 36.0037 | 4187 | 0.0058939 | 6.9028 | 6.9086 | -2.2366 | 169.668 | 5550.6263 | -0.013182
151 |  | 1.459 | 35.9905 | 4187 | 0.0058917 | 6.9086 | 6.9145 | -2.2366 | 169.7301 | 5586.6169 | -0.013178
152 |  | 1.459 | 35.9774 | 4187 | 0.0058895 | 6.9145 | 6.9204 | -2.2366 | 169.7923 | 5622.5943 | -0.013173
153 |  | 1.459 | 35.9642 | 4187 | 0.0058874 | 6.9204 | 6.9263 | -2.2366 | 169.8545 | 5658.5585 | -0.013168
154 |  | 1.459 | 35.951 | 4187 | 0.0058852 | 6.9263 | 6.9322 | -2.2366 | 169.9167 | 5694.5095 | -0.013163
155 |  | 1.459 | 35.9379 | 4187 | 0.0058831 | 6.9322 | 6.9381 | -2.2366 | 169.9789 | 5730.4473 | -0.013158
156 |  | 1.459 | 35.9247 | 4187 | 0.0058809 | 6.9381 | 6.944 | -2.2366 | 170.0412 | 5766.3721 | -0.013154
157 |  | 1.459 | 35.9116 | 4187 | 0.0058788 | 6.944 | 6.9498 | -2.2366 | 170.1035 | 5802.2836 | -0.013149
158 |  | 1.459 | 35.8984 | 4187 | 0.0058766 | 6.9498 | 6.9557 | -2.2366 | 170.1658 | 5838.182 | -0.013144
159 |  | 1.459 | 35.8853 | 4187 | 0.0058745 | 6.9557 | 6.9616 | -2.2366 | 170.2281 | 5874.0673 | -0.013139
160 |  | 1.459 | 35.8721 | 4187 | 0.0058723 | 6.9616 | 6.9675 | -2.2366 | 170.2905 | 5909.9394 | -0.013134
161 |  | 1.459 | 35.859 | 4187 | 0.0058702 | 6.9675 | 6.9733 | -2.2366 | 170.3528 | 5945.7984 | -0.013129
162 |  | 1.459 | 35.8459 | 4187 | 0.005868 | 6.9733 | 6.9792 | -2.2366 | 170.4152 | 5981.6442 | -0.013125
163 |  | 1.459 | 35.8327 | 4187 | 0.0058659 | 6.9792 | 6.9851 | -2.2366 | 170.4776 | 6017.477 | -0.01312
164 |  | 1.459 | 35.8196 | 4187 | 0.0058637 | 6.9851 | 6.9909 | -2.2366 | 170.5401 | 6053.2966 | -0.013115
165 |  | 1.459 | 35.8065 | 4187 | 0.0058616 | 6.9909 | 6.9968 | -2.2366 | 170.6026 | 6089.1031 | -0.01311
166 |  | 1.459 | 35.7934 | 4187 | 0.0058594 | 6.9968 | 7.0027 | -2.2366 | 170.665 | 6124.8965 | -0.013105
167 |  | 1.459 | 35.7803 | 4187 | 0.0058573 | 7.0027 | 7.0085 | -2.2366 | 170.7275 | 6160.6768 | -0.013101
168 |  | 1.459 | 35.7672 | 4187 | 0.0058551 | 7.0085 | 7.0144 | -2.2366 | 170.7901 | 6196.4439 | -0.013096
169 |  | 1.459 | 35.7541 | 4187 | 0.005853 | 7.0144 | 7.0202 | -2.2366 | 170.8526 | 6232.198 | -0.013091
170 |  | 1.459 | 35.741 | 4187 | 0.0058509 | 7.0202 | 7.0261 | -2.2366 | 170.9152 | 6267.939 | -0.013086
171 |  | 1.459 | 35.7279 | 4187 | 0.0058487 | 7.0261 | 7.0319 | -2.2366 | 170.9778 | 6303.6669 | -0.013081
172 |  | 1.459 | 35.7148 | 4187 | 0.0058466 | 7.0319 | 7.0378 | -2.2366 | 171.0404 | 6339.3818 | -0.013077
173 |  | 1.459 | 35.7018 | 4187 | 0.0058444 | 7.0378 | 7.0436 | -2.2366 | 171.1031 | 6375.0835 | -0.013072
174 |  | 1.459 | 35.6887 | 4187 | 0.0058423 | 7.0436 | 7.0495 | -2.2366 | 171.1658 | 6410.7722 | -0.013067
175 |  | 1.459 | 35.6756 | 4187 | 0.0058402 | 7.0495 | 7.0553 | -2.2366 | 171.2285 | 6446.4478 | -0.013062
176 |  | 1.459 | 35.6626 | 4187 | 0.005838 | 7.0553 | 7.0611 | -2.2366 | 171.2912 | 6482.1104 | -0.013058
177 |  | 1.459 | 35.6495 | 4187 | 0.0058359 | 7.0611 | 7.067 | -2.2366 | 171.3539 | 6517.7599 | -0.013053
178 |  | 1.459 | 35.6364 | 4187 | 0.0058337 | 7.067 | 7.0728 | -2.2366 | 171.4167 | 6553.3963 | -0.013048
179 |  | 1.459 | 35.6234 | 4187 | 0.0058316 | 7.0728 | 7.0786 | -2.2366 | 171.4795 | 6589.0197 | -0.013043
180 |  | 1.459 | 35.6103 | 4187 | 0.0058295 | 7.0786 | 7.0845 | -2.2366 | 171.5423 | 6624.63 | -0.013038
181 |  | 1.459 | 35.5973 | 4187 | 0.0058273 | 7.0845 | 7.0903 | -2.2366 | 171.6051 | 6660.2273 | -0.013034
182 |  | 1.459 | 35.5843 | 4187 | 0.0058252 | 7.0903 | 7.0961 | -2.2366 | 171.668 | 6695.8116 | -0.013029
183 |  | 1.459 | 35.5712 | 4187 | 0.0058231 | 7.0961 | 7.1019 | -2.2366 | 171.7308 | 6731.3829 | -0.013024
184 |  | 1.459 | 35.5582 | 4187 | 0.0058209 | 7.1019 | 7.1078 | -2.2366 | 171.7937 | 6766.9411 | -0.013019
185 |  | 1.459 | 35.5452 | 4187 | 0.0058188 | 7.1078 | 7.1136 | -2.2366 | 171.8567 | 6802.4863 | -0.013015
186 |  | 1.459 | 35.5322 | 4187 | 0.0058167 | 7.1136 | 7.1194 | -2.2366 | 171.9196 | 6838.0185 | -0.01301
187 |  | 1.459 | 35.5192 | 4187 | 0.0058145 | 7.1194 | 7.1252 | -2.2366 | 171.9826 | 6873.5377 | -0.013005
188 |  | 1.459 | 35.5062 | 4187 | 0.0058124 | 7.1252 | 7.131 | -2.2366 | 172.0456 | 6909.0438 | -0.013
189 |  | 1.459 | 35.4932 | 4187 | 0.0058103 | 7.131 | 7.1368 | -2.2366 | 172.1086 | 6944.537 | -0.012996
190 |  | 1.459 | 35.4802 | 4187 | 0.0058082 | 7.1368 | 7.1426 | -2.2366 | 172.1716 | 6980.0172 | -0.012991
191 |  | 1.459 | 35.4672 | 4187 | 0.005806 | 7.1426 | 7.1484 | -2.2366 | 172.2347 | 7015.4844 | -0.012986
192 |  | 1.459 | 35.4542 | 4187 | 0.0058039 | 7.1484 | 7.1542 | -2.2366 | 172.2978 | 7050.9386 | -0.012981
193 |  | 1.459 | 35.4412 | 4187 | 0.0058018 | 7.1542 | 7.1601 | -2.2366 | 172.3609 | 7086.3798 | -0.012976
194 |  | 1.459 | 35.4282 | 4187 | 0.0057997 | 7.1601 | 7.1659 | -2.2366 | 172.424 | 7121.8081 | -0.012972
195 |  | 1.459 | 35.4153 | 4187 | 0.0057975 | 7.1659 | 7.1716 | -2.2366 | 172.4872 | 7157.2233 | -0.012967
196 |  | 1.459 | 35.4023 | 4187 | 0.0057954 | 7.1716 | 7.1774 | -2.2366 | 172.5503 | 7192.6256 | -0.012962
197 |  | 1.459 | 35.3893 | 4187 | 0.0057933 | 7.1774 | 7.1832 | -2.2366 | 172.6135 | 7228.015 | -0.012957
198 |  | 1.459 | 35.3764 | 4187 | 0.0057912 | 7.1832 | 7.189 | -2.2366 | 172.6768 | 7263.3914 | -0.012953
199 |  | 1.459 | 35.3634 | 4187 | 0.005789 | 7.189 | 7.1948 | -2.2366 | 172.74 | 7298.7548 | -0.012948
200 |  | 1.459 | 35.3505 | 4187 | 0.0057869 | 7.1948 | 7.2006 | -2.2366 | 172.8033 | 7334.1053 | -0.012943
201 |  | 1.459 | 35.3375 | 4187 | 0.0057848 | 7.2006 | 7.2064 | -2.2366 | 172.8666 | 7369.4428 | -0.012939
202 |  | 1.459 | 35.3246 | 4187 | 0.0057827 | 7.2064 | 7.2122 | -2.2366 | 172.9299 | 7404.7674 | -0.012934
203 |  | 1.459 | 35.3117 | 4187 | 0.0057806 | 7.2122 | 7.218 | -2.2366 | 172.9932 | 7440.0791 | -0.012929
204 |  | 1.459 | 35.2987 | 4187 | 0.0057785 | 7.218 | 7.2237 | -2.2366 | 173.0566 | 7475.3778 | -0.012924
205 |  | 1.459 | 35.2858 | 4187 | 0.0057763 | 7.2237 | 7.2295 | -2.2366 | 173.12 | 7510.6637 | -0.01292
206 |  | 1.459 | 35.2729 | 4187 | 0.0057742 | 7.2295 | 7.2353 | -2.2366 | 173.1834 | 7545.9366 | -0.012915
207 |  | 1.459 | 35.26 | 4187 | 0.0057721 | 7.2353 | 7.2411 | -2.2366 | 173.2468 | 7581.1965 | -0.01291
208 |  | 1.459 | 35.2471 | 4187 | 0.00577 | 7.2411 | 7.2468 | -2.2366 | 173.3103 | 7616.4436 | -0.012905
209 |  | 1.459 | 35.2342 | 4187 | 0.0057679 | 7.2468 | 7.2526 | -2.2366 | 173.3738 | 7651.6778 | -0.012901
210 |  | 1.459 | 35.2213 | 4187 | 0.0057658 | 7.2526 | 7.2584 | -2.2366 | 173.4373 | 7686.899 | -0.012896
211 |  | 1.459 | 35.2084 | 4187 | 0.0057637 | 7.2584 | 7.2641 | -2.2366 | 173.5008 | 7722.1074 | -0.012891
212 |  | 1.459 | 35.1955 | 4187 | 0.0057616 | 7.2641 | 7.2699 | -2.2366 | 173.5643 | 7757.3029 | -0.012887
213 |  | 1.459 | 35.1826 | 4187 | 0.0057594 | 7.2699 | 7.2756 | -2.2366 | 173.6279 | 7792.4855 | -0.012882
214 |  | 1.459 | 35.1697 | 4187 | 0.0057573 | 7.2756 | 7.2814 | -2.2366 | 173.6915 | 7827.6552 | -0.012877
215 |  | 1.459 | 35.1568 | 4187 | 0.0057552 | 7.2814 | 7.2872 | -2.2366 | 173.7551 | 7862.812 | -0.012872
216 |  | 1.459 | 35.144 | 4187 | 0.0057531 | 7.2872 | 7.2929 | -2.2366 | 173.8188 | 7897.956 | -0.012868
217 |  | 1.459 | 35.1311 | 4187 | 0.005751 | 7.2929 | 7.2987 | -2.2366 | 173.8824 | 7933.0871 | -0.012863
218 |  | 1.459 | 35.1182 | 4187 | 0.0057489 | 7.2987 | 7.3044 | -2.2366 | 173.9461 | 7968.2053 | -0.012858
219 |  | 1.459 | 35.1054 | 4187 | 0.0057468 | 7.3044 | 7.3102 | -2.2366 | 174.0098 | 8003.3107 | -0.012854
220 |  | 1.459 | 35.0925 | 4187 | 0.0057447 | 7.3102 | 7.3159 | -2.2366 | 174.0736 | 8038.4032 | -0.012849
221 |  | 1.459 | 35.0797 | 4187 | 0.0057426 | 7.3159 | 7.3216 | -2.2366 | 174.1373 | 8073.4829 | -0.012844
222 |  | 1.459 | 35.0668 | 4187 | 0.0057405 | 7.3216 | 7.3274 | -2.2366 | 174.2011 | 8108.5497 | -0.012839
223 |  | 1.459 | 35.054 | 4187 | 0.0057384 | 7.3274 | 7.3331 | -2.2366 | 174.2649 | 8143.6037 | -0.012835
224 |  | 1.459 | 35.0412 | 4187 | 0.0057363 | 7.3331 | 7.3389 | -2.2366 | 174.3287 | 8178.6448 | -0.01283
225 |  | 1.459 | 35.0283 | 4187 | 0.0057342 | 7.3389 | 7.3446 | -2.2366 | 174.3926 | 8213.6732 | -0.012825
226 |  | 1.459 | 35.0155 | 4187 | 0.0057321 | 7.3446 | 7.3503 | -2.2366 | 174.4565 | 8248.6886 | -0.012821
227 |  | 1.459 | 35.0027 | 4187 | 0.00573 | 7.3503 | 7.3561 | -2.2366 | 174.5204 | 8283.6913 | -0.012816
228 |  | 1.459 | 34.9899 | 4187 | 0.0057279 | 7.3561 | 7.3618 | -2.2366 | 174.5843 | 8318.6812 | -0.012811
229 |  | 1.459 | 34.977 | 4187 | 0.0057258 | 7.3618 | 7.3675 | -2.2366 | 174.6482 | 8353.6582 | -0.012807
230 |  | 1.459 | 34.9642 | 4187 | 0.0057237 | 7.3675 | 7.3732 | -2.2366 | 174.7122 | 8388.6225 | -0.012802
231 |  | 1.459 | 34.9514 | 4187 | 0.0057216 | 7.3732 | 7.379 | -2.2366 | 174.7762 | 8423.5739 | -0.012797
232 |  | 1.459 | 34.9386 | 4187 | 0.0057195 | 7.379 | 7.3847 | -2.2366 | 174.8402 | 8458.5126 | -0.012792
233 |  | 1.459 | 34.9259 | 4187 | 0.0057174 | 7.3847 | 7.3904 | -2.2366 | 174.9043 | 8493.4384 | -0.012788
234 |  | 1.459 | 34.9131 | 4187 | 0.0057153 | 7.3904 | 7.3961 | -2.2366 | 174.9683 | 8528.3515 | -0.012783
235 |  | 1.459 | 34.9003 | 4187 | 0.0057132 | 7.3961 | 7.4018 | -2.2366 | 175.0324 | 8563.2518 | -0.012778
236 |  | 1.459 | 34.8875 | 4187 | 0.0057111 | 7.4018 | 7.4075 | -2.2366 | 175.0965 | 8598.1393 | -0.012774

## St60
|  |  | buis | verlies W/M | L /°C/sec
diam | wandikte |  | inhoud l/m |  | W/M
60.3 | 2.9 | 3.1416 | 2.3328 | 47.4753 | 4187
|  |  |  | 6 |  |  |  | J/sec/mtr | aantal mtr. | verlies
|  | buis | verlies W/M | L /°C/sec | verlies temp | begintemp | eindtemp | verlies | bij 1°C | totaal J/sec
|  | inhoud L |  | W/M | °C per M | °C | °C | per m°C | daling | aantal mtr
1 | 60.3 | 2.3328 | 47.4753 | 4187 | 0.0048605 | 6 | 6.0049 | -2.7927 | 205.7396 | 47.4753 | -0.013574
2 |  | 2.3328 | 47.4617 | 4187 | 0.0048591 | 6.0049 | 6.0097 | -2.7927 | 205.7985 | 94.9371 | -0.01357
3 |  | 2.3328 | 47.4482 | 4187 | 0.0048577 | 6.0097 | 6.0146 | -2.7927 | 205.8573 | 142.3852 | -0.013566
4 |  | 2.3328 | 47.4346 | 4187 | 0.0048563 | 6.0146 | 6.0194 | -2.7927 | 205.9162 | 189.8198 | -0.013562
5 |  | 2.3328 | 47.421 | 4187 | 0.004855 | 6.0194 | 6.0243 | -2.7927 | 205.9751 | 237.2409 | -0.013558
6 |  | 2.3328 | 47.4075 | 4187 | 0.0048536 | 6.0243 | 6.0291 | -2.7927 | 206.034 | 284.6484 | -0.013554
7 |  | 2.3328 | 47.3939 | 4187 | 0.0048522 | 6.0291 | 6.034 | -2.7927 | 206.0929 | 332.0423 | -0.013551
8 |  | 2.3328 | 47.3804 | 4187 | 0.0048508 | 6.034 | 6.0388 | -2.7927 | 206.1519 | 379.4227 | -0.013547
9 |  | 2.3328 | 47.3668 | 4187 | 0.0048494 | 6.0388 | 6.0437 | -2.7927 | 206.2108 | 426.7895 | -0.013543
10 |  | 2.3328 | 47.3533 | 4187 | 0.004848 | 6.0437 | 6.0485 | -2.7927 | 206.2698 | 474.1428 | -0.013539
11 |  | 2.3328 | 47.3398 | 4187 | 0.0048466 | 6.0485 | 6.0534 | -2.7927 | 206.3288 | 521.4826 | -0.013535
12 |  | 2.3328 | 47.3262 | 4187 | 0.0048452 | 6.0534 | 6.0582 | -2.7927 | 206.3878 | 568.8088 | -0.013531
13 |  | 2.3328 | 47.3127 | 4187 | 0.0048439 | 6.0582 | 6.0631 | -2.7927 | 206.4468 | 616.1215 | -0.013527
14 |  | 2.3328 | 47.2992 | 4187 | 0.0048425 | 6.0631 | 6.0679 | -2.7927 | 206.5059 | 663.4206 | -0.013523
15 |  | 2.3328 | 47.2856 | 4187 | 0.0048411 | 6.0679 | 6.0728 | -2.7927 | 206.5649 | 710.7062 | -0.01352
16 |  | 2.3328 | 47.2721 | 4187 | 0.0048397 | 6.0728 | 6.0776 | -2.7927 | 206.624 | 757.9784 | -0.013516
17 |  | 2.3328 | 47.2586 | 4187 | 0.0048383 | 6.0776 | 6.0824 | -2.7927 | 206.6831 | 805.237 | -0.013512
18 |  | 2.3328 | 47.2451 | 4187 | 0.0048369 | 6.0824 | 6.0873 | -2.7927 | 206.7422 | 852.4821 | -0.013508
19 |  | 2.3328 | 47.2316 | 4187 | 0.0048356 | 6.0873 | 6.0921 | -2.7927 | 206.8014 | 899.7136 | -0.013504
20 |  | 2.3328 | 47.2181 | 4187 | 0.0048342 | 6.0921 | 6.0969 | -2.7927 | 206.8605 | 946.9317 | -0.0135
21 |  | 2.3328 | 47.2046 | 4187 | 0.0048328 | 6.0969 | 6.1018 | -2.7927 | 206.9197 | 994.1363 | -0.013496
22 |  | 2.3328 | 47.1911 | 4187 | 0.0048314 | 6.1018 | 6.1066 | -2.7927 | 206.9788 | 1041.3274 | -0.013493
23 |  | 2.3328 | 47.1776 | 4187 | 0.00483 | 6.1066 | 6.1114 | -2.7927 | 207.038 | 1088.5049 | -0.013489
24 |  | 2.3328 | 47.1641 | 4187 | 0.0048286 | 6.1114 | 6.1163 | -2.7927 | 207.0972 | 1135.669 | -0.013485
25 |  | 2.3328 | 47.1506 | 4187 | 0.0048273 | 6.1163 | 6.1211 | -2.7927 | 207.1565 | 1182.8197 | -0.013481
26 |  | 2.3328 | 47.1371 | 4187 | 0.0048259 | 6.1211 | 6.1259 | -2.7927 | 207.2157 | 1229.9568 | -0.013477
27 |  | 2.3328 | 47.1237 | 4187 | 0.0048245 | 6.1259 | 6.1307 | -2.7927 | 207.275 | 1277.0804 | -0.013473
28 |  | 2.3328 | 47.1102 | 4187 | 0.0048231 | 6.1307 | 6.1356 | -2.7927 | 207.3343 | 1324.1906 | -0.013469
29 |  | 2.3328 | 47.0967 | 4187 | 0.0048218 | 6.1356 | 6.1404 | -2.7927 | 207.3936 | 1371.2873 | -0.013466
30 |  | 2.3328 | 47.0832 | 4187 | 0.0048204 | 6.1404 | 6.1452 | -2.7927 | 207.4529 | 1418.3706 | -0.013462
31 |  | 2.3328 | 47.0698 | 4187 | 0.004819 | 6.1452 | 6.15 | -2.7927 | 207.5122 | 1465.4404 | -0.013458
32 |  | 2.3328 | 47.0563 | 4187 | 0.0048176 | 6.15 | 6.1548 | -2.7927 | 207.5715 | 1512.4967 | -0.013454
33 |  | 2.3328 | 47.0429 | 4187 | 0.0048162 | 6.1548 | 6.1597 | -2.7927 | 207.6309 | 1559.5396 | -0.01345
34 |  | 2.3328 | 47.0294 | 4187 | 0.0048149 | 6.1597 | 6.1645 | -2.7927 | 207.6903 | 1606.569 | -0.013446
35 |  | 2.3328 | 47.016 | 4187 | 0.0048135 | 6.1645 | 6.1693 | -2.7927 | 207.7497 | 1653.585 | -0.013442
36 |  | 2.3328 | 47.0025 | 4187 | 0.0048121 | 6.1693 | 6.1741 | -2.7927 | 207.8091 | 1700.5875 | -0.013439
37 |  | 2.3328 | 46.9891 | 4187 | 0.0048107 | 6.1741 | 6.1789 | -2.7927 | 207.8685 | 1747.5766 | -0.013435
38 |  | 2.3328 | 46.9757 | 4187 | 0.0048094 | 6.1789 | 6.1837 | -2.7927 | 207.928 | 1794.5523 | -0.013431
39 |  | 2.3328 | 46.9622 | 4187 | 0.004808 | 6.1837 | 6.1885 | -2.7927 | 207.9875 | 1841.5145 | -0.013427
40 |  | 2.3328 | 46.9488 | 4187 | 0.0048066 | 6.1885 | 6.1933 | -2.7927 | 208.0469 | 1888.4633 | -0.013423
41 |  | 2.3328 | 46.9354 | 4187 | 0.0048052 | 6.1933 | 6.1981 | -2.7927 | 208.1064 | 1935.3987 | -0.013419
42 |  | 2.3328 | 46.922 | 4187 | 0.0048039 | 6.1981 | 6.2029 | -2.7927 | 208.166 | 1982.3206 | -0.013416
43 |  | 2.3328 | 46.9085 | 4187 | 0.0048025 | 6.2029 | 6.2078 | -2.7927 | 208.2255 | 2029.2292 | -0.013412
44 |  | 2.3328 | 46.8951 | 4187 | 0.0048011 | 6.2078 | 6.2126 | -2.7927 | 208.285 | 2076.1243 | -0.013408
45 |  | 2.3328 | 46.8817 | 4187 | 0.0047997 | 6.2126 | 6.2174 | -2.7927 | 208.3446 | 2123.006 | -0.013404
46 |  | 2.3328 | 46.8683 | 4187 | 0.0047984 | 6.2174 | 6.2222 | -2.7927 | 208.4042 | 2169.8744 | -0.0134
47 |  | 2.3328 | 46.8549 | 4187 | 0.004797 | 6.2222 | 6.2269 | -2.7927 | 208.4638 | 2216.7293 | -0.013396
48 |  | 2.3328 | 46.8415 | 4187 | 0.0047956 | 6.2269 | 6.2317 | -2.7927 | 208.5234 | 2263.5708 | -0.013393
49 |  | 2.3328 | 46.8281 | 4187 | 0.0047943 | 6.2317 | 6.2365 | -2.7927 | 208.583 | 2310.3989 | -0.013389
50 |  | 2.3328 | 46.8147 | 4187 | 0.0047929 | 6.2365 | 6.2413 | -2.7927 | 208.6427 | 2357.2137 | -0.013385
51 |  | 2.3328 | 46.8014 | 4187 | 0.0047915 | 6.2413 | 6.2461 | -2.7927 | 208.7024 | 2404.0151 | -0.013381
52 |  | 2.3328 | 46.788 | 4187 | 0.0047901 | 6.2461 | 6.2509 | -2.7927 | 208.7621 | 2450.803 | -0.013377
53 |  | 2.3328 | 46.7746 | 4187 | 0.0047888 | 6.2509 | 6.2557 | -2.7927 | 208.8218 | 2497.5776 | -0.013373
54 |  | 2.3328 | 46.7612 | 4187 | 0.0047874 | 6.2557 | 6.2605 | -2.7927 | 208.8815 | 2544.3389 | -0.01337
55 |  | 2.3328 | 46.7479 | 4187 | 0.004786 | 6.2605 | 6.2653 | -2.7927 | 208.9412 | 2591.0867 | -0.013366
56 |  | 2.3328 | 46.7345 | 4187 | 0.0047847 | 6.2653 | 6.2701 | -2.7927 | 209.001 | 2637.8212 | -0.013362
57 |  | 2.3328 | 46.7211 | 4187 | 0.0047833 | 6.2701 | 6.2748 | -2.7927 | 209.0608 | 2684.5423 | -0.013358
58 |  | 2.3328 | 46.7078 | 4187 | 0.0047819 | 6.2748 | 6.2796 | -2.7927 | 209.1205 | 2731.2501 | -0.013354
59 |  | 2.3328 | 46.6944 | 4187 | 0.0047806 | 6.2796 | 6.2844 | -2.7927 | 209.1804 | 2777.9445 | -0.013351
60 |  | 2.3328 | 46.6811 | 4187 | 0.0047792 | 6.2844 | 6.2892 | -2.7927 | 209.2402 | 2824.6256 | -0.013347
61 |  | 2.3328 | 46.6677 | 4187 | 0.0047778 | 6.2892 | 6.294 | -2.7927 | 209.3 | 2871.2933 | -0.013343
62 |  | 2.3328 | 46.6544 | 4187 | 0.0047765 | 6.294 | 6.2987 | -2.7927 | 209.3599 | 2917.9477 | -0.013339
63 |  | 2.3328 | 46.641 | 4187 | 0.0047751 | 6.2987 | 6.3035 | -2.7927 | 209.4198 | 2964.5887 | -0.013335
64 |  | 2.3328 | 46.6277 | 4187 | 0.0047737 | 6.3035 | 6.3083 | -2.7927 | 209.4796 | 3011.2164 | -0.013331
65 |  | 2.3328 | 46.6144 | 4187 | 0.0047724 | 6.3083 | 6.3131 | -2.7927 | 209.5396 | 3057.8308 | -0.013328
66 |  | 2.3328 | 46.601 | 4187 | 0.004771 | 6.3131 | 6.3178 | -2.7927 | 209.5995 | 3104.4318 | -0.013324
67 |  | 2.3328 | 46.5877 | 4187 | 0.0047696 | 6.3178 | 6.3226 | -2.7927 | 209.6594 | 3151.0196 | -0.01332
68 |  | 2.3328 | 46.5744 | 4187 | 0.0047683 | 6.3226 | 6.3274 | -2.7927 | 209.7194 | 3197.594 | -0.013316
69 |  | 2.3328 | 46.5611 | 4187 | 0.0047669 | 6.3274 | 6.3321 | -2.7927 | 209.7794 | 3244.155 | -0.013312
70 |  | 2.3328 | 46.5478 | 4187 | 0.0047656 | 6.3321 | 6.3369 | -2.7927 | 209.8394 | 3290.7028 | -0.013309
71 |  | 2.3328 | 46.5345 | 4187 | 0.0047642 | 6.3369 | 6.3417 | -2.7927 | 209.8994 | 3337.2373 | -0.013305
72 |  | 2.3328 | 46.5212 | 4187 | 0.0047628 | 6.3417 | 6.3464 | -2.7927 | 209.9594 | 3383.7584 | -0.013301
73 |  | 2.3328 | 46.5079 | 4187 | 0.0047615 | 6.3464 | 6.3512 | -2.7927 | 210.0195 | 3430.2663 | -0.013297
74 |  | 2.3328 | 46.4946 | 4187 | 0.0047601 | 6.3512 | 6.3559 | -2.7927 | 210.0795 | 3476.7608 | -0.013293
75 |  | 2.3328 | 46.4813 | 4187 | 0.0047587 | 6.3559 | 6.3607 | -2.7927 | 210.1396 | 3523.2421 | -0.01329
76 |  | 2.3328 | 46.468 | 4187 | 0.0047574 | 6.3607 | 6.3655 | -2.7927 | 210.1997 | 3569.7101 | -0.013286
77 |  | 2.3328 | 46.4547 | 4187 | 0.004756 | 6.3655 | 6.3702 | -2.7927 | 210.2598 | 3616.1648 | -0.013282
78 |  | 2.3328 | 46.4414 | 4187 | 0.0047547 | 6.3702 | 6.375 | -2.7927 | 210.3199 | 3662.6062 | -0.013278
79 |  | 2.3328 | 46.4281 | 4187 | 0.0047533 | 6.375 | 6.3797 | -2.7927 | 210.3801 | 3709.0343 | -0.013274
80 |  | 2.3328 | 46.4149 | 4187 | 0.0047519 | 6.3797 | 6.3845 | -2.7927 | 210.4403 | 3755.4492 | -0.013271
81 |  | 2.3328 | 46.4016 | 4187 | 0.0047506 | 6.3845 | 6.3892 | -2.7927 | 210.5004 | 3801.8508 | -0.013267
82 |  | 2.3328 | 46.3883 | 4187 | 0.0047492 | 6.3892 | 6.394 | -2.7927 | 210.5607 | 3848.2391 | -0.013263
83 |  | 2.3328 | 46.3751 | 4187 | 0.0047479 | 6.394 | 6.3987 | -2.7927 | 210.6209 | 3894.6141 | -0.013259
84 |  | 2.3328 | 46.3618 | 4187 | 0.0047465 | 6.3987 | 6.4035 | -2.7927 | 210.6811 | 3940.9759 | -0.013255
85 |  | 2.3328 | 46.3485 | 4187 | 0.0047452 | 6.4035 | 6.4082 | -2.7927 | 210.7414 | 3987.3245 | -0.013252
86 |  | 2.3328 | 46.3353 | 4187 | 0.0047438 | 6.4082 | 6.413 | -2.7927 | 210.8016 | 4033.6598 | -0.013248
87 |  | 2.3328 | 46.322 | 4187 | 0.0047424 | 6.413 | 6.4177 | -2.7927 | 210.8619 | 4079.9818 | -0.013244
88 |  | 2.3328 | 46.3088 | 4187 | 0.0047411 | 6.4177 | 6.4224 | -2.7927 | 210.9222 | 4126.2906 | -0.01324
89 |  | 2.3328 | 46.2956 | 4187 | 0.0047397 | 6.4224 | 6.4272 | -2.7927 | 210.9825 | 4172.5862 | -0.013236
90 |  | 2.3328 | 46.2823 | 4187 | 0.0047384 | 6.4272 | 6.4319 | -2.7927 | 211.0429 | 4218.8685 | -0.013233
91 |  | 2.3328 | 46.2691 | 4187 | 0.004737 | 6.4319 | 6.4367 | -2.7927 | 211.1032 | 4265.1376 | -0.013229
92 |  | 2.3328 | 46.2559 | 4187 | 0.0047357 | 6.4367 | 6.4414 | -2.7927 | 211.1636 | 4311.3934 | -0.013225
93 |  | 2.3328 | 46.2426 | 4187 | 0.0047343 | 6.4414 | 6.4461 | -2.7927 | 211.224 | 4357.6361 | -0.013221
94 |  | 2.3328 | 46.2294 | 4187 | 0.004733 | 6.4461 | 6.4509 | -2.7927 | 211.2844 | 4403.8655 | -0.013218
95 |  | 2.3328 | 46.2162 | 4187 | 0.0047316 | 6.4509 | 6.4556 | -2.7927 | 211.3448 | 4450.0817 | -0.013214
96 |  | 2.3328 | 46.203 | 4187 | 0.0047303 | 6.4556 | 6.4603 | -2.7927 | 211.4053 | 4496.2847 | -0.01321
97 |  | 2.3328 | 46.1898 | 4187 | 0.0047289 | 6.4603 | 6.4651 | -2.7927 | 211.4657 | 4542.4744 | -0.013206
98 |  | 2.3328 | 46.1766 | 4187 | 0.0047275 | 6.4651 | 6.4698 | -2.7927 | 211.5262 | 4588.651 | -0.013202
99 |  | 2.3328 | 46.1634 | 4187 | 0.0047262 | 6.4698 | 6.4745 | -2.7927 | 211.5867 | 4634.8144 | -0.013199
100 |  | 2.3328 | 46.1502 | 4187 | 0.0047248 | 6.4745 | 6.4792 | -2.7927 | 211.6472 | 4680.9645 | -0.013195
101 |  | 2.3328 | 46.137 | 4187 | 0.0047235 | 6.4792 | 6.484 | -2.7927 | 211.7078 | 4727.1015 | -0.013191
102 |  | 2.3328 | 46.1238 | 4187 | 0.0047221 | 6.484 | 6.4887 | -2.7927 | 211.7683 | 4773.2253 | -0.013187
103 |  | 2.3328 | 46.1106 | 4187 | 0.0047208 | 6.4887 | 6.4934 | -2.7927 | 211.8289 | 4819.3359 | -0.013184
104 |  | 2.3328 | 46.0974 | 4187 | 0.0047194 | 6.4934 | 6.4981 | -2.7927 | 211.8895 | 4865.4333 | -0.01318
105 |  | 2.3328 | 46.0842 | 4187 | 0.0047181 | 6.4981 | 6.5028 | -2.7927 | 211.9501 | 4911.5175 | -0.013176
106 |  | 2.3328 | 46.0711 | 4187 | 0.0047167 | 6.5028 | 6.5076 | -2.7927 | 212.0107 | 4957.5885 | -0.013172
107 |  | 2.3328 | 46.0579 | 4187 | 0.0047154 | 6.5076 | 6.5123 | -2.7927 | 212.0713 | 5003.6464 | -0.013169
108 |  | 2.3328 | 46.0447 | 4187 | 0.004714 | 6.5123 | 6.517 | -2.7927 | 212.132 | 5049.6911 | -0.013165
109 |  | 2.3328 | 46.0315 | 4187 | 0.0047127 | 6.517 | 6.5217 | -2.7927 | 212.1926 | 5095.7227 | -0.013161
110 |  | 2.3328 | 46.0184 | 4187 | 0.0047114 | 6.5217 | 6.5264 | -2.7927 | 212.2533 | 5141.7411 | -0.013157
111 |  | 2.3328 | 46.0052 | 4187 | 0.00471 | 6.5264 | 6.5311 | -2.7927 | 212.314 | 5187.7463 | -0.013153
112 |  | 2.3328 | 45.9921 | 4187 | 0.0047087 | 6.5311 | 6.5358 | -2.7927 | 212.3747 | 5233.7384 | -0.01315
113 |  | 2.3328 | 45.9789 | 4187 | 0.0047073 | 6.5358 | 6.5405 | -2.7927 | 212.4355 | 5279.7173 | -0.013146
114 |  | 2.3328 | 45.9658 | 4187 | 0.004706 | 6.5405 | 6.5452 | -2.7927 | 212.4962 | 5325.6831 | -0.013142
115 |  | 2.3328 | 45.9526 | 4187 | 0.0047046 | 6.5452 | 6.5499 | -2.7927 | 212.557 | 5371.6357 | -0.013138
116 |  | 2.3328 | 45.9395 | 4187 | 0.0047033 | 6.5499 | 6.5547 | -2.7927 | 212.6178 | 5417.5752 | -0.013135
117 |  | 2.3328 | 45.9264 | 4187 | 0.0047019 | 6.5547 | 6.5594 | -2.7927 | 212.6786 | 5463.5016 | -0.013131
118 |  | 2.3328 | 45.9132 | 4187 | 0.0047006 | 6.5594 | 6.5641 | -2.7927 | 212.7394 | 5509.4148 | -0.013127
119 |  | 2.3328 | 45.9001 | 4187 | 0.0046992 | 6.5641 | 6.5688 | -2.7927 | 212.8003 | 5555.3149 | -0.013123
120 |  | 2.3328 | 45.887 | 4187 | 0.0046979 | 6.5688 | 6.5734 | -2.7927 | 212.8611 | 5601.2019 | -0.01312
121 |  | 2.3328 | 45.8739 | 4187 | 0.0046966 | 6.5734 | 6.5781 | -2.7927 | 212.922 | 5647.0757 | -0.013116
122 |  | 2.3328 | 45.8607 | 4187 | 0.0046952 | 6.5781 | 6.5828 | -2.7927 | 212.9829 | 5692.9365 | -0.013112
123 |  | 2.3328 | 45.8476 | 4187 | 0.0046939 | 6.5828 | 6.5875 | -2.7927 | 213.0438 | 5738.7841 | -0.013108
124 |  | 2.3328 | 45.8345 | 4187 | 0.0046925 | 6.5875 | 6.5922 | -2.7927 | 213.1047 | 5784.6187 | -0.013105
125 |  | 2.3328 | 45.8214 | 4187 | 0.0046912 | 6.5922 | 6.5969 | -2.7927 | 213.1657 | 5830.4401 | -0.013101
126 |  | 2.3328 | 45.8083 | 4187 | 0.0046898 | 6.5969 | 6.6016 | -2.7927 | 213.2266 | 5876.2484 | -0.013097
127 |  | 2.3328 | 45.7952 | 4187 | 0.0046885 | 6.6016 | 6.6063 | -2.7927 | 213.2876 | 5922.0436 | -0.013093
128 |  | 2.3328 | 45.7821 | 4187 | 0.0046872 | 6.6063 | 6.611 | -2.7927 | 213.3486 | 5967.8257 | -0.01309
129 |  | 2.3328 | 45.769 | 4187 | 0.0046858 | 6.611 | 6.6157 | -2.7927 | 213.4096 | 6013.5948 | -0.013086
130 |  | 2.3328 | 45.756 | 4187 | 0.0046845 | 6.6157 | 6.6204 | -2.7927 | 213.4707 | 6059.3507 | -0.013082
131 |  | 2.3328 | 45.7429 | 4187 | 0.0046831 | 6.6204 | 6.625 | -2.7927 | 213.5317 | 6105.0936 | -0.013078
132 |  | 2.3328 | 45.7298 | 4187 | 0.0046818 | 6.625 | 6.6297 | -2.7927 | 213.5928 | 6150.8234 | -0.013075
133 |  | 2.3328 | 45.7167 | 4187 | 0.0046805 | 6.6297 | 6.6344 | -2.7927 | 213.6539 | 6196.5401 | -0.013071
134 |  | 2.3328 | 45.7036 | 4187 | 0.0046791 | 6.6344 | 6.6391 | -2.7927 | 213.715 | 6242.2438 | -0.013067
135 |  | 2.3328 | 45.6906 | 4187 | 0.0046778 | 6.6391 | 6.6438 | -2.7927 | 213.7761 | 6287.9343 | -0.013064
136 |  | 2.3328 | 45.6775 | 4187 | 0.0046765 | 6.6438 | 6.6484 | -2.7927 | 213.8373 | 6333.6119 | -0.01306
137 |  | 2.3328 | 45.6645 | 4187 | 0.0046751 | 6.6484 | 6.6531 | -2.7927 | 213.8984 | 6379.2763 | -0.013056
138 |  | 2.3328 | 45.6514 | 4187 | 0.0046738 | 6.6531 | 6.6578 | -2.7927 | 213.9596 | 6424.9277 | -0.013052
139 |  | 2.3328 | 45.6383 | 4187 | 0.0046724 | 6.6578 | 6.6625 | -2.7927 | 214.0208 | 6470.5661 | -0.013049
140 |  | 2.3328 | 45.6253 | 4187 | 0.0046711 | 6.6625 | 6.6671 | -2.7927 | 214.082 | 6516.1914 | -0.013045
141 |  | 2.3328 | 45.6123 | 4187 | 0.0046698 | 6.6671 | 6.6718 | -2.7927 | 214.1432 | 6561.8036 | -0.013041
142 |  | 2.3328 | 45.5992 | 4187 | 0.0046684 | 6.6718 | 6.6765 | -2.7927 | 214.2045 | 6607.4028 | -0.013037
143 |  | 2.3328 | 45.5862 | 4187 | 0.0046671 | 6.6765 | 6.6811 | -2.7927 | 214.2657 | 6652.989 | -0.013034
144 |  | 2.3328 | 45.5731 | 4187 | 0.0046658 | 6.6811 | 6.6858 | -2.7927 | 214.327 | 6698.5622 | -0.01303
145 |  | 2.3328 | 45.5601 | 4187 | 0.0046644 | 6.6858 | 6.6905 | -2.7927 | 214.3883 | 6744.1223 | -0.013026
146 |  | 2.3328 | 45.5471 | 4187 | 0.0046631 | 6.6905 | 6.6951 | -2.7927 | 214.4496 | 6789.6694 | -0.013022
147 |  | 2.3328 | 45.5341 | 4187 | 0.0046618 | 6.6951 | 6.6998 | -2.7927 | 214.5109 | 6835.2034 | -0.013019
148 |  | 2.3328 | 45.521 | 4187 | 0.0046604 | 6.6998 | 6.7044 | -2.7927 | 214.5723 | 6880.7245 | -0.013015
149 |  | 2.3328 | 45.508 | 4187 | 0.0046591 | 6.7044 | 6.7091 | -2.7927 | 214.6336 | 6926.2325 | -0.013011
150 |  | 2.3328 | 45.495 | 4187 | 0.0046578 | 6.7091 | 6.7138 | -2.7927 | 214.695 | 6971.7275 | -0.013008
151 |  | 2.3328 | 45.482 | 4187 | 0.0046564 | 6.7138 | 6.7184 | -2.7927 | 214.7564 | 7017.2095 | -0.013004
152 |  | 2.3328 | 45.469 | 4187 | 0.0046551 | 6.7184 | 6.7231 | -2.7927 | 214.8179 | 7062.6785 | -0.013
153 |  | 2.3328 | 45.456 | 4187 | 0.0046538 | 6.7231 | 6.7277 | -2.7927 | 214.8793 | 7108.1345 | -0.012996
154 |  | 2.3328 | 45.443 | 4187 | 0.0046524 | 6.7277 | 6.7324 | -2.7927 | 214.9407 | 7153.5776 | -0.012993
155 |  | 2.3328 | 45.43 | 4187 | 0.0046511 | 6.7324 | 6.737 | -2.7927 | 215.0022 | 7199.0076 | -0.012989
156 |  | 2.3328 | 45.417 | 4187 | 0.0046498 | 6.737 | 6.7417 | -2.7927 | 215.0637 | 7244.4246 | -0.012985
157 |  | 2.3328 | 45.404 | 4187 | 0.0046485 | 6.7417 | 6.7463 | -2.7927 | 215.1252 | 7289.8286 | -0.012982
158 |  | 2.3328 | 45.3911 | 4187 | 0.0046471 | 6.7463 | 6.751 | -2.7927 | 215.1867 | 7335.2197 | -0.012978
159 |  | 2.3328 | 45.3781 | 4187 | 0.0046458 | 6.751 | 6.7556 | -2.7927 | 215.2483 | 7380.5978 | -0.012974
160 |  | 2.3328 | 45.3651 | 4187 | 0.0046445 | 6.7556 | 6.7603 | -2.7927 | 215.3098 | 7425.9629 | -0.01297
161 |  | 2.3328 | 45.3521 | 4187 | 0.0046431 | 6.7603 | 6.7649 | -2.7927 | 215.3714 | 7471.315 | -0.012967
162 |  | 2.3328 | 45.3392 | 4187 | 0.0046418 | 6.7649 | 6.7696 | -2.7927 | 215.433 | 7516.6542 | -0.012963
163 |  | 2.3328 | 45.3262 | 4187 | 0.0046405 | 6.7696 | 6.7742 | -2.7927 | 215.4946 | 7561.9804 | -0.012959
164 |  | 2.3328 | 45.3133 | 4187 | 0.0046392 | 6.7742 | 6.7788 | -2.7927 | 215.5563 | 7607.2937 | -0.012956
165 |  | 2.3328 | 45.3003 | 4187 | 0.0046378 | 6.7788 | 6.7835 | -2.7927 | 215.6179 | 7652.594 | -0.012952
166 |  | 2.3328 | 45.2873 | 4187 | 0.0046365 | 6.7835 | 6.7881 | -2.7927 | 215.6796 | 7697.8813 | -0.012948
167 |  | 2.3328 | 45.2744 | 4187 | 0.0046352 | 6.7881 | 6.7927 | -2.7927 | 215.7412 | 7743.1557 | -0.012945
168 |  | 2.3328 | 45.2615 | 4187 | 0.0046339 | 6.7927 | 6.7974 | -2.7927 | 215.803 | 7788.4172 | -0.012941
169 |  | 2.3328 | 45.2485 | 4187 | 0.0046325 | 6.7974 | 6.802 | -2.7927 | 215.8647 | 7833.6657 | -0.012937
170 |  | 2.3328 | 45.2356 | 4187 | 0.0046312 | 6.802 | 6.8066 | -2.7927 | 215.9264 | 7878.9012 | -0.012933
171 |  | 2.3328 | 45.2226 | 4187 | 0.0046299 | 6.8066 | 6.8113 | -2.7927 | 215.9882 | 7924.1239 | -0.01293
172 |  | 2.3328 | 45.2097 | 4187 | 0.0046286 | 6.8113 | 6.8159 | -2.7927 | 216.0499 | 7969.3336 | -0.012926
173 |  | 2.3328 | 45.1968 | 4187 | 0.0046272 | 6.8159 | 6.8205 | -2.7927 | 216.1117 | 8014.5304 | -0.012922
174 |  | 2.3328 | 45.1839 | 4187 | 0.0046259 | 6.8205 | 6.8252 | -2.7927 | 216.1735 | 8059.7142 | -0.012919
175 |  | 2.3328 | 45.1709 | 4187 | 0.0046246 | 6.8252 | 6.8298 | -2.7927 | 216.2354 | 8104.8852 | -0.012915
176 |  | 2.3328 | 45.158 | 4187 | 0.0046233 | 6.8298 | 6.8344 | -2.7927 | 216.2972 | 8150.0432 | -0.012911
177 |  | 2.3328 | 45.1451 | 4187 | 0.0046219 | 6.8344 | 6.839 | -2.7927 | 216.3591 | 8195.1883 | -0.012908
178 |  | 2.3328 | 45.1322 | 4187 | 0.0046206 | 6.839 | 6.8436 | -2.7927 | 216.4209 | 8240.3205 | -0.012904
179 |  | 2.3328 | 45.1193 | 4187 | 0.0046193 | 6.8436 | 6.8483 | -2.7927 | 216.4828 | 8285.4398 | -0.0129
180 |  | 2.3328 | 45.1064 | 4187 | 0.004618 | 6.8483 | 6.8529 | -2.7927 | 216.5447 | 8330.5462 | -0.012896
181 |  | 2.3328 | 45.0935 | 4187 | 0.0046167 | 6.8529 | 6.8575 | -2.7927 | 216.6067 | 8375.6398 | -0.012893
182 |  | 2.3328 | 45.0806 | 4187 | 0.0046153 | 6.8575 | 6.8621 | -2.7927 | 216.6686 | 8420.7204 | -0.012889
183 |  | 2.3328 | 45.0677 | 4187 | 0.004614 | 6.8621 | 6.8667 | -2.7927 | 216.7306 | 8465.7881 | -0.012885
184 |  | 2.3328 | 45.0548 | 4187 | 0.0046127 | 6.8667 | 6.8713 | -2.7927 | 216.7926 | 8510.8429 | -0.012882
185 |  | 2.3328 | 45.042 | 4187 | 0.0046114 | 6.8713 | 6.8759 | -2.7927 | 216.8546 | 8555.8849 | -0.012878
186 |  | 2.3328 | 45.0291 | 4187 | 0.0046101 | 6.8759 | 6.8806 | -2.7927 | 216.9166 | 8600.914 | -0.012874
187 |  | 2.3328 | 45.0162 | 4187 | 0.0046087 | 6.8806 | 6.8852 | -2.7927 | 216.9786 | 8645.9302 | -0.012871
188 |  | 2.3328 | 45.0033 | 4187 | 0.0046074 | 6.8852 | 6.8898 | -2.7927 | 217.0407 | 8690.9335 | -0.012867
189 |  | 2.3328 | 44.9905 | 4187 | 0.0046061 | 6.8898 | 6.8944 | -2.7927 | 217.1028 | 8735.924 | -0.012863
190 |  | 2.3328 | 44.9776 | 4187 | 0.0046048 | 6.8944 | 6.899 | -2.7927 | 217.1648 | 8780.9016 | -0.01286
191 |  | 2.3328 | 44.9647 | 4187 | 0.0046035 | 6.899 | 6.9036 | -2.7927 | 217.2269 | 8825.8663 | -0.012856
192 |  | 2.3328 | 44.9519 | 4187 | 0.0046022 | 6.9036 | 6.9082 | -2.7927 | 217.2891 | 8870.8182 | -0.012852
193 |  | 2.3328 | 44.939 | 4187 | 0.0046008 | 6.9082 | 6.9128 | -2.7927 | 217.3512 | 8915.7573 | -0.012849
194 |  | 2.3328 | 44.9262 | 4187 | 0.0045995 | 6.9128 | 6.9174 | -2.7927 | 217.4134 | 8960.6835 | -0.012845
195 |  | 2.3328 | 44.9133 | 4187 | 0.0045982 | 6.9174 | 6.922 | -2.7927 | 217.4756 | 9005.5968 | -0.012841
196 |  | 2.3328 | 44.9005 | 4187 | 0.0045969 | 6.922 | 6.9266 | -2.7927 | 217.5378 | 9050.4973 | -0.012838
197 |  | 2.3328 | 44.8877 | 4187 | 0.0045956 | 6.9266 | 6.9312 | -2.7927 | 217.6 | 9095.385 | -0.012834
198 |  | 2.3328 | 44.8748 | 4187 | 0.0045943 | 6.9312 | 6.9358 | -2.7927 | 217.6622 | 9140.2598 | -0.01283
199 |  | 2.3328 | 44.862 | 4187 | 0.004593 | 6.9358 | 6.9404 | -2.7927 | 217.7245 | 9185.1218 | -0.012827
200 |  | 2.3328 | 44.8492 | 4187 | 0.0045916 | 6.9404 | 6.945 | -2.7927 | 217.7867 | 9229.971 | -0.012823
201 |  | 2.3328 | 44.8364 | 4187 | 0.0045903 | 6.945 | 6.9496 | -2.7927 | 217.849 | 9274.8073 | -0.012819
202 |  | 2.3328 | 44.8235 | 4187 | 0.004589 | 6.9496 | 6.9541 | -2.7927 | 217.9113 | 9319.6309 | -0.012816
203 |  | 2.3328 | 44.8107 | 4187 | 0.0045877 | 6.9541 | 6.9587 | -2.7927 | 217.9736 | 9364.4416 | -0.012812
204 |  | 2.3328 | 44.7979 | 4187 | 0.0045864 | 6.9587 | 6.9633 | -2.7927 | 218.036 | 9409.2395 | -0.012808
205 |  | 2.3328 | 44.7851 | 4187 | 0.0045851 | 6.9633 | 6.9679 | -2.7927 | 218.0983 | 9454.0246 | -0.012805
206 |  | 2.3328 | 44.7723 | 4187 | 0.0045838 | 6.9679 | 6.9725 | -2.7927 | 218.1607 | 9498.7969 | -0.012801
207 |  | 2.3328 | 44.7595 | 4187 | 0.0045825 | 6.9725 | 6.9771 | -2.7927 | 218.2231 | 9543.5564 | -0.012797
208 |  | 2.3328 | 44.7467 | 4187 | 0.0045812 | 6.9771 | 6.9816 | -2.7927 | 218.2855 | 9588.3031 | -0.012794
209 |  | 2.3328 | 44.7339 | 4187 | 0.0045798 | 6.9816 | 6.9862 | -2.7927 | 218.3479 | 9633.037 | -0.01279
210 |  | 2.3328 | 44.7211 | 4187 | 0.0045785 | 6.9862 | 6.9908 | -2.7927 | 218.4104 | 9677.7581 | -0.012786
211 |  | 2.3328 | 44.7083 | 4187 | 0.0045772 | 6.9908 | 6.9954 | -2.7927 | 218.4728 | 9722.4664 | -0.012783
212 |  | 2.3328 | 44.6955 | 4187 | 0.0045759 | 6.9954 | 7 | -2.7927 | 218.5353 | 9767.1619 | -0.012779
213 |  | 2.3328 | 44.6828 | 4187 | 0.0045746 | 7 | 7.0045 | -2.7927 | 218.5978 | 9811.8447 | -0.012775
214 |  | 2.3328 | 44.67 | 4187 | 0.0045733 | 7.0045 | 7.0091 | -2.7927 | 218.6603 | 9856.5147 | -0.012772
215 |  | 2.3328 | 44.6572 | 4187 | 0.004572 | 7.0091 | 7.0137 | -2.7927 | 218.7229 | 9901.1719 | -0.012768
216 |  | 2.3328 | 44.6444 | 4187 | 0.0045707 | 7.0137 | 7.0183 | -2.7927 | 218.7854 | 9945.8163 | -0.012764
217 |  | 2.3328 | 44.6317 | 4187 | 0.0045694 | 7.0183 | 7.0228 | -2.7927 | 218.848 | 9990.448 | -0.012761
218 |  | 2.3328 | 44.6189 | 4187 | 0.0045681 | 7.0228 | 7.0274 | -2.7927 | 218.9106 | 10035.0669 | -0.012757
219 |  | 2.3328 | 44.6062 | 4187 | 0.0045668 | 7.0274 | 7.032 | -2.7927 | 218.9732 | 10079.6731 | -0.012753
220 |  | 2.3328 | 44.5934 | 4187 | 0.0045655 | 7.032 | 7.0365 | -2.7927 | 219.0358 | 10124.2665 | -0.01275
221 |  | 2.3328 | 44.5807 | 4187 | 0.0045642 | 7.0365 | 7.0411 | -2.7927 | 219.0985 | 10168.8472 | -0.012746
222 |  | 2.3328 | 44.5679 | 4187 | 0.0045629 | 7.0411 | 7.0456 | -2.7927 | 219.1611 | 10213.4151 | -0.012743
223 |  | 2.3328 | 44.5552 | 4187 | 0.0045615 | 7.0456 | 7.0502 | -2.7927 | 219.2238 | 10257.9703 | -0.012739
224 |  | 2.3328 | 44.5424 | 4187 | 0.0045602 | 7.0502 | 7.0548 | -2.7927 | 219.2865 | 10302.5127 | -0.012735
225 |  | 2.3328 | 44.5297 | 4187 | 0.0045589 | 7.0548 | 7.0593 | -2.7927 | 219.3492 | 10347.0424 | -0.012732
226 |  | 2.3328 | 44.517 | 4187 | 0.0045576 | 7.0593 | 7.0639 | -2.7927 | 219.412 | 10391.5594 | -0.012728
227 |  | 2.3328 | 44.5042 | 4187 | 0.0045563 | 7.0639 | 7.0684 | -2.7927 | 219.4747 | 10436.0636 | -0.012724
228 |  | 2.3328 | 44.4915 | 4187 | 0.004555 | 7.0684 | 7.073 | -2.7927 | 219.5375 | 10480.5551 | -0.012721
229 |  | 2.3328 | 44.4788 | 4187 | 0.0045537 | 7.073 | 7.0776 | -2.7927 | 219.6003 | 10525.0339 | -0.012717
230 |  | 2.3328 | 44.4661 | 4187 | 0.0045524 | 7.0776 | 7.0821 | -2.7927 | 219.6631 | 10569.5 | -0.012713
231 |  | 2.3328 | 44.4534 | 4187 | 0.0045511 | 7.0821 | 7.0867 | -2.7927 | 219.7259 | 10613.9534 | -0.01271
232 |  | 2.3328 | 44.4407 | 4187 | 0.0045498 | 7.0867 | 7.0912 | -2.7927 | 219.7887 | 10658.394 | -0.012706
233 |  | 2.3328 | 44.4279 | 4187 | 0.0045485 | 7.0912 | 7.0958 | -2.7927 | 219.8516 | 10702.822 | -0.012703
234 |  | 2.3328 | 44.4152 | 4187 | 0.0045472 | 7.0958 | 7.1003 | -2.7927 | 219.9145 | 10747.2372 | -0.012699
235 |  | 2.3328 | 44.4025 | 4187 | 0.0045459 | 7.1003 | 7.1048 | -2.7927 | 219.9774 | 10791.6397 | -0.012695
236 |  | 2.3328 | 44.3899 | 4187 | 0.0045446 | 7.1048 | 7.1094 | -2.7927 | 220.0403 | 10836.0296 | -0.012692

## St76
|  |  | buis | verlies W/M | L /°C/sec
diam | wandikte |  | inhoud l/m |  | W/M
76.1 | 2.6 | 3.1416 | 3.948 | 59.9367 | 4187
[8 empty] | J/sec/mtr | aantal mtr. | verlies
|  | buis | verlies W/M | L /°C/sec | verlies temp | begintemp | eindtemp | verlies | bij 1°C | totaal J/sec
|  | inhoud L |  | W/M | °C per M | °C | °C | per m°C | daling | aantal mtr
1 | 76.1 | 3.948 | 59.9367 | 4187 | 0.0036258 | 6 | 6.0036 | -3.5257 | 275.7991 | 59.9367 | -0.012784
2 |  | 3.948 | 59.9239 | 4187 | 0.0036251 | 6.0036 | 6.0073 | -3.5257 | 275.8579 | 119.8605 | -0.012781
3 |  | 3.948 | 59.9111 | 4187 | 0.0036243 | 6.0073 | 6.0109 | -3.5257 | 275.9167 | 179.7716 | -0.012778
4 |  | 3.948 | 59.8983 | 4187 | 0.0036235 | 6.0109 | 6.0145 | -3.5257 | 275.9756 | 239.67 | -0.012775
5 |  | 3.948 | 59.8855 | 4187 | 0.0036227 | 6.0145 | 6.0181 | -3.5257 | 276.0345 | 299.5555 | -0.012773
6 |  | 3.948 | 59.8728 | 4187 | 0.003622 | 6.0181 | 6.0217 | -3.5257 | 276.0934 | 359.4283 | -0.01277
7 |  | 3.948 | 59.86 | 4187 | 0.0036212 | 6.0217 | 6.0254 | -3.5257 | 276.1523 | 419.2883 | -0.012767
8 |  | 3.948 | 59.8472 | 4187 | 0.0036204 | 6.0254 | 6.029 | -3.5257 | 276.2112 | 479.1355 | -0.012764
9 |  | 3.948 | 59.8345 | 4187 | 0.0036196 | 6.029 | 6.0326 | -3.5257 | 276.2701 | 538.97 | -0.012762
10 |  | 3.948 | 59.8217 | 4187 | 0.0036189 | 6.0326 | 6.0362 | -3.5257 | 276.329 | 598.7917 | -0.012759
11 |  | 3.948 | 59.8089 | 4187 | 0.0036181 | 6.0362 | 6.0398 | -3.5257 | 276.388 | 658.6006 | -0.012756
12 |  | 3.948 | 59.7962 | 4187 | 0.0036173 | 6.0398 | 6.0435 | -3.5257 | 276.4469 | 718.3968 | -0.012754
13 |  | 3.948 | 59.7834 | 4187 | 0.0036166 | 6.0435 | 6.0471 | -3.5257 | 276.5059 | 778.1803 | -0.012751
14 |  | 3.948 | 59.7707 | 4187 | 0.0036158 | 6.0471 | 6.0507 | -3.5257 | 276.5649 | 837.9509 | -0.012748
15 |  | 3.948 | 59.7579 | 4187 | 0.003615 | 6.0507 | 6.0543 | -3.5257 | 276.6239 | 897.7089 | -0.012745
16 |  | 3.948 | 59.7452 | 4187 | 0.0036142 | 6.0543 | 6.0579 | -3.5257 | 276.6829 | 957.4541 | -0.012743
17 |  | 3.948 | 59.7325 | 4187 | 0.0036135 | 6.0579 | 6.0615 | -3.5257 | 276.7419 | 1017.1865 | -0.01274
18 |  | 3.948 | 59.7197 | 4187 | 0.0036127 | 6.0615 | 6.0651 | -3.5257 | 276.801 | 1076.9062 | -0.012737
19 |  | 3.948 | 59.707 | 4187 | 0.0036119 | 6.0651 | 6.0688 | -3.5257 | 276.86 | 1136.6132 | -0.012735
20 |  | 3.948 | 59.6942 | 4187 | 0.0036112 | 6.0688 | 6.0724 | -3.5257 | 276.9191 | 1196.3075 | -0.012732
21 |  | 3.948 | 59.6815 | 4187 | 0.0036104 | 6.0724 | 6.076 | -3.5257 | 276.9782 | 1255.989 | -0.012729
22 |  | 3.948 | 59.6688 | 4187 | 0.0036096 | 6.076 | 6.0796 | -3.5257 | 277.0372 | 1315.6577 | -0.012726
23 |  | 3.948 | 59.6561 | 4187 | 0.0036089 | 6.0796 | 6.0832 | -3.5257 | 277.0963 | 1375.3138 | -0.012724
24 |  | 3.948 | 59.6433 | 4187 | 0.0036081 | 6.0832 | 6.0868 | -3.5257 | 277.1555 | 1434.9571 | -0.012721
25 |  | 3.948 | 59.6306 | 4187 | 0.0036073 | 6.0868 | 6.0904 | -3.5257 | 277.2146 | 1494.5877 | -0.012718
26 |  | 3.948 | 59.6179 | 4187 | 0.0036065 | 6.0904 | 6.094 | -3.5257 | 277.2737 | 1554.2056 | -0.012716
27 |  | 3.948 | 59.6052 | 4187 | 0.0036058 | 6.094 | 6.0976 | -3.5257 | 277.3329 | 1613.8108 | -0.012713
28 |  | 3.948 | 59.5925 | 4187 | 0.003605 | 6.0976 | 6.1012 | -3.5257 | 277.392 | 1673.4032 | -0.01271
29 |  | 3.948 | 59.5798 | 4187 | 0.0036042 | 6.1012 | 6.1048 | -3.5257 | 277.4512 | 1732.983 | -0.012707
30 |  | 3.948 | 59.567 | 4187 | 0.0036035 | 6.1048 | 6.1084 | -3.5257 | 277.5104 | 1792.55 | -0.012705
31 |  | 3.948 | 59.5543 | 4187 | 0.0036027 | 6.1084 | 6.112 | -3.5257 | 277.5696 | 1852.1044 | -0.012702
32 |  | 3.948 | 59.5416 | 4187 | 0.0036019 | 6.112 | 6.1156 | -3.5257 | 277.6288 | 1911.646 | -0.012699
33 |  | 3.948 | 59.5289 | 4187 | 0.0036012 | 6.1156 | 6.1192 | -3.5257 | 277.688 | 1971.175 | -0.012697
34 |  | 3.948 | 59.5162 | 4187 | 0.0036004 | 6.1192 | 6.1228 | -3.5257 | 277.7473 | 2030.6912 | -0.012694
35 |  | 3.948 | 59.5035 | 4187 | 0.0035996 | 6.1228 | 6.1264 | -3.5257 | 277.8065 | 2090.1947 | -0.012691
36 |  | 3.948 | 59.4909 | 4187 | 0.0035989 | 6.1264 | 6.13 | -3.5257 | 277.8658 | 2149.6856 | -0.012688
37 |  | 3.948 | 59.4782 | 4187 | 0.0035981 | 6.13 | 6.1336 | -3.5257 | 277.9251 | 2209.1638 | -0.012686
38 |  | 3.948 | 59.4655 | 4187 | 0.0035973 | 6.1336 | 6.1372 | -3.5257 | 277.9844 | 2268.6292 | -0.012683
39 |  | 3.948 | 59.4528 | 4187 | 0.0035966 | 6.1372 | 6.1408 | -3.5257 | 278.0437 | 2328.082 | -0.01268
40 |  | 3.948 | 59.4401 | 4187 | 0.0035958 | 6.1408 | 6.1444 | -3.5257 | 278.103 | 2387.5222 | -0.012678
41 |  | 3.948 | 59.4274 | 4187 | 0.003595 | 6.1444 | 6.148 | -3.5257 | 278.1623 | 2446.9496 | -0.012675
42 |  | 3.948 | 59.4148 | 4187 | 0.0035943 | 6.148 | 6.1516 | -3.5257 | 278.2217 | 2506.3644 | -0.012672
43 |  | 3.948 | 59.4021 | 4187 | 0.0035935 | 6.1516 | 6.1552 | -3.5257 | 278.281 | 2565.7665 | -0.01267
44 |  | 3.948 | 59.3894 | 4187 | 0.0035927 | 6.1552 | 6.1588 | -3.5257 | 278.3404 | 2625.1559 | -0.012667
45 |  | 3.948 | 59.3768 | 4187 | 0.003592 | 6.1588 | 6.1624 | -3.5257 | 278.3997 | 2684.5326 | -0.012664
46 |  | 3.948 | 59.3641 | 4187 | 0.0035912 | 6.1624 | 6.166 | -3.5257 | 278.4591 | 2743.8967 | -0.012661
47 |  | 3.948 | 59.3514 | 4187 | 0.0035904 | 6.166 | 6.1696 | -3.5257 | 278.5185 | 2803.2482 | -0.012659
48 |  | 3.948 | 59.3388 | 4187 | 0.0035897 | 6.1696 | 6.1732 | -3.5257 | 278.578 | 2862.5869 | -0.012656
49 |  | 3.948 | 59.3261 | 4187 | 0.0035889 | 6.1732 | 6.1768 | -3.5257 | 278.6374 | 2921.9131 | -0.012653
50 |  | 3.948 | 59.3135 | 4187 | 0.0035881 | 6.1768 | 6.1803 | -3.5257 | 278.6968 | 2981.2265 | -0.012651
51 |  | 3.948 | 59.3008 | 4187 | 0.0035874 | 6.1803 | 6.1839 | -3.5257 | 278.7563 | 3040.5273 | -0.012648
52 |  | 3.948 | 59.2882 | 4187 | 0.0035866 | 6.1839 | 6.1875 | -3.5257 | 278.8158 | 3099.8155 | -0.012645
53 |  | 3.948 | 59.2755 | 4187 | 0.0035858 | 6.1875 | 6.1911 | -3.5257 | 278.8752 | 3159.091 | -0.012643
54 |  | 3.948 | 59.2629 | 4187 | 0.0035851 | 6.1911 | 6.1947 | -3.5257 | 278.9347 | 3218.3539 | -0.01264
55 |  | 3.948 | 59.2502 | 4187 | 0.0035843 | 6.1947 | 6.1983 | -3.5257 | 278.9942 | 3277.6041 | -0.012637
56 |  | 3.948 | 59.2376 | 4187 | 0.0035835 | 6.1983 | 6.2019 | -3.5257 | 279.0537 | 3336.8417 | -0.012634
57 |  | 3.948 | 59.225 | 4187 | 0.0035828 | 6.2019 | 6.2054 | -3.5257 | 279.1133 | 3396.0667 | -0.012632
58 |  | 3.948 | 59.2123 | 4187 | 0.003582 | 6.2054 | 6.209 | -3.5257 | 279.1728 | 3455.279 | -0.012629
59 |  | 3.948 | 59.1997 | 4187 | 0.0035812 | 6.209 | 6.2126 | -3.5257 | 279.2324 | 3514.4787 | -0.012626
60 |  | 3.948 | 59.1871 | 4187 | 0.0035805 | 6.2126 | 6.2162 | -3.5257 | 279.2919 | 3573.6658 | -0.012624
61 |  | 3.948 | 59.1745 | 4187 | 0.0035797 | 6.2162 | 6.2198 | -3.5257 | 279.3515 | 3632.8403 | -0.012621
62 |  | 3.948 | 59.1618 | 4187 | 0.003579 | 6.2198 | 6.2233 | -3.5257 | 279.4111 | 3692.0021 | -0.012618
63 |  | 3.948 | 59.1492 | 4187 | 0.0035782 | 6.2233 | 6.2269 | -3.5257 | 279.4707 | 3751.1513 | -0.012616
64 |  | 3.948 | 59.1366 | 4187 | 0.0035774 | 6.2269 | 6.2305 | -3.5257 | 279.5303 | 3810.2879 | -0.012613
65 |  | 3.948 | 59.124 | 4187 | 0.0035767 | 6.2305 | 6.2341 | -3.5257 | 279.59 | 3869.4119 | -0.01261
66 |  | 3.948 | 59.1114 | 4187 | 0.0035759 | 6.2341 | 6.2377 | -3.5257 | 279.6496 | 3928.5233 | -0.012608
67 |  | 3.948 | 59.0988 | 4187 | 0.0035751 | 6.2377 | 6.2412 | -3.5257 | 279.7093 | 3987.6221 | -0.012605
68 |  | 3.948 | 59.0862 | 4187 | 0.0035744 | 6.2412 | 6.2448 | -3.5257 | 279.7689 | 4046.7082 | -0.012602
69 |  | 3.948 | 59.0736 | 4187 | 0.0035736 | 6.2448 | 6.2484 | -3.5257 | 279.8286 | 4105.7818 | -0.012599
70 |  | 3.948 | 59.061 | 4187 | 0.0035729 | 6.2484 | 6.2519 | -3.5257 | 279.8883 | 4164.8428 | -0.012597
71 |  | 3.948 | 59.0484 | 4187 | 0.0035721 | 6.2519 | 6.2555 | -3.5257 | 279.948 | 4223.8911 | -0.012594
72 |  | 3.948 | 59.0358 | 4187 | 0.0035713 | 6.2555 | 6.2591 | -3.5257 | 280.0078 | 4282.9269 | -0.012591
73 |  | 3.948 | 59.0232 | 4187 | 0.0035706 | 6.2591 | 6.2627 | -3.5257 | 280.0675 | 4341.9501 | -0.012589
74 |  | 3.948 | 59.0106 | 4187 | 0.0035698 | 6.2627 | 6.2662 | -3.5257 | 280.1272 | 4400.9607 | -0.012586
75 |  | 3.948 | 58.998 | 4187 | 0.003569 | 6.2662 | 6.2698 | -3.5257 | 280.187 | 4459.9587 | -0.012583
76 |  | 3.948 | 58.9854 | 4187 | 0.0035683 | 6.2698 | 6.2734 | -3.5257 | 280.2468 | 4518.9441 | -0.012581
77 |  | 3.948 | 58.9728 | 4187 | 0.0035675 | 6.2734 | 6.2769 | -3.5257 | 280.3066 | 4577.9169 | -0.012578
78 |  | 3.948 | 58.9603 | 4187 | 0.0035668 | 6.2769 | 6.2805 | -3.5257 | 280.3664 | 4636.8772 | -0.012575
79 |  | 3.948 | 58.9477 | 4187 | 0.003566 | 6.2805 | 6.2841 | -3.5257 | 280.4262 | 4695.8249 | -0.012573
80 |  | 3.948 | 58.9351 | 4187 | 0.0035652 | 6.2841 | 6.2876 | -3.5257 | 280.486 | 4754.76 | -0.01257
81 |  | 3.948 | 58.9225 | 4187 | 0.0035645 | 6.2876 | 6.2912 | -3.5257 | 280.5458 | 4813.6826 | -0.012567
82 |  | 3.948 | 58.91 | 4187 | 0.0035637 | 6.2912 | 6.2948 | -3.5257 | 280.6057 | 4872.5925 | -0.012565
83 |  | 3.948 | 58.8974 | 4187 | 0.003563 | 6.2948 | 6.2983 | -3.5257 | 280.6655 | 4931.4899 | -0.012562
84 |  | 3.948 | 58.8849 | 4187 | 0.0035622 | 6.2983 | 6.3019 | -3.5257 | 280.7254 | 4990.3748 | -0.012559
85 |  | 3.948 | 58.8723 | 4187 | 0.0035614 | 6.3019 | 6.3055 | -3.5257 | 280.7853 | 5049.2471 | -0.012557
86 |  | 3.948 | 58.8597 | 4187 | 0.0035607 | 6.3055 | 6.309 | -3.5257 | 280.8452 | 5108.1068 | -0.012554
87 |  | 3.948 | 58.8472 | 4187 | 0.0035599 | 6.309 | 6.3126 | -3.5257 | 280.9051 | 5166.954 | -0.012551
88 |  | 3.948 | 58.8346 | 4187 | 0.0035592 | 6.3126 | 6.3161 | -3.5257 | 280.965 | 5225.7886 | -0.012548
89 |  | 3.948 | 58.8221 | 4187 | 0.0035584 | 6.3161 | 6.3197 | -3.5257 | 281.025 | 5284.6107 | -0.012546
90 |  | 3.948 | 58.8095 | 4187 | 0.0035576 | 6.3197 | 6.3232 | -3.5257 | 281.0849 | 5343.4203 | -0.012543
91 |  | 3.948 | 58.797 | 4187 | 0.0035569 | 6.3232 | 6.3268 | -3.5257 | 281.1449 | 5402.2173 | -0.01254
92 |  | 3.948 | 58.7845 | 4187 | 0.0035561 | 6.3268 | 6.3304 | -3.5257 | 281.2049 | 5461.0017 | -0.012538
93 |  | 3.948 | 58.7719 | 4187 | 0.0035554 | 6.3304 | 6.3339 | -3.5257 | 281.2648 | 5519.7736 | -0.012535
94 |  | 3.948 | 58.7594 | 4187 | 0.0035546 | 6.3339 | 6.3375 | -3.5257 | 281.3249 | 5578.533 | -0.012532
95 |  | 3.948 | 58.7468 | 4187 | 0.0035539 | 6.3375 | 6.341 | -3.5257 | 281.3849 | 5637.2799 | -0.01253
96 |  | 3.948 | 58.7343 | 4187 | 0.0035531 | 6.341 | 6.3446 | -3.5257 | 281.4449 | 5696.0142 | -0.012527
97 |  | 3.948 | 58.7218 | 4187 | 0.0035523 | 6.3446 | 6.3481 | -3.5257 | 281.5049 | 5754.736 | -0.012524
98 |  | 3.948 | 58.7093 | 4187 | 0.0035516 | 6.3481 | 6.3517 | -3.5257 | 281.565 | 5813.4452 | -0.012522
99 |  | 3.948 | 58.6967 | 4187 | 0.0035508 | 6.3517 | 6.3552 | -3.5257 | 281.6251 | 5872.142 | -0.012519
100 |  | 3.948 | 58.6842 | 4187 | 0.0035501 | 6.3552 | 6.3588 | -3.5257 | 281.6851 | 5930.8262 | -0.012516
101 |  | 3.948 | 58.6717 | 4187 | 0.0035493 | 6.3588 | 6.3623 | -3.5257 | 281.7452 | 5989.4979 | -0.012514
102 |  | 3.948 | 58.6592 | 4187 | 0.0035485 | 6.3623 | 6.3659 | -3.5257 | 281.8053 | 6048.1571 | -0.012511
103 |  | 3.948 | 58.6467 | 4187 | 0.0035478 | 6.3659 | 6.3694 | -3.5257 | 281.8654 | 6106.8038 | -0.012508
104 |  | 3.948 | 58.6342 | 4187 | 0.003547 | 6.3694 | 6.373 | -3.5257 | 281.9256 | 6165.438 | -0.012506
105 |  | 3.948 | 58.6217 | 4187 | 0.0035463 | 6.373 | 6.3765 | -3.5257 | 281.9857 | 6224.0597 | -0.012503
106 |  | 3.948 | 58.6092 | 4187 | 0.0035455 | 6.3765 | 6.3801 | -3.5257 | 282.0459 | 6282.6688 | -0.0125
107 |  | 3.948 | 58.5967 | 4187 | 0.0035448 | 6.3801 | 6.3836 | -3.5257 | 282.106 | 6341.2655 | -0.012498
108 |  | 3.948 | 58.5842 | 4187 | 0.003544 | 6.3836 | 6.3872 | -3.5257 | 282.1662 | 6399.8497 | -0.012495
109 |  | 3.948 | 58.5717 | 4187 | 0.0035433 | 6.3872 | 6.3907 | -3.5257 | 282.2264 | 6458.4213 | -0.012492
110 |  | 3.948 | 58.5592 | 4187 | 0.0035425 | 6.3907 | 6.3942 | -3.5257 | 282.2866 | 6516.9805 | -0.01249
111 |  | 3.948 | 58.5467 | 4187 | 0.0035417 | 6.3942 | 6.3978 | -3.5257 | 282.3468 | 6575.5272 | -0.012487
112 |  | 3.948 | 58.5342 | 4187 | 0.003541 | 6.3978 | 6.4013 | -3.5257 | 282.4071 | 6634.0614 | -0.012484
113 |  | 3.948 | 58.5217 | 4187 | 0.0035402 | 6.4013 | 6.4049 | -3.5257 | 282.4673 | 6692.5831 | -0.012482
114 |  | 3.948 | 58.5092 | 4187 | 0.0035395 | 6.4049 | 6.4084 | -3.5257 | 282.5276 | 6751.0924 | -0.012479
115 |  | 3.948 | 58.4968 | 4187 | 0.0035387 | 6.4084 | 6.4119 | -3.5257 | 282.5879 | 6809.5891 | -0.012476
116 |  | 3.948 | 58.4843 | 4187 | 0.003538 | 6.4119 | 6.4155 | -3.5257 | 282.6481 | 6868.0734 | -0.012474
117 |  | 3.948 | 58.4718 | 4187 | 0.0035372 | 6.4155 | 6.419 | -3.5257 | 282.7084 | 6926.5452 | -0.012471
118 |  | 3.948 | 58.4593 | 4187 | 0.0035365 | 6.419 | 6.4226 | -3.5257 | 282.7687 | 6985.0046 | -0.012468
119 |  | 3.948 | 58.4469 | 4187 | 0.0035357 | 6.4226 | 6.4261 | -3.5257 | 282.8291 | 7043.4514 | -0.012466
120 |  | 3.948 | 58.4344 | 4187 | 0.003535 | 6.4261 | 6.4296 | -3.5257 | 282.8894 | 7101.8859 | -0.012463
121 |  | 3.948 | 58.4219 | 4187 | 0.0035342 | 6.4296 | 6.4332 | -3.5257 | 282.9498 | 7160.3078 | -0.01246
122 |  | 3.948 | 58.4095 | 4187 | 0.0035334 | 6.4332 | 6.4367 | -3.5257 | 283.0101 | 7218.7173 | -0.012458
123 |  | 3.948 | 58.397 | 4187 | 0.0035327 | 6.4367 | 6.4402 | -3.5257 | 283.0705 | 7277.1143 | -0.012455
124 |  | 3.948 | 58.3846 | 4187 | 0.0035319 | 6.4402 | 6.4438 | -3.5257 | 283.1309 | 7335.4989 | -0.012452
125 |  | 3.948 | 58.3721 | 4187 | 0.0035312 | 6.4438 | 6.4473 | -3.5257 | 283.1913 | 7393.871 | -0.01245
126 |  | 3.948 | 58.3597 | 4187 | 0.0035304 | 6.4473 | 6.4508 | -3.5257 | 283.2517 | 7452.2307 | -0.012447
127 |  | 3.948 | 58.3472 | 4187 | 0.0035297 | 6.4508 | 6.4543 | -3.5257 | 283.3121 | 7510.5779 | -0.012445
128 |  | 3.948 | 58.3348 | 4187 | 0.0035289 | 6.4543 | 6.4579 | -3.5257 | 283.3726 | 7568.9126 | -0.012442
129 |  | 3.948 | 58.3223 | 4187 | 0.0035282 | 6.4579 | 6.4614 | -3.5257 | 283.433 | 7627.235 | -0.012439
130 |  | 3.948 | 58.3099 | 4187 | 0.0035274 | 6.4614 | 6.4649 | -3.5257 | 283.4935 | 7685.5449 | -0.012437
131 |  | 3.948 | 58.2975 | 4187 | 0.0035267 | 6.4649 | 6.4685 | -3.5257 | 283.554 | 7743.8423 | -0.012434
132 |  | 3.948 | 58.285 | 4187 | 0.0035259 | 6.4685 | 6.472 | -3.5257 | 283.6144 | 7802.1274 | -0.012431
133 |  | 3.948 | 58.2726 | 4187 | 0.0035252 | 6.472 | 6.4755 | -3.5257 | 283.6749 | 7860.3999 | -0.012429
134 |  | 3.948 | 58.2602 | 4187 | 0.0035244 | 6.4755 | 6.479 | -3.5257 | 283.7355 | 7918.6601 | -0.012426
135 |  | 3.948 | 58.2477 | 4187 | 0.0035237 | 6.479 | 6.4826 | -3.5257 | 283.796 | 7976.9078 | -0.012423
136 |  | 3.948 | 58.2353 | 4187 | 0.0035229 | 6.4826 | 6.4861 | -3.5257 | 283.8565 | 8035.1432 | -0.012421
137 |  | 3.948 | 58.2229 | 4187 | 0.0035222 | 6.4861 | 6.4896 | -3.5257 | 283.9171 | 8093.3661 | -0.012418
138 |  | 3.948 | 58.2105 | 4187 | 0.0035214 | 6.4896 | 6.4931 | -3.5257 | 283.9777 | 8151.5765 | -0.012415
139 |  | 3.948 | 58.1981 | 4187 | 0.0035207 | 6.4931 | 6.4966 | -3.5257 | 284.0382 | 8209.7746 | -0.012413
140 |  | 3.948 | 58.1856 | 4187 | 0.0035199 | 6.4966 | 6.5002 | -3.5257 | 284.0988 | 8267.9602 | -0.01241
141 |  | 3.948 | 58.1732 | 4187 | 0.0035192 | 6.5002 | 6.5037 | -3.5257 | 284.1594 | 8326.1335 | -0.012407
142 |  | 3.948 | 58.1608 | 4187 | 0.0035184 | 6.5037 | 6.5072 | -3.5257 | 284.2201 | 8384.2943 | -0.012405
143 |  | 3.948 | 58.1484 | 4187 | 0.0035177 | 6.5072 | 6.5107 | -3.5257 | 284.2807 | 8442.4427 | -0.012402
144 |  | 3.948 | 58.136 | 4187 | 0.0035169 | 6.5107 | 6.5142 | -3.5257 | 284.3413 | 8500.5787 | -0.012399
145 |  | 3.948 | 58.1236 | 4187 | 0.0035161 | 6.5142 | 6.5178 | -3.5257 | 284.402 | 8558.7024 | -0.012397
146 |  | 3.948 | 58.1112 | 4187 | 0.0035154 | 6.5178 | 6.5213 | -3.5257 | 284.4627 | 8616.8136 | -0.012394
147 |  | 3.948 | 58.0988 | 4187 | 0.0035147 | 6.5213 | 6.5248 | -3.5257 | 284.5233 | 8674.9124 | -0.012392
148 |  | 3.948 | 58.0864 | 4187 | 0.0035139 | 6.5248 | 6.5283 | -3.5257 | 284.584 | 8732.9989 | -0.012389
149 |  | 3.948 | 58.0741 | 4187 | 0.0035132 | 6.5283 | 6.5318 | -3.5257 | 284.6448 | 8791.0729 | -0.012386
150 |  | 3.948 | 58.0617 | 4187 | 0.0035124 | 6.5318 | 6.5353 | -3.5257 | 284.7055 | 8849.1346 | -0.012384
151 |  | 3.948 | 58.0493 | 4187 | 0.0035117 | 6.5353 | 6.5388 | -3.5257 | 284.7662 | 8907.1839 | -0.012381
152 |  | 3.948 | 58.0369 | 4187 | 0.0035109 | 6.5388 | 6.5423 | -3.5257 | 284.827 | 8965.2208 | -0.012378
153 |  | 3.948 | 58.0245 | 4187 | 0.0035102 | 6.5423 | 6.5459 | -3.5257 | 284.8877 | 9023.2453 | -0.012376
154 |  | 3.948 | 58.0121 | 4187 | 0.0035094 | 6.5459 | 6.5494 | -3.5257 | 284.9485 | 9081.2574 | -0.012373
155 |  | 3.948 | 57.9998 | 4187 | 0.0035087 | 6.5494 | 6.5529 | -3.5257 | 285.0093 | 9139.2572 | -0.01237
156 |  | 3.948 | 57.9874 | 4187 | 0.0035079 | 6.5529 | 6.5564 | -3.5257 | 285.0701 | 9197.2446 | -0.012368
157 |  | 3.948 | 57.975 | 4187 | 0.0035072 | 6.5564 | 6.5599 | -3.5257 | 285.1309 | 9255.2197 | -0.012365
158 |  | 3.948 | 57.9627 | 4187 | 0.0035064 | 6.5599 | 6.5634 | -3.5257 | 285.1917 | 9313.1823 | -0.012363
159 |  | 3.948 | 57.9503 | 4187 | 0.0035057 | 6.5634 | 6.5669 | -3.5257 | 285.2526 | 9371.1326 | -0.01236
160 |  | 3.948 | 57.9379 | 4187 | 0.0035049 | 6.5669 | 6.5704 | -3.5257 | 285.3134 | 9429.0706 | -0.012357
161 |  | 3.948 | 57.9256 | 4187 | 0.0035042 | 6.5704 | 6.5739 | -3.5257 | 285.3743 | 9486.9962 | -0.012355
162 |  | 3.948 | 57.9132 | 4187 | 0.0035034 | 6.5739 | 6.5774 | -3.5257 | 285.4352 | 9544.9094 | -0.012352
163 |  | 3.948 | 57.9009 | 4187 | 0.0035027 | 6.5774 | 6.5809 | -3.5257 | 285.4961 | 9602.8103 | -0.012349
164 |  | 3.948 | 57.8885 | 4187 | 0.0035019 | 6.5809 | 6.5844 | -3.5257 | 285.557 | 9660.6988 | -0.012347
165 |  | 3.948 | 57.8762 | 4187 | 0.0035012 | 6.5844 | 6.5879 | -3.5257 | 285.6179 | 9718.575 | -0.012344
166 |  | 3.948 | 57.8638 | 4187 | 0.0035004 | 6.5879 | 6.5914 | -3.5257 | 285.6788 | 9776.4389 | -0.012341
167 |  | 3.948 | 57.8515 | 4187 | 0.0034997 | 6.5914 | 6.5949 | -3.5257 | 285.7398 | 9834.2904 | -0.012339
168 |  | 3.948 | 57.8392 | 4187 | 0.0034989 | 6.5949 | 6.5984 | -3.5257 | 285.8007 | 9892.1295 | -0.012336
169 |  | 3.948 | 57.8268 | 4187 | 0.0034982 | 6.5984 | 6.6019 | -3.5257 | 285.8617 | 9949.9564 | -0.012334
170 |  | 3.948 | 57.8145 | 4187 | 0.0034974 | 6.6019 | 6.6054 | -3.5257 | 285.9227 | 10007.7708 | -0.012331
171 |  | 3.948 | 57.8022 | 4187 | 0.0034967 | 6.6054 | 6.6089 | -3.5257 | 285.9837 | 10065.573 | -0.012328
172 |  | 3.948 | 57.7898 | 4187 | 0.003496 | 6.6089 | 6.6124 | -3.5257 | 286.0447 | 10123.3628 | -0.012326
173 |  | 3.948 | 57.7775 | 4187 | 0.0034952 | 6.6124 | 6.6159 | -3.5257 | 286.1057 | 10181.1404 | -0.012323
174 |  | 3.948 | 57.7652 | 4187 | 0.0034945 | 6.6159 | 6.6194 | -3.5257 | 286.1667 | 10238.9055 | -0.01232
175 |  | 3.948 | 57.7529 | 4187 | 0.0034937 | 6.6194 | 6.6229 | -3.5257 | 286.2278 | 10296.6584 | -0.012318
176 |  | 3.948 | 57.7405 | 4187 | 0.003493 | 6.6229 | 6.6264 | -3.5257 | 286.2888 | 10354.399 | -0.012315
177 |  | 3.948 | 57.7282 | 4187 | 0.0034922 | 6.6264 | 6.6299 | -3.5257 | 286.3499 | 10412.1272 | -0.012313
178 |  | 3.948 | 57.7159 | 4187 | 0.0034915 | 6.6299 | 6.6334 | -3.5257 | 286.411 | 10469.8431 | -0.01231
179 |  | 3.948 | 57.7036 | 4187 | 0.0034907 | 6.6334 | 6.6369 | -3.5257 | 286.4721 | 10527.5467 | -0.012307
180 |  | 3.948 | 57.6913 | 4187 | 0.00349 | 6.6369 | 6.6403 | -3.5257 | 286.5332 | 10585.238 | -0.012305
181 |  | 3.948 | 57.679 | 4187 | 0.0034893 | 6.6403 | 6.6438 | -3.5257 | 286.5943 | 10642.917 | -0.012302
182 |  | 3.948 | 57.6667 | 4187 | 0.0034885 | 6.6438 | 6.6473 | -3.5257 | 286.6555 | 10700.5837 | -0.012299
183 |  | 3.948 | 57.6544 | 4187 | 0.0034878 | 6.6473 | 6.6508 | -3.5257 | 286.7166 | 10758.2381 | -0.012297
184 |  | 3.948 | 57.6421 | 4187 | 0.003487 | 6.6508 | 6.6543 | -3.5257 | 286.7778 | 10815.8802 | -0.012294
185 |  | 3.948 | 57.6298 | 4187 | 0.0034863 | 6.6543 | 6.6578 | -3.5257 | 286.839 | 10873.51 | -0.012292
186 |  | 3.948 | 57.6175 | 4187 | 0.0034855 | 6.6578 | 6.6613 | -3.5257 | 286.9002 | 10931.1275 | -0.012289
187 |  | 3.948 | 57.6052 | 4187 | 0.0034848 | 6.6613 | 6.6648 | -3.5257 | 286.9614 | 10988.7328 | -0.012286
188 |  | 3.948 | 57.5929 | 4187 | 0.003484 | 6.6648 | 6.6682 | -3.5257 | 287.0226 | 11046.3257 | -0.012284
189 |  | 3.948 | 57.5807 | 4187 | 0.0034833 | 6.6682 | 6.6717 | -3.5257 | 287.0838 | 11103.9064 | -0.012281
190 |  | 3.948 | 57.5684 | 4187 | 0.0034826 | 6.6717 | 6.6752 | -3.5257 | 287.1451 | 11161.4747 | -0.012278
191 |  | 3.948 | 57.5561 | 4187 | 0.0034818 | 6.6752 | 6.6787 | -3.5257 | 287.2063 | 11219.0308 | -0.012276
192 |  | 3.948 | 57.5438 | 4187 | 0.0034811 | 6.6787 | 6.6822 | -3.5257 | 287.2676 | 11276.5747 | -0.012273
193 |  | 3.948 | 57.5315 | 4187 | 0.0034803 | 6.6822 | 6.6856 | -3.5257 | 287.3289 | 11334.1062 | -0.012271
194 |  | 3.948 | 57.5193 | 4187 | 0.0034796 | 6.6856 | 6.6891 | -3.5257 | 287.3902 | 11391.6255 | -0.012268
195 |  | 3.948 | 57.507 | 4187 | 0.0034788 | 6.6891 | 6.6926 | -3.5257 | 287.4515 | 11449.1325 | -0.012265
196 |  | 3.948 | 57.4947 | 4187 | 0.0034781 | 6.6926 | 6.6961 | -3.5257 | 287.5128 | 11506.6272 | -0.012263
197 |  | 3.948 | 57.4825 | 4187 | 0.0034774 | 6.6961 | 6.6996 | -3.5257 | 287.5741 | 11564.1097 | -0.01226
198 |  | 3.948 | 57.4702 | 4187 | 0.0034766 | 6.6996 | 6.703 | -3.5257 | 287.6355 | 11621.5799 | -0.012257
199 |  | 3.948 | 57.458 | 4187 | 0.0034759 | 6.703 | 6.7065 | -3.5257 | 287.6968 | 11679.0379 | -0.012255
200 |  | 3.948 | 57.4457 | 4187 | 0.0034751 | 6.7065 | 6.71 | -3.5257 | 287.7582 | 11736.4836 | -0.012252
201 |  | 3.948 | 57.4335 | 4187 | 0.0034744 | 6.71 | 6.7135 | -3.5257 | 287.8196 | 11793.9171 | -0.01225
202 |  | 3.948 | 57.4212 | 4187 | 0.0034737 | 6.7135 | 6.7169 | -3.5257 | 287.881 | 11851.3383 | -0.012247
203 |  | 3.948 | 57.409 | 4187 | 0.0034729 | 6.7169 | 6.7204 | -3.5257 | 287.9424 | 11908.7472 | -0.012244
204 |  | 3.948 | 57.3967 | 4187 | 0.0034722 | 6.7204 | 6.7239 | -3.5257 | 288.0038 | 11966.1439 | -0.012242
205 |  | 3.948 | 57.3845 | 4187 | 0.0034714 | 6.7239 | 6.7274 | -3.5257 | 288.0653 | 12023.5284 | -0.012239
206 |  | 3.948 | 57.3722 | 4187 | 0.0034707 | 6.7274 | 6.7308 | -3.5257 | 288.1267 | 12080.9007 | -0.012237
207 |  | 3.948 | 57.36 | 4187 | 0.00347 | 6.7308 | 6.7343 | -3.5257 | 288.1882 | 12138.2607 | -0.012234
208 |  | 3.948 | 57.3478 | 4187 | 0.0034692 | 6.7343 | 6.7378 | -3.5257 | 288.2497 | 12195.6084 | -0.012231
209 |  | 3.948 | 57.3355 | 4187 | 0.0034685 | 6.7378 | 6.7412 | -3.5257 | 288.3112 | 12252.9439 | -0.012229
210 |  | 3.948 | 57.3233 | 4187 | 0.0034677 | 6.7412 | 6.7447 | -3.5257 | 288.3727 | 12310.2673 | -0.012226
211 |  | 3.948 | 57.3111 | 4187 | 0.003467 | 6.7447 | 6.7482 | -3.5257 | 288.4342 | 12367.5783 | -0.012224
212 |  | 3.948 | 57.2989 | 4187 | 0.0034663 | 6.7482 | 6.7516 | -3.5257 | 288.4957 | 12424.8772 | -0.012221
213 |  | 3.948 | 57.2866 | 4187 | 0.0034655 | 6.7516 | 6.7551 | -3.5257 | 288.5573 | 12482.1638 | -0.012218
214 |  | 3.948 | 57.2744 | 4187 | 0.0034648 | 6.7551 | 6.7586 | -3.5257 | 288.6188 | 12539.4382 | -0.012216
215 |  | 3.948 | 57.2622 | 4187 | 0.003464 | 6.7586 | 6.762 | -3.5257 | 288.6804 | 12596.7004 | -0.012213
216 |  | 3.948 | 57.25 | 4187 | 0.0034633 | 6.762 | 6.7655 | -3.5257 | 288.742 | 12653.9504 | -0.012211
217 |  | 3.948 | 57.2378 | 4187 | 0.0034626 | 6.7655 | 6.769 | -3.5257 | 288.8036 | 12711.1882 | -0.012208
218 |  | 3.948 | 57.2256 | 4187 | 0.0034618 | 6.769 | 6.7724 | -3.5257 | 288.8652 | 12768.4138 | -0.012205
219 |  | 3.948 | 57.2134 | 4187 | 0.0034611 | 6.7724 | 6.7759 | -3.5257 | 288.9268 | 12825.6271 | -0.012203
220 |  | 3.948 | 57.2012 | 4187 | 0.0034603 | 6.7759 | 6.7793 | -3.5257 | 288.9884 | 12882.8283 | -0.0122
221 |  | 3.948 | 57.189 | 4187 | 0.0034596 | 6.7793 | 6.7828 | -3.5257 | 289.0501 | 12940.0172 | -0.012197
222 |  | 3.948 | 57.1768 | 4187 | 0.0034589 | 6.7828 | 6.7863 | -3.5257 | 289.1118 | 12997.194 | -0.012195
223 |  | 3.948 | 57.1646 | 4187 | 0.0034581 | 6.7863 | 6.7897 | -3.5257 | 289.1734 | 13054.3586 | -0.012192
224 |  | 3.948 | 57.1524 | 4187 | 0.0034574 | 6.7897 | 6.7932 | -3.5257 | 289.2351 | 13111.5109 | -0.01219
225 |  | 3.948 | 57.1402 | 4187 | 0.0034567 | 6.7932 | 6.7966 | -3.5257 | 289.2968 | 13168.6511 | -0.012187
226 |  | 3.948 | 57.128 | 4187 | 0.0034559 | 6.7966 | 6.8001 | -3.5257 | 289.3585 | 13225.7791 | -0.012184
227 |  | 3.948 | 57.1158 | 4187 | 0.0034552 | 6.8001 | 6.8035 | -3.5257 | 289.4203 | 13282.8949 | -0.012182
228 |  | 3.948 | 57.1036 | 4187 | 0.0034544 | 6.8035 | 6.807 | -3.5257 | 289.482 | 13339.9986 | -0.012179
229 |  | 3.948 | 57.0915 | 4187 | 0.0034537 | 6.807 | 6.8104 | -3.5257 | 289.5438 | 13397.09 | -0.012177
230 |  | 3.948 | 57.0793 | 4187 | 0.003453 | 6.8104 | 6.8139 | -3.5257 | 289.6055 | 13454.1693 | -0.012174
231 |  | 3.948 | 57.0671 | 4187 | 0.0034522 | 6.8139 | 6.8174 | -3.5257 | 289.6673 | 13511.2364 | -0.012172
232 |  | 3.948 | 57.0549 | 4187 | 0.0034515 | 6.8174 | 6.8208 | -3.5257 | 289.7291 | 13568.2913 | -0.012169
233 |  | 3.948 | 57.0428 | 4187 | 0.0034508 | 6.8208 | 6.8243 | -3.5257 | 289.7909 | 13625.3341 | -0.012166
234 |  | 3.948 | 57.0306 | 4187 | 0.00345 | 6.8243 | 6.8277 | -3.5257 | 289.8527 | 13682.3647 | -0.012164
235 |  | 3.948 | 57.0184 | 4187 | 0.0034493 | 6.8277 | 6.8312 | -3.5257 | 289.9146 | 13739.3831 | -0.012161
236 |  | 3.948 | 57.0063 | 4187 | 0.0034486 | 6.8312 | 6.8346 | -3.5257 | 289.9764 | 13796.3894 | -0.012159

## St88
|  |  | buis | verlies W/M | L /°C/sec
diam | wandikte |  | inhoud l/m |  | W/M
88.9 | 3.2 | 3.1416 | 5.3456 | 70.0168 | 4187
[8 empty] | J/sec/mtr | aantal mtr. | verlies
|  | buis | verlies W/M | L /°C/sec | verlies temp | begintemp | eindtemp | verlies | bij 1°C | totaal J/sec
|  | inhoud L |  | W/M | °C per M | °C | °C | per m°C | daling | aantal mtr
1 | 88.9 | 5.3456 | 70.0168 | 4187 | 0.0031283 | 6 | 6.0031 | -4.1186 | 319.6675 | 70.0168 | -0.012884
2 |  | 5.3456 | 70.0039 | 4187 | 0.0031277 | 6.0031 | 6.0063 | -4.1186 | 319.7264 | 140.0207 | -0.012882
3 |  | 5.3456 | 69.991 | 4187 | 0.0031271 | 6.0063 | 6.0094 | -4.1186 | 319.7852 | 210.0117 | -0.012879
4 |  | 5.3456 | 69.9781 | 4187 | 0.0031265 | 6.0094 | 6.0125 | -4.1186 | 319.8441 | 279.9899 | -0.012877
5 |  | 5.3456 | 69.9653 | 4187 | 0.0031259 | 6.0125 | 6.0156 | -4.1186 | 319.9029 | 349.9551 | -0.012875
6 |  | 5.3456 | 69.9524 | 4187 | 0.0031254 | 6.0156 | 6.0188 | -4.1186 | 319.9618 | 419.9075 | -0.012872
7 |  | 5.3456 | 69.9395 | 4187 | 0.0031248 | 6.0188 | 6.0219 | -4.1186 | 320.0207 | 489.847 | -0.01287
8 |  | 5.3456 | 69.9267 | 4187 | 0.0031242 | 6.0219 | 6.025 | -4.1186 | 320.0796 | 559.7737 | -0.012868
9 |  | 5.3456 | 69.9138 | 4187 | 0.0031236 | 6.025 | 6.0281 | -4.1186 | 320.1385 | 629.6875 | -0.012865
10 |  | 5.3456 | 69.9009 | 4187 | 0.0031231 | 6.0281 | 6.0313 | -4.1186 | 320.1974 | 699.5884 | -0.012863
11 |  | 5.3456 | 69.8881 | 4187 | 0.0031225 | 6.0313 | 6.0344 | -4.1186 | 320.2564 | 769.4765 | -0.01286
12 |  | 5.3456 | 69.8752 | 4187 | 0.0031219 | 6.0344 | 6.0375 | -4.1186 | 320.3153 | 839.3517 | -0.012858
13 |  | 5.3456 | 69.8623 | 4187 | 0.0031213 | 6.0375 | 6.0406 | -4.1186 | 320.3743 | 909.214 | -0.012856
14 |  | 5.3456 | 69.8495 | 4187 | 0.0031208 | 6.0406 | 6.0437 | -4.1186 | 320.4332 | 979.0635 | -0.012853
15 |  | 5.3456 | 69.8366 | 4187 | 0.0031202 | 6.0437 | 6.0469 | -4.1186 | 320.4922 | 1048.9001 | -0.012851
16 |  | 5.3456 | 69.8238 | 4187 | 0.0031196 | 6.0469 | 6.05 | -4.1186 | 320.5512 | 1118.7239 | -0.012849
17 |  | 5.3456 | 69.8109 | 4187 | 0.0031191 | 6.05 | 6.0531 | -4.1186 | 320.6102 | 1188.5348 | -0.012846
18 |  | 5.3456 | 69.7981 | 4187 | 0.0031185 | 6.0531 | 6.0562 | -4.1186 | 320.6692 | 1258.3329 | -0.012844
19 |  | 5.3456 | 69.7852 | 4187 | 0.0031179 | 6.0562 | 6.0593 | -4.1186 | 320.7282 | 1328.1181 | -0.012842
20 |  | 5.3456 | 69.7724 | 4187 | 0.0031173 | 6.0593 | 6.0625 | -4.1186 | 320.7872 | 1397.8905 | -0.012839
21 |  | 5.3456 | 69.7596 | 4187 | 0.0031168 | 6.0625 | 6.0656 | -4.1186 | 320.8463 | 1467.6501 | -0.012837
22 |  | 5.3456 | 69.7467 | 4187 | 0.0031162 | 6.0656 | 6.0687 | -4.1186 | 320.9053 | 1537.3968 | -0.012834
23 |  | 5.3456 | 69.7339 | 4187 | 0.0031156 | 6.0687 | 6.0718 | -4.1186 | 320.9644 | 1607.1307 | -0.012832
24 |  | 5.3456 | 69.7211 | 4187 | 0.003115 | 6.0718 | 6.0749 | -4.1186 | 321.0235 | 1676.8517 | -0.01283
25 |  | 5.3456 | 69.7082 | 4187 | 0.0031145 | 6.0749 | 6.078 | -4.1186 | 321.0826 | 1746.56 | -0.012827
26 |  | 5.3456 | 69.6954 | 4187 | 0.0031139 | 6.078 | 6.0811 | -4.1186 | 321.1417 | 1816.2554 | -0.012825
27 |  | 5.3456 | 69.6826 | 4187 | 0.0031133 | 6.0811 | 6.0843 | -4.1186 | 321.2008 | 1885.9379 | -0.012823
28 |  | 5.3456 | 69.6697 | 4187 | 0.0031127 | 6.0843 | 6.0874 | -4.1186 | 321.2599 | 1955.6077 | -0.01282
29 |  | 5.3456 | 69.6569 | 4187 | 0.0031122 | 6.0874 | 6.0905 | -4.1186 | 321.319 | 2025.2646 | -0.012818
30 |  | 5.3456 | 69.6441 | 4187 | 0.0031116 | 6.0905 | 6.0936 | -4.1186 | 321.3781 | 2094.9087 | -0.012816
31 |  | 5.3456 | 69.6313 | 4187 | 0.003111 | 6.0936 | 6.0967 | -4.1186 | 321.4373 | 2164.54 | -0.012813
32 |  | 5.3456 | 69.6185 | 4187 | 0.0031105 | 6.0967 | 6.0998 | -4.1186 | 321.4965 | 2234.1585 | -0.012811
33 |  | 5.3456 | 69.6057 | 4187 | 0.0031099 | 6.0998 | 6.1029 | -4.1186 | 321.5556 | 2303.7642 | -0.012808
34 |  | 5.3456 | 69.5929 | 4187 | 0.0031093 | 6.1029 | 6.106 | -4.1186 | 321.6148 | 2373.357 | -0.012806
35 |  | 5.3456 | 69.5801 | 4187 | 0.0031087 | 6.106 | 6.1091 | -4.1186 | 321.674 | 2442.9371 | -0.012804
36 |  | 5.3456 | 69.5673 | 4187 | 0.0031082 | 6.1091 | 6.1123 | -4.1186 | 321.7332 | 2512.5044 | -0.012801
37 |  | 5.3456 | 69.5545 | 4187 | 0.0031076 | 6.1123 | 6.1154 | -4.1186 | 321.7924 | 2582.0588 | -0.012799
38 |  | 5.3456 | 69.5417 | 4187 | 0.003107 | 6.1154 | 6.1185 | -4.1186 | 321.8516 | 2651.6005 | -0.012797
39 |  | 5.3456 | 69.5289 | 4187 | 0.0031064 | 6.1185 | 6.1216 | -4.1186 | 321.9109 | 2721.1293 | -0.012794
40 |  | 5.3456 | 69.5161 | 4187 | 0.0031059 | 6.1216 | 6.1247 | -4.1186 | 321.9701 | 2790.6454 | -0.012792
41 |  | 5.3456 | 69.5033 | 4187 | 0.0031053 | 6.1247 | 6.1278 | -4.1186 | 322.0294 | 2860.1486 | -0.01279
42 |  | 5.3456 | 69.4905 | 4187 | 0.0031047 | 6.1278 | 6.1309 | -4.1186 | 322.0887 | 2929.6391 | -0.012787
43 |  | 5.3456 | 69.4777 | 4187 | 0.0031042 | 6.1309 | 6.134 | -4.1186 | 322.1479 | 2999.1168 | -0.012785
44 |  | 5.3456 | 69.4649 | 4187 | 0.0031036 | 6.134 | 6.1371 | -4.1186 | 322.2072 | 3068.5817 | -0.012783
45 |  | 5.3456 | 69.4521 | 4187 | 0.003103 | 6.1371 | 6.1402 | -4.1186 | 322.2665 | 3138.0339 | -0.01278
46 |  | 5.3456 | 69.4393 | 4187 | 0.0031025 | 6.1402 | 6.1433 | -4.1186 | 322.3258 | 3207.4732 | -0.012778
47 |  | 5.3456 | 69.4266 | 4187 | 0.0031019 | 6.1433 | 6.1464 | -4.1186 | 322.3852 | 3276.8998 | -0.012776
48 |  | 5.3456 | 69.4138 | 4187 | 0.0031013 | 6.1464 | 6.1495 | -4.1186 | 322.4445 | 3346.3136 | -0.012773
49 |  | 5.3456 | 69.401 | 4187 | 0.0031007 | 6.1495 | 6.1526 | -4.1186 | 322.5038 | 3415.7146 | -0.012771
50 |  | 5.3456 | 69.3882 | 4187 | 0.0031002 | 6.1526 | 6.1557 | -4.1186 | 322.5632 | 3485.1028 | -0.012768
51 |  | 5.3456 | 69.3755 | 4187 | 0.0030996 | 6.1557 | 6.1588 | -4.1186 | 322.6226 | 3554.4783 | -0.012766
52 |  | 5.3456 | 69.3627 | 4187 | 0.003099 | 6.1588 | 6.1619 | -4.1186 | 322.6819 | 3623.841 | -0.012764
53 |  | 5.3456 | 69.35 | 4187 | 0.0030985 | 6.1619 | 6.165 | -4.1186 | 322.7413 | 3693.191 | -0.012761
54 |  | 5.3456 | 69.3372 | 4187 | 0.0030979 | 6.165 | 6.1681 | -4.1186 | 322.8007 | 3762.5282 | -0.012759
55 |  | 5.3456 | 69.3244 | 4187 | 0.0030973 | 6.1681 | 6.1712 | -4.1186 | 322.8601 | 3831.8526 | -0.012757
56 |  | 5.3456 | 69.3117 | 4187 | 0.0030967 | 6.1712 | 6.1743 | -4.1186 | 322.9196 | 3901.1643 | -0.012754
57 |  | 5.3456 | 69.2989 | 4187 | 0.0030962 | 6.1743 | 6.1774 | -4.1186 | 322.979 | 3970.4632 | -0.012752
58 |  | 5.3456 | 69.2862 | 4187 | 0.0030956 | 6.1774 | 6.1805 | -4.1186 | 323.0384 | 4039.7494 | -0.01275
59 |  | 5.3456 | 69.2734 | 4187 | 0.003095 | 6.1805 | 6.1836 | -4.1186 | 323.0979 | 4109.0228 | -0.012747
60 |  | 5.3456 | 69.2607 | 4187 | 0.0030945 | 6.1836 | 6.1867 | -4.1186 | 323.1574 | 4178.2834 | -0.012745
61 |  | 5.3456 | 69.2479 | 4187 | 0.0030939 | 6.1867 | 6.1898 | -4.1186 | 323.2168 | 4247.5314 | -0.012743
62 |  | 5.3456 | 69.2352 | 4187 | 0.0030933 | 6.1898 | 6.1929 | -4.1186 | 323.2763 | 4316.7665 | -0.01274
63 |  | 5.3456 | 69.2224 | 4187 | 0.0030928 | 6.1929 | 6.196 | -4.1186 | 323.3358 | 4385.989 | -0.012738
64 |  | 5.3456 | 69.2097 | 4187 | 0.0030922 | 6.196 | 6.1991 | -4.1186 | 323.3953 | 4455.1987 | -0.012736
65 |  | 5.3456 | 69.197 | 4187 | 0.0030916 | 6.1991 | 6.2021 | -4.1186 | 323.4549 | 4524.3957 | -0.012733
66 |  | 5.3456 | 69.1842 | 4187 | 0.0030911 | 6.2021 | 6.2052 | -4.1186 | 323.5144 | 4593.5799 | -0.012731
67 |  | 5.3456 | 69.1715 | 4187 | 0.0030905 | 6.2052 | 6.2083 | -4.1186 | 323.5739 | 4662.7514 | -0.012729
68 |  | 5.3456 | 69.1588 | 4187 | 0.0030899 | 6.2083 | 6.2114 | -4.1186 | 323.6335 | 4731.9102 | -0.012726
69 |  | 5.3456 | 69.146 | 4187 | 0.0030893 | 6.2114 | 6.2145 | -4.1186 | 323.693 | 4801.0562 | -0.012724
70 |  | 5.3456 | 69.1333 | 4187 | 0.0030888 | 6.2145 | 6.2176 | -4.1186 | 323.7526 | 4870.1895 | -0.012722
71 |  | 5.3456 | 69.1206 | 4187 | 0.0030882 | 6.2176 | 6.2207 | -4.1186 | 323.8122 | 4939.3102 | -0.012719
72 |  | 5.3456 | 69.1079 | 4187 | 0.0030876 | 6.2207 | 6.2238 | -4.1186 | 323.8718 | 5008.418 | -0.012717
73 |  | 5.3456 | 69.0952 | 4187 | 0.0030871 | 6.2238 | 6.2269 | -4.1186 | 323.9314 | 5077.5132 | -0.012715
74 |  | 5.3456 | 69.0825 | 4187 | 0.0030865 | 6.2269 | 6.2299 | -4.1186 | 323.991 | 5146.5957 | -0.012712
75 |  | 5.3456 | 69.0697 | 4187 | 0.0030859 | 6.2299 | 6.233 | -4.1186 | 324.0507 | 5215.6654 | -0.01271
76 |  | 5.3456 | 69.057 | 4187 | 0.0030854 | 6.233 | 6.2361 | -4.1186 | 324.1103 | 5284.7224 | -0.012708
77 |  | 5.3456 | 69.0443 | 4187 | 0.0030848 | 6.2361 | 6.2392 | -4.1186 | 324.17 | 5353.7668 | -0.012705
78 |  | 5.3456 | 69.0316 | 4187 | 0.0030842 | 6.2392 | 6.2423 | -4.1186 | 324.2296 | 5422.7984 | -0.012703
79 |  | 5.3456 | 69.0189 | 4187 | 0.0030837 | 6.2423 | 6.2454 | -4.1186 | 324.2893 | 5491.8173 | -0.0127
80 |  | 5.3456 | 69.0062 | 4187 | 0.0030831 | 6.2454 | 6.2484 | -4.1186 | 324.349 | 5560.8235 | -0.012698
81 |  | 5.3456 | 68.9935 | 4187 | 0.0030825 | 6.2484 | 6.2515 | -4.1186 | 324.4087 | 5629.817 | -0.012696
82 |  | 5.3456 | 68.9808 | 4187 | 0.003082 | 6.2515 | 6.2546 | -4.1186 | 324.4684 | 5698.7978 | -0.012693
83 |  | 5.3456 | 68.9681 | 4187 | 0.0030814 | 6.2546 | 6.2577 | -4.1186 | 324.5281 | 5767.766 | -0.012691
84 |  | 5.3456 | 68.9554 | 4187 | 0.0030808 | 6.2577 | 6.2608 | -4.1186 | 324.5878 | 5836.7214 | -0.012689
85 |  | 5.3456 | 68.9427 | 4187 | 0.0030803 | 6.2608 | 6.2639 | -4.1186 | 324.6476 | 5905.6642 | -0.012686
86 |  | 5.3456 | 68.9301 | 4187 | 0.0030797 | 6.2639 | 6.2669 | -4.1186 | 324.7073 | 5974.5942 | -0.012684
87 |  | 5.3456 | 68.9174 | 4187 | 0.0030791 | 6.2669 | 6.27 | -4.1186 | 324.7671 | 6043.5116 | -0.012682
88 |  | 5.3456 | 68.9047 | 4187 | 0.0030786 | 6.27 | 6.2731 | -4.1186 | 324.8269 | 6112.4163 | -0.012679
89 |  | 5.3456 | 68.892 | 4187 | 0.003078 | 6.2731 | 6.2762 | -4.1186 | 324.8866 | 6181.3083 | -0.012677
90 |  | 5.3456 | 68.8793 | 4187 | 0.0030774 | 6.2762 | 6.2792 | -4.1186 | 324.9464 | 6250.1876 | -0.012675
91 |  | 5.3456 | 68.8667 | 4187 | 0.0030769 | 6.2792 | 6.2823 | -4.1186 | 325.0062 | 6319.0543 | -0.012672
92 |  | 5.3456 | 68.854 | 4187 | 0.0030763 | 6.2823 | 6.2854 | -4.1186 | 325.0661 | 6387.9083 | -0.01267
93 |  | 5.3456 | 68.8413 | 4187 | 0.0030757 | 6.2854 | 6.2885 | -4.1186 | 325.1259 | 6456.7496 | -0.012668
94 |  | 5.3456 | 68.8287 | 4187 | 0.0030752 | 6.2885 | 6.2916 | -4.1186 | 325.1857 | 6525.5783 | -0.012665
95 |  | 5.3456 | 68.816 | 4187 | 0.0030746 | 6.2916 | 6.2946 | -4.1186 | 325.2456 | 6594.3943 | -0.012663
96 |  | 5.3456 | 68.8033 | 4187 | 0.003074 | 6.2946 | 6.2977 | -4.1186 | 325.3054 | 6663.1976 | -0.012661
97 |  | 5.3456 | 68.7907 | 4187 | 0.0030735 | 6.2977 | 6.3008 | -4.1186 | 325.3653 | 6731.9882 | -0.012658
98 |  | 5.3456 | 68.778 | 4187 | 0.0030729 | 6.3008 | 6.3038 | -4.1186 | 325.4252 | 6800.7662 | -0.012656
99 |  | 5.3456 | 68.7653 | 4187 | 0.0030723 | 6.3038 | 6.3069 | -4.1186 | 325.4851 | 6869.5316 | -0.012654
100 |  | 5.3456 | 68.7527 | 4187 | 0.0030718 | 6.3069 | 6.31 | -4.1186 | 325.545 | 6938.2843 | -0.012652
101 |  | 5.3456 | 68.74 | 4187 | 0.0030712 | 6.31 | 6.3131 | -4.1186 | 325.6049 | 7007.0243 | -0.012649
102 |  | 5.3456 | 68.7274 | 4187 | 0.0030706 | 6.3131 | 6.3161 | -4.1186 | 325.6648 | 7075.7517 | -0.012647
103 |  | 5.3456 | 68.7147 | 4187 | 0.0030701 | 6.3161 | 6.3192 | -4.1186 | 325.7248 | 7144.4665 | -0.012645
104 |  | 5.3456 | 68.7021 | 4187 | 0.0030695 | 6.3192 | 6.3223 | -4.1186 | 325.7847 | 7213.1686 | -0.012642
105 |  | 5.3456 | 68.6895 | 4187 | 0.0030689 | 6.3223 | 6.3253 | -4.1186 | 325.8447 | 7281.858 | -0.01264
106 |  | 5.3456 | 68.6768 | 4187 | 0.0030684 | 6.3253 | 6.3284 | -4.1186 | 325.9046 | 7350.5349 | -0.012638
107 |  | 5.3456 | 68.6642 | 4187 | 0.0030678 | 6.3284 | 6.3315 | -4.1186 | 325.9646 | 7419.199 | -0.012635
108 |  | 5.3456 | 68.6515 | 4187 | 0.0030673 | 6.3315 | 6.3345 | -4.1186 | 326.0246 | 7487.8506 | -0.012633
109 |  | 5.3456 | 68.6389 | 4187 | 0.0030667 | 6.3345 | 6.3376 | -4.1186 | 326.0846 | 7556.4895 | -0.012631
110 |  | 5.3456 | 68.6263 | 4187 | 0.0030661 | 6.3376 | 6.3407 | -4.1186 | 326.1446 | 7625.1158 | -0.012628
111 |  | 5.3456 | 68.6137 | 4187 | 0.0030656 | 6.3407 | 6.3437 | -4.1186 | 326.2047 | 7693.7295 | -0.012626
112 |  | 5.3456 | 68.601 | 4187 | 0.003065 | 6.3437 | 6.3468 | -4.1186 | 326.2647 | 7762.3305 | -0.012624
113 |  | 5.3456 | 68.5884 | 4187 | 0.0030644 | 6.3468 | 6.3499 | -4.1186 | 326.3248 | 7830.9189 | -0.012621
114 |  | 5.3456 | 68.5758 | 4187 | 0.0030639 | 6.3499 | 6.3529 | -4.1186 | 326.3848 | 7899.4947 | -0.012619
115 |  | 5.3456 | 68.5632 | 4187 | 0.0030633 | 6.3529 | 6.356 | -4.1186 | 326.4449 | 7968.0578 | -0.012617
116 |  | 5.3456 | 68.5506 | 4187 | 0.0030627 | 6.356 | 6.3591 | -4.1186 | 326.505 | 8036.6084 | -0.012614
117 |  | 5.3456 | 68.5379 | 4187 | 0.0030622 | 6.3591 | 6.3621 | -4.1186 | 326.5651 | 8105.1463 | -0.012612
118 |  | 5.3456 | 68.5253 | 4187 | 0.0030616 | 6.3621 | 6.3652 | -4.1186 | 326.6252 | 8173.6717 | -0.01261
119 |  | 5.3456 | 68.5127 | 4187 | 0.0030611 | 6.3652 | 6.3682 | -4.1186 | 326.6853 | 8242.1844 | -0.012607
120 |  | 5.3456 | 68.5001 | 4187 | 0.0030605 | 6.3682 | 6.3713 | -4.1186 | 326.7454 | 8310.6845 | -0.012605
121 |  | 5.3456 | 68.4875 | 4187 | 0.0030599 | 6.3713 | 6.3744 | -4.1186 | 326.8055 | 8379.172 | -0.012603
122 |  | 5.3456 | 68.4749 | 4187 | 0.0030594 | 6.3744 | 6.3774 | -4.1186 | 326.8657 | 8447.6469 | -0.0126
123 |  | 5.3456 | 68.4623 | 4187 | 0.0030588 | 6.3774 | 6.3805 | -4.1186 | 326.9258 | 8516.1092 | -0.012598
124 |  | 5.3456 | 68.4497 | 4187 | 0.0030582 | 6.3805 | 6.3835 | -4.1186 | 326.986 | 8584.5589 | -0.012596
125 |  | 5.3456 | 68.4371 | 4187 | 0.0030577 | 6.3835 | 6.3866 | -4.1186 | 327.0462 | 8652.996 | -0.012593
126 |  | 5.3456 | 68.4245 | 4187 | 0.0030571 | 6.3866 | 6.3897 | -4.1186 | 327.1064 | 8721.4205 | -0.012591
127 |  | 5.3456 | 68.4119 | 4187 | 0.0030565 | 6.3897 | 6.3927 | -4.1186 | 327.1666 | 8789.8324 | -0.012589
128 |  | 5.3456 | 68.3993 | 4187 | 0.003056 | 6.3927 | 6.3958 | -4.1186 | 327.2268 | 8858.2317 | -0.012586
129 |  | 5.3456 | 68.3867 | 4187 | 0.0030554 | 6.3958 | 6.3988 | -4.1186 | 327.287 | 8926.6185 | -0.012584
130 |  | 5.3456 | 68.3742 | 4187 | 0.0030549 | 6.3988 | 6.4019 | -4.1186 | 327.3473 | 8994.9927 | -0.012582
131 |  | 5.3456 | 68.3616 | 4187 | 0.0030543 | 6.4019 | 6.4049 | -4.1186 | 327.4075 | 9063.3542 | -0.01258
132 |  | 5.3456 | 68.349 | 4187 | 0.0030537 | 6.4049 | 6.408 | -4.1186 | 327.4678 | 9131.7032 | -0.012577
133 |  | 5.3456 | 68.3364 | 4187 | 0.0030532 | 6.408 | 6.411 | -4.1186 | 327.5281 | 9200.0397 | -0.012575
134 |  | 5.3456 | 68.3238 | 4187 | 0.0030526 | 6.411 | 6.4141 | -4.1186 | 327.5883 | 9268.3635 | -0.012573
135 |  | 5.3456 | 68.3113 | 4187 | 0.0030521 | 6.4141 | 6.4171 | -4.1186 | 327.6486 | 9336.6748 | -0.01257
136 |  | 5.3456 | 68.2987 | 4187 | 0.0030515 | 6.4171 | 6.4202 | -4.1186 | 327.7089 | 9404.9735 | -0.012568
137 |  | 5.3456 | 68.2861 | 4187 | 0.0030509 | 6.4202 | 6.4233 | -4.1186 | 327.7692 | 9473.2596 | -0.012566
138 |  | 5.3456 | 68.2736 | 4187 | 0.0030504 | 6.4233 | 6.4263 | -4.1186 | 327.8296 | 9541.5332 | -0.012563
139 |  | 5.3456 | 68.261 | 4187 | 0.0030498 | 6.4263 | 6.4294 | -4.1186 | 327.8899 | 9609.7942 | -0.012561
140 |  | 5.3456 | 68.2484 | 4187 | 0.0030492 | 6.4294 | 6.4324 | -4.1186 | 327.9503 | 9678.0426 | -0.012559
141 |  | 5.3456 | 68.2359 | 4187 | 0.0030487 | 6.4324 | 6.4354 | -4.1186 | 328.0106 | 9746.2785 | -0.012556
142 |  | 5.3456 | 68.2233 | 4187 | 0.0030481 | 6.4354 | 6.4385 | -4.1186 | 328.071 | 9814.5019 | -0.012554
143 |  | 5.3456 | 68.2108 | 4187 | 0.0030476 | 6.4385 | 6.4415 | -4.1186 | 328.1314 | 9882.7126 | -0.012552
144 |  | 5.3456 | 68.1982 | 4187 | 0.003047 | 6.4415 | 6.4446 | -4.1186 | 328.1918 | 9950.9109 | -0.012549
145 |  | 5.3456 | 68.1857 | 4187 | 0.0030464 | 6.4446 | 6.4476 | -4.1186 | 328.2522 | 10019.0965 | -0.012547
146 |  | 5.3456 | 68.1731 | 4187 | 0.0030459 | 6.4476 | 6.4507 | -4.1186 | 328.3126 | 10087.2697 | -0.012545
147 |  | 5.3456 | 68.1606 | 4187 | 0.0030453 | 6.4507 | 6.4537 | -4.1186 | 328.373 | 10155.4303 | -0.012543
148 |  | 5.3456 | 68.148 | 4187 | 0.0030448 | 6.4537 | 6.4568 | -4.1186 | 328.4334 | 10223.5783 | -0.01254
149 |  | 5.3456 | 68.1355 | 4187 | 0.0030442 | 6.4568 | 6.4598 | -4.1186 | 328.4939 | 10291.7138 | -0.012538
150 |  | 5.3456 | 68.123 | 4187 | 0.0030436 | 6.4598 | 6.4629 | -4.1186 | 328.5543 | 10359.8368 | -0.012536
151 |  | 5.3456 | 68.1104 | 4187 | 0.0030431 | 6.4629 | 6.4659 | -4.1186 | 328.6148 | 10427.9472 | -0.012533
152 |  | 5.3456 | 68.0979 | 4187 | 0.0030425 | 6.4659 | 6.4689 | -4.1186 | 328.6753 | 10496.0451 | -0.012531
153 |  | 5.3456 | 68.0854 | 4187 | 0.003042 | 6.4689 | 6.472 | -4.1186 | 328.7358 | 10564.1305 | -0.012529
154 |  | 5.3456 | 68.0728 | 4187 | 0.0030414 | 6.472 | 6.475 | -4.1186 | 328.7963 | 10632.2033 | -0.012526
155 |  | 5.3456 | 68.0603 | 4187 | 0.0030408 | 6.475 | 6.4781 | -4.1186 | 328.8568 | 10700.2636 | -0.012524
156 |  | 5.3456 | 68.0478 | 4187 | 0.0030403 | 6.4781 | 6.4811 | -4.1186 | 328.9173 | 10768.3114 | -0.012522
157 |  | 5.3456 | 68.0353 | 4187 | 0.0030397 | 6.4811 | 6.4842 | -4.1186 | 328.9779 | 10836.3466 | -0.012519
158 |  | 5.3456 | 68.0227 | 4187 | 0.0030392 | 6.4842 | 6.4872 | -4.1186 | 329.0384 | 10904.3694 | -0.012517
159 |  | 5.3456 | 68.0102 | 4187 | 0.0030386 | 6.4872 | 6.4902 | -4.1186 | 329.099 | 10972.3796 | -0.012515
160 |  | 5.3456 | 67.9977 | 4187 | 0.003038 | 6.4902 | 6.4933 | -4.1186 | 329.1595 | 11040.3773 | -0.012513
161 |  | 5.3456 | 67.9852 | 4187 | 0.0030375 | 6.4933 | 6.4963 | -4.1186 | 329.2201 | 11108.3625 | -0.01251
162 |  | 5.3456 | 67.9727 | 4187 | 0.0030369 | 6.4963 | 6.4993 | -4.1186 | 329.2807 | 11176.3352 | -0.012508
163 |  | 5.3456 | 67.9602 | 4187 | 0.0030364 | 6.4993 | 6.5024 | -4.1186 | 329.3413 | 11244.2954 | -0.012506
164 |  | 5.3456 | 67.9477 | 4187 | 0.0030358 | 6.5024 | 6.5054 | -4.1186 | 329.4019 | 11312.2431 | -0.012503
165 |  | 5.3456 | 67.9352 | 4187 | 0.0030352 | 6.5054 | 6.5085 | -4.1186 | 329.4626 | 11380.1782 | -0.012501
166 |  | 5.3456 | 67.9227 | 4187 | 0.0030347 | 6.5085 | 6.5115 | -4.1186 | 329.5232 | 11448.1009 | -0.012499
167 |  | 5.3456 | 67.9102 | 4187 | 0.0030341 | 6.5115 | 6.5145 | -4.1186 | 329.5838 | 11516.0111 | -0.012496
168 |  | 5.3456 | 67.8977 | 4187 | 0.0030336 | 6.5145 | 6.5176 | -4.1186 | 329.6445 | 11583.9087 | -0.012494
169 |  | 5.3456 | 67.8852 | 4187 | 0.003033 | 6.5176 | 6.5206 | -4.1186 | 329.7052 | 11651.7939 | -0.012492
170 |  | 5.3456 | 67.8727 | 4187 | 0.0030325 | 6.5206 | 6.5236 | -4.1186 | 329.7659 | 11719.6666 | -0.01249
171 |  | 5.3456 | 67.8602 | 4187 | 0.0030319 | 6.5236 | 6.5266 | -4.1186 | 329.8265 | 11787.5268 | -0.012487
172 |  | 5.3456 | 67.8477 | 4187 | 0.0030313 | 6.5266 | 6.5297 | -4.1186 | 329.8873 | 11855.3745 | -0.012485
173 |  | 5.3456 | 67.8352 | 4187 | 0.0030308 | 6.5297 | 6.5327 | -4.1186 | 329.948 | 11923.2098 | -0.012483
174 |  | 5.3456 | 67.8227 | 4187 | 0.0030302 | 6.5327 | 6.5357 | -4.1186 | 330.0087 | 11991.0325 | -0.01248
175 |  | 5.3456 | 67.8103 | 4187 | 0.0030297 | 6.5357 | 6.5388 | -4.1186 | 330.0694 | 12058.8428 | -0.012478
176 |  | 5.3456 | 67.7978 | 4187 | 0.0030291 | 6.5388 | 6.5418 | -4.1186 | 330.1302 | 12126.6406 | -0.012476
177 |  | 5.3456 | 67.7853 | 4187 | 0.0030286 | 6.5418 | 6.5448 | -4.1186 | 330.1909 | 12194.4259 | -0.012473
178 |  | 5.3456 | 67.7728 | 4187 | 0.003028 | 6.5448 | 6.5479 | -4.1186 | 330.2517 | 12262.1987 | -0.012471
179 |  | 5.3456 | 67.7604 | 4187 | 0.0030274 | 6.5479 | 6.5509 | -4.1186 | 330.3125 | 12329.9591 | -0.012469
180 |  | 5.3456 | 67.7479 | 4187 | 0.0030269 | 6.5509 | 6.5539 | -4.1186 | 330.3733 | 12397.707 | -0.012467
181 |  | 5.3456 | 67.7354 | 4187 | 0.0030263 | 6.5539 | 6.5569 | -4.1186 | 330.4341 | 12465.4424 | -0.012464
182 |  | 5.3456 | 67.723 | 4187 | 0.0030258 | 6.5569 | 6.56 | -4.1186 | 330.4949 | 12533.1654 | -0.012462
183 |  | 5.3456 | 67.7105 | 4187 | 0.0030252 | 6.56 | 6.563 | -4.1186 | 330.5557 | 12600.8759 | -0.01246
184 |  | 5.3456 | 67.698 | 4187 | 0.0030247 | 6.563 | 6.566 | -4.1186 | 330.6166 | 12668.5739 | -0.012457
185 |  | 5.3456 | 67.6856 | 4187 | 0.0030241 | 6.566 | 6.569 | -4.1186 | 330.6774 | 12736.2595 | -0.012455
186 |  | 5.3456 | 67.6731 | 4187 | 0.0030235 | 6.569 | 6.5721 | -4.1186 | 330.7383 | 12803.9326 | -0.012453
187 |  | 5.3456 | 67.6607 | 4187 | 0.003023 | 6.5721 | 6.5751 | -4.1186 | 330.7992 | 12871.5933 | -0.012451
188 |  | 5.3456 | 67.6482 | 4187 | 0.0030224 | 6.5751 | 6.5781 | -4.1186 | 330.86 | 12939.2415 | -0.012448
189 |  | 5.3456 | 67.6358 | 4187 | 0.0030219 | 6.5781 | 6.5811 | -4.1186 | 330.9209 | 13006.8773 | -0.012446
190 |  | 5.3456 | 67.6233 | 4187 | 0.0030213 | 6.5811 | 6.5841 | -4.1186 | 330.9818 | 13074.5006 | -0.012444
191 |  | 5.3456 | 67.6109 | 4187 | 0.0030208 | 6.5841 | 6.5872 | -4.1186 | 331.0428 | 13142.1115 | -0.012441
192 |  | 5.3456 | 67.5984 | 4187 | 0.0030202 | 6.5872 | 6.5902 | -4.1186 | 331.1037 | 13209.71 | -0.012439
193 |  | 5.3456 | 67.586 | 4187 | 0.0030196 | 6.5902 | 6.5932 | -4.1186 | 331.1646 | 13277.296 | -0.012437
194 |  | 5.3456 | 67.5736 | 4187 | 0.0030191 | 6.5932 | 6.5962 | -4.1186 | 331.2256 | 13344.8696 | -0.012435
195 |  | 5.3456 | 67.5611 | 4187 | 0.0030185 | 6.5962 | 6.5992 | -4.1186 | 331.2865 | 13412.4307 | -0.012432
196 |  | 5.3456 | 67.5487 | 4187 | 0.003018 | 6.5992 | 6.6023 | -4.1186 | 331.3475 | 13479.9794 | -0.01243
197 |  | 5.3456 | 67.5363 | 4187 | 0.0030174 | 6.6023 | 6.6053 | -4.1186 | 331.4085 | 13547.5157 | -0.012428
198 |  | 5.3456 | 67.5238 | 4187 | 0.0030169 | 6.6053 | 6.6083 | -4.1186 | 331.4695 | 13615.0395 | -0.012425
199 |  | 5.3456 | 67.5114 | 4187 | 0.0030163 | 6.6083 | 6.6113 | -4.1186 | 331.5305 | 13682.5509 | -0.012423
200 |  | 5.3456 | 67.499 | 4187 | 0.0030158 | 6.6113 | 6.6143 | -4.1186 | 331.5915 | 13750.0499 | -0.012421
201 |  | 5.3456 | 67.4866 | 4187 | 0.0030152 | 6.6143 | 6.6173 | -4.1186 | 331.6525 | 13817.5365 | -0.012419
202 |  | 5.3456 | 67.4742 | 4187 | 0.0030146 | 6.6173 | 6.6204 | -4.1186 | 331.7136 | 13885.0107 | -0.012416
203 |  | 5.3456 | 67.4617 | 4187 | 0.0030141 | 6.6204 | 6.6234 | -4.1186 | 331.7746 | 13952.4724 | -0.012414
204 |  | 5.3456 | 67.4493 | 4187 | 0.0030135 | 6.6234 | 6.6264 | -4.1186 | 331.8357 | 14019.9218 | -0.012412
205 |  | 5.3456 | 67.4369 | 4187 | 0.003013 | 6.6264 | 6.6294 | -4.1186 | 331.8968 | 14087.3587 | -0.012409
206 |  | 5.3456 | 67.4245 | 4187 | 0.0030124 | 6.6294 | 6.6324 | -4.1186 | 331.9579 | 14154.7832 | -0.012407
207 |  | 5.3456 | 67.4121 | 4187 | 0.0030119 | 6.6324 | 6.6354 | -4.1186 | 332.0189 | 14222.1953 | -0.012405
208 |  | 5.3456 | 67.3997 | 4187 | 0.0030113 | 6.6354 | 6.6384 | -4.1186 | 332.0801 | 14289.595 | -0.012403
209 |  | 5.3456 | 67.3873 | 4187 | 0.0030108 | 6.6384 | 6.6414 | -4.1186 | 332.1412 | 14356.9823 | -0.0124
210 |  | 5.3456 | 67.3749 | 4187 | 0.0030102 | 6.6414 | 6.6445 | -4.1186 | 332.2023 | 14424.3572 | -0.012398
211 |  | 5.3456 | 67.3625 | 4187 | 0.0030097 | 6.6445 | 6.6475 | -4.1186 | 332.2634 | 14491.7197 | -0.012396
212 |  | 5.3456 | 67.3501 | 4187 | 0.0030091 | 6.6475 | 6.6505 | -4.1186 | 332.3246 | 14559.0698 | -0.012393
213 |  | 5.3456 | 67.3377 | 4187 | 0.0030086 | 6.6505 | 6.6535 | -4.1186 | 332.3858 | 14626.4075 | -0.012391
214 |  | 5.3456 | 67.3253 | 4187 | 0.003008 | 6.6535 | 6.6565 | -4.1186 | 332.4469 | 14693.7328 | -0.012389
215 |  | 5.3456 | 67.3129 | 4187 | 0.0030074 | 6.6565 | 6.6595 | -4.1186 | 332.5081 | 14761.0457 | -0.012387
216 |  | 5.3456 | 67.3005 | 4187 | 0.0030069 | 6.6595 | 6.6625 | -4.1186 | 332.5693 | 14828.3463 | -0.012384
217 |  | 5.3456 | 67.2882 | 4187 | 0.0030063 | 6.6625 | 6.6655 | -4.1186 | 332.6305 | 14895.6344 | -0.012382
218 |  | 5.3456 | 67.2758 | 4187 | 0.0030058 | 6.6655 | 6.6685 | -4.1186 | 332.6918 | 14962.9102 | -0.01238
219 |  | 5.3456 | 67.2634 | 4187 | 0.0030052 | 6.6685 | 6.6715 | -4.1186 | 332.753 | 15030.1736 | -0.012377
220 |  | 5.3456 | 67.251 | 4187 | 0.0030047 | 6.6715 | 6.6745 | -4.1186 | 332.8142 | 15097.4246 | -0.012375
221 |  | 5.3456 | 67.2386 | 4187 | 0.0030041 | 6.6745 | 6.6775 | -4.1186 | 332.8755 | 15164.6632 | -0.012373
222 |  | 5.3456 | 67.2263 | 4187 | 0.0030036 | 6.6775 | 6.6805 | -4.1186 | 332.9367 | 15231.8895 | -0.012371
223 |  | 5.3456 | 67.2139 | 4187 | 0.003003 | 6.6805 | 6.6835 | -4.1186 | 332.998 | 15299.1034 | -0.012368
224 |  | 5.3456 | 67.2015 | 4187 | 0.0030025 | 6.6835 | 6.6865 | -4.1186 | 333.0593 | 15366.3049 | -0.012366
225 |  | 5.3456 | 67.1892 | 4187 | 0.0030019 | 6.6865 | 6.6895 | -4.1186 | 333.1206 | 15433.4941 | -0.012364
226 |  | 5.3456 | 67.1768 | 4187 | 0.0030014 | 6.6895 | 6.6925 | -4.1186 | 333.1819 | 15500.6709 | -0.012362
227 |  | 5.3456 | 67.1644 | 4187 | 0.0030008 | 6.6925 | 6.6955 | -4.1186 | 333.2432 | 15567.8353 | -0.012359
228 |  | 5.3456 | 67.1521 | 4187 | 0.0030003 | 6.6955 | 6.6985 | -4.1186 | 333.3046 | 15634.9874 | -0.012357
229 |  | 5.3456 | 67.1397 | 4187 | 0.0029997 | 6.6985 | 6.7015 | -4.1186 | 333.3659 | 15702.1272 | -0.012355
230 |  | 5.3456 | 67.1274 | 4187 | 0.0029992 | 6.7015 | 6.7045 | -4.1186 | 333.4273 | 15769.2545 | -0.012352
231 |  | 5.3456 | 67.115 | 4187 | 0.0029986 | 6.7045 | 6.7075 | -4.1186 | 333.4886 | 15836.3695 | -0.01235
232 |  | 5.3456 | 67.1027 | 4187 | 0.0029981 | 6.7075 | 6.7105 | -4.1186 | 333.55 | 15903.4722 | -0.012348
233 |  | 5.3456 | 67.0903 | 4187 | 0.0029975 | 6.7105 | 6.7135 | -4.1186 | 333.6114 | 15970.5625 | -0.012346
234 |  | 5.3456 | 67.078 | 4187 | 0.0029969 | 6.7135 | 6.7165 | -4.1186 | 333.6728 | 16037.6405 | -0.012343
235 |  | 5.3456 | 67.0656 | 4187 | 0.0029964 | 6.7165 | 6.7195 | -4.1186 | 333.7342 | 16104.7061 | -0.012341
236 |  | 5.3456 | 67.0533 | 4187 | 0.0029958 | 6.7195 | 6.7225 | -4.1186 | 333.7956 | 16171.7594 | -0.012339

## St114
|  |  | buis | verlies W/M | L /°C/sec
diam | wandikte |  | inhoud l/m |  | W/M
114.3 | 3.6 | 3.1416 | 9.0088 | 90.0248 | 4187
[8 empty] | J/sec/mtr | aantal mtr. | verlies
|  | buis | verlies W/M | L /°C/sec | verlies temp | begintemp | eindtemp | verlies | bij 1°C | totaal J/sec
|  | inhoud L |  | W/M | °C per M | °C | °C | per m°C | daling | aantal mtr
1 | 114.3 | 9.0088 | 90.0248 | 4187 | 0.0023867 | 6 | 6.0024 | -5.2956 | 418.9959 | 90.0248 | -0.012639
2 |  | 9.0088 | 90.0121 | 4187 | 0.0023863 | 6.0024 | 6.0048 | -5.2956 | 419.0547 | 180.0369 | -0.012637
3 |  | 9.0088 | 89.9995 | 4187 | 0.002386 | 6.0048 | 6.0072 | -5.2956 | 419.1135 | 270.0364 | -0.012635
4 |  | 9.0088 | 89.9869 | 4187 | 0.0023857 | 6.0072 | 6.0095 | -5.2956 | 419.1724 | 360.0233 | -0.012633
5 |  | 9.0088 | 89.9742 | 4187 | 0.0023853 | 6.0095 | 6.0119 | -5.2956 | 419.2312 | 449.9975 | -0.012632
6 |  | 9.0088 | 89.9616 | 4187 | 0.002385 | 6.0119 | 6.0143 | -5.2956 | 419.2901 | 539.9591 | -0.01263
7 |  | 9.0088 | 89.949 | 4187 | 0.0023846 | 6.0143 | 6.0167 | -5.2956 | 419.349 | 629.9081 | -0.012628
8 |  | 9.0088 | 89.9363 | 4187 | 0.0023843 | 6.0167 | 6.0191 | -5.2956 | 419.4079 | 719.8444 | -0.012626
9 |  | 9.0088 | 89.9237 | 4187 | 0.002384 | 6.0191 | 6.0215 | -5.2956 | 419.4667 | 809.7681 | -0.012625
10 |  | 9.0088 | 89.9111 | 4187 | 0.0023836 | 6.0215 | 6.0239 | -5.2956 | 419.5256 | 899.6792 | -0.012623
11 |  | 9.0088 | 89.8985 | 4187 | 0.0023833 | 6.0239 | 6.0262 | -5.2956 | 419.5846 | 989.5777 | -0.012621
12 |  | 9.0088 | 89.8858 | 4187 | 0.002383 | 6.0262 | 6.0286 | -5.2956 | 419.6435 | 1079.4635 | -0.012619
13 |  | 9.0088 | 89.8732 | 4187 | 0.0023826 | 6.0286 | 6.031 | -5.2956 | 419.7024 | 1169.3368 | -0.012617
14 |  | 9.0088 | 89.8606 | 4187 | 0.0023823 | 6.031 | 6.0334 | -5.2956 | 419.7613 | 1259.1974 | -0.012616
15 |  | 9.0088 | 89.848 | 4187 | 0.002382 | 6.0334 | 6.0358 | -5.2956 | 419.8203 | 1349.0454 | -0.012614
16 |  | 9.0088 | 89.8354 | 4187 | 0.0023816 | 6.0358 | 6.0381 | -5.2956 | 419.8792 | 1438.8808 | -0.012612
17 |  | 9.0088 | 89.8228 | 4187 | 0.0023813 | 6.0381 | 6.0405 | -5.2956 | 419.9382 | 1528.7035 | -0.01261
18 |  | 9.0088 | 89.8102 | 4187 | 0.002381 | 6.0405 | 6.0429 | -5.2956 | 419.9971 | 1618.5137 | -0.012609
19 |  | 9.0088 | 89.7976 | 4187 | 0.0023806 | 6.0429 | 6.0453 | -5.2956 | 420.0561 | 1708.3112 | -0.012607
20 |  | 9.0088 | 89.7849 | 4187 | 0.0023803 | 6.0453 | 6.0477 | -5.2956 | 420.1151 | 1798.0962 | -0.012605
21 |  | 9.0088 | 89.7723 | 4187 | 0.00238 | 6.0477 | 6.05 | -5.2956 | 420.1741 | 1887.8685 | -0.012603
22 |  | 9.0088 | 89.7597 | 4187 | 0.0023796 | 6.05 | 6.0524 | -5.2956 | 420.2331 | 1977.6283 | -0.012602
23 |  | 9.0088 | 89.7471 | 4187 | 0.0023793 | 6.0524 | 6.0548 | -5.2956 | 420.2921 | 2067.3754 | -0.0126
24 |  | 9.0088 | 89.7345 | 4187 | 0.002379 | 6.0548 | 6.0572 | -5.2956 | 420.3511 | 2157.1099 | -0.012598
25 |  | 9.0088 | 89.7219 | 4187 | 0.0023786 | 6.0572 | 6.0596 | -5.2956 | 420.4101 | 2246.8319 | -0.012596
26 |  | 9.0088 | 89.7093 | 4187 | 0.0023783 | 6.0596 | 6.0619 | -5.2956 | 420.4691 | 2336.5412 | -0.012594
27 |  | 9.0088 | 89.6967 | 4187 | 0.002378 | 6.0619 | 6.0643 | -5.2956 | 420.5282 | 2426.2379 | -0.012593
28 |  | 9.0088 | 89.6842 | 4187 | 0.0023776 | 6.0643 | 6.0667 | -5.2956 | 420.5872 | 2515.9221 | -0.012591
29 |  | 9.0088 | 89.6716 | 4187 | 0.0023773 | 6.0667 | 6.0691 | -5.2956 | 420.6463 | 2605.5937 | -0.012589
30 |  | 9.0088 | 89.659 | 4187 | 0.002377 | 6.0691 | 6.0715 | -5.2956 | 420.7053 | 2695.2526 | -0.012587
31 |  | 9.0088 | 89.6464 | 4187 | 0.0023766 | 6.0715 | 6.0738 | -5.2956 | 420.7644 | 2784.899 | -0.012586
32 |  | 9.0088 | 89.6338 | 4187 | 0.0023763 | 6.0738 | 6.0762 | -5.2956 | 420.8235 | 2874.5328 | -0.012584
33 |  | 9.0088 | 89.6212 | 4187 | 0.002376 | 6.0762 | 6.0786 | -5.2956 | 420.8826 | 2964.154 | -0.012582
34 |  | 9.0088 | 89.6086 | 4187 | 0.0023756 | 6.0786 | 6.081 | -5.2956 | 420.9417 | 3053.7627 | -0.01258
35 |  | 9.0088 | 89.5961 | 4187 | 0.0023753 | 6.081 | 6.0833 | -5.2956 | 421.0008 | 3143.3587 | -0.012579
36 |  | 9.0088 | 89.5835 | 4187 | 0.002375 | 6.0833 | 6.0857 | -5.2956 | 421.0599 | 3232.9422 | -0.012577
37 |  | 9.0088 | 89.5709 | 4187 | 0.0023746 | 6.0857 | 6.0881 | -5.2956 | 421.119 | 3322.5131 | -0.012575
38 |  | 9.0088 | 89.5583 | 4187 | 0.0023743 | 6.0881 | 6.0905 | -5.2956 | 421.1781 | 3412.0714 | -0.012573
39 |  | 9.0088 | 89.5457 | 4187 | 0.002374 | 6.0905 | 6.0928 | -5.2956 | 421.2373 | 3501.6172 | -0.012571
40 |  | 9.0088 | 89.5332 | 4187 | 0.0023736 | 6.0928 | 6.0952 | -5.2956 | 421.2964 | 3591.1503 | -0.01257
41 |  | 9.0088 | 89.5206 | 4187 | 0.0023733 | 6.0952 | 6.0976 | -5.2956 | 421.3556 | 3680.6709 | -0.012568
42 |  | 9.0088 | 89.508 | 4187 | 0.002373 | 6.0976 | 6.1 | -5.2956 | 421.4148 | 3770.179 | -0.012566
43 |  | 9.0088 | 89.4955 | 4187 | 0.0023726 | 6.1 | 6.1023 | -5.2956 | 421.4739 | 3859.6745 | -0.012564
44 |  | 9.0088 | 89.4829 | 4187 | 0.0023723 | 6.1023 | 6.1047 | -5.2956 | 421.5331 | 3949.1574 | -0.012563
45 |  | 9.0088 | 89.4703 | 4187 | 0.002372 | 6.1047 | 6.1071 | -5.2956 | 421.5923 | 4038.6277 | -0.012561
46 |  | 9.0088 | 89.4578 | 4187 | 0.0023716 | 6.1071 | 6.1094 | -5.2956 | 421.6515 | 4128.0855 | -0.012559
47 |  | 9.0088 | 89.4452 | 4187 | 0.0023713 | 6.1094 | 6.1118 | -5.2956 | 421.7107 | 4217.5307 | -0.012557
48 |  | 9.0088 | 89.4327 | 4187 | 0.002371 | 6.1118 | 6.1142 | -5.2956 | 421.7699 | 4306.9634 | -0.012556
49 |  | 9.0088 | 89.4201 | 4187 | 0.0023706 | 6.1142 | 6.1166 | -5.2956 | 421.8291 | 4396.3835 | -0.012554
50 |  | 9.0088 | 89.4076 | 4187 | 0.0023703 | 6.1166 | 6.1189 | -5.2956 | 421.8884 | 4485.7911 | -0.012552
51 |  | 9.0088 | 89.395 | 4187 | 0.00237 | 6.1189 | 6.1213 | -5.2956 | 421.9476 | 4575.1861 | -0.01255
52 |  | 9.0088 | 89.3825 | 4187 | 0.0023696 | 6.1213 | 6.1237 | -5.2956 | 422.0068 | 4664.5685 | -0.012549
53 |  | 9.0088 | 89.3699 | 4187 | 0.0023693 | 6.1237 | 6.126 | -5.2956 | 422.0661 | 4753.9385 | -0.012547
54 |  | 9.0088 | 89.3574 | 4187 | 0.002369 | 6.126 | 6.1284 | -5.2956 | 422.1254 | 4843.2958 | -0.012545
55 |  | 9.0088 | 89.3448 | 4187 | 0.0023686 | 6.1284 | 6.1308 | -5.2956 | 422.1846 | 4932.6406 | -0.012543
56 |  | 9.0088 | 89.3323 | 4187 | 0.0023683 | 6.1308 | 6.1331 | -5.2956 | 422.2439 | 5021.9729 | -0.012542
57 |  | 9.0088 | 89.3197 | 4187 | 0.002368 | 6.1331 | 6.1355 | -5.2956 | 422.3032 | 5111.2926 | -0.01254
58 |  | 9.0088 | 89.3072 | 4187 | 0.0023676 | 6.1355 | 6.1379 | -5.2956 | 422.3625 | 5200.5998 | -0.012538
59 |  | 9.0088 | 89.2947 | 4187 | 0.0023673 | 6.1379 | 6.1402 | -5.2956 | 422.4218 | 5289.8945 | -0.012536
60 |  | 9.0088 | 89.2821 | 4187 | 0.002367 | 6.1402 | 6.1426 | -5.2956 | 422.4811 | 5379.1766 | -0.012534
61 |  | 9.0088 | 89.2696 | 4187 | 0.0023666 | 6.1426 | 6.145 | -5.2956 | 422.5404 | 5468.4462 | -0.012533
62 |  | 9.0088 | 89.2571 | 4187 | 0.0023663 | 6.145 | 6.1473 | -5.2956 | 422.5998 | 5557.7032 | -0.012531
63 |  | 9.0088 | 89.2445 | 4187 | 0.002366 | 6.1473 | 6.1497 | -5.2956 | 422.6591 | 5646.9478 | -0.012529
64 |  | 9.0088 | 89.232 | 4187 | 0.0023656 | 6.1497 | 6.1521 | -5.2956 | 422.7184 | 5736.1798 | -0.012527
65 |  | 9.0088 | 89.2195 | 4187 | 0.0023653 | 6.1521 | 6.1544 | -5.2956 | 422.7778 | 5825.3992 | -0.012526
66 |  | 9.0088 | 89.2069 | 4187 | 0.002365 | 6.1544 | 6.1568 | -5.2956 | 422.8372 | 5914.6062 | -0.012524
67 |  | 9.0088 | 89.1944 | 4187 | 0.0023646 | 6.1568 | 6.1592 | -5.2956 | 422.8965 | 6003.8006 | -0.012522
68 |  | 9.0088 | 89.1819 | 4187 | 0.0023643 | 6.1592 | 6.1615 | -5.2956 | 422.9559 | 6092.9825 | -0.01252
69 |  | 9.0088 | 89.1694 | 4187 | 0.002364 | 6.1615 | 6.1639 | -5.2956 | 423.0153 | 6182.1518 | -0.012519
70 |  | 9.0088 | 89.1569 | 4187 | 0.0023636 | 6.1639 | 6.1663 | -5.2956 | 423.0747 | 6271.3087 | -0.012517
71 |  | 9.0088 | 89.1443 | 4187 | 0.0023633 | 6.1663 | 6.1686 | -5.2956 | 423.1341 | 6360.453 | -0.012515
72 |  | 9.0088 | 89.1318 | 4187 | 0.002363 | 6.1686 | 6.171 | -5.2956 | 423.1935 | 6449.5848 | -0.012513
73 |  | 9.0088 | 89.1193 | 4187 | 0.0023627 | 6.171 | 6.1733 | -5.2956 | 423.2529 | 6538.7042 | -0.012512
74 |  | 9.0088 | 89.1068 | 4187 | 0.0023623 | 6.1733 | 6.1757 | -5.2956 | 423.3124 | 6627.811 | -0.01251
75 |  | 9.0088 | 89.0943 | 4187 | 0.002362 | 6.1757 | 6.1781 | -5.2956 | 423.3718 | 6716.9052 | -0.012508
76 |  | 9.0088 | 89.0818 | 4187 | 0.0023617 | 6.1781 | 6.1804 | -5.2956 | 423.4312 | 6805.987 | -0.012506
77 |  | 9.0088 | 89.0693 | 4187 | 0.0023613 | 6.1804 | 6.1828 | -5.2956 | 423.4907 | 6895.0563 | -0.012505
78 |  | 9.0088 | 89.0568 | 4187 | 0.002361 | 6.1828 | 6.1852 | -5.2956 | 423.5502 | 6984.1131 | -0.012503
79 |  | 9.0088 | 89.0443 | 4187 | 0.0023607 | 6.1852 | 6.1875 | -5.2956 | 423.6096 | 7073.1573 | -0.012501
80 |  | 9.0088 | 89.0318 | 4187 | 0.0023603 | 6.1875 | 6.1899 | -5.2956 | 423.6691 | 7162.1891 | -0.012499
81 |  | 9.0088 | 89.0193 | 4187 | 0.00236 | 6.1899 | 6.1922 | -5.2956 | 423.7286 | 7251.2084 | -0.012498
82 |  | 9.0088 | 89.0068 | 4187 | 0.0023597 | 6.1922 | 6.1946 | -5.2956 | 423.7881 | 7340.2151 | -0.012496
83 |  | 9.0088 | 88.9943 | 4187 | 0.0023593 | 6.1946 | 6.197 | -5.2956 | 423.8476 | 7429.2094 | -0.012494
84 |  | 9.0088 | 88.9818 | 4187 | 0.002359 | 6.197 | 6.1993 | -5.2956 | 423.9071 | 7518.1912 | -0.012492
85 |  | 9.0088 | 88.9693 | 4187 | 0.0023587 | 6.1993 | 6.2017 | -5.2956 | 423.9666 | 7607.1604 | -0.012491
86 |  | 9.0088 | 88.9568 | 4187 | 0.0023583 | 6.2017 | 6.204 | -5.2956 | 424.0262 | 7696.1172 | -0.012489
87 |  | 9.0088 | 88.9443 | 4187 | 0.002358 | 6.204 | 6.2064 | -5.2956 | 424.0857 | 7785.0615 | -0.012487
88 |  | 9.0088 | 88.9318 | 4187 | 0.0023577 | 6.2064 | 6.2087 | -5.2956 | 424.1453 | 7873.9934 | -0.012485
89 |  | 9.0088 | 88.9193 | 4187 | 0.0023574 | 6.2087 | 6.2111 | -5.2956 | 424.2048 | 7962.9127 | -0.012484
90 |  | 9.0088 | 88.9068 | 4187 | 0.002357 | 6.2111 | 6.2135 | -5.2956 | 424.2644 | 8051.8195 | -0.012482
91 |  | 9.0088 | 88.8944 | 4187 | 0.0023567 | 6.2135 | 6.2158 | -5.2956 | 424.3239 | 8140.7139 | -0.01248
92 |  | 9.0088 | 88.8819 | 4187 | 0.0023564 | 6.2158 | 6.2182 | -5.2956 | 424.3835 | 8229.5958 | -0.012478
93 |  | 9.0088 | 88.8694 | 4187 | 0.002356 | 6.2182 | 6.2205 | -5.2956 | 424.4431 | 8318.4652 | -0.012477
94 |  | 9.0088 | 88.8569 | 4187 | 0.0023557 | 6.2205 | 6.2229 | -5.2956 | 424.5027 | 8407.3221 | -0.012475
95 |  | 9.0088 | 88.8445 | 4187 | 0.0023554 | 6.2229 | 6.2252 | -5.2956 | 424.5623 | 8496.1666 | -0.012473
96 |  | 9.0088 | 88.832 | 4187 | 0.002355 | 6.2252 | 6.2276 | -5.2956 | 424.6219 | 8584.9986 | -0.012471
97 |  | 9.0088 | 88.8195 | 4187 | 0.0023547 | 6.2276 | 6.23 | -5.2956 | 424.6815 | 8673.8181 | -0.01247
98 |  | 9.0088 | 88.807 | 4187 | 0.0023544 | 6.23 | 6.2323 | -5.2956 | 424.7412 | 8762.6251 | -0.012468
99 |  | 9.0088 | 88.7946 | 4187 | 0.002354 | 6.2323 | 6.2347 | -5.2956 | 424.8008 | 8851.4197 | -0.012466
100 |  | 9.0088 | 88.7821 | 4187 | 0.0023537 | 6.2347 | 6.237 | -5.2956 | 424.8605 | 8940.2018 | -0.012464
101 |  | 9.0088 | 88.7696 | 4187 | 0.0023534 | 6.237 | 6.2394 | -5.2956 | 424.9201 | 9028.9715 | -0.012463
102 |  | 9.0088 | 88.7572 | 4187 | 0.0023531 | 6.2394 | 6.2417 | -5.2956 | 424.9798 | 9117.7287 | -0.012461
103 |  | 9.0088 | 88.7447 | 4187 | 0.0023527 | 6.2417 | 6.2441 | -5.2956 | 425.0395 | 9206.4734 | -0.012459
104 |  | 9.0088 | 88.7323 | 4187 | 0.0023524 | 6.2441 | 6.2464 | -5.2956 | 425.0991 | 9295.2057 | -0.012457
105 |  | 9.0088 | 88.7198 | 4187 | 0.0023521 | 6.2464 | 6.2488 | -5.2956 | 425.1588 | 9383.9255 | -0.012456
106 |  | 9.0088 | 88.7074 | 4187 | 0.0023517 | 6.2488 | 6.2511 | -5.2956 | 425.2185 | 9472.6328 | -0.012454
107 |  | 9.0088 | 88.6949 | 4187 | 0.0023514 | 6.2511 | 6.2535 | -5.2956 | 425.2782 | 9561.3277 | -0.012452
108 |  | 9.0088 | 88.6824 | 4187 | 0.0023511 | 6.2535 | 6.2558 | -5.2956 | 425.3379 | 9650.0102 | -0.01245
109 |  | 9.0088 | 88.67 | 4187 | 0.0023507 | 6.2558 | 6.2582 | -5.2956 | 425.3977 | 9738.6801 | -0.012449
110 |  | 9.0088 | 88.6575 | 4187 | 0.0023504 | 6.2582 | 6.2605 | -5.2956 | 425.4574 | 9827.3377 | -0.012447
111 |  | 9.0088 | 88.6451 | 4187 | 0.0023501 | 6.2605 | 6.2629 | -5.2956 | 425.5171 | 9915.9828 | -0.012445
112 |  | 9.0088 | 88.6327 | 4187 | 0.0023498 | 6.2629 | 6.2652 | -5.2956 | 425.5769 | 10004.6154 | -0.012443
113 |  | 9.0088 | 88.6202 | 4187 | 0.0023494 | 6.2652 | 6.2676 | -5.2956 | 425.6366 | 10093.2357 | -0.012442
114 |  | 9.0088 | 88.6078 | 4187 | 0.0023491 | 6.2676 | 6.2699 | -5.2956 | 425.6964 | 10181.8434 | -0.01244
115 |  | 9.0088 | 88.5953 | 4187 | 0.0023488 | 6.2699 | 6.2723 | -5.2956 | 425.7562 | 10270.4388 | -0.012438
116 |  | 9.0088 | 88.5829 | 4187 | 0.0023484 | 6.2723 | 6.2746 | -5.2956 | 425.816 | 10359.0216 | -0.012436
117 |  | 9.0088 | 88.5705 | 4187 | 0.0023481 | 6.2746 | 6.277 | -5.2956 | 425.8757 | 10447.5921 | -0.012435
118 |  | 9.0088 | 88.558 | 4187 | 0.0023478 | 6.277 | 6.2793 | -5.2956 | 425.9355 | 10536.1501 | -0.012433
119 |  | 9.0088 | 88.5456 | 4187 | 0.0023474 | 6.2793 | 6.2817 | -5.2956 | 425.9953 | 10624.6957 | -0.012431
120 |  | 9.0088 | 88.5332 | 4187 | 0.0023471 | 6.2817 | 6.284 | -5.2956 | 426.0552 | 10713.2289 | -0.012429
121 |  | 9.0088 | 88.5207 | 4187 | 0.0023468 | 6.284 | 6.2864 | -5.2956 | 426.115 | 10801.7496 | -0.012428
122 |  | 9.0088 | 88.5083 | 4187 | 0.0023465 | 6.2864 | 6.2887 | -5.2956 | 426.1748 | 10890.2579 | -0.012426
123 |  | 9.0088 | 88.4959 | 4187 | 0.0023461 | 6.2887 | 6.2911 | -5.2956 | 426.2347 | 10978.7538 | -0.012424
124 |  | 9.0088 | 88.4835 | 4187 | 0.0023458 | 6.2911 | 6.2934 | -5.2956 | 426.2945 | 11067.2372 | -0.012422
125 |  | 9.0088 | 88.471 | 4187 | 0.0023455 | 6.2934 | 6.2958 | -5.2956 | 426.3544 | 11155.7083 | -0.012421
126 |  | 9.0088 | 88.4586 | 4187 | 0.0023451 | 6.2958 | 6.2981 | -5.2956 | 426.4142 | 11244.1669 | -0.012419
127 |  | 9.0088 | 88.4462 | 4187 | 0.0023448 | 6.2981 | 6.3004 | -5.2956 | 426.4741 | 11332.613 | -0.012417
128 |  | 9.0088 | 88.4338 | 4187 | 0.0023445 | 6.3004 | 6.3028 | -5.2956 | 426.534 | 11421.0468 | -0.012415
129 |  | 9.0088 | 88.4214 | 4187 | 0.0023441 | 6.3028 | 6.3051 | -5.2956 | 426.5939 | 11509.4682 | -0.012414
130 |  | 9.0088 | 88.4089 | 4187 | 0.0023438 | 6.3051 | 6.3075 | -5.2956 | 426.6538 | 11597.8771 | -0.012412
131 |  | 9.0088 | 88.3965 | 4187 | 0.0023435 | 6.3075 | 6.3098 | -5.2956 | 426.7137 | 11686.2736 | -0.01241
132 |  | 9.0088 | 88.3841 | 4187 | 0.0023432 | 6.3098 | 6.3122 | -5.2956 | 426.7736 | 11774.6578 | -0.012408
133 |  | 9.0088 | 88.3717 | 4187 | 0.0023428 | 6.3122 | 6.3145 | -5.2956 | 426.8335 | 11863.0295 | -0.012407
134 |  | 9.0088 | 88.3593 | 4187 | 0.0023425 | 6.3145 | 6.3168 | -5.2956 | 426.8934 | 11951.3888 | -0.012405
135 |  | 9.0088 | 88.3469 | 4187 | 0.0023422 | 6.3168 | 6.3192 | -5.2956 | 426.9534 | 12039.7357 | -0.012403
136 |  | 9.0088 | 88.3345 | 4187 | 0.0023418 | 6.3192 | 6.3215 | -5.2956 | 427.0133 | 12128.0702 | -0.012401
137 |  | 9.0088 | 88.3221 | 4187 | 0.0023415 | 6.3215 | 6.3239 | -5.2956 | 427.0733 | 12216.3923 | -0.0124
138 |  | 9.0088 | 88.3097 | 4187 | 0.0023412 | 6.3239 | 6.3262 | -5.2956 | 427.1333 | 12304.702 | -0.012398
139 |  | 9.0088 | 88.2973 | 4187 | 0.0023409 | 6.3262 | 6.3286 | -5.2956 | 427.1932 | 12392.9993 | -0.012396
140 |  | 9.0088 | 88.2849 | 4187 | 0.0023405 | 6.3286 | 6.3309 | -5.2956 | 427.2532 | 12481.2842 | -0.012394
141 |  | 9.0088 | 88.2725 | 4187 | 0.0023402 | 6.3309 | 6.3332 | -5.2956 | 427.3132 | 12569.5567 | -0.012393
142 |  | 9.0088 | 88.2601 | 4187 | 0.0023399 | 6.3332 | 6.3356 | -5.2956 | 427.3732 | 12657.8168 | -0.012391
143 |  | 9.0088 | 88.2477 | 4187 | 0.0023395 | 6.3356 | 6.3379 | -5.2956 | 427.4332 | 12746.0645 | -0.012389
144 |  | 9.0088 | 88.2353 | 4187 | 0.0023392 | 6.3379 | 6.3403 | -5.2956 | 427.4932 | 12834.2999 | -0.012388
145 |  | 9.0088 | 88.2229 | 4187 | 0.0023389 | 6.3403 | 6.3426 | -5.2956 | 427.5533 | 12922.5228 | -0.012386
146 |  | 9.0088 | 88.2106 | 4187 | 0.0023386 | 6.3426 | 6.3449 | -5.2956 | 427.6133 | 13010.7334 | -0.012384
147 |  | 9.0088 | 88.1982 | 4187 | 0.0023382 | 6.3449 | 6.3473 | -5.2956 | 427.6733 | 13098.9315 | -0.012382
148 |  | 9.0088 | 88.1858 | 4187 | 0.0023379 | 6.3473 | 6.3496 | -5.2956 | 427.7334 | 13187.1173 | -0.012381
149 |  | 9.0088 | 88.1734 | 4187 | 0.0023376 | 6.3496 | 6.3519 | -5.2956 | 427.7934 | 13275.2908 | -0.012379
150 |  | 9.0088 | 88.161 | 4187 | 0.0023372 | 6.3519 | 6.3543 | -5.2956 | 427.8535 | 13363.4518 | -0.012377
151 |  | 9.0088 | 88.1487 | 4187 | 0.0023369 | 6.3543 | 6.3566 | -5.2956 | 427.9136 | 13451.6004 | -0.012375
152 |  | 9.0088 | 88.1363 | 4187 | 0.0023366 | 6.3566 | 6.359 | -5.2956 | 427.9737 | 13539.7367 | -0.012374
153 |  | 9.0088 | 88.1239 | 4187 | 0.0023363 | 6.359 | 6.3613 | -5.2956 | 428.0338 | 13627.8606 | -0.012372
154 |  | 9.0088 | 88.1115 | 4187 | 0.0023359 | 6.3613 | 6.3636 | -5.2956 | 428.0939 | 13715.9722 | -0.01237
155 |  | 9.0088 | 88.0992 | 4187 | 0.0023356 | 6.3636 | 6.366 | -5.2956 | 428.154 | 13804.0713 | -0.012368
156 |  | 9.0088 | 88.0868 | 4187 | 0.0023353 | 6.366 | 6.3683 | -5.2956 | 428.2141 | 13892.1581 | -0.012367
157 |  | 9.0088 | 88.0744 | 4187 | 0.002335 | 6.3683 | 6.3706 | -5.2956 | 428.2742 | 13980.2326 | -0.012365
158 |  | 9.0088 | 88.0621 | 4187 | 0.0023346 | 6.3706 | 6.373 | -5.2956 | 428.3344 | 14068.2946 | -0.012363
159 |  | 9.0088 | 88.0497 | 4187 | 0.0023343 | 6.373 | 6.3753 | -5.2956 | 428.3945 | 14156.3444 | -0.012361
160 |  | 9.0088 | 88.0373 | 4187 | 0.002334 | 6.3753 | 6.3776 | -5.2956 | 428.4546 | 14244.3817 | -0.01236
161 |  | 9.0088 | 88.025 | 4187 | 0.0023336 | 6.3776 | 6.38 | -5.2956 | 428.5148 | 14332.4067 | -0.012358
162 |  | 9.0088 | 88.0126 | 4187 | 0.0023333 | 6.38 | 6.3823 | -5.2956 | 428.575 | 14420.4193 | -0.012356
163 |  | 9.0088 | 88.0003 | 4187 | 0.002333 | 6.3823 | 6.3846 | -5.2956 | 428.6352 | 14508.4196 | -0.012355
164 |  | 9.0088 | 87.9879 | 4187 | 0.0023327 | 6.3846 | 6.387 | -5.2956 | 428.6953 | 14596.4075 | -0.012353
165 |  | 9.0088 | 87.9756 | 4187 | 0.0023323 | 6.387 | 6.3893 | -5.2956 | 428.7555 | 14684.383 | -0.012351
166 |  | 9.0088 | 87.9632 | 4187 | 0.002332 | 6.3893 | 6.3916 | -5.2956 | 428.8157 | 14772.3463 | -0.012349
167 |  | 9.0088 | 87.9509 | 4187 | 0.0023317 | 6.3916 | 6.394 | -5.2956 | 428.8759 | 14860.2971 | -0.012348
168 |  | 9.0088 | 87.9385 | 4187 | 0.0023313 | 6.394 | 6.3963 | -5.2956 | 428.9362 | 14948.2356 | -0.012346
169 |  | 9.0088 | 87.9262 | 4187 | 0.002331 | 6.3963 | 6.3986 | -5.2956 | 428.9964 | 15036.1618 | -0.012344
170 |  | 9.0088 | 87.9138 | 4187 | 0.0023307 | 6.3986 | 6.401 | -5.2956 | 429.0566 | 15124.0756 | -0.012342
171 |  | 9.0088 | 87.9015 | 4187 | 0.0023304 | 6.401 | 6.4033 | -5.2956 | 429.1169 | 15211.9771 | -0.012341
172 |  | 9.0088 | 87.8891 | 4187 | 0.00233 | 6.4033 | 6.4056 | -5.2956 | 429.1771 | 15299.8663 | -0.012339
173 |  | 9.0088 | 87.8768 | 4187 | 0.0023297 | 6.4056 | 6.4079 | -5.2956 | 429.2374 | 15387.7431 | -0.012337
174 |  | 9.0088 | 87.8645 | 4187 | 0.0023294 | 6.4079 | 6.4103 | -5.2956 | 429.2977 | 15475.6075 | -0.012335
175 |  | 9.0088 | 87.8521 | 4187 | 0.0023291 | 6.4103 | 6.4126 | -5.2956 | 429.3579 | 15563.4596 | -0.012334
176 |  | 9.0088 | 87.8398 | 4187 | 0.0023287 | 6.4126 | 6.4149 | -5.2956 | 429.4182 | 15651.2994 | -0.012332
177 |  | 9.0088 | 87.8275 | 4187 | 0.0023284 | 6.4149 | 6.4173 | -5.2956 | 429.4785 | 15739.1269 | -0.01233
178 |  | 9.0088 | 87.8151 | 4187 | 0.0023281 | 6.4173 | 6.4196 | -5.2956 | 429.5388 | 15826.942 | -0.012329
179 |  | 9.0088 | 87.8028 | 4187 | 0.0023278 | 6.4196 | 6.4219 | -5.2956 | 429.5991 | 15914.7448 | -0.012327
180 |  | 9.0088 | 87.7905 | 4187 | 0.0023274 | 6.4219 | 6.4242 | -5.2956 | 429.6595 | 16002.5353 | -0.012325
181 |  | 9.0088 | 87.7782 | 4187 | 0.0023271 | 6.4242 | 6.4266 | -5.2956 | 429.7198 | 16090.3135 | -0.012323
182 |  | 9.0088 | 87.7658 | 4187 | 0.0023268 | 6.4266 | 6.4289 | -5.2956 | 429.7801 | 16178.0793 | -0.012322
183 |  | 9.0088 | 87.7535 | 4187 | 0.0023264 | 6.4289 | 6.4312 | -5.2956 | 429.8405 | 16265.8328 | -0.01232
184 |  | 9.0088 | 87.7412 | 4187 | 0.0023261 | 6.4312 | 6.4336 | -5.2956 | 429.9008 | 16353.574 | -0.012318
185 |  | 9.0088 | 87.7289 | 4187 | 0.0023258 | 6.4336 | 6.4359 | -5.2956 | 429.9612 | 16441.3029 | -0.012316
186 |  | 9.0088 | 87.7166 | 4187 | 0.0023255 | 6.4359 | 6.4382 | -5.2956 | 430.0216 | 16529.0194 | -0.012315
187 |  | 9.0088 | 87.7042 | 4187 | 0.0023251 | 6.4382 | 6.4405 | -5.2956 | 430.0819 | 16616.7237 | -0.012313
188 |  | 9.0088 | 87.6919 | 4187 | 0.0023248 | 6.4405 | 6.4429 | -5.2956 | 430.1423 | 16704.4156 | -0.012311
189 |  | 9.0088 | 87.6796 | 4187 | 0.0023245 | 6.4429 | 6.4452 | -5.2956 | 430.2027 | 16792.0952 | -0.012309
190 |  | 9.0088 | 87.6673 | 4187 | 0.0023242 | 6.4452 | 6.4475 | -5.2956 | 430.2631 | 16879.7625 | -0.012308
191 |  | 9.0088 | 87.655 | 4187 | 0.0023238 | 6.4475 | 6.4498 | -5.2956 | 430.3235 | 16967.4175 | -0.012306
192 |  | 9.0088 | 87.6427 | 4187 | 0.0023235 | 6.4498 | 6.4521 | -5.2956 | 430.384 | 17055.0602 | -0.012304
193 |  | 9.0088 | 87.6304 | 4187 | 0.0023232 | 6.4521 | 6.4545 | -5.2956 | 430.4444 | 17142.6906 | -0.012303
194 |  | 9.0088 | 87.6181 | 4187 | 0.0023229 | 6.4545 | 6.4568 | -5.2956 | 430.5048 | 17230.3087 | -0.012301
195 |  | 9.0088 | 87.6058 | 4187 | 0.0023225 | 6.4568 | 6.4591 | -5.2956 | 430.5653 | 17317.9145 | -0.012299
196 |  | 9.0088 | 87.5935 | 4187 | 0.0023222 | 6.4591 | 6.4614 | -5.2956 | 430.6257 | 17405.5079 | -0.012297
197 |  | 9.0088 | 87.5812 | 4187 | 0.0023219 | 6.4614 | 6.4638 | -5.2956 | 430.6862 | 17493.0891 | -0.012296
198 |  | 9.0088 | 87.5689 | 4187 | 0.0023216 | 6.4638 | 6.4661 | -5.2956 | 430.7467 | 17580.658 | -0.012294
199 |  | 9.0088 | 87.5566 | 4187 | 0.0023212 | 6.4661 | 6.4684 | -5.2956 | 430.8072 | 17668.2146 | -0.012292
200 |  | 9.0088 | 87.5443 | 4187 | 0.0023209 | 6.4684 | 6.4707 | -5.2956 | 430.8676 | 17755.7589 | -0.01229
201 |  | 9.0088 | 87.532 | 4187 | 0.0023206 | 6.4707 | 6.473 | -5.2956 | 430.9281 | 17843.2909 | -0.012289
202 |  | 9.0088 | 87.5197 | 4187 | 0.0023202 | 6.473 | 6.4754 | -5.2956 | 430.9886 | 17930.8107 | -0.012287
203 |  | 9.0088 | 87.5074 | 4187 | 0.0023199 | 6.4754 | 6.4777 | -5.2956 | 431.0492 | 18018.3181 | -0.012285
204 |  | 9.0088 | 87.4952 | 4187 | 0.0023196 | 6.4777 | 6.48 | -5.2956 | 431.1097 | 18105.8133 | -0.012284
205 |  | 9.0088 | 87.4829 | 4187 | 0.0023193 | 6.48 | 6.4823 | -5.2956 | 431.1702 | 18193.2961 | -0.012282
206 |  | 9.0088 | 87.4706 | 4187 | 0.0023189 | 6.4823 | 6.4846 | -5.2956 | 431.2308 | 18280.7667 | -0.01228
207 |  | 9.0088 | 87.4583 | 4187 | 0.0023186 | 6.4846 | 6.487 | -5.2956 | 431.2913 | 18368.225 | -0.012278
208 |  | 9.0088 | 87.446 | 4187 | 0.0023183 | 6.487 | 6.4893 | -5.2956 | 431.3519 | 18455.6711 | -0.012277
209 |  | 9.0088 | 87.4338 | 4187 | 0.002318 | 6.4893 | 6.4916 | -5.2956 | 431.4124 | 18543.1048 | -0.012275
210 |  | 9.0088 | 87.4215 | 4187 | 0.0023176 | 6.4916 | 6.4939 | -5.2956 | 431.473 | 18630.5263 | -0.012273
211 |  | 9.0088 | 87.4092 | 4187 | 0.0023173 | 6.4939 | 6.4962 | -5.2956 | 431.5336 | 18717.9355 | -0.012272
212 |  | 9.0088 | 87.3969 | 4187 | 0.002317 | 6.4962 | 6.4986 | -5.2956 | 431.5942 | 18805.3324 | -0.01227
213 |  | 9.0088 | 87.3847 | 4187 | 0.0023167 | 6.4986 | 6.5009 | -5.2956 | 431.6548 | 18892.7171 | -0.012268
214 |  | 9.0088 | 87.3724 | 4187 | 0.0023163 | 6.5009 | 6.5032 | -5.2956 | 431.7154 | 18980.0895 | -0.012266
215 |  | 9.0088 | 87.3601 | 4187 | 0.002316 | 6.5032 | 6.5055 | -5.2956 | 431.776 | 19067.4496 | -0.012265
216 |  | 9.0088 | 87.3479 | 4187 | 0.0023157 | 6.5055 | 6.5078 | -5.2956 | 431.8366 | 19154.7975 | -0.012263
217 |  | 9.0088 | 87.3356 | 4187 | 0.0023154 | 6.5078 | 6.5101 | -5.2956 | 431.8973 | 19242.1331 | -0.012261
218 |  | 9.0088 | 87.3233 | 4187 | 0.002315 | 6.5101 | 6.5124 | -5.2956 | 431.9579 | 19329.4564 | -0.012259
219 |  | 9.0088 | 87.3111 | 4187 | 0.0023147 | 6.5124 | 6.5148 | -5.2956 | 432.0186 | 19416.7675 | -0.012258
220 |  | 9.0088 | 87.2988 | 4187 | 0.0023144 | 6.5148 | 6.5171 | -5.2956 | 432.0792 | 19504.0663 | -0.012256
221 |  | 9.0088 | 87.2866 | 4187 | 0.0023141 | 6.5171 | 6.5194 | -5.2956 | 432.1399 | 19591.3529 | -0.012254
222 |  | 9.0088 | 87.2743 | 4187 | 0.0023137 | 6.5194 | 6.5217 | -5.2956 | 432.2006 | 19678.6272 | -0.012253
223 |  | 9.0088 | 87.2621 | 4187 | 0.0023134 | 6.5217 | 6.524 | -5.2956 | 432.2613 | 19765.8893 | -0.012251
224 |  | 9.0088 | 87.2498 | 4187 | 0.0023131 | 6.524 | 6.5263 | -5.2956 | 432.322 | 19853.1391 | -0.012249
225 |  | 9.0088 | 87.2376 | 4187 | 0.0023128 | 6.5263 | 6.5286 | -5.2956 | 432.3827 | 19940.3766 | -0.012247
226 |  | 9.0088 | 87.2253 | 4187 | 0.0023124 | 6.5286 | 6.531 | -5.2956 | 432.4434 | 20027.602 | -0.012246
227 |  | 9.0088 | 87.2131 | 4187 | 0.0023121 | 6.531 | 6.5333 | -5.2956 | 432.5041 | 20114.815 | -0.012244
228 |  | 9.0088 | 87.2008 | 4187 | 0.0023118 | 6.5333 | 6.5356 | -5.2956 | 432.5648 | 20202.0159 | -0.012242
229 |  | 9.0088 | 87.1886 | 4187 | 0.0023115 | 6.5356 | 6.5379 | -5.2956 | 432.6256 | 20289.2044 | -0.012241
230 |  | 9.0088 | 87.1763 | 4187 | 0.0023111 | 6.5379 | 6.5402 | -5.2956 | 432.6863 | 20376.3808 | -0.012239
231 |  | 9.0088 | 87.1641 | 4187 | 0.0023108 | 6.5402 | 6.5425 | -5.2956 | 432.7471 | 20463.5449 | -0.012237
232 |  | 9.0088 | 87.1519 | 4187 | 0.0023105 | 6.5425 | 6.5448 | -5.2956 | 432.8078 | 20550.6967 | -0.012235
233 |  | 9.0088 | 87.1396 | 4187 | 0.0023102 | 6.5448 | 6.5471 | -5.2956 | 432.8686 | 20637.8364 | -0.012234
234 |  | 9.0088 | 87.1274 | 4187 | 0.0023098 | 6.5471 | 6.5494 | -5.2956 | 432.9294 | 20724.9638 | -0.012232
235 |  | 9.0088 | 87.1152 | 4187 | 0.0023095 | 6.5494 | 6.5518 | -5.2956 | 432.9902 | 20812.0789 | -0.01223
236 |  | 9.0088 | 87.1029 | 4187 | 0.0023092 | 6.5518 | 6.5541 | -5.2956 | 433.051 | 20899.1819 | -0.012229

## St127
|  |  | buis | verlies W/M | L /°C/sec
diam | wandikte |  | inhoud l/m |  | W/M
127 | 4 | 3.1416 | 11.122 | 100.0169 | 4187
[8 empty] | J/sec/mtr | aantal mtr. | verlies
|  | buis | verlies W/M | L /°C/sec | verlies temp | begintemp | eindtemp | verlies | bij 1°C | totaal J/sec
|  | inhoud L |  | W/M | °C per M | °C | °C | per m°C | daling | aantal mtr
1 | 127 | 11.122 | 100.0169 | 4187 | 0.0021478 | 6 | 6.0021 | -5.8833 | 465.6004 | 100.0169 | -0.012636
2 |  | 11.122 | 100.0043 | 4187 | 0.0021475 | 6.0021 | 6.0043 | -5.8833 | 465.6592 | 200.0212 | -0.012634
3 |  | 11.122 | 99.9916 | 4187 | 0.0021472 | 6.0043 | 6.0064 | -5.8833 | 465.718 | 300.0128 | -0.012633
4 |  | 11.122 | 99.979 | 4187 | 0.002147 | 6.0064 | 6.0086 | -5.8833 | 465.7769 | 399.9918 | -0.012631
5 |  | 11.122 | 99.9664 | 4187 | 0.0021467 | 6.0086 | 6.0107 | -5.8833 | 465.8357 | 499.9582 | -0.01263
6 |  | 11.122 | 99.9537 | 4187 | 0.0021464 | 6.0107 | 6.0129 | -5.8833 | 465.8946 | 599.912 | -0.012628
7 |  | 11.122 | 99.9411 | 4187 | 0.0021461 | 6.0129 | 6.015 | -5.8833 | 465.9535 | 699.8531 | -0.012626
8 |  | 11.122 | 99.9285 | 4187 | 0.0021459 | 6.015 | 6.0172 | -5.8833 | 466.0123 | 799.7816 | -0.012625
9 |  | 11.122 | 99.9159 | 4187 | 0.0021456 | 6.0172 | 6.0193 | -5.8833 | 466.0712 | 899.6975 | -0.012623
10 |  | 11.122 | 99.9032 | 4187 | 0.0021453 | 6.0193 | 6.0215 | -5.8833 | 466.1301 | 999.6007 | -0.012622
11 |  | 11.122 | 99.8906 | 4187 | 0.0021451 | 6.0215 | 6.0236 | -5.8833 | 466.189 | 1099.4913 | -0.01262
12 |  | 11.122 | 99.878 | 4187 | 0.0021448 | 6.0236 | 6.0258 | -5.8833 | 466.2479 | 1199.3693 | -0.012618
13 |  | 11.122 | 99.8654 | 4187 | 0.0021445 | 6.0258 | 6.0279 | -5.8833 | 466.3068 | 1299.2347 | -0.012617
14 |  | 11.122 | 99.8528 | 4187 | 0.0021442 | 6.0279 | 6.03 | -5.8833 | 466.3658 | 1399.0875 | -0.012615
15 |  | 11.122 | 99.8402 | 4187 | 0.002144 | 6.03 | 6.0322 | -5.8833 | 466.4247 | 1498.9276 | -0.012614
16 |  | 11.122 | 99.8275 | 4187 | 0.0021437 | 6.0322 | 6.0343 | -5.8833 | 466.4836 | 1598.7552 | -0.012612
17 |  | 11.122 | 99.8149 | 4187 | 0.0021434 | 6.0343 | 6.0365 | -5.8833 | 466.5426 | 1698.5701 | -0.012611
18 |  | 11.122 | 99.8023 | 4187 | 0.0021432 | 6.0365 | 6.0386 | -5.8833 | 466.6015 | 1798.3724 | -0.012609
19 |  | 11.122 | 99.7897 | 4187 | 0.0021429 | 6.0386 | 6.0408 | -5.8833 | 466.6605 | 1898.1621 | -0.012607
20 |  | 11.122 | 99.7771 | 4187 | 0.0021426 | 6.0408 | 6.0429 | -5.8833 | 466.7194 | 1997.9392 | -0.012606
21 |  | 11.122 | 99.7645 | 4187 | 0.0021423 | 6.0429 | 6.045 | -5.8833 | 466.7784 | 2097.7037 | -0.012604
22 |  | 11.122 | 99.7519 | 4187 | 0.0021421 | 6.045 | 6.0472 | -5.8833 | 466.8374 | 2197.4556 | -0.012603
23 |  | 11.122 | 99.7393 | 4187 | 0.0021418 | 6.0472 | 6.0493 | -5.8833 | 466.8964 | 2297.1949 | -0.012601
24 |  | 11.122 | 99.7267 | 4187 | 0.0021415 | 6.0493 | 6.0515 | -5.8833 | 466.9554 | 2396.9216 | -0.012599
25 |  | 11.122 | 99.7141 | 4187 | 0.0021413 | 6.0515 | 6.0536 | -5.8833 | 467.0144 | 2496.6357 | -0.012598
26 |  | 11.122 | 99.7015 | 4187 | 0.002141 | 6.0536 | 6.0558 | -5.8833 | 467.0734 | 2596.3372 | -0.012596
27 |  | 11.122 | 99.6889 | 4187 | 0.0021407 | 6.0558 | 6.0579 | -5.8833 | 467.1324 | 2696.0261 | -0.012595
28 |  | 11.122 | 99.6763 | 4187 | 0.0021405 | 6.0579 | 6.06 | -5.8833 | 467.1914 | 2795.7024 | -0.012593
29 |  | 11.122 | 99.6637 | 4187 | 0.0021402 | 6.06 | 6.0622 | -5.8833 | 467.2505 | 2895.3661 | -0.012591
30 |  | 11.122 | 99.6511 | 4187 | 0.0021399 | 6.0622 | 6.0643 | -5.8833 | 467.3095 | 2995.0172 | -0.01259
31 |  | 11.122 | 99.6385 | 4187 | 0.0021396 | 6.0643 | 6.0665 | -5.8833 | 467.3685 | 3094.6557 | -0.012588
32 |  | 11.122 | 99.6259 | 4187 | 0.0021394 | 6.0665 | 6.0686 | -5.8833 | 467.4276 | 3194.2817 | -0.012587
33 |  | 11.122 | 99.6134 | 4187 | 0.0021391 | 6.0686 | 6.0707 | -5.8833 | 467.4867 | 3293.895 | -0.012585
34 |  | 11.122 | 99.6008 | 4187 | 0.0021388 | 6.0707 | 6.0729 | -5.8833 | 467.5457 | 3393.4958 | -0.012583
35 |  | 11.122 | 99.5882 | 4187 | 0.0021386 | 6.0729 | 6.075 | -5.8833 | 467.6048 | 3493.084 | -0.012582
36 |  | 11.122 | 99.5756 | 4187 | 0.0021383 | 6.075 | 6.0771 | -5.8833 | 467.6639 | 3592.6596 | -0.01258
37 |  | 11.122 | 99.563 | 4187 | 0.002138 | 6.0771 | 6.0793 | -5.8833 | 467.723 | 3692.2226 | -0.012579
38 |  | 11.122 | 99.5504 | 4187 | 0.0021377 | 6.0793 | 6.0814 | -5.8833 | 467.7821 | 3791.773 | -0.012577
39 |  | 11.122 | 99.5379 | 4187 | 0.0021375 | 6.0814 | 6.0836 | -5.8833 | 467.8412 | 3891.3109 | -0.012576
40 |  | 11.122 | 99.5253 | 4187 | 0.0021372 | 6.0836 | 6.0857 | -5.8833 | 467.9003 | 3990.8362 | -0.012574
41 |  | 11.122 | 99.5127 | 4187 | 0.0021369 | 6.0857 | 6.0878 | -5.8833 | 467.9594 | 4090.3489 | -0.012572
42 |  | 11.122 | 99.5001 | 4187 | 0.0021367 | 6.0878 | 6.09 | -5.8833 | 468.0185 | 4189.849 | -0.012571
43 |  | 11.122 | 99.4876 | 4187 | 0.0021364 | 6.09 | 6.0921 | -5.8833 | 468.0777 | 4289.3366 | -0.012569
44 |  | 11.122 | 99.475 | 4187 | 0.0021361 | 6.0921 | 6.0942 | -5.8833 | 468.1368 | 4388.8116 | -0.012568
45 |  | 11.122 | 99.4624 | 4187 | 0.0021359 | 6.0942 | 6.0964 | -5.8833 | 468.196 | 4488.274 | -0.012566
46 |  | 11.122 | 99.4499 | 4187 | 0.0021356 | 6.0964 | 6.0985 | -5.8833 | 468.2551 | 4587.7239 | -0.012564
47 |  | 11.122 | 99.4373 | 4187 | 0.0021353 | 6.0985 | 6.1007 | -5.8833 | 468.3143 | 4687.1612 | -0.012563
48 |  | 11.122 | 99.4247 | 4187 | 0.002135 | 6.1007 | 6.1028 | -5.8833 | 468.3735 | 4786.586 | -0.012561
49 |  | 11.122 | 99.4122 | 4187 | 0.0021348 | 6.1028 | 6.1049 | -5.8833 | 468.4327 | 4885.9981 | -0.01256
50 |  | 11.122 | 99.3996 | 4187 | 0.0021345 | 6.1049 | 6.1071 | -5.8833 | 468.4918 | 4985.3978 | -0.012558
51 |  | 11.122 | 99.3871 | 4187 | 0.0021342 | 6.1071 | 6.1092 | -5.8833 | 468.551 | 5084.7848 | -0.012556
52 |  | 11.122 | 99.3745 | 4187 | 0.002134 | 6.1092 | 6.1113 | -5.8833 | 468.6102 | 5184.1593 | -0.012555
53 |  | 11.122 | 99.362 | 4187 | 0.0021337 | 6.1113 | 6.1135 | -5.8833 | 468.6695 | 5283.5213 | -0.012553
54 |  | 11.122 | 99.3494 | 4187 | 0.0021334 | 6.1135 | 6.1156 | -5.8833 | 468.7287 | 5382.8707 | -0.012552
55 |  | 11.122 | 99.3368 | 4187 | 0.0021332 | 6.1156 | 6.1177 | -5.8833 | 468.7879 | 5482.2075 | -0.01255
56 |  | 11.122 | 99.3243 | 4187 | 0.0021329 | 6.1177 | 6.1199 | -5.8833 | 468.8471 | 5581.5318 | -0.012549
57 |  | 11.122 | 99.3117 | 4187 | 0.0021326 | 6.1199 | 6.122 | -5.8833 | 468.9064 | 5680.8436 | -0.012547
58 |  | 11.122 | 99.2992 | 4187 | 0.0021324 | 6.122 | 6.1241 | -5.8833 | 468.9656 | 5780.1428 | -0.012545
59 |  | 11.122 | 99.2867 | 4187 | 0.0021321 | 6.1241 | 6.1263 | -5.8833 | 469.0249 | 5879.4294 | -0.012544
60 |  | 11.122 | 99.2741 | 4187 | 0.0021318 | 6.1263 | 6.1284 | -5.8833 | 469.0841 | 5978.7035 | -0.012542
61 |  | 11.122 | 99.2616 | 4187 | 0.0021315 | 6.1284 | 6.1305 | -5.8833 | 469.1434 | 6077.9651 | -0.012541
62 |  | 11.122 | 99.249 | 4187 | 0.0021313 | 6.1305 | 6.1326 | -5.8833 | 469.2027 | 6177.2141 | -0.012539
63 |  | 11.122 | 99.2365 | 4187 | 0.002131 | 6.1326 | 6.1348 | -5.8833 | 469.262 | 6276.4506 | -0.012537
64 |  | 11.122 | 99.224 | 4187 | 0.0021307 | 6.1348 | 6.1369 | -5.8833 | 469.3213 | 6375.6746 | -0.012536
65 |  | 11.122 | 99.2114 | 4187 | 0.0021305 | 6.1369 | 6.139 | -5.8833 | 469.3806 | 6474.886 | -0.012534
66 |  | 11.122 | 99.1989 | 4187 | 0.0021302 | 6.139 | 6.1412 | -5.8833 | 469.4399 | 6574.0849 | -0.012533
67 |  | 11.122 | 99.1863 | 4187 | 0.0021299 | 6.1412 | 6.1433 | -5.8833 | 469.4992 | 6673.2712 | -0.012531
68 |  | 11.122 | 99.1738 | 4187 | 0.0021297 | 6.1433 | 6.1454 | -5.8833 | 469.5585 | 6772.445 | -0.01253
69 |  | 11.122 | 99.1613 | 4187 | 0.0021294 | 6.1454 | 6.1476 | -5.8833 | 469.6179 | 6871.6063 | -0.012528
70 |  | 11.122 | 99.1488 | 4187 | 0.0021291 | 6.1476 | 6.1497 | -5.8833 | 469.6772 | 6970.7551 | -0.012526
71 |  | 11.122 | 99.1362 | 4187 | 0.0021289 | 6.1497 | 6.1518 | -5.8833 | 469.7365 | 7069.8913 | -0.012525
72 |  | 11.122 | 99.1237 | 4187 | 0.0021286 | 6.1518 | 6.1539 | -5.8833 | 469.7959 | 7169.015 | -0.012523
73 |  | 11.122 | 99.1112 | 4187 | 0.0021283 | 6.1539 | 6.1561 | -5.8833 | 469.8553 | 7268.1262 | -0.012522
74 |  | 11.122 | 99.0987 | 4187 | 0.002128 | 6.1561 | 6.1582 | -5.8833 | 469.9146 | 7367.2249 | -0.01252
75 |  | 11.122 | 99.0861 | 4187 | 0.0021278 | 6.1582 | 6.1603 | -5.8833 | 469.974 | 7466.311 | -0.012518
76 |  | 11.122 | 99.0736 | 4187 | 0.0021275 | 6.1603 | 6.1625 | -5.8833 | 470.0334 | 7565.3847 | -0.012517
77 |  | 11.122 | 99.0611 | 4187 | 0.0021272 | 6.1625 | 6.1646 | -5.8833 | 470.0928 | 7664.4458 | -0.012515
78 |  | 11.122 | 99.0486 | 4187 | 0.002127 | 6.1646 | 6.1667 | -5.8833 | 470.1522 | 7763.4944 | -0.012514
79 |  | 11.122 | 99.0361 | 4187 | 0.0021267 | 6.1667 | 6.1688 | -5.8833 | 470.2116 | 7862.5304 | -0.012512
80 |  | 11.122 | 99.0236 | 4187 | 0.0021264 | 6.1688 | 6.171 | -5.8833 | 470.271 | 7961.554 | -0.012511
81 |  | 11.122 | 99.0111 | 4187 | 0.0021262 | 6.171 | 6.1731 | -5.8833 | 470.3304 | 8060.5651 | -0.012509
82 |  | 11.122 | 98.9985 | 4187 | 0.0021259 | 6.1731 | 6.1752 | -5.8833 | 470.3898 | 8159.5636 | -0.012507
83 |  | 11.122 | 98.986 | 4187 | 0.0021256 | 6.1752 | 6.1773 | -5.8833 | 470.4493 | 8258.5497 | -0.012506
84 |  | 11.122 | 98.9735 | 4187 | 0.0021254 | 6.1773 | 6.1795 | -5.8833 | 470.5087 | 8357.5232 | -0.012504
85 |  | 11.122 | 98.961 | 4187 | 0.0021251 | 6.1795 | 6.1816 | -5.8833 | 470.5682 | 8456.4842 | -0.012503
86 |  | 11.122 | 98.9485 | 4187 | 0.0021248 | 6.1816 | 6.1837 | -5.8833 | 470.6276 | 8555.4328 | -0.012501
87 |  | 11.122 | 98.936 | 4187 | 0.0021246 | 6.1837 | 6.1858 | -5.8833 | 470.6871 | 8654.3688 | -0.012499
88 |  | 11.122 | 98.9235 | 4187 | 0.0021243 | 6.1858 | 6.188 | -5.8833 | 470.7466 | 8753.2923 | -0.012498
89 |  | 11.122 | 98.911 | 4187 | 0.002124 | 6.188 | 6.1901 | -5.8833 | 470.8061 | 8852.2033 | -0.012496
90 |  | 11.122 | 98.8985 | 4187 | 0.0021237 | 6.1901 | 6.1922 | -5.8833 | 470.8655 | 8951.1019 | -0.012495
91 |  | 11.122 | 98.886 | 4187 | 0.0021235 | 6.1922 | 6.1943 | -5.8833 | 470.925 | 9049.9879 | -0.012493
92 |  | 11.122 | 98.8735 | 4187 | 0.0021232 | 6.1943 | 6.1965 | -5.8833 | 470.9845 | 9148.8615 | -0.012492
93 |  | 11.122 | 98.8611 | 4187 | 0.0021229 | 6.1965 | 6.1986 | -5.8833 | 471.0441 | 9247.7225 | -0.01249
94 |  | 11.122 | 98.8486 | 4187 | 0.0021227 | 6.1986 | 6.2007 | -5.8833 | 471.1036 | 9346.5711 | -0.012488
95 |  | 11.122 | 98.8361 | 4187 | 0.0021224 | 6.2007 | 6.2028 | -5.8833 | 471.1631 | 9445.4072 | -0.012487
96 |  | 11.122 | 98.8236 | 4187 | 0.0021221 | 6.2028 | 6.205 | -5.8833 | 471.2226 | 9544.2307 | -0.012485
97 |  | 11.122 | 98.8111 | 4187 | 0.0021219 | 6.205 | 6.2071 | -5.8833 | 471.2822 | 9643.0419 | -0.012484
98 |  | 11.122 | 98.7986 | 4187 | 0.0021216 | 6.2071 | 6.2092 | -5.8833 | 471.3417 | 9741.8405 | -0.012482
99 |  | 11.122 | 98.7861 | 4187 | 0.0021213 | 6.2092 | 6.2113 | -5.8833 | 471.4013 | 9840.6266 | -0.012481
100 |  | 11.122 | 98.7737 | 4187 | 0.0021211 | 6.2113 | 6.2134 | -5.8833 | 471.4608 | 9939.4003 | -0.012479
101 |  | 11.122 | 98.7612 | 4187 | 0.0021208 | 6.2134 | 6.2156 | -5.8833 | 471.5204 | 10038.1614 | -0.012477
102 |  | 11.122 | 98.7487 | 4187 | 0.0021205 | 6.2156 | 6.2177 | -5.8833 | 471.58 | 10136.9101 | -0.012476
103 |  | 11.122 | 98.7362 | 4187 | 0.0021203 | 6.2177 | 6.2198 | -5.8833 | 471.6396 | 10235.6464 | -0.012474
104 |  | 11.122 | 98.7238 | 4187 | 0.00212 | 6.2198 | 6.2219 | -5.8833 | 471.6992 | 10334.3701 | -0.012473
105 |  | 11.122 | 98.7113 | 4187 | 0.0021197 | 6.2219 | 6.224 | -5.8833 | 471.7588 | 10433.0814 | -0.012471
106 |  | 11.122 | 98.6988 | 4187 | 0.0021195 | 6.224 | 6.2262 | -5.8833 | 471.8184 | 10531.7802 | -0.01247
107 |  | 11.122 | 98.6863 | 4187 | 0.0021192 | 6.2262 | 6.2283 | -5.8833 | 471.878 | 10630.4665 | -0.012468
108 |  | 11.122 | 98.6739 | 4187 | 0.0021189 | 6.2283 | 6.2304 | -5.8833 | 471.9376 | 10729.1404 | -0.012466
109 |  | 11.122 | 98.6614 | 4187 | 0.0021187 | 6.2304 | 6.2325 | -5.8833 | 471.9973 | 10827.8018 | -0.012465
110 |  | 11.122 | 98.6489 | 4187 | 0.0021184 | 6.2325 | 6.2346 | -5.8833 | 472.0569 | 10926.4508 | -0.012463
111 |  | 11.122 | 98.6365 | 4187 | 0.0021181 | 6.2346 | 6.2368 | -5.8833 | 472.1165 | 11025.0872 | -0.012462
112 |  | 11.122 | 98.624 | 4187 | 0.0021179 | 6.2368 | 6.2389 | -5.8833 | 472.1762 | 11123.7113 | -0.01246
113 |  | 11.122 | 98.6116 | 4187 | 0.0021176 | 6.2389 | 6.241 | -5.8833 | 472.2359 | 11222.3228 | -0.012458
114 |  | 11.122 | 98.5991 | 4187 | 0.0021173 | 6.241 | 6.2431 | -5.8833 | 472.2955 | 11320.9219 | -0.012457
115 |  | 11.122 | 98.5866 | 4187 | 0.0021171 | 6.2431 | 6.2452 | -5.8833 | 472.3552 | 11419.5085 | -0.012455
116 |  | 11.122 | 98.5742 | 4187 | 0.0021168 | 6.2452 | 6.2473 | -5.8833 | 472.4149 | 11518.0827 | -0.012454
117 |  | 11.122 | 98.5617 | 4187 | 0.0021165 | 6.2473 | 6.2495 | -5.8833 | 472.4746 | 11616.6445 | -0.012452
118 |  | 11.122 | 98.5493 | 4187 | 0.0021162 | 6.2495 | 6.2516 | -5.8833 | 472.5343 | 11715.1937 | -0.012451
119 |  | 11.122 | 98.5368 | 4187 | 0.002116 | 6.2516 | 6.2537 | -5.8833 | 472.594 | 11813.7306 | -0.012449
120 |  | 11.122 | 98.5244 | 4187 | 0.0021157 | 6.2537 | 6.2558 | -5.8833 | 472.6537 | 11912.2549 | -0.012447
121 |  | 11.122 | 98.5119 | 4187 | 0.0021154 | 6.2558 | 6.2579 | -5.8833 | 472.7134 | 12010.7669 | -0.012446
122 |  | 11.122 | 98.4995 | 4187 | 0.0021152 | 6.2579 | 6.26 | -5.8833 | 472.7732 | 12109.2663 | -0.012444
123 |  | 11.122 | 98.487 | 4187 | 0.0021149 | 6.26 | 6.2621 | -5.8833 | 472.8329 | 12207.7534 | -0.012443
124 |  | 11.122 | 98.4746 | 4187 | 0.0021146 | 6.2621 | 6.2643 | -5.8833 | 472.8926 | 12306.228 | -0.012441
125 |  | 11.122 | 98.4622 | 4187 | 0.0021144 | 6.2643 | 6.2664 | -5.8833 | 472.9524 | 12404.6901 | -0.01244
126 |  | 11.122 | 98.4497 | 4187 | 0.0021141 | 6.2664 | 6.2685 | -5.8833 | 473.0122 | 12503.1399 | -0.012438
127 |  | 11.122 | 98.4373 | 4187 | 0.0021138 | 6.2685 | 6.2706 | -5.8833 | 473.0719 | 12601.5771 | -0.012436
128 |  | 11.122 | 98.4248 | 4187 | 0.0021136 | 6.2706 | 6.2727 | -5.8833 | 473.1317 | 12700.002 | -0.012435
129 |  | 11.122 | 98.4124 | 4187 | 0.0021133 | 6.2727 | 6.2748 | -5.8833 | 473.1915 | 12798.4144 | -0.012433
130 |  | 11.122 | 98.4 | 4187 | 0.002113 | 6.2748 | 6.2769 | -5.8833 | 473.2513 | 12896.8144 | -0.012432
131 |  | 11.122 | 98.3875 | 4187 | 0.0021128 | 6.2769 | 6.2791 | -5.8833 | 473.3111 | 12995.2019 | -0.01243
132 |  | 11.122 | 98.3751 | 4187 | 0.0021125 | 6.2791 | 6.2812 | -5.8833 | 473.3709 | 13093.577 | -0.012429
133 |  | 11.122 | 98.3627 | 4187 | 0.0021122 | 6.2812 | 6.2833 | -5.8833 | 473.4307 | 13191.9397 | -0.012427
134 |  | 11.122 | 98.3503 | 4187 | 0.002112 | 6.2833 | 6.2854 | -5.8833 | 473.4905 | 13290.2899 | -0.012425
135 |  | 11.122 | 98.3378 | 4187 | 0.0021117 | 6.2854 | 6.2875 | -5.8833 | 473.5503 | 13388.6278 | -0.012424
136 |  | 11.122 | 98.3254 | 4187 | 0.0021114 | 6.2875 | 6.2896 | -5.8833 | 473.6102 | 13486.9532 | -0.012422
137 |  | 11.122 | 98.313 | 4187 | 0.0021112 | 6.2896 | 6.2917 | -5.8833 | 473.67 | 13585.2662 | -0.012421
138 |  | 11.122 | 98.3006 | 4187 | 0.0021109 | 6.2917 | 6.2938 | -5.8833 | 473.7299 | 13683.5667 | -0.012419
139 |  | 11.122 | 98.2881 | 4187 | 0.0021106 | 6.2938 | 6.296 | -5.8833 | 473.7897 | 13781.8549 | -0.012418
140 |  | 11.122 | 98.2757 | 4187 | 0.0021104 | 6.296 | 6.2981 | -5.8833 | 473.8496 | 13880.1306 | -0.012416
141 |  | 11.122 | 98.2633 | 4187 | 0.0021101 | 6.2981 | 6.3002 | -5.8833 | 473.9095 | 13978.3939 | -0.012414
142 |  | 11.122 | 98.2509 | 4187 | 0.0021098 | 6.3002 | 6.3023 | -5.8833 | 473.9693 | 14076.6448 | -0.012413
143 |  | 11.122 | 98.2385 | 4187 | 0.0021096 | 6.3023 | 6.3044 | -5.8833 | 474.0292 | 14174.8833 | -0.012411
144 |  | 11.122 | 98.2261 | 4187 | 0.0021093 | 6.3044 | 6.3065 | -5.8833 | 474.0891 | 14273.1094 | -0.01241
145 |  | 11.122 | 98.2137 | 4187 | 0.002109 | 6.3065 | 6.3086 | -5.8833 | 474.149 | 14371.323 | -0.012408
146 |  | 11.122 | 98.2013 | 4187 | 0.0021088 | 6.3086 | 6.3107 | -5.8833 | 474.2089 | 14469.5243 | -0.012407
147 |  | 11.122 | 98.1888 | 4187 | 0.0021085 | 6.3107 | 6.3128 | -5.8833 | 474.2689 | 14567.7131 | -0.012405
148 |  | 11.122 | 98.1764 | 4187 | 0.0021082 | 6.3128 | 6.3149 | -5.8833 | 474.3288 | 14665.8896 | -0.012404
149 |  | 11.122 | 98.164 | 4187 | 0.002108 | 6.3149 | 6.317 | -5.8833 | 474.3887 | 14764.0536 | -0.012402
150 |  | 11.122 | 98.1516 | 4187 | 0.0021077 | 6.317 | 6.3192 | -5.8833 | 474.4487 | 14862.2052 | -0.0124
151 |  | 11.122 | 98.1392 | 4187 | 0.0021074 | 6.3192 | 6.3213 | -5.8833 | 474.5086 | 14960.3445 | -0.012399
152 |  | 11.122 | 98.1268 | 4187 | 0.0021072 | 6.3213 | 6.3234 | -5.8833 | 474.5686 | 15058.4713 | -0.012397
153 |  | 11.122 | 98.1144 | 4187 | 0.0021069 | 6.3234 | 6.3255 | -5.8833 | 474.6285 | 15156.5858 | -0.012396
154 |  | 11.122 | 98.102 | 4187 | 0.0021066 | 6.3255 | 6.3276 | -5.8833 | 474.6885 | 15254.6878 | -0.012394
155 |  | 11.122 | 98.0897 | 4187 | 0.0021064 | 6.3276 | 6.3297 | -5.8833 | 474.7485 | 15352.7774 | -0.012393
156 |  | 11.122 | 98.0773 | 4187 | 0.0021061 | 6.3297 | 6.3318 | -5.8833 | 474.8085 | 15450.8547 | -0.012391
157 |  | 11.122 | 98.0649 | 4187 | 0.0021058 | 6.3318 | 6.3339 | -5.8833 | 474.8685 | 15548.9196 | -0.012389
158 |  | 11.122 | 98.0525 | 4187 | 0.0021056 | 6.3339 | 6.336 | -5.8833 | 474.9285 | 15646.972 | -0.012388
159 |  | 11.122 | 98.0401 | 4187 | 0.0021053 | 6.336 | 6.3381 | -5.8833 | 474.9885 | 15745.0121 | -0.012386
160 |  | 11.122 | 98.0277 | 4187 | 0.002105 | 6.3381 | 6.3402 | -5.8833 | 475.0485 | 15843.0398 | -0.012385
161 |  | 11.122 | 98.0153 | 4187 | 0.0021048 | 6.3402 | 6.3423 | -5.8833 | 475.1085 | 15941.0552 | -0.012383
162 |  | 11.122 | 98.0029 | 4187 | 0.0021045 | 6.3423 | 6.3444 | -5.8833 | 475.1685 | 16039.0581 | -0.012382
163 |  | 11.122 | 97.9906 | 4187 | 0.0021043 | 6.3444 | 6.3465 | -5.8833 | 475.2286 | 16137.0486 | -0.01238
164 |  | 11.122 | 97.9782 | 4187 | 0.002104 | 6.3465 | 6.3486 | -5.8833 | 475.2886 | 16235.0268 | -0.012378
165 |  | 11.122 | 97.9658 | 4187 | 0.0021037 | 6.3486 | 6.3507 | -5.8833 | 475.3487 | 16332.9926 | -0.012377
166 |  | 11.122 | 97.9534 | 4187 | 0.0021035 | 6.3507 | 6.3528 | -5.8833 | 475.4087 | 16430.946 | -0.012375
167 |  | 11.122 | 97.941 | 4187 | 0.0021032 | 6.3528 | 6.3549 | -5.8833 | 475.4688 | 16528.8871 | -0.012374
168 |  | 11.122 | 97.9287 | 4187 | 0.0021029 | 6.3549 | 6.357 | -5.8833 | 475.5289 | 16626.8157 | -0.012372
169 |  | 11.122 | 97.9163 | 4187 | 0.0021027 | 6.357 | 6.3591 | -5.8833 | 475.589 | 16724.732 | -0.012371
170 |  | 11.122 | 97.9039 | 4187 | 0.0021024 | 6.3591 | 6.3612 | -5.8833 | 475.6491 | 16822.636 | -0.012369
171 |  | 11.122 | 97.8916 | 4187 | 0.0021021 | 6.3612 | 6.3634 | -5.8833 | 475.7092 | 16920.5275 | -0.012368
172 |  | 11.122 | 97.8792 | 4187 | 0.0021019 | 6.3634 | 6.3655 | -5.8833 | 475.7693 | 17018.4067 | -0.012366
173 |  | 11.122 | 97.8668 | 4187 | 0.0021016 | 6.3655 | 6.3676 | -5.8833 | 475.8294 | 17116.2735 | -0.012364
174 |  | 11.122 | 97.8545 | 4187 | 0.0021013 | 6.3676 | 6.3697 | -5.8833 | 475.8895 | 17214.128 | -0.012363
175 |  | 11.122 | 97.8421 | 4187 | 0.0021011 | 6.3697 | 6.3718 | -5.8833 | 475.9497 | 17311.9701 | -0.012361
176 |  | 11.122 | 97.8297 | 4187 | 0.0021008 | 6.3718 | 6.3739 | -5.8833 | 476.0098 | 17409.7998 | -0.01236
177 |  | 11.122 | 97.8174 | 4187 | 0.0021005 | 6.3739 | 6.376 | -5.8833 | 476.0699 | 17507.6172 | -0.012358
178 |  | 11.122 | 97.805 | 4187 | 0.0021003 | 6.376 | 6.3781 | -5.8833 | 476.1301 | 17605.4222 | -0.012357
179 |  | 11.122 | 97.7927 | 4187 | 0.0021 | 6.3781 | 6.3802 | -5.8833 | 476.1903 | 17703.2149 | -0.012355
180 |  | 11.122 | 97.7803 | 4187 | 0.0020997 | 6.3802 | 6.3823 | -5.8833 | 476.2504 | 17800.9952 | -0.012353
181 |  | 11.122 | 97.768 | 4187 | 0.0020995 | 6.3823 | 6.3844 | -5.8833 | 476.3106 | 17898.7631 | -0.012352
182 |  | 11.122 | 97.7556 | 4187 | 0.0020992 | 6.3844 | 6.3865 | -5.8833 | 476.3708 | 17996.5187 | -0.01235
183 |  | 11.122 | 97.7432 | 4187 | 0.0020989 | 6.3865 | 6.3886 | -5.8833 | 476.431 | 18094.262 | -0.012349
184 |  | 11.122 | 97.7309 | 4187 | 0.0020987 | 6.3886 | 6.3907 | -5.8833 | 476.4912 | 18191.9929 | -0.012347
185 |  | 11.122 | 97.7186 | 4187 | 0.0020984 | 6.3907 | 6.3928 | -5.8833 | 476.5514 | 18289.7114 | -0.012346
186 |  | 11.122 | 97.7062 | 4187 | 0.0020981 | 6.3928 | 6.3949 | -5.8833 | 476.6116 | 18387.4176 | -0.012344
187 |  | 11.122 | 97.6939 | 4187 | 0.0020979 | 6.3949 | 6.3969 | -5.8833 | 476.6718 | 18485.1115 | -0.012343
188 |  | 11.122 | 97.6815 | 4187 | 0.0020976 | 6.3969 | 6.399 | -5.8833 | 476.7321 | 18582.793 | -0.012341
189 |  | 11.122 | 97.6692 | 4187 | 0.0020973 | 6.399 | 6.4011 | -5.8833 | 476.7923 | 18680.4622 | -0.012339
190 |  | 11.122 | 97.6568 | 4187 | 0.0020971 | 6.4011 | 6.4032 | -5.8833 | 476.8525 | 18778.1191 | -0.012338
191 |  | 11.122 | 97.6445 | 4187 | 0.0020968 | 6.4032 | 6.4053 | -5.8833 | 476.9128 | 18875.7636 | -0.012336
192 |  | 11.122 | 97.6322 | 4187 | 0.0020966 | 6.4053 | 6.4074 | -5.8833 | 476.973 | 18973.3957 | -0.012335
193 |  | 11.122 | 97.6198 | 4187 | 0.0020963 | 6.4074 | 6.4095 | -5.8833 | 477.0333 | 19071.0156 | -0.012333
194 |  | 11.122 | 97.6075 | 4187 | 0.002096 | 6.4095 | 6.4116 | -5.8833 | 477.0936 | 19168.6231 | -0.012332
195 |  | 11.122 | 97.5952 | 4187 | 0.0020958 | 6.4116 | 6.4137 | -5.8833 | 477.1539 | 19266.2182 | -0.01233
196 |  | 11.122 | 97.5828 | 4187 | 0.0020955 | 6.4137 | 6.4158 | -5.8833 | 477.2142 | 19363.8011 | -0.012329
197 |  | 11.122 | 97.5705 | 4187 | 0.0020952 | 6.4158 | 6.4179 | -5.8833 | 477.2745 | 19461.3716 | -0.012327
198 |  | 11.122 | 97.5582 | 4187 | 0.002095 | 6.4179 | 6.42 | -5.8833 | 477.3348 | 19558.9297 | -0.012325
199 |  | 11.122 | 97.5459 | 4187 | 0.0020947 | 6.42 | 6.4221 | -5.8833 | 477.3951 | 19656.4756 | -0.012324
200 |  | 11.122 | 97.5335 | 4187 | 0.0020944 | 6.4221 | 6.4242 | -5.8833 | 477.4554 | 19754.0091 | -0.012322
201 |  | 11.122 | 97.5212 | 4187 | 0.0020942 | 6.4242 | 6.4263 | -5.8833 | 477.5157 | 19851.5303 | -0.012321
202 |  | 11.122 | 97.5089 | 4187 | 0.0020939 | 6.4263 | 6.4284 | -5.8833 | 477.5761 | 19949.0392 | -0.012319
203 |  | 11.122 | 97.4966 | 4187 | 0.0020936 | 6.4284 | 6.4305 | -5.8833 | 477.6364 | 20046.5358 | -0.012318
204 |  | 11.122 | 97.4843 | 4187 | 0.0020934 | 6.4305 | 6.4326 | -5.8833 | 477.6968 | 20144.0201 | -0.012316
205 |  | 11.122 | 97.4719 | 4187 | 0.0020931 | 6.4326 | 6.4347 | -5.8833 | 477.7571 | 20241.492 | -0.012315
206 |  | 11.122 | 97.4596 | 4187 | 0.0020928 | 6.4347 | 6.4368 | -5.8833 | 477.8175 | 20338.9516 | -0.012313
207 |  | 11.122 | 97.4473 | 4187 | 0.0020926 | 6.4368 | 6.4389 | -5.8833 | 477.8779 | 20436.3989 | -0.012311
208 |  | 11.122 | 97.435 | 4187 | 0.0020923 | 6.4389 | 6.4409 | -5.8833 | 477.9382 | 20533.8339 | -0.01231
209 |  | 11.122 | 97.4227 | 4187 | 0.0020921 | 6.4409 | 6.443 | -5.8833 | 477.9986 | 20631.2566 | -0.012308
210 |  | 11.122 | 97.4104 | 4187 | 0.0020918 | 6.443 | 6.4451 | -5.8833 | 478.059 | 20728.667 | -0.012307
211 |  | 11.122 | 97.3981 | 4187 | 0.0020915 | 6.4451 | 6.4472 | -5.8833 | 478.1194 | 20826.0651 | -0.012305
212 |  | 11.122 | 97.3858 | 4187 | 0.0020913 | 6.4472 | 6.4493 | -5.8833 | 478.1799 | 20923.4508 | -0.012304
213 |  | 11.122 | 97.3735 | 4187 | 0.002091 | 6.4493 | 6.4514 | -5.8833 | 478.2403 | 21020.8243 | -0.012302
214 |  | 11.122 | 97.3612 | 4187 | 0.0020907 | 6.4514 | 6.4535 | -5.8833 | 478.3007 | 21118.1855 | -0.012301
215 |  | 11.122 | 97.3489 | 4187 | 0.0020905 | 6.4535 | 6.4556 | -5.8833 | 478.3611 | 21215.5343 | -0.012299
216 |  | 11.122 | 97.3366 | 4187 | 0.0020902 | 6.4556 | 6.4577 | -5.8833 | 478.4216 | 21312.8709 | -0.012297
217 |  | 11.122 | 97.3243 | 4187 | 0.0020899 | 6.4577 | 6.4598 | -5.8833 | 478.482 | 21410.1951 | -0.012296
218 |  | 11.122 | 97.312 | 4187 | 0.0020897 | 6.4598 | 6.4619 | -5.8833 | 478.5425 | 21507.5071 | -0.012294
219 |  | 11.122 | 97.2997 | 4187 | 0.0020894 | 6.4619 | 6.4639 | -5.8833 | 478.603 | 21604.8068 | -0.012293
220 |  | 11.122 | 97.2874 | 4187 | 0.0020892 | 6.4639 | 6.466 | -5.8833 | 478.6634 | 21702.0942 | -0.012291
221 |  | 11.122 | 97.2751 | 4187 | 0.0020889 | 6.466 | 6.4681 | -5.8833 | 478.7239 | 21799.3693 | -0.01229
222 |  | 11.122 | 97.2628 | 4187 | 0.0020886 | 6.4681 | 6.4702 | -5.8833 | 478.7844 | 21896.6321 | -0.012288
223 |  | 11.122 | 97.2505 | 4187 | 0.0020884 | 6.4702 | 6.4723 | -5.8833 | 478.8449 | 21993.8826 | -0.012287
224 |  | 11.122 | 97.2382 | 4187 | 0.0020881 | 6.4723 | 6.4744 | -5.8833 | 478.9054 | 22091.1208 | -0.012285
225 |  | 11.122 | 97.2259 | 4187 | 0.0020878 | 6.4744 | 6.4765 | -5.8833 | 478.9659 | 22188.3467 | -0.012283
226 |  | 11.122 | 97.2137 | 4187 | 0.0020876 | 6.4765 | 6.4786 | -5.8833 | 479.0264 | 22285.5604 | -0.012282
227 |  | 11.122 | 97.2014 | 4187 | 0.0020873 | 6.4786 | 6.4806 | -5.8833 | 479.087 | 22382.7618 | -0.01228
228 |  | 11.122 | 97.1891 | 4187 | 0.002087 | 6.4806 | 6.4827 | -5.8833 | 479.1475 | 22479.9509 | -0.012279
229 |  | 11.122 | 97.1768 | 4187 | 0.0020868 | 6.4827 | 6.4848 | -5.8833 | 479.208 | 22577.1277 | -0.012277
230 |  | 11.122 | 97.1645 | 4187 | 0.0020865 | 6.4848 | 6.4869 | -5.8833 | 479.2686 | 22674.2922 | -0.012276
231 |  | 11.122 | 97.1523 | 4187 | 0.0020862 | 6.4869 | 6.489 | -5.8833 | 479.3291 | 22771.4445 | -0.012274
232 |  | 11.122 | 97.14 | 4187 | 0.002086 | 6.489 | 6.4911 | -5.8833 | 479.3897 | 22868.5845 | -0.012273
233 |  | 11.122 | 97.1277 | 4187 | 0.0020857 | 6.4911 | 6.4932 | -5.8833 | 479.4503 | 22965.7122 | -0.012271
234 |  | 11.122 | 97.1154 | 4187 | 0.0020855 | 6.4932 | 6.4953 | -5.8833 | 479.5109 | 23062.8276 | -0.012269
235 |  | 11.122 | 97.1032 | 4187 | 0.0020852 | 6.4953 | 6.4973 | -5.8833 | 479.5715 | 23159.9308 | -0.012268
236 |  | 11.122 | 97.0909 | 4187 | 0.0020849 | 6.4973 | 6.4994 | -5.8833 | 479.6321 | 23257.0217 | -0.012266

## St168
|  |  | buis | verlies W/M | L /°C/sec
diam | wandikte |  | inhoud l/m |  | W/M
168.3 | 4.5 | 3.1416 | 19.9306 | 132.5458 | 4187
[8 empty] | J/sec/mtr | aantal mtr. | verlies
|  | buis | verlies W/M | L /°C/sec | verlies temp | begintemp | eindtemp | verlies | bij 1°C | totaal J/sec
|  | inhoud L |  | W/M | °C per M | °C | °C | per m°C | daling | aantal mtr
1 | 168.3 | 19.9306 | 132.5458 | 4187 | 0.0015883 | 6 | 6.0016 | -7.7968 | 629.5907 | 132.5458 | -0.012384
2 |  | 19.9306 | 132.5334 | 4187 | 0.0015882 | 6.0016 | 6.0032 | -7.7968 | 629.6496 | 265.0793 | -0.012383
3 |  | 19.9306 | 132.5211 | 4187 | 0.001588 | 6.0032 | 6.0048 | -7.7968 | 629.7084 | 397.6003 | -0.012382
4 |  | 19.9306 | 132.5087 | 4187 | 0.0015879 | 6.0048 | 6.0064 | -7.7968 | 629.7672 | 530.109 | -0.01238
5 |  | 19.9306 | 132.4963 | 4187 | 0.0015877 | 6.0064 | 6.0079 | -7.7968 | 629.8261 | 662.6053 | -0.012379
6 |  | 19.9306 | 132.4839 | 4187 | 0.0015876 | 6.0079 | 6.0095 | -7.7968 | 629.8849 | 795.0892 | -0.012378
7 |  | 19.9306 | 132.4715 | 4187 | 0.0015874 | 6.0095 | 6.0111 | -7.7968 | 629.9438 | 927.5608 | -0.012377
8 |  | 19.9306 | 132.4592 | 4187 | 0.0015873 | 6.0111 | 6.0127 | -7.7968 | 630.0027 | 1060.0199 | -0.012376
9 |  | 19.9306 | 132.4468 | 4187 | 0.0015871 | 6.0127 | 6.0143 | -7.7968 | 630.0615 | 1192.4667 | -0.012375
10 |  | 19.9306 | 132.4344 | 4187 | 0.001587 | 6.0143 | 6.0159 | -7.7968 | 630.1204 | 1324.9011 | -0.012374
11 |  | 19.9306 | 132.422 | 4187 | 0.0015869 | 6.0159 | 6.0175 | -7.7968 | 630.1793 | 1457.3232 | -0.012372
12 |  | 19.9306 | 132.4097 | 4187 | 0.0015867 | 6.0175 | 6.0191 | -7.7968 | 630.2382 | 1589.7328 | -0.012371
13 |  | 19.9306 | 132.3973 | 4187 | 0.0015866 | 6.0191 | 6.0206 | -7.7968 | 630.2971 | 1722.1301 | -0.01237
14 |  | 19.9306 | 132.3849 | 4187 | 0.0015864 | 6.0206 | 6.0222 | -7.7968 | 630.356 | 1854.5151 | -0.012369
15 |  | 19.9306 | 132.3726 | 4187 | 0.0015863 | 6.0222 | 6.0238 | -7.7968 | 630.4149 | 1986.8876 | -0.012368
16 |  | 19.9306 | 132.3602 | 4187 | 0.0015861 | 6.0238 | 6.0254 | -7.7968 | 630.4738 | 2119.2478 | -0.012367
17 |  | 19.9306 | 132.3478 | 4187 | 0.001586 | 6.0254 | 6.027 | -7.7968 | 630.5327 | 2251.5956 | -0.012365
18 |  | 19.9306 | 132.3355 | 4187 | 0.0015858 | 6.027 | 6.0286 | -7.7968 | 630.5916 | 2383.9311 | -0.012364
19 |  | 19.9306 | 132.3231 | 4187 | 0.0015857 | 6.0286 | 6.0302 | -7.7968 | 630.6505 | 2516.2542 | -0.012363
20 |  | 19.9306 | 132.3107 | 4187 | 0.0015855 | 6.0302 | 6.0317 | -7.7968 | 630.7094 | 2648.5649 | -0.012362
21 |  | 19.9306 | 132.2984 | 4187 | 0.0015854 | 6.0317 | 6.0333 | -7.7968 | 630.7684 | 2780.8633 | -0.012361
22 |  | 19.9306 | 132.286 | 4187 | 0.0015852 | 6.0333 | 6.0349 | -7.7968 | 630.8273 | 2913.1493 | -0.01236
23 |  | 19.9306 | 132.2736 | 4187 | 0.0015851 | 6.0349 | 6.0365 | -7.7968 | 630.8863 | 3045.4229 | -0.012359
24 |  | 19.9306 | 132.2613 | 4187 | 0.0015849 | 6.0365 | 6.0381 | -7.7968 | 630.9452 | 3177.6842 | -0.012357
25 |  | 19.9306 | 132.2489 | 4187 | 0.0015848 | 6.0381 | 6.0397 | -7.7968 | 631.0042 | 3309.9331 | -0.012356
26 |  | 19.9306 | 132.2366 | 4187 | 0.0015846 | 6.0397 | 6.0412 | -7.7968 | 631.0631 | 3442.1697 | -0.012355
27 |  | 19.9306 | 132.2242 | 4187 | 0.0015845 | 6.0412 | 6.0428 | -7.7968 | 631.1221 | 3574.3939 | -0.012354
28 |  | 19.9306 | 132.2119 | 4187 | 0.0015843 | 6.0428 | 6.0444 | -7.7968 | 631.1811 | 3706.6058 | -0.012353
29 |  | 19.9306 | 132.1995 | 4187 | 0.0015842 | 6.0444 | 6.046 | -7.7968 | 631.24 | 3838.8053 | -0.012352
30 |  | 19.9306 | 132.1872 | 4187 | 0.001584 | 6.046 | 6.0476 | -7.7968 | 631.299 | 3970.9925 | -0.01235
31 |  | 19.9306 | 132.1748 | 4187 | 0.0015839 | 6.0476 | 6.0492 | -7.7968 | 631.358 | 4103.1673 | -0.012349
32 |  | 19.9306 | 132.1625 | 4187 | 0.0015837 | 6.0492 | 6.0508 | -7.7968 | 631.417 | 4235.3298 | -0.012348
33 |  | 19.9306 | 132.1501 | 4187 | 0.0015836 | 6.0508 | 6.0523 | -7.7968 | 631.476 | 4367.4799 | -0.012347
34 |  | 19.9306 | 132.1378 | 4187 | 0.0015834 | 6.0523 | 6.0539 | -7.7968 | 631.535 | 4499.6176 | -0.012346
35 |  | 19.9306 | 132.1254 | 4187 | 0.0015833 | 6.0539 | 6.0555 | -7.7968 | 631.594 | 4631.7431 | -0.012345
36 |  | 19.9306 | 132.1131 | 4187 | 0.0015831 | 6.0555 | 6.0571 | -7.7968 | 631.653 | 4763.8561 | -0.012344
37 |  | 19.9306 | 132.1007 | 4187 | 0.001583 | 6.0571 | 6.0587 | -7.7968 | 631.7121 | 4895.9569 | -0.012342
38 |  | 19.9306 | 132.0884 | 4187 | 0.0015829 | 6.0587 | 6.0603 | -7.7968 | 631.7711 | 5028.0453 | -0.012341
39 |  | 19.9306 | 132.076 | 4187 | 0.0015827 | 6.0603 | 6.0618 | -7.7968 | 631.8301 | 5160.1213 | -0.01234
40 |  | 19.9306 | 132.0637 | 4187 | 0.0015826 | 6.0618 | 6.0634 | -7.7968 | 631.8892 | 5292.185 | -0.012339
41 |  | 19.9306 | 132.0514 | 4187 | 0.0015824 | 6.0634 | 6.065 | -7.7968 | 631.9482 | 5424.2364 | -0.012338
42 |  | 19.9306 | 132.039 | 4187 | 0.0015823 | 6.065 | 6.0666 | -7.7968 | 632.0072 | 5556.2754 | -0.012337
43 |  | 19.9306 | 132.0267 | 4187 | 0.0015821 | 6.0666 | 6.0682 | -7.7968 | 632.0663 | 5688.3021 | -0.012335
44 |  | 19.9306 | 132.0144 | 4187 | 0.001582 | 6.0682 | 6.0697 | -7.7968 | 632.1254 | 5820.3165 | -0.012334
45 |  | 19.9306 | 132.002 | 4187 | 0.0015818 | 6.0697 | 6.0713 | -7.7968 | 632.1844 | 5952.3185 | -0.012333
46 |  | 19.9306 | 131.9897 | 4187 | 0.0015817 | 6.0713 | 6.0729 | -7.7968 | 632.2435 | 6084.3082 | -0.012332
47 |  | 19.9306 | 131.9774 | 4187 | 0.0015815 | 6.0729 | 6.0745 | -7.7968 | 632.3026 | 6216.2856 | -0.012331
48 |  | 19.9306 | 131.965 | 4187 | 0.0015814 | 6.0745 | 6.0761 | -7.7968 | 632.3617 | 6348.2506 | -0.01233
49 |  | 19.9306 | 131.9527 | 4187 | 0.0015812 | 6.0761 | 6.0777 | -7.7968 | 632.4207 | 6480.2033 | -0.012329
50 |  | 19.9306 | 131.9404 | 4187 | 0.0015811 | 6.0777 | 6.0792 | -7.7968 | 632.4798 | 6612.1437 | -0.012327
51 |  | 19.9306 | 131.928 | 4187 | 0.0015809 | 6.0792 | 6.0808 | -7.7968 | 632.5389 | 6744.0717 | -0.012326
52 |  | 19.9306 | 131.9157 | 4187 | 0.0015808 | 6.0808 | 6.0824 | -7.7968 | 632.598 | 6875.9874 | -0.012325
53 |  | 19.9306 | 131.9034 | 4187 | 0.0015806 | 6.0824 | 6.084 | -7.7968 | 632.6572 | 7007.8908 | -0.012324
54 |  | 19.9306 | 131.8911 | 4187 | 0.0015805 | 6.084 | 6.0856 | -7.7968 | 632.7163 | 7139.7819 | -0.012323
55 |  | 19.9306 | 131.8787 | 4187 | 0.0015803 | 6.0856 | 6.0871 | -7.7968 | 632.7754 | 7271.6606 | -0.012322
56 |  | 19.9306 | 131.8664 | 4187 | 0.0015802 | 6.0871 | 6.0887 | -7.7968 | 632.8345 | 7403.5271 | -0.01232
57 |  | 19.9306 | 131.8541 | 4187 | 0.00158 | 6.0887 | 6.0903 | -7.7968 | 632.8937 | 7535.3812 | -0.012319
58 |  | 19.9306 | 131.8418 | 4187 | 0.0015799 | 6.0903 | 6.0919 | -7.7968 | 632.9528 | 7667.2229 | -0.012318
59 |  | 19.9306 | 131.8295 | 4187 | 0.0015797 | 6.0919 | 6.0935 | -7.7968 | 633.0119 | 7799.0524 | -0.012317
60 |  | 19.9306 | 131.8172 | 4187 | 0.0015796 | 6.0935 | 6.095 | -7.7968 | 633.0711 | 7930.8696 | -0.012316
61 |  | 19.9306 | 131.8048 | 4187 | 0.0015795 | 6.095 | 6.0966 | -7.7968 | 633.1302 | 8062.6744 | -0.012315
62 |  | 19.9306 | 131.7925 | 4187 | 0.0015793 | 6.0966 | 6.0982 | -7.7968 | 633.1894 | 8194.4669 | -0.012314
63 |  | 19.9306 | 131.7802 | 4187 | 0.0015792 | 6.0982 | 6.0998 | -7.7968 | 633.2486 | 8326.2471 | -0.012312
64 |  | 19.9306 | 131.7679 | 4187 | 0.001579 | 6.0998 | 6.1014 | -7.7968 | 633.3077 | 8458.015 | -0.012311
65 |  | 19.9306 | 131.7556 | 4187 | 0.0015789 | 6.1014 | 6.1029 | -7.7968 | 633.3669 | 8589.7706 | -0.01231
66 |  | 19.9306 | 131.7433 | 4187 | 0.0015787 | 6.1029 | 6.1045 | -7.7968 | 633.4261 | 8721.5139 | -0.012309
67 |  | 19.9306 | 131.731 | 4187 | 0.0015786 | 6.1045 | 6.1061 | -7.7968 | 633.4853 | 8853.2448 | -0.012308
68 |  | 19.9306 | 131.7187 | 4187 | 0.0015784 | 6.1061 | 6.1077 | -7.7968 | 633.5445 | 8984.9635 | -0.012307
69 |  | 19.9306 | 131.7063 | 4187 | 0.0015783 | 6.1077 | 6.1092 | -7.7968 | 633.6037 | 9116.6698 | -0.012306
70 |  | 19.9306 | 131.694 | 4187 | 0.0015781 | 6.1092 | 6.1108 | -7.7968 | 633.6629 | 9248.3639 | -0.012304
71 |  | 19.9306 | 131.6817 | 4187 | 0.001578 | 6.1108 | 6.1124 | -7.7968 | 633.7221 | 9380.0456 | -0.012303
72 |  | 19.9306 | 131.6694 | 4187 | 0.0015778 | 6.1124 | 6.114 | -7.7968 | 633.7813 | 9511.7151 | -0.012302
73 |  | 19.9306 | 131.6571 | 4187 | 0.0015777 | 6.114 | 6.1156 | -7.7968 | 633.8405 | 9643.3722 | -0.012301
74 |  | 19.9306 | 131.6448 | 4187 | 0.0015775 | 6.1156 | 6.1171 | -7.7968 | 633.8997 | 9775.017 | -0.0123
75 |  | 19.9306 | 131.6325 | 4187 | 0.0015774 | 6.1171 | 6.1187 | -7.7968 | 633.959 | 9906.6496 | -0.012299
76 |  | 19.9306 | 131.6202 | 4187 | 0.0015772 | 6.1187 | 6.1203 | -7.7968 | 634.0182 | 10038.2698 | -0.012297
77 |  | 19.9306 | 131.6079 | 4187 | 0.0015771 | 6.1203 | 6.1219 | -7.7968 | 634.0775 | 10169.8777 | -0.012296
78 |  | 19.9306 | 131.5956 | 4187 | 0.0015769 | 6.1219 | 6.1234 | -7.7968 | 634.1367 | 10301.4734 | -0.012295
79 |  | 19.9306 | 131.5833 | 4187 | 0.0015768 | 6.1234 | 6.125 | -7.7968 | 634.196 | 10433.0567 | -0.012294
80 |  | 19.9306 | 131.5711 | 4187 | 0.0015767 | 6.125 | 6.1266 | -7.7968 | 634.2552 | 10564.6278 | -0.012293
81 |  | 19.9306 | 131.5588 | 4187 | 0.0015765 | 6.1266 | 6.1282 | -7.7968 | 634.3145 | 10696.1865 | -0.012292
82 |  | 19.9306 | 131.5465 | 4187 | 0.0015764 | 6.1282 | 6.1298 | -7.7968 | 634.3738 | 10827.733 | -0.012291
83 |  | 19.9306 | 131.5342 | 4187 | 0.0015762 | 6.1298 | 6.1313 | -7.7968 | 634.433 | 10959.2672 | -0.012289
84 |  | 19.9306 | 131.5219 | 4187 | 0.0015761 | 6.1313 | 6.1329 | -7.7968 | 634.4923 | 11090.7891 | -0.012288
85 |  | 19.9306 | 131.5096 | 4187 | 0.0015759 | 6.1329 | 6.1345 | -7.7968 | 634.5516 | 11222.2987 | -0.012287
86 |  | 19.9306 | 131.4973 | 4187 | 0.0015758 | 6.1345 | 6.1361 | -7.7968 | 634.6109 | 11353.796 | -0.012286
87 |  | 19.9306 | 131.485 | 4187 | 0.0015756 | 6.1361 | 6.1376 | -7.7968 | 634.6702 | 11485.281 | -0.012285
88 |  | 19.9306 | 131.4727 | 4187 | 0.0015755 | 6.1376 | 6.1392 | -7.7968 | 634.7295 | 11616.7537 | -0.012284
89 |  | 19.9306 | 131.4605 | 4187 | 0.0015753 | 6.1392 | 6.1408 | -7.7968 | 634.7888 | 11748.2142 | -0.012283
90 |  | 19.9306 | 131.4482 | 4187 | 0.0015752 | 6.1408 | 6.1424 | -7.7968 | 634.8481 | 11879.6624 | -0.012281
91 |  | 19.9306 | 131.4359 | 4187 | 0.001575 | 6.1424 | 6.1439 | -7.7968 | 634.9074 | 12011.0983 | -0.01228
92 |  | 19.9306 | 131.4236 | 4187 | 0.0015749 | 6.1439 | 6.1455 | -7.7968 | 634.9668 | 12142.5219 | -0.012279
93 |  | 19.9306 | 131.4113 | 4187 | 0.0015747 | 6.1455 | 6.1471 | -7.7968 | 635.0261 | 12273.9332 | -0.012278
94 |  | 19.9306 | 131.3991 | 4187 | 0.0015746 | 6.1471 | 6.1487 | -7.7968 | 635.0854 | 12405.3323 | -0.012277
95 |  | 19.9306 | 131.3868 | 4187 | 0.0015744 | 6.1487 | 6.1502 | -7.7968 | 635.1448 | 12536.719 | -0.012276
96 |  | 19.9306 | 131.3745 | 4187 | 0.0015743 | 6.1502 | 6.1518 | -7.7968 | 635.2041 | 12668.0935 | -0.012275
97 |  | 19.9306 | 131.3622 | 4187 | 0.0015742 | 6.1518 | 6.1534 | -7.7968 | 635.2635 | 12799.4558 | -0.012273
98 |  | 19.9306 | 131.35 | 4187 | 0.001574 | 6.1534 | 6.155 | -7.7968 | 635.3228 | 12930.8057 | -0.012272
99 |  | 19.9306 | 131.3377 | 4187 | 0.0015739 | 6.155 | 6.1565 | -7.7968 | 635.3822 | 13062.1434 | -0.012271
100 |  | 19.9306 | 131.3254 | 4187 | 0.0015737 | 6.1565 | 6.1581 | -7.7968 | 635.4416 | 13193.4688 | -0.01227
101 |  | 19.9306 | 131.3131 | 4187 | 0.0015736 | 6.1581 | 6.1597 | -7.7968 | 635.5009 | 13324.782 | -0.012269
102 |  | 19.9306 | 131.3009 | 4187 | 0.0015734 | 6.1597 | 6.1612 | -7.7968 | 635.5603 | 13456.0828 | -0.012268
103 |  | 19.9306 | 131.2886 | 4187 | 0.0015733 | 6.1612 | 6.1628 | -7.7968 | 635.6197 | 13587.3714 | -0.012266
104 |  | 19.9306 | 131.2763 | 4187 | 0.0015731 | 6.1628 | 6.1644 | -7.7968 | 635.6791 | 13718.6478 | -0.012265
105 |  | 19.9306 | 131.2641 | 4187 | 0.001573 | 6.1644 | 6.166 | -7.7968 | 635.7385 | 13849.9119 | -0.012264
106 |  | 19.9306 | 131.2518 | 4187 | 0.0015728 | 6.166 | 6.1675 | -7.7968 | 635.7979 | 13981.1637 | -0.012263
107 |  | 19.9306 | 131.2395 | 4187 | 0.0015727 | 6.1675 | 6.1691 | -7.7968 | 635.8573 | 14112.4032 | -0.012262
108 |  | 19.9306 | 131.2273 | 4187 | 0.0015725 | 6.1691 | 6.1707 | -7.7968 | 635.9167 | 14243.6305 | -0.012261
109 |  | 19.9306 | 131.215 | 4187 | 0.0015724 | 6.1707 | 6.1723 | -7.7968 | 635.9761 | 14374.8455 | -0.01226
110 |  | 19.9306 | 131.2028 | 4187 | 0.0015722 | 6.1723 | 6.1738 | -7.7968 | 636.0356 | 14506.0483 | -0.012258
111 |  | 19.9306 | 131.1905 | 4187 | 0.0015721 | 6.1738 | 6.1754 | -7.7968 | 636.095 | 14637.2388 | -0.012257
112 |  | 19.9306 | 131.1782 | 4187 | 0.0015719 | 6.1754 | 6.177 | -7.7968 | 636.1544 | 14768.4171 | -0.012256
113 |  | 19.9306 | 131.166 | 4187 | 0.0015718 | 6.177 | 6.1785 | -7.7968 | 636.2139 | 14899.583 | -0.012255
114 |  | 19.9306 | 131.1537 | 4187 | 0.0015717 | 6.1785 | 6.1801 | -7.7968 | 636.2733 | 15030.7368 | -0.012254
115 |  | 19.9306 | 131.1415 | 4187 | 0.0015715 | 6.1801 | 6.1817 | -7.7968 | 636.3328 | 15161.8783 | -0.012253
116 |  | 19.9306 | 131.1292 | 4187 | 0.0015714 | 6.1817 | 6.1833 | -7.7968 | 636.3922 | 15293.0075 | -0.012252
117 |  | 19.9306 | 131.117 | 4187 | 0.0015712 | 6.1833 | 6.1848 | -7.7968 | 636.4517 | 15424.1245 | -0.01225
118 |  | 19.9306 | 131.1047 | 4187 | 0.0015711 | 6.1848 | 6.1864 | -7.7968 | 636.5112 | 15555.2292 | -0.012249
119 |  | 19.9306 | 131.0925 | 4187 | 0.0015709 | 6.1864 | 6.188 | -7.7968 | 636.5707 | 15686.3217 | -0.012248
120 |  | 19.9306 | 131.0802 | 4187 | 0.0015708 | 6.188 | 6.1895 | -7.7968 | 636.6301 | 15817.4019 | -0.012247
121 |  | 19.9306 | 131.068 | 4187 | 0.0015706 | 6.1895 | 6.1911 | -7.7968 | 636.6896 | 15948.4699 | -0.012246
122 |  | 19.9306 | 131.0557 | 4187 | 0.0015705 | 6.1911 | 6.1927 | -7.7968 | 636.7491 | 16079.5256 | -0.012245
123 |  | 19.9306 | 131.0435 | 4187 | 0.0015703 | 6.1927 | 6.1943 | -7.7968 | 636.8086 | 16210.5691 | -0.012244
124 |  | 19.9306 | 131.0313 | 4187 | 0.0015702 | 6.1943 | 6.1958 | -7.7968 | 636.8681 | 16341.6004 | -0.012242
125 |  | 19.9306 | 131.019 | 4187 | 0.00157 | 6.1958 | 6.1974 | -7.7968 | 636.9276 | 16472.6194 | -0.012241
126 |  | 19.9306 | 131.0068 | 4187 | 0.0015699 | 6.1974 | 6.199 | -7.7968 | 636.9871 | 16603.6262 | -0.01224
127 |  | 19.9306 | 130.9945 | 4187 | 0.0015697 | 6.199 | 6.2005 | -7.7968 | 637.0467 | 16734.6207 | -0.012239
128 |  | 19.9306 | 130.9823 | 4187 | 0.0015696 | 6.2005 | 6.2021 | -7.7968 | 637.1062 | 16865.603 | -0.012238
129 |  | 19.9306 | 130.9701 | 4187 | 0.0015695 | 6.2021 | 6.2037 | -7.7968 | 637.1657 | 16996.573 | -0.012237
130 |  | 19.9306 | 130.9578 | 4187 | 0.0015693 | 6.2037 | 6.2052 | -7.7968 | 637.2253 | 17127.5308 | -0.012236
131 |  | 19.9306 | 130.9456 | 4187 | 0.0015692 | 6.2052 | 6.2068 | -7.7968 | 637.2848 | 17258.4764 | -0.012234
132 |  | 19.9306 | 130.9333 | 4187 | 0.001569 | 6.2068 | 6.2084 | -7.7968 | 637.3443 | 17389.4098 | -0.012233
133 |  | 19.9306 | 130.9211 | 4187 | 0.0015689 | 6.2084 | 6.21 | -7.7968 | 637.4039 | 17520.3309 | -0.012232
134 |  | 19.9306 | 130.9089 | 4187 | 0.0015687 | 6.21 | 6.2115 | -7.7968 | 637.4635 | 17651.2397 | -0.012231
135 |  | 19.9306 | 130.8966 | 4187 | 0.0015686 | 6.2115 | 6.2131 | -7.7968 | 637.523 | 17782.1364 | -0.01223
136 |  | 19.9306 | 130.8844 | 4187 | 0.0015684 | 6.2131 | 6.2147 | -7.7968 | 637.5826 | 17913.0208 | -0.012229
137 |  | 19.9306 | 130.8722 | 4187 | 0.0015683 | 6.2147 | 6.2162 | -7.7968 | 637.6422 | 18043.893 | -0.012228
138 |  | 19.9306 | 130.86 | 4187 | 0.0015681 | 6.2162 | 6.2178 | -7.7968 | 637.7017 | 18174.753 | -0.012226
139 |  | 19.9306 | 130.8477 | 4187 | 0.001568 | 6.2178 | 6.2194 | -7.7968 | 637.7613 | 18305.6007 | -0.012225
140 |  | 19.9306 | 130.8355 | 4187 | 0.0015678 | 6.2194 | 6.2209 | -7.7968 | 637.8209 | 18436.4362 | -0.012224
141 |  | 19.9306 | 130.8233 | 4187 | 0.0015677 | 6.2209 | 6.2225 | -7.7968 | 637.8805 | 18567.2595 | -0.012223
142 |  | 19.9306 | 130.8111 | 4187 | 0.0015675 | 6.2225 | 6.2241 | -7.7968 | 637.9401 | 18698.0706 | -0.012222
143 |  | 19.9306 | 130.7988 | 4187 | 0.0015674 | 6.2241 | 6.2256 | -7.7968 | 637.9997 | 18828.8694 | -0.012221
144 |  | 19.9306 | 130.7866 | 4187 | 0.0015673 | 6.2256 | 6.2272 | -7.7968 | 638.0594 | 18959.656 | -0.01222
145 |  | 19.9306 | 130.7744 | 4187 | 0.0015671 | 6.2272 | 6.2288 | -7.7968 | 638.119 | 19090.4304 | -0.012218
146 |  | 19.9306 | 130.7622 | 4187 | 0.001567 | 6.2288 | 6.2303 | -7.7968 | 638.1786 | 19221.1926 | -0.012217
147 |  | 19.9306 | 130.75 | 4187 | 0.0015668 | 6.2303 | 6.2319 | -7.7968 | 638.2382 | 19351.9426 | -0.012216
148 |  | 19.9306 | 130.7377 | 4187 | 0.0015667 | 6.2319 | 6.2335 | -7.7968 | 638.2979 | 19482.6803 | -0.012215
149 |  | 19.9306 | 130.7255 | 4187 | 0.0015665 | 6.2335 | 6.235 | -7.7968 | 638.3575 | 19613.4058 | -0.012214
150 |  | 19.9306 | 130.7133 | 4187 | 0.0015664 | 6.235 | 6.2366 | -7.7968 | 638.4172 | 19744.1192 | -0.012213
151 |  | 19.9306 | 130.7011 | 4187 | 0.0015662 | 6.2366 | 6.2382 | -7.7968 | 638.4768 | 19874.8203 | -0.012212
152 |  | 19.9306 | 130.6889 | 4187 | 0.0015661 | 6.2382 | 6.2397 | -7.7968 | 638.5365 | 20005.5092 | -0.01221
153 |  | 19.9306 | 130.6767 | 4187 | 0.0015659 | 6.2397 | 6.2413 | -7.7968 | 638.5961 | 20136.1858 | -0.012209
154 |  | 19.9306 | 130.6645 | 4187 | 0.0015658 | 6.2413 | 6.2429 | -7.7968 | 638.6558 | 20266.8503 | -0.012208
155 |  | 19.9306 | 130.6523 | 4187 | 0.0015656 | 6.2429 | 6.2444 | -7.7968 | 638.7155 | 20397.5026 | -0.012207
156 |  | 19.9306 | 130.6401 | 4187 | 0.0015655 | 6.2444 | 6.246 | -7.7968 | 638.7752 | 20528.1426 | -0.012206
157 |  | 19.9306 | 130.6279 | 4187 | 0.0015653 | 6.246 | 6.2476 | -7.7968 | 638.8349 | 20658.7705 | -0.012205
158 |  | 19.9306 | 130.6156 | 4187 | 0.0015652 | 6.2476 | 6.2491 | -7.7968 | 638.8945 | 20789.3861 | -0.012204
159 |  | 19.9306 | 130.6034 | 4187 | 0.0015651 | 6.2491 | 6.2507 | -7.7968 | 638.9542 | 20919.9896 | -0.012202
160 |  | 19.9306 | 130.5912 | 4187 | 0.0015649 | 6.2507 | 6.2523 | -7.7968 | 639.0139 | 21050.5808 | -0.012201
161 |  | 19.9306 | 130.579 | 4187 | 0.0015648 | 6.2523 | 6.2538 | -7.7968 | 639.0737 | 21181.1599 | -0.0122
162 |  | 19.9306 | 130.5668 | 4187 | 0.0015646 | 6.2538 | 6.2554 | -7.7968 | 639.1334 | 21311.7267 | -0.012199
163 |  | 19.9306 | 130.5546 | 4187 | 0.0015645 | 6.2554 | 6.2569 | -7.7968 | 639.1931 | 21442.2814 | -0.012198
164 |  | 19.9306 | 130.5424 | 4187 | 0.0015643 | 6.2569 | 6.2585 | -7.7968 | 639.2528 | 21572.8238 | -0.012197
165 |  | 19.9306 | 130.5302 | 4187 | 0.0015642 | 6.2585 | 6.2601 | -7.7968 | 639.3126 | 21703.3541 | -0.012196
166 |  | 19.9306 | 130.5181 | 4187 | 0.001564 | 6.2601 | 6.2616 | -7.7968 | 639.3723 | 21833.8721 | -0.012194
167 |  | 19.9306 | 130.5059 | 4187 | 0.0015639 | 6.2616 | 6.2632 | -7.7968 | 639.432 | 21964.378 | -0.012193
168 |  | 19.9306 | 130.4937 | 4187 | 0.0015637 | 6.2632 | 6.2648 | -7.7968 | 639.4918 | 22094.8716 | -0.012192
169 |  | 19.9306 | 130.4815 | 4187 | 0.0015636 | 6.2648 | 6.2663 | -7.7968 | 639.5515 | 22225.3531 | -0.012191
170 |  | 19.9306 | 130.4693 | 4187 | 0.0015634 | 6.2663 | 6.2679 | -7.7968 | 639.6113 | 22355.8224 | -0.01219
171 |  | 19.9306 | 130.4571 | 4187 | 0.0015633 | 6.2679 | 6.2695 | -7.7968 | 639.6711 | 22486.2795 | -0.012189
172 |  | 19.9306 | 130.4449 | 4187 | 0.0015632 | 6.2695 | 6.271 | -7.7968 | 639.7308 | 22616.7244 | -0.012188
173 |  | 19.9306 | 130.4327 | 4187 | 0.001563 | 6.271 | 6.2726 | -7.7968 | 639.7906 | 22747.1571 | -0.012187
174 |  | 19.9306 | 130.4205 | 4187 | 0.0015629 | 6.2726 | 6.2741 | -7.7968 | 639.8504 | 22877.5776 | -0.012185
175 |  | 19.9306 | 130.4083 | 4187 | 0.0015627 | 6.2741 | 6.2757 | -7.7968 | 639.9102 | 23007.986 | -0.012184
176 |  | 19.9306 | 130.3962 | 4187 | 0.0015626 | 6.2757 | 6.2773 | -7.7968 | 639.97 | 23138.3821 | -0.012183
177 |  | 19.9306 | 130.384 | 4187 | 0.0015624 | 6.2773 | 6.2788 | -7.7968 | 640.0298 | 23268.7661 | -0.012182
178 |  | 19.9306 | 130.3718 | 4187 | 0.0015623 | 6.2788 | 6.2804 | -7.7968 | 640.0896 | 23399.1379 | -0.012181
179 |  | 19.9306 | 130.3596 | 4187 | 0.0015621 | 6.2804 | 6.282 | -7.7968 | 640.1494 | 23529.4975 | -0.01218
180 |  | 19.9306 | 130.3474 | 4187 | 0.001562 | 6.282 | 6.2835 | -7.7968 | 640.2092 | 23659.8449 | -0.012179
181 |  | 19.9306 | 130.3353 | 4187 | 0.0015618 | 6.2835 | 6.2851 | -7.7968 | 640.269 | 23790.1802 | -0.012177
182 |  | 19.9306 | 130.3231 | 4187 | 0.0015617 | 6.2851 | 6.2866 | -7.7968 | 640.3288 | 23920.5033 | -0.012176
183 |  | 19.9306 | 130.3109 | 4187 | 0.0015616 | 6.2866 | 6.2882 | -7.7968 | 640.3887 | 24050.8142 | -0.012175
184 |  | 19.9306 | 130.2987 | 4187 | 0.0015614 | 6.2882 | 6.2898 | -7.7968 | 640.4485 | 24181.1129 | -0.012174
185 |  | 19.9306 | 130.2866 | 4187 | 0.0015613 | 6.2898 | 6.2913 | -7.7968 | 640.5084 | 24311.3994 | -0.012173
186 |  | 19.9306 | 130.2744 | 4187 | 0.0015611 | 6.2913 | 6.2929 | -7.7968 | 640.5682 | 24441.6738 | -0.012172
187 |  | 19.9306 | 130.2622 | 4187 | 0.001561 | 6.2929 | 6.2945 | -7.7968 | 640.6281 | 24571.936 | -0.012171
188 |  | 19.9306 | 130.25 | 4187 | 0.0015608 | 6.2945 | 6.296 | -7.7968 | 640.6879 | 24702.1861 | -0.012169
189 |  | 19.9306 | 130.2379 | 4187 | 0.0015607 | 6.296 | 6.2976 | -7.7968 | 640.7478 | 24832.4239 | -0.012168
190 |  | 19.9306 | 130.2257 | 4187 | 0.0015605 | 6.2976 | 6.2991 | -7.7968 | 640.8077 | 24962.6496 | -0.012167
191 |  | 19.9306 | 130.2135 | 4187 | 0.0015604 | 6.2991 | 6.3007 | -7.7968 | 640.8675 | 25092.8632 | -0.012166
192 |  | 19.9306 | 130.2014 | 4187 | 0.0015602 | 6.3007 | 6.3023 | -7.7968 | 640.9274 | 25223.0645 | -0.012165
193 |  | 19.9306 | 130.1892 | 4187 | 0.0015601 | 6.3023 | 6.3038 | -7.7968 | 640.9873 | 25353.2537 | -0.012164
194 |  | 19.9306 | 130.177 | 4187 | 0.0015599 | 6.3038 | 6.3054 | -7.7968 | 641.0472 | 25483.4308 | -0.012163
195 |  | 19.9306 | 130.1649 | 4187 | 0.0015598 | 6.3054 | 6.3069 | -7.7968 | 641.1071 | 25613.5956 | -0.012161
196 |  | 19.9306 | 130.1527 | 4187 | 0.0015597 | 6.3069 | 6.3085 | -7.7968 | 641.167 | 25743.7484 | -0.01216
197 |  | 19.9306 | 130.1406 | 4187 | 0.0015595 | 6.3085 | 6.3101 | -7.7968 | 641.2269 | 25873.8889 | -0.012159
198 |  | 19.9306 | 130.1284 | 4187 | 0.0015594 | 6.3101 | 6.3116 | -7.7968 | 641.2868 | 26004.0173 | -0.012158
199 |  | 19.9306 | 130.1162 | 4187 | 0.0015592 | 6.3116 | 6.3132 | -7.7968 | 641.3468 | 26134.1335 | -0.012157
200 |  | 19.9306 | 130.1041 | 4187 | 0.0015591 | 6.3132 | 6.3147 | -7.7968 | 641.4067 | 26264.2376 | -0.012156
201 |  | 19.9306 | 130.0919 | 4187 | 0.0015589 | 6.3147 | 6.3163 | -7.7968 | 641.4666 | 26394.3295 | -0.012155
202 |  | 19.9306 | 130.0798 | 4187 | 0.0015588 | 6.3163 | 6.3178 | -7.7968 | 641.5266 | 26524.4093 | -0.012154
203 |  | 19.9306 | 130.0676 | 4187 | 0.0015586 | 6.3178 | 6.3194 | -7.7968 | 641.5865 | 26654.4769 | -0.012152
204 |  | 19.9306 | 130.0555 | 4187 | 0.0015585 | 6.3194 | 6.321 | -7.7968 | 641.6465 | 26784.5324 | -0.012151
205 |  | 19.9306 | 130.0433 | 4187 | 0.0015583 | 6.321 | 6.3225 | -7.7968 | 641.7064 | 26914.5757 | -0.01215
206 |  | 19.9306 | 130.0312 | 4187 | 0.0015582 | 6.3225 | 6.3241 | -7.7968 | 641.7664 | 27044.6069 | -0.012149
207 |  | 19.9306 | 130.019 | 4187 | 0.0015581 | 6.3241 | 6.3256 | -7.7968 | 641.8263 | 27174.6259 | -0.012148
208 |  | 19.9306 | 130.0069 | 4187 | 0.0015579 | 6.3256 | 6.3272 | -7.7968 | 641.8863 | 27304.6327 | -0.012147
209 |  | 19.9306 | 129.9947 | 4187 | 0.0015578 | 6.3272 | 6.3288 | -7.7968 | 641.9463 | 27434.6275 | -0.012146
210 |  | 19.9306 | 129.9826 | 4187 | 0.0015576 | 6.3288 | 6.3303 | -7.7968 | 642.0063 | 27564.61 | -0.012144
211 |  | 19.9306 | 129.9704 | 4187 | 0.0015575 | 6.3303 | 6.3319 | -7.7968 | 642.0663 | 27694.5805 | -0.012143
212 |  | 19.9306 | 129.9583 | 4187 | 0.0015573 | 6.3319 | 6.3334 | -7.7968 | 642.1263 | 27824.5387 | -0.012142
213 |  | 19.9306 | 129.9461 | 4187 | 0.0015572 | 6.3334 | 6.335 | -7.7968 | 642.1863 | 27954.4849 | -0.012141
214 |  | 19.9306 | 129.934 | 4187 | 0.001557 | 6.335 | 6.3365 | -7.7968 | 642.2463 | 28084.4189 | -0.01214
215 |  | 19.9306 | 129.9219 | 4187 | 0.0015569 | 6.3365 | 6.3381 | -7.7968 | 642.3063 | 28214.3407 | -0.012139
216 |  | 19.9306 | 129.9097 | 4187 | 0.0015567 | 6.3381 | 6.3397 | -7.7968 | 642.3663 | 28344.2505 | -0.012138
217 |  | 19.9306 | 129.8976 | 4187 | 0.0015566 | 6.3397 | 6.3412 | -7.7968 | 642.4263 | 28474.148 | -0.012137
218 |  | 19.9306 | 129.8854 | 4187 | 0.0015565 | 6.3412 | 6.3428 | -7.7968 | 642.4863 | 28604.0335 | -0.012135
219 |  | 19.9306 | 129.8733 | 4187 | 0.0015563 | 6.3428 | 6.3443 | -7.7968 | 642.5464 | 28733.9068 | -0.012134
220 |  | 19.9306 | 129.8612 | 4187 | 0.0015562 | 6.3443 | 6.3459 | -7.7968 | 642.6064 | 28863.768 | -0.012133
221 |  | 19.9306 | 129.849 | 4187 | 0.001556 | 6.3459 | 6.3474 | -7.7968 | 642.6665 | 28993.617 | -0.012132
222 |  | 19.9306 | 129.8369 | 4187 | 0.0015559 | 6.3474 | 6.349 | -7.7968 | 642.7265 | 29123.4539 | -0.012131
223 |  | 19.9306 | 129.8248 | 4187 | 0.0015557 | 6.349 | 6.3506 | -7.7968 | 642.7866 | 29253.2787 | -0.01213
224 |  | 19.9306 | 129.8127 | 4187 | 0.0015556 | 6.3506 | 6.3521 | -7.7968 | 642.8466 | 29383.0914 | -0.012129
225 |  | 19.9306 | 129.8005 | 4187 | 0.0015554 | 6.3521 | 6.3537 | -7.7968 | 642.9067 | 29512.8919 | -0.012127
226 |  | 19.9306 | 129.7884 | 4187 | 0.0015553 | 6.3537 | 6.3552 | -7.7968 | 642.9668 | 29642.6803 | -0.012126
227 |  | 19.9306 | 129.7763 | 4187 | 0.0015551 | 6.3552 | 6.3568 | -7.7968 | 643.0268 | 29772.4566 | -0.012125
228 |  | 19.9306 | 129.7641 | 4187 | 0.001555 | 6.3568 | 6.3583 | -7.7968 | 643.0869 | 29902.2207 | -0.012124
229 |  | 19.9306 | 129.752 | 4187 | 0.0015549 | 6.3583 | 6.3599 | -7.7968 | 643.147 | 30031.9727 | -0.012123
230 |  | 19.9306 | 129.7399 | 4187 | 0.0015547 | 6.3599 | 6.3614 | -7.7968 | 643.2071 | 30161.7126 | -0.012122
231 |  | 19.9306 | 129.7278 | 4187 | 0.0015546 | 6.3614 | 6.363 | -7.7968 | 643.2672 | 30291.4404 | -0.012121
232 |  | 19.9306 | 129.7157 | 4187 | 0.0015544 | 6.363 | 6.3645 | -7.7968 | 643.3273 | 30421.1561 | -0.01212
233 |  | 19.9306 | 129.7035 | 4187 | 0.0015543 | 6.3645 | 6.3661 | -7.7968 | 643.3874 | 30550.8596 | -0.012118
234 |  | 19.9306 | 129.6914 | 4187 | 0.0015541 | 6.3661 | 6.3677 | -7.7968 | 643.4476 | 30680.551 | -0.012117
235 |  | 19.9306 | 129.6793 | 4187 | 0.001554 | 6.3677 | 6.3692 | -7.7968 | 643.5077 | 30810.2303 | -0.012116
236 |  | 19.9306 | 129.6672 | 4187 | 0.0015538 | 6.3692 | 6.3708 | -7.7968 | 643.5678 | 30939.8975 | -0.012115

## St219
|  |  | buis | verlies W/M | L /°C/sec
diam | wandikte |  | inhoud l/m |  | W/M
219.1 | 5.9 | 3.1416 | 33.7511 | 172.4821 | 4187
[8 empty] | J/sec/mtr | aantal mtr. | verlies
|  | buis | verlies W/M | L /°C/sec | verlies temp | begintemp | eindtemp | verlies | bij 1°C | totaal J/sec
|  | inhoud L |  | W/M | °C per M | °C | °C | per m°C | daling | aantal mtr
1 | 219.1 | 33.7511 | 172.4821 | 4187 | 0.0012205 | 6 | 6.0012 | -10.146 | 819.3086 | 172.4821 | -0.012384
2 |  | 33.7511 | 172.4697 | 4187 | 0.0012205 | 6.0012 | 6.0024 | -10.146 | 819.3674 | 344.9517 | -0.012383
3 |  | 33.7511 | 172.4573 | 4187 | 0.0012204 | 6.0024 | 6.0037 | -10.146 | 819.4263 | 517.409 | -0.012382
4 |  | 33.7511 | 172.4449 | 4187 | 0.0012203 | 6.0037 | 6.0049 | -10.146 | 819.4851 | 689.8539 | -0.012381
5 |  | 33.7511 | 172.4325 | 4187 | 0.0012202 | 6.0049 | 6.0061 | -10.146 | 819.5439 | 862.2865 | -0.01238
6 |  | 33.7511 | 172.4201 | 4187 | 0.0012201 | 6.0061 | 6.0073 | -10.146 | 819.6028 | 1034.7066 | -0.012379
7 |  | 33.7511 | 172.4078 | 4187 | 0.00122 | 6.0073 | 6.0085 | -10.146 | 819.6616 | 1207.1144 | -0.012378
8 |  | 33.7511 | 172.3954 | 4187 | 0.0012199 | 6.0085 | 6.0098 | -10.146 | 819.7205 | 1379.5098 | -0.012377
9 |  | 33.7511 | 172.383 | 4187 | 0.0012198 | 6.0098 | 6.011 | -10.146 | 819.7793 | 1551.8928 | -0.012377
10 |  | 33.7511 | 172.3706 | 4187 | 0.0012198 | 6.011 | 6.0122 | -10.146 | 819.8382 | 1724.2634 | -0.012376
11 |  | 33.7511 | 172.3583 | 4187 | 0.0012197 | 6.0122 | 6.0134 | -10.146 | 819.8971 | 1896.6217 | -0.012375
12 |  | 33.7511 | 172.3459 | 4187 | 0.0012196 | 6.0134 | 6.0146 | -10.146 | 819.9559 | 2068.9676 | -0.012374
13 |  | 33.7511 | 172.3335 | 4187 | 0.0012195 | 6.0146 | 6.0159 | -10.146 | 820.0148 | 2241.3011 | -0.012373
14 |  | 33.7511 | 172.3211 | 4187 | 0.0012194 | 6.0159 | 6.0171 | -10.146 | 820.0737 | 2413.6222 | -0.012372
15 |  | 33.7511 | 172.3088 | 4187 | 0.0012193 | 6.0171 | 6.0183 | -10.146 | 820.1326 | 2585.931 | -0.012371
16 |  | 33.7511 | 172.2964 | 4187 | 0.0012192 | 6.0183 | 6.0195 | -10.146 | 820.1915 | 2758.2274 | -0.01237
17 |  | 33.7511 | 172.284 | 4187 | 0.0012191 | 6.0195 | 6.0207 | -10.146 | 820.2504 | 2930.5114 | -0.012369
18 |  | 33.7511 | 172.2717 | 4187 | 0.0012191 | 6.0207 | 6.022 | -10.146 | 820.3093 | 3102.7831 | -0.012369
19 |  | 33.7511 | 172.2593 | 4187 | 0.001219 | 6.022 | 6.0232 | -10.146 | 820.3682 | 3275.0424 | -0.012368
20 |  | 33.7511 | 172.2469 | 4187 | 0.0012189 | 6.0232 | 6.0244 | -10.146 | 820.4271 | 3447.2893 | -0.012367
21 |  | 33.7511 | 172.2346 | 4187 | 0.0012188 | 6.0244 | 6.0256 | -10.146 | 820.486 | 3619.5239 | -0.012366
22 |  | 33.7511 | 172.2222 | 4187 | 0.0012187 | 6.0256 | 6.0268 | -10.146 | 820.5449 | 3791.7461 | -0.012365
23 |  | 33.7511 | 172.2098 | 4187 | 0.0012186 | 6.0268 | 6.0281 | -10.146 | 820.6038 | 3963.9559 | -0.012364
24 |  | 33.7511 | 172.1975 | 4187 | 0.0012185 | 6.0281 | 6.0293 | -10.146 | 820.6627 | 4136.1533 | -0.012363
25 |  | 33.7511 | 172.1851 | 4187 | 0.0012184 | 6.0293 | 6.0305 | -10.146 | 820.7216 | 4308.3384 | -0.012362
26 |  | 33.7511 | 172.1727 | 4187 | 0.0012184 | 6.0305 | 6.0317 | -10.146 | 820.7806 | 4480.5112 | -0.012361
27 |  | 33.7511 | 172.1604 | 4187 | 0.0012183 | 6.0317 | 6.0329 | -10.146 | 820.8395 | 4652.6715 | -0.012361
28 |  | 33.7511 | 172.148 | 4187 | 0.0012182 | 6.0329 | 6.0341 | -10.146 | 820.8984 | 4824.8196 | -0.01236
29 |  | 33.7511 | 172.1357 | 4187 | 0.0012181 | 6.0341 | 6.0354 | -10.146 | 820.9574 | 4996.9552 | -0.012359
30 |  | 33.7511 | 172.1233 | 4187 | 0.001218 | 6.0354 | 6.0366 | -10.146 | 821.0163 | 5169.0785 | -0.012358
31 |  | 33.7511 | 172.1109 | 4187 | 0.0012179 | 6.0366 | 6.0378 | -10.146 | 821.0753 | 5341.1894 | -0.012357
32 |  | 33.7511 | 172.0986 | 4187 | 0.0012178 | 6.0378 | 6.039 | -10.146 | 821.1342 | 5513.288 | -0.012356
33 |  | 33.7511 | 172.0862 | 4187 | 0.0012177 | 6.039 | 6.0402 | -10.146 | 821.1932 | 5685.3742 | -0.012355
34 |  | 33.7511 | 172.0739 | 4187 | 0.0012177 | 6.0402 | 6.0414 | -10.146 | 821.2522 | 5857.4481 | -0.012354
35 |  | 33.7511 | 172.0615 | 4187 | 0.0012176 | 6.0414 | 6.0427 | -10.146 | 821.3111 | 6029.5096 | -0.012353
36 |  | 33.7511 | 172.0492 | 4187 | 0.0012175 | 6.0427 | 6.0439 | -10.146 | 821.3701 | 6201.5588 | -0.012353
37 |  | 33.7511 | 172.0368 | 4187 | 0.0012174 | 6.0439 | 6.0451 | -10.146 | 821.4291 | 6373.5956 | -0.012352
38 |  | 33.7511 | 172.0245 | 4187 | 0.0012173 | 6.0451 | 6.0463 | -10.146 | 821.4881 | 6545.6201 | -0.012351
39 |  | 33.7511 | 172.0121 | 4187 | 0.0012172 | 6.0463 | 6.0475 | -10.146 | 821.547 | 6717.6322 | -0.01235
40 |  | 33.7511 | 171.9998 | 4187 | 0.0012171 | 6.0475 | 6.0488 | -10.146 | 821.606 | 6889.6319 | -0.012349
41 |  | 33.7511 | 171.9874 | 4187 | 0.001217 | 6.0488 | 6.05 | -10.146 | 821.665 | 7061.6193 | -0.012348
42 |  | 33.7511 | 171.9751 | 4187 | 0.001217 | 6.05 | 6.0512 | -10.146 | 821.724 | 7233.5944 | -0.012347
43 |  | 33.7511 | 171.9627 | 4187 | 0.0012169 | 6.0512 | 6.0524 | -10.146 | 821.783 | 7405.5571 | -0.012346
44 |  | 33.7511 | 171.9504 | 4187 | 0.0012168 | 6.0524 | 6.0536 | -10.146 | 821.842 | 7577.5075 | -0.012345
45 |  | 33.7511 | 171.938 | 4187 | 0.0012167 | 6.0536 | 6.0548 | -10.146 | 821.901 | 7749.4455 | -0.012345
46 |  | 33.7511 | 171.9257 | 4187 | 0.0012166 | 6.0548 | 6.0561 | -10.146 | 821.96 | 7921.3712 | -0.012344
47 |  | 33.7511 | 171.9133 | 4187 | 0.0012165 | 6.0561 | 6.0573 | -10.146 | 822.0191 | 8093.2845 | -0.012343
48 |  | 33.7511 | 171.901 | 4187 | 0.0012164 | 6.0573 | 6.0585 | -10.146 | 822.0781 | 8265.1855 | -0.012342
49 |  | 33.7511 | 171.8886 | 4187 | 0.0012163 | 6.0585 | 6.0597 | -10.146 | 822.1371 | 8437.0741 | -0.012341
50 |  | 33.7511 | 171.8763 | 4187 | 0.0012163 | 6.0597 | 6.0609 | -10.146 | 822.1961 | 8608.9504 | -0.01234
51 |  | 33.7511 | 171.864 | 4187 | 0.0012162 | 6.0609 | 6.0621 | -10.146 | 822.2552 | 8780.8144 | -0.012339
52 |  | 33.7511 | 171.8516 | 4187 | 0.0012161 | 6.0621 | 6.0634 | -10.146 | 822.3142 | 8952.666 | -0.012338
53 |  | 33.7511 | 171.8393 | 4187 | 0.001216 | 6.0634 | 6.0646 | -10.146 | 822.3733 | 9124.5053 | -0.012337
54 |  | 33.7511 | 171.827 | 4187 | 0.0012159 | 6.0646 | 6.0658 | -10.146 | 822.4323 | 9296.3323 | -0.012337
55 |  | 33.7511 | 171.8146 | 4187 | 0.0012158 | 6.0658 | 6.067 | -10.146 | 822.4914 | 9468.1469 | -0.012336
56 |  | 33.7511 | 171.8023 | 4187 | 0.0012157 | 6.067 | 6.0682 | -10.146 | 822.5504 | 9639.9492 | -0.012335
57 |  | 33.7511 | 171.7899 | 4187 | 0.0012156 | 6.0682 | 6.0694 | -10.146 | 822.6095 | 9811.7391 | -0.012334
58 |  | 33.7511 | 171.7776 | 4187 | 0.0012156 | 6.0694 | 6.0706 | -10.146 | 822.6685 | 9983.5167 | -0.012333
59 |  | 33.7511 | 171.7653 | 4187 | 0.0012155 | 6.0706 | 6.0719 | -10.146 | 822.7276 | 10155.282 | -0.012332
60 |  | 33.7511 | 171.7529 | 4187 | 0.0012154 | 6.0719 | 6.0731 | -10.146 | 822.7867 | 10327.0349 | -0.012331
61 |  | 33.7511 | 171.7406 | 4187 | 0.0012153 | 6.0731 | 6.0743 | -10.146 | 822.8458 | 10498.7755 | -0.01233
62 |  | 33.7511 | 171.7283 | 4187 | 0.0012152 | 6.0743 | 6.0755 | -10.146 | 822.9048 | 10670.5038 | -0.012329
63 |  | 33.7511 | 171.716 | 4187 | 0.0012151 | 6.0755 | 6.0767 | -10.146 | 822.9639 | 10842.2198 | -0.012329
64 |  | 33.7511 | 171.7036 | 4187 | 0.001215 | 6.0767 | 6.0779 | -10.146 | 823.023 | 11013.9234 | -0.012328
65 |  | 33.7511 | 171.6913 | 4187 | 0.0012149 | 6.0779 | 6.0792 | -10.146 | 823.0821 | 11185.6147 | -0.012327
66 |  | 33.7511 | 171.679 | 4187 | 0.0012149 | 6.0792 | 6.0804 | -10.146 | 823.1412 | 11357.2937 | -0.012326
67 |  | 33.7511 | 171.6666 | 4187 | 0.0012148 | 6.0804 | 6.0816 | -10.146 | 823.2003 | 11528.9603 | -0.012325
68 |  | 33.7511 | 171.6543 | 4187 | 0.0012147 | 6.0816 | 6.0828 | -10.146 | 823.2594 | 11700.6146 | -0.012324
69 |  | 33.7511 | 171.642 | 4187 | 0.0012146 | 6.0828 | 6.084 | -10.146 | 823.3185 | 11872.2566 | -0.012323
70 |  | 33.7511 | 171.6297 | 4187 | 0.0012145 | 6.084 | 6.0852 | -10.146 | 823.3776 | 12043.8863 | -0.012322
71 |  | 33.7511 | 171.6173 | 4187 | 0.0012144 | 6.0852 | 6.0864 | -10.146 | 823.4368 | 12215.5037 | -0.012322
72 |  | 33.7511 | 171.605 | 4187 | 0.0012143 | 6.0864 | 6.0877 | -10.146 | 823.4959 | 12387.1087 | -0.012321
73 |  | 33.7511 | 171.5927 | 4187 | 0.0012142 | 6.0877 | 6.0889 | -10.146 | 823.555 | 12558.7014 | -0.01232
74 |  | 33.7511 | 171.5804 | 4187 | 0.0012142 | 6.0889 | 6.0901 | -10.146 | 823.6142 | 12730.2818 | -0.012319
75 |  | 33.7511 | 171.5681 | 4187 | 0.0012141 | 6.0901 | 6.0913 | -10.146 | 823.6733 | 12901.8499 | -0.012318
76 |  | 33.7511 | 171.5558 | 4187 | 0.001214 | 6.0913 | 6.0925 | -10.146 | 823.7324 | 13073.4056 | -0.012317
77 |  | 33.7511 | 171.5434 | 4187 | 0.0012139 | 6.0925 | 6.0937 | -10.146 | 823.7916 | 13244.949 | -0.012316
78 |  | 33.7511 | 171.5311 | 4187 | 0.0012138 | 6.0937 | 6.0949 | -10.146 | 823.8507 | 13416.4802 | -0.012315
79 |  | 33.7511 | 171.5188 | 4187 | 0.0012137 | 6.0949 | 6.0962 | -10.146 | 823.9099 | 13587.999 | -0.012314
80 |  | 33.7511 | 171.5065 | 4187 | 0.0012136 | 6.0962 | 6.0974 | -10.146 | 823.969 | 13759.5054 | -0.012314
81 |  | 33.7511 | 171.4942 | 4187 | 0.0012136 | 6.0974 | 6.0986 | -10.146 | 824.0282 | 13930.9996 | -0.012313
82 |  | 33.7511 | 171.4819 | 4187 | 0.0012135 | 6.0986 | 6.0998 | -10.146 | 824.0874 | 14102.4815 | -0.012312
83 |  | 33.7511 | 171.4695 | 4187 | 0.0012134 | 6.0998 | 6.101 | -10.146 | 824.1465 | 14273.951 | -0.012311
84 |  | 33.7511 | 171.4572 | 4187 | 0.0012133 | 6.101 | 6.1022 | -10.146 | 824.2057 | 14445.4083 | -0.01231
85 |  | 33.7511 | 171.4449 | 4187 | 0.0012132 | 6.1022 | 6.1034 | -10.146 | 824.2649 | 14616.8532 | -0.012309
86 |  | 33.7511 | 171.4326 | 4187 | 0.0012131 | 6.1034 | 6.1046 | -10.146 | 824.3241 | 14788.2858 | -0.012308
87 |  | 33.7511 | 171.4203 | 4187 | 0.001213 | 6.1046 | 6.1059 | -10.146 | 824.3833 | 14959.7061 | -0.012307
88 |  | 33.7511 | 171.408 | 4187 | 0.0012129 | 6.1059 | 6.1071 | -10.146 | 824.4425 | 15131.1141 | -0.012307
89 |  | 33.7511 | 171.3957 | 4187 | 0.0012129 | 6.1071 | 6.1083 | -10.146 | 824.5017 | 15302.5098 | -0.012306
90 |  | 33.7511 | 171.3834 | 4187 | 0.0012128 | 6.1083 | 6.1095 | -10.146 | 824.5609 | 15473.8932 | -0.012305
91 |  | 33.7511 | 171.3711 | 4187 | 0.0012127 | 6.1095 | 6.1107 | -10.146 | 824.6201 | 15645.2643 | -0.012304
92 |  | 33.7511 | 171.3588 | 4187 | 0.0012126 | 6.1107 | 6.1119 | -10.146 | 824.6793 | 15816.6231 | -0.012303
93 |  | 33.7511 | 171.3465 | 4187 | 0.0012125 | 6.1119 | 6.1131 | -10.146 | 824.7385 | 15987.9696 | -0.012302
94 |  | 33.7511 | 171.3342 | 4187 | 0.0012124 | 6.1131 | 6.1143 | -10.146 | 824.7977 | 16159.3037 | -0.012301
95 |  | 33.7511 | 171.3219 | 4187 | 0.0012123 | 6.1143 | 6.1156 | -10.146 | 824.8569 | 16330.6256 | -0.0123
96 |  | 33.7511 | 171.3096 | 4187 | 0.0012122 | 6.1156 | 6.1168 | -10.146 | 824.9161 | 16501.9352 | -0.012299
97 |  | 33.7511 | 171.2973 | 4187 | 0.0012122 | 6.1168 | 6.118 | -10.146 | 824.9754 | 16673.2325 | -0.012299
98 |  | 33.7511 | 171.285 | 4187 | 0.0012121 | 6.118 | 6.1192 | -10.146 | 825.0346 | 16844.5175 | -0.012298
99 |  | 33.7511 | 171.2727 | 4187 | 0.001212 | 6.1192 | 6.1204 | -10.146 | 825.0939 | 17015.7901 | -0.012297
100 |  | 33.7511 | 171.2604 | 4187 | 0.0012119 | 6.1204 | 6.1216 | -10.146 | 825.1531 | 17187.0505 | -0.012296
101 |  | 33.7511 | 171.2481 | 4187 | 0.0012118 | 6.1216 | 6.1228 | -10.146 | 825.2123 | 17358.2986 | -0.012295
102 |  | 33.7511 | 171.2358 | 4187 | 0.0012117 | 6.1228 | 6.124 | -10.146 | 825.2716 | 17529.5344 | -0.012294
103 |  | 33.7511 | 171.2235 | 4187 | 0.0012116 | 6.124 | 6.1253 | -10.146 | 825.3308 | 17700.7579 | -0.012293
104 |  | 33.7511 | 171.2112 | 4187 | 0.0012115 | 6.1253 | 6.1265 | -10.146 | 825.3901 | 17871.9691 | -0.012292
105 |  | 33.7511 | 171.1989 | 4187 | 0.0012115 | 6.1265 | 6.1277 | -10.146 | 825.4494 | 18043.168 | -0.012291
106 |  | 33.7511 | 171.1866 | 4187 | 0.0012114 | 6.1277 | 6.1289 | -10.146 | 825.5086 | 18214.3546 | -0.012291
107 |  | 33.7511 | 171.1743 | 4187 | 0.0012113 | 6.1289 | 6.1301 | -10.146 | 825.5679 | 18385.529 | -0.01229
108 |  | 33.7511 | 171.162 | 4187 | 0.0012112 | 6.1301 | 6.1313 | -10.146 | 825.6272 | 18556.691 | -0.012289
109 |  | 33.7511 | 171.1498 | 4187 | 0.0012111 | 6.1313 | 6.1325 | -10.146 | 825.6865 | 18727.8408 | -0.012288
110 |  | 33.7511 | 171.1375 | 4187 | 0.001211 | 6.1325 | 6.1337 | -10.146 | 825.7458 | 18898.9782 | -0.012287
111 |  | 33.7511 | 171.1252 | 4187 | 0.0012109 | 6.1337 | 6.1349 | -10.146 | 825.8051 | 19070.1034 | -0.012286
112 |  | 33.7511 | 171.1129 | 4187 | 0.0012109 | 6.1349 | 6.1362 | -10.146 | 825.8643 | 19241.2163 | -0.012285
113 |  | 33.7511 | 171.1006 | 4187 | 0.0012108 | 6.1362 | 6.1374 | -10.146 | 825.9236 | 19412.3169 | -0.012284
114 |  | 33.7511 | 171.0883 | 4187 | 0.0012107 | 6.1374 | 6.1386 | -10.146 | 825.9829 | 19583.4052 | -0.012284
115 |  | 33.7511 | 171.076 | 4187 | 0.0012106 | 6.1386 | 6.1398 | -10.146 | 826.0423 | 19754.4813 | -0.012283
116 |  | 33.7511 | 171.0638 | 4187 | 0.0012105 | 6.1398 | 6.141 | -10.146 | 826.1016 | 19925.545 | -0.012282
117 |  | 33.7511 | 171.0515 | 4187 | 0.0012104 | 6.141 | 6.1422 | -10.146 | 826.1609 | 20096.5965 | -0.012281
118 |  | 33.7511 | 171.0392 | 4187 | 0.0012103 | 6.1422 | 6.1434 | -10.146 | 826.2202 | 20267.6357 | -0.01228
119 |  | 33.7511 | 171.0269 | 4187 | 0.0012102 | 6.1434 | 6.1446 | -10.146 | 826.2795 | 20438.6626 | -0.012279
120 |  | 33.7511 | 171.0146 | 4187 | 0.0012102 | 6.1446 | 6.1458 | -10.146 | 826.3389 | 20609.6772 | -0.012278
121 |  | 33.7511 | 171.0024 | 4187 | 0.0012101 | 6.1458 | 6.1471 | -10.146 | 826.3982 | 20780.6796 | -0.012277
122 |  | 33.7511 | 170.9901 | 4187 | 0.00121 | 6.1471 | 6.1483 | -10.146 | 826.4575 | 20951.6697 | -0.012276
123 |  | 33.7511 | 170.9778 | 4187 | 0.0012099 | 6.1483 | 6.1495 | -10.146 | 826.5169 | 21122.6475 | -0.012276
124 |  | 33.7511 | 170.9655 | 4187 | 0.0012098 | 6.1495 | 6.1507 | -10.146 | 826.5762 | 21293.613 | -0.012275
125 |  | 33.7511 | 170.9533 | 4187 | 0.0012097 | 6.1507 | 6.1519 | -10.146 | 826.6356 | 21464.5662 | -0.012274
126 |  | 33.7511 | 170.941 | 4187 | 0.0012096 | 6.1519 | 6.1531 | -10.146 | 826.6949 | 21635.5072 | -0.012273
127 |  | 33.7511 | 170.9287 | 4187 | 0.0012095 | 6.1531 | 6.1543 | -10.146 | 826.7543 | 21806.4359 | -0.012272
128 |  | 33.7511 | 170.9164 | 4187 | 0.0012095 | 6.1543 | 6.1555 | -10.146 | 826.8136 | 21977.3524 | -0.012271
129 |  | 33.7511 | 170.9042 | 4187 | 0.0012094 | 6.1555 | 6.1567 | -10.146 | 826.873 | 22148.2565 | -0.01227
130 |  | 33.7511 | 170.8919 | 4187 | 0.0012093 | 6.1567 | 6.1579 | -10.146 | 826.9324 | 22319.1484 | -0.012269
131 |  | 33.7511 | 170.8796 | 4187 | 0.0012092 | 6.1579 | 6.1591 | -10.146 | 826.9917 | 22490.028 | -0.012269
132 |  | 33.7511 | 170.8674 | 4187 | 0.0012091 | 6.1591 | 6.1604 | -10.146 | 827.0511 | 22660.8954 | -0.012268
133 |  | 33.7511 | 170.8551 | 4187 | 0.001209 | 6.1604 | 6.1616 | -10.146 | 827.1105 | 22831.7505 | -0.012267
134 |  | 33.7511 | 170.8428 | 4187 | 0.0012089 | 6.1616 | 6.1628 | -10.146 | 827.1699 | 23002.5933 | -0.012266
135 |  | 33.7511 | 170.8306 | 4187 | 0.0012089 | 6.1628 | 6.164 | -10.146 | 827.2293 | 23173.4238 | -0.012265
136 |  | 33.7511 | 170.8183 | 4187 | 0.0012088 | 6.164 | 6.1652 | -10.146 | 827.2887 | 23344.2421 | -0.012264
137 |  | 33.7511 | 170.806 | 4187 | 0.0012087 | 6.1652 | 6.1664 | -10.146 | 827.3481 | 23515.0482 | -0.012263
138 |  | 33.7511 | 170.7938 | 4187 | 0.0012086 | 6.1664 | 6.1676 | -10.146 | 827.4075 | 23685.8419 | -0.012262
139 |  | 33.7511 | 170.7815 | 4187 | 0.0012085 | 6.1676 | 6.1688 | -10.146 | 827.4669 | 23856.6234 | -0.012262
140 |  | 33.7511 | 170.7692 | 4187 | 0.0012084 | 6.1688 | 6.17 | -10.146 | 827.5263 | 24027.3926 | -0.012261
141 |  | 33.7511 | 170.757 | 4187 | 0.0012083 | 6.17 | 6.1712 | -10.146 | 827.5857 | 24198.1496 | -0.01226
142 |  | 33.7511 | 170.7447 | 4187 | 0.0012082 | 6.1712 | 6.1724 | -10.146 | 827.6452 | 24368.8943 | -0.012259
143 |  | 33.7511 | 170.7325 | 4187 | 0.0012082 | 6.1724 | 6.1737 | -10.146 | 827.7046 | 24539.6268 | -0.012258
144 |  | 33.7511 | 170.7202 | 4187 | 0.0012081 | 6.1737 | 6.1749 | -10.146 | 827.764 | 24710.347 | -0.012257
145 |  | 33.7511 | 170.7079 | 4187 | 0.001208 | 6.1749 | 6.1761 | -10.146 | 827.8234 | 24881.0549 | -0.012256
146 |  | 33.7511 | 170.6957 | 4187 | 0.0012079 | 6.1761 | 6.1773 | -10.146 | 827.8829 | 25051.7506 | -0.012255
147 |  | 33.7511 | 170.6834 | 4187 | 0.0012078 | 6.1773 | 6.1785 | -10.146 | 827.9423 | 25222.434 | -0.012254
148 |  | 33.7511 | 170.6712 | 4187 | 0.0012077 | 6.1785 | 6.1797 | -10.146 | 828.0018 | 25393.1052 | -0.012254
149 |  | 33.7511 | 170.6589 | 4187 | 0.0012076 | 6.1797 | 6.1809 | -10.146 | 828.0612 | 25563.7641 | -0.012253
150 |  | 33.7511 | 170.6467 | 4187 | 0.0012076 | 6.1809 | 6.1821 | -10.146 | 828.1207 | 25734.4108 | -0.012252
151 |  | 33.7511 | 170.6344 | 4187 | 0.0012075 | 6.1821 | 6.1833 | -10.146 | 828.1801 | 25905.0452 | -0.012251
152 |  | 33.7511 | 170.6222 | 4187 | 0.0012074 | 6.1833 | 6.1845 | -10.146 | 828.2396 | 26075.6674 | -0.01225
153 |  | 33.7511 | 170.6099 | 4187 | 0.0012073 | 6.1845 | 6.1857 | -10.146 | 828.2991 | 26246.2773 | -0.012249
154 |  | 33.7511 | 170.5977 | 4187 | 0.0012072 | 6.1857 | 6.1869 | -10.146 | 828.3585 | 26416.875 | -0.012248
155 |  | 33.7511 | 170.5854 | 4187 | 0.0012071 | 6.1869 | 6.1881 | -10.146 | 828.418 | 26587.4604 | -0.012247
156 |  | 33.7511 | 170.5732 | 4187 | 0.001207 | 6.1881 | 6.1893 | -10.146 | 828.4775 | 26758.0336 | -0.012247
157 |  | 33.7511 | 170.5609 | 4187 | 0.0012069 | 6.1893 | 6.1906 | -10.146 | 828.537 | 26928.5945 | -0.012246
158 |  | 33.7511 | 170.5487 | 4187 | 0.0012069 | 6.1906 | 6.1918 | -10.146 | 828.5965 | 27099.1432 | -0.012245
159 |  | 33.7511 | 170.5364 | 4187 | 0.0012068 | 6.1918 | 6.193 | -10.146 | 828.656 | 27269.6796 | -0.012244
160 |  | 33.7511 | 170.5242 | 4187 | 0.0012067 | 6.193 | 6.1942 | -10.146 | 828.7155 | 27440.2038 | -0.012243
161 |  | 33.7511 | 170.5119 | 4187 | 0.0012066 | 6.1942 | 6.1954 | -10.146 | 828.775 | 27610.7157 | -0.012242
162 |  | 33.7511 | 170.4997 | 4187 | 0.0012065 | 6.1954 | 6.1966 | -10.146 | 828.8345 | 27781.2155 | -0.012241
163 |  | 33.7511 | 170.4875 | 4187 | 0.0012064 | 6.1966 | 6.1978 | -10.146 | 828.894 | 27951.7029 | -0.01224
164 |  | 33.7511 | 170.4752 | 4187 | 0.0012063 | 6.1978 | 6.199 | -10.146 | 828.9535 | 28122.1781 | -0.01224
165 |  | 33.7511 | 170.463 | 4187 | 0.0012063 | 6.199 | 6.2002 | -10.146 | 829.013 | 28292.6411 | -0.012239
166 |  | 33.7511 | 170.4507 | 4187 | 0.0012062 | 6.2002 | 6.2014 | -10.146 | 829.0726 | 28463.0919 | -0.012238
167 |  | 33.7511 | 170.4385 | 4187 | 0.0012061 | 6.2014 | 6.2026 | -10.146 | 829.1321 | 28633.5304 | -0.012237
168 |  | 33.7511 | 170.4263 | 4187 | 0.001206 | 6.2026 | 6.2038 | -10.146 | 829.1916 | 28803.9566 | -0.012236
169 |  | 33.7511 | 170.414 | 4187 | 0.0012059 | 6.2038 | 6.205 | -10.146 | 829.2512 | 28974.3707 | -0.012235
170 |  | 33.7511 | 170.4018 | 4187 | 0.0012058 | 6.205 | 6.2062 | -10.146 | 829.3107 | 29144.7725 | -0.012234
171 |  | 33.7511 | 170.3896 | 4187 | 0.0012057 | 6.2062 | 6.2074 | -10.146 | 829.3702 | 29315.162 | -0.012233
172 |  | 33.7511 | 170.3773 | 4187 | 0.0012056 | 6.2074 | 6.2086 | -10.146 | 829.4298 | 29485.5394 | -0.012233
173 |  | 33.7511 | 170.3651 | 4187 | 0.0012056 | 6.2086 | 6.2099 | -10.146 | 829.4894 | 29655.9045 | -0.012232
174 |  | 33.7511 | 170.3529 | 4187 | 0.0012055 | 6.2099 | 6.2111 | -10.146 | 829.5489 | 29826.2573 | -0.012231
175 |  | 33.7511 | 170.3406 | 4187 | 0.0012054 | 6.2111 | 6.2123 | -10.146 | 829.6085 | 29996.598 | -0.01223
176 |  | 33.7511 | 170.3284 | 4187 | 0.0012053 | 6.2123 | 6.2135 | -10.146 | 829.668 | 30166.9264 | -0.012229
177 |  | 33.7511 | 170.3162 | 4187 | 0.0012052 | 6.2135 | 6.2147 | -10.146 | 829.7276 | 30337.2426 | -0.012228
178 |  | 33.7511 | 170.3039 | 4187 | 0.0012051 | 6.2147 | 6.2159 | -10.146 | 829.7872 | 30507.5465 | -0.012227
179 |  | 33.7511 | 170.2917 | 4187 | 0.001205 | 6.2159 | 6.2171 | -10.146 | 829.8468 | 30677.8382 | -0.012226
180 |  | 33.7511 | 170.2795 | 4187 | 0.001205 | 6.2171 | 6.2183 | -10.146 | 829.9064 | 30848.1177 | -0.012225
181 |  | 33.7511 | 170.2673 | 4187 | 0.0012049 | 6.2183 | 6.2195 | -10.146 | 829.9659 | 31018.385 | -0.012225
182 |  | 33.7511 | 170.255 | 4187 | 0.0012048 | 6.2195 | 6.2207 | -10.146 | 830.0255 | 31188.64 | -0.012224
183 |  | 33.7511 | 170.2428 | 4187 | 0.0012047 | 6.2207 | 6.2219 | -10.146 | 830.0851 | 31358.8829 | -0.012223
184 |  | 33.7511 | 170.2306 | 4187 | 0.0012046 | 6.2219 | 6.2231 | -10.146 | 830.1447 | 31529.1135 | -0.012222
185 |  | 33.7511 | 170.2184 | 4187 | 0.0012045 | 6.2231 | 6.2243 | -10.146 | 830.2043 | 31699.3318 | -0.012221
186 |  | 33.7511 | 170.2062 | 4187 | 0.0012044 | 6.2243 | 6.2255 | -10.146 | 830.264 | 31869.538 | -0.01222
187 |  | 33.7511 | 170.1939 | 4187 | 0.0012043 | 6.2255 | 6.2267 | -10.146 | 830.3236 | 32039.7319 | -0.012219
188 |  | 33.7511 | 170.1817 | 4187 | 0.0012043 | 6.2267 | 6.2279 | -10.146 | 830.3832 | 32209.9137 | -0.012218
189 |  | 33.7511 | 170.1695 | 4187 | 0.0012042 | 6.2279 | 6.2291 | -10.146 | 830.4428 | 32380.0832 | -0.012218
190 |  | 33.7511 | 170.1573 | 4187 | 0.0012041 | 6.2291 | 6.2303 | -10.146 | 830.5024 | 32550.2404 | -0.012217
191 |  | 33.7511 | 170.1451 | 4187 | 0.001204 | 6.2303 | 6.2315 | -10.146 | 830.5621 | 32720.3855 | -0.012216
192 |  | 33.7511 | 170.1328 | 4187 | 0.0012039 | 6.2315 | 6.2327 | -10.146 | 830.6217 | 32890.5183 | -0.012215
193 |  | 33.7511 | 170.1206 | 4187 | 0.0012038 | 6.2327 | 6.2339 | -10.146 | 830.6813 | 33060.639 | -0.012214
194 |  | 33.7511 | 170.1084 | 4187 | 0.0012037 | 6.2339 | 6.2352 | -10.146 | 830.741 | 33230.7474 | -0.012213
195 |  | 33.7511 | 170.0962 | 4187 | 0.0012037 | 6.2352 | 6.2364 | -10.146 | 830.8006 | 33400.8436 | -0.012212
196 |  | 33.7511 | 170.084 | 4187 | 0.0012036 | 6.2364 | 6.2376 | -10.146 | 830.8603 | 33570.9276 | -0.012211
197 |  | 33.7511 | 170.0718 | 4187 | 0.0012035 | 6.2376 | 6.2388 | -10.146 | 830.9199 | 33740.9994 | -0.012211
198 |  | 33.7511 | 170.0596 | 4187 | 0.0012034 | 6.2388 | 6.24 | -10.146 | 830.9796 | 33911.059 | -0.01221
199 |  | 33.7511 | 170.0474 | 4187 | 0.0012033 | 6.24 | 6.2412 | -10.146 | 831.0393 | 34081.1063 | -0.012209
200 |  | 33.7511 | 170.0352 | 4187 | 0.0012032 | 6.2412 | 6.2424 | -10.146 | 831.0989 | 34251.1415 | -0.012208
201 |  | 33.7511 | 170.0229 | 4187 | 0.0012031 | 6.2424 | 6.2436 | -10.146 | 831.1586 | 34421.1644 | -0.012207
202 |  | 33.7511 | 170.0107 | 4187 | 0.0012031 | 6.2436 | 6.2448 | -10.146 | 831.2183 | 34591.1752 | -0.012206
203 |  | 33.7511 | 169.9985 | 4187 | 0.001203 | 6.2448 | 6.246 | -10.146 | 831.278 | 34761.1737 | -0.012205
204 |  | 33.7511 | 169.9863 | 4187 | 0.0012029 | 6.246 | 6.2472 | -10.146 | 831.3377 | 34931.16 | -0.012204
205 |  | 33.7511 | 169.9741 | 4187 | 0.0012028 | 6.2472 | 6.2484 | -10.146 | 831.3974 | 35101.1341 | -0.012204
206 |  | 33.7511 | 169.9619 | 4187 | 0.0012027 | 6.2484 | 6.2496 | -10.146 | 831.4571 | 35271.0961 | -0.012203
207 |  | 33.7511 | 169.9497 | 4187 | 0.0012026 | 6.2496 | 6.2508 | -10.146 | 831.5168 | 35441.0458 | -0.012202
208 |  | 33.7511 | 169.9375 | 4187 | 0.0012025 | 6.2508 | 6.252 | -10.146 | 831.5765 | 35610.9833 | -0.012201
209 |  | 33.7511 | 169.9253 | 4187 | 0.0012024 | 6.252 | 6.2532 | -10.146 | 831.6362 | 35780.9086 | -0.0122
210 |  | 33.7511 | 169.9131 | 4187 | 0.0012024 | 6.2532 | 6.2544 | -10.146 | 831.6959 | 35950.8217 | -0.012199
211 |  | 33.7511 | 169.9009 | 4187 | 0.0012023 | 6.2544 | 6.2556 | -10.146 | 831.7556 | 36120.7226 | -0.012198
212 |  | 33.7511 | 169.8887 | 4187 | 0.0012022 | 6.2556 | 6.2568 | -10.146 | 831.8153 | 36290.6113 | -0.012197
213 |  | 33.7511 | 169.8765 | 4187 | 0.0012021 | 6.2568 | 6.258 | -10.146 | 831.875 | 36460.4879 | -0.012197
214 |  | 33.7511 | 169.8643 | 4187 | 0.001202 | 6.258 | 6.2592 | -10.146 | 831.9348 | 36630.3522 | -0.012196
215 |  | 33.7511 | 169.8521 | 4187 | 0.0012019 | 6.2592 | 6.2604 | -10.146 | 831.9945 | 36800.2043 | -0.012195
216 |  | 33.7511 | 169.8399 | 4187 | 0.0012018 | 6.2604 | 6.2616 | -10.146 | 832.0542 | 36970.0442 | -0.012194
217 |  | 33.7511 | 169.8277 | 4187 | 0.0012018 | 6.2616 | 6.2628 | -10.146 | 832.114 | 37139.872 | -0.012193
218 |  | 33.7511 | 169.8155 | 4187 | 0.0012017 | 6.2628 | 6.264 | -10.146 | 832.1737 | 37309.6875 | -0.012192
219 |  | 33.7511 | 169.8034 | 4187 | 0.0012016 | 6.264 | 6.2652 | -10.146 | 832.2335 | 37479.4909 | -0.012191
220 |  | 33.7511 | 169.7912 | 4187 | 0.0012015 | 6.2652 | 6.2664 | -10.146 | 832.2932 | 37649.282 | -0.01219
221 |  | 33.7511 | 169.779 | 4187 | 0.0012014 | 6.2664 | 6.2676 | -10.146 | 832.353 | 37819.061 | -0.01219
222 |  | 33.7511 | 169.7668 | 4187 | 0.0012013 | 6.2676 | 6.2688 | -10.146 | 832.4128 | 37988.8278 | -0.012189
223 |  | 33.7511 | 169.7546 | 4187 | 0.0012012 | 6.2688 | 6.27 | -10.146 | 832.4725 | 38158.5824 | -0.012188
224 |  | 33.7511 | 169.7424 | 4187 | 0.0012012 | 6.27 | 6.2712 | -10.146 | 832.5323 | 38328.3248 | -0.012187
225 |  | 33.7511 | 169.7302 | 4187 | 0.0012011 | 6.2712 | 6.2724 | -10.146 | 832.5921 | 38498.055 | -0.012186
226 |  | 33.7511 | 169.718 | 4187 | 0.001201 | 6.2724 | 6.2736 | -10.146 | 832.6519 | 38667.773 | -0.012185
227 |  | 33.7511 | 169.7058 | 4187 | 0.0012009 | 6.2736 | 6.2748 | -10.146 | 832.7117 | 38837.4789 | -0.012184
228 |  | 33.7511 | 169.6937 | 4187 | 0.0012008 | 6.2748 | 6.276 | -10.146 | 832.7714 | 39007.1725 | -0.012183
229 |  | 33.7511 | 169.6815 | 4187 | 0.0012007 | 6.276 | 6.2772 | -10.146 | 832.8312 | 39176.854 | -0.012183
230 |  | 33.7511 | 169.6693 | 4187 | 0.0012006 | 6.2772 | 6.2784 | -10.146 | 832.891 | 39346.5233 | -0.012182
231 |  | 33.7511 | 169.6571 | 4187 | 0.0012006 | 6.2784 | 6.2796 | -10.146 | 832.9508 | 39516.1804 | -0.012181
232 |  | 33.7511 | 169.6449 | 4187 | 0.0012005 | 6.2796 | 6.2808 | -10.146 | 833.0106 | 39685.8254 | -0.01218
233 |  | 33.7511 | 169.6328 | 4187 | 0.0012004 | 6.2808 | 6.282 | -10.146 | 833.0705 | 39855.4581 | -0.012179
234 |  | 33.7511 | 169.6206 | 4187 | 0.0012003 | 6.282 | 6.2832 | -10.146 | 833.1303 | 40025.0787 | -0.012178
235 |  | 33.7511 | 169.6084 | 4187 | 0.0012002 | 6.2832 | 6.2844 | -10.146 | 833.1901 | 40194.6871 | -0.012177
236 |  | 33.7511 | 169.5962 | 4187 | 0.0012001 | 6.2844 | 6.2856 | -10.146 | 833.2499 | 40364.2833 | -0.012176

## St273
|  |  | buis | verlies W/M | L /°C/sec
diam | wandikte |  | inhoud l/m |  | W/M
273 | 6.3 | 3.1416 | 53.2564 | 214.9196 | 4187
[8 empty] | J/sec/mtr | aantal mtr. | verlies
|  | buis | verlies W/M | L /°C/sec | verlies temp | begintemp | eindtemp | verlies | bij 1°C | totaal J/sec
|  | inhoud L |  | W/M | °C per M | °C | °C | per m°C | daling | aantal mtr
1 | 273 | 53.2564 | 214.9196 | 4187 | 0.00096383 | 6 | 6.001 | -12.6423 | 1037.5255 | 214.9196 | -0.012185
2 |  | 53.2564 | 214.9074 | 4187 | 0.00096378 | 6.001 | 6.0019 | -12.6423 | 1037.5843 | 429.827 | -0.012184
3 |  | 53.2564 | 214.8952 | 4187 | 0.00096372 | 6.0019 | 6.0029 | -12.6423 | 1037.6432 | 644.7222 | -0.012184
4 |  | 53.2564 | 214.883 | 4187 | 0.00096367 | 6.0029 | 6.0039 | -12.6423 | 1037.702 | 859.6053 | -0.012183
5 |  | 53.2564 | 214.8709 | 4187 | 0.00096361 | 6.0039 | 6.0048 | -12.6423 | 1037.7608 | 1074.4761 | -0.012182
6 |  | 53.2564 | 214.8587 | 4187 | 0.00096356 | 6.0048 | 6.0058 | -12.6423 | 1037.8197 | 1289.3348 | -0.012182
7 |  | 53.2564 | 214.8465 | 4187 | 0.0009635 | 6.0058 | 6.0067 | -12.6423 | 1037.8785 | 1504.1813 | -0.012181
8 |  | 53.2564 | 214.8343 | 4187 | 0.00096345 | 6.0067 | 6.0077 | -12.6423 | 1037.9374 | 1719.0156 | -0.01218
9 |  | 53.2564 | 214.8221 | 4187 | 0.00096339 | 6.0077 | 6.0087 | -12.6423 | 1037.9962 | 1933.8378 | -0.01218
10 |  | 53.2564 | 214.81 | 4187 | 0.00096334 | 6.0087 | 6.0096 | -12.6423 | 1038.0551 | 2148.6477 | -0.012179
11 |  | 53.2564 | 214.7978 | 4187 | 0.00096329 | 6.0096 | 6.0106 | -12.6423 | 1038.1139 | 2363.4455 | -0.012178
12 |  | 53.2564 | 214.7856 | 4187 | 0.00096323 | 6.0106 | 6.0116 | -12.6423 | 1038.1728 | 2578.2311 | -0.012177
13 |  | 53.2564 | 214.7734 | 4187 | 0.00096318 | 6.0116 | 6.0125 | -12.6423 | 1038.2316 | 2793.0045 | -0.012177
14 |  | 53.2564 | 214.7612 | 4187 | 0.00096312 | 6.0125 | 6.0135 | -12.6423 | 1038.2905 | 3007.7658 | -0.012176
15 |  | 53.2564 | 214.7491 | 4187 | 0.00096307 | 6.0135 | 6.0145 | -12.6423 | 1038.3494 | 3222.5149 | -0.012175
16 |  | 53.2564 | 214.7369 | 4187 | 0.00096301 | 6.0145 | 6.0154 | -12.6423 | 1038.4083 | 3437.2518 | -0.012175
17 |  | 53.2564 | 214.7247 | 4187 | 0.00096296 | 6.0154 | 6.0164 | -12.6423 | 1038.4671 | 3651.9765 | -0.012174
18 |  | 53.2564 | 214.7125 | 4187 | 0.0009629 | 6.0164 | 6.0173 | -12.6423 | 1038.526 | 3866.689 | -0.012173
19 |  | 53.2564 | 214.7004 | 4187 | 0.00096285 | 6.0173 | 6.0183 | -12.6423 | 1038.5849 | 4081.3894 | -0.012173
20 |  | 53.2564 | 214.6882 | 4187 | 0.00096279 | 6.0183 | 6.0193 | -12.6423 | 1038.6438 | 4296.0776 | -0.012172
21 |  | 53.2564 | 214.676 | 4187 | 0.00096274 | 6.0193 | 6.0202 | -12.6423 | 1038.7027 | 4510.7536 | -0.012171
22 |  | 53.2564 | 214.6639 | 4187 | 0.00096268 | 6.0202 | 6.0212 | -12.6423 | 1038.7616 | 4725.4175 | -0.012171
23 |  | 53.2564 | 214.6517 | 4187 | 0.00096263 | 6.0212 | 6.0222 | -12.6423 | 1038.8205 | 4940.0692 | -0.01217
24 |  | 53.2564 | 214.6395 | 4187 | 0.00096258 | 6.0222 | 6.0231 | -12.6423 | 1038.8794 | 5154.7087 | -0.012169
25 |  | 53.2564 | 214.6273 | 4187 | 0.00096252 | 6.0231 | 6.0241 | -12.6423 | 1038.9383 | 5369.336 | -0.012169
26 |  | 53.2564 | 214.6152 | 4187 | 0.00096247 | 6.0241 | 6.025 | -12.6423 | 1038.9972 | 5583.9512 | -0.012168
27 |  | 53.2564 | 214.603 | 4187 | 0.00096241 | 6.025 | 6.026 | -12.6423 | 1039.0561 | 5798.5542 | -0.012167
28 |  | 53.2564 | 214.5908 | 4187 | 0.00096236 | 6.026 | 6.027 | -12.6423 | 1039.115 | 6013.1451 | -0.012166
29 |  | 53.2564 | 214.5787 | 4187 | 0.0009623 | 6.027 | 6.0279 | -12.6423 | 1039.1739 | 6227.7237 | -0.012166
30 |  | 53.2564 | 214.5665 | 4187 | 0.00096225 | 6.0279 | 6.0289 | -12.6423 | 1039.2328 | 6442.2902 | -0.012165
31 |  | 53.2564 | 214.5543 | 4187 | 0.00096219 | 6.0289 | 6.0299 | -12.6423 | 1039.2918 | 6656.8446 | -0.012164
32 |  | 53.2564 | 214.5422 | 4187 | 0.00096214 | 6.0299 | 6.0308 | -12.6423 | 1039.3507 | 6871.3868 | -0.012164
33 |  | 53.2564 | 214.53 | 4187 | 0.00096208 | 6.0308 | 6.0318 | -12.6423 | 1039.4096 | 7085.9168 | -0.012163
34 |  | 53.2564 | 214.5179 | 4187 | 0.00096203 | 6.0318 | 6.0327 | -12.6423 | 1039.4686 | 7300.4347 | -0.012162
35 |  | 53.2564 | 214.5057 | 4187 | 0.00096198 | 6.0327 | 6.0337 | -12.6423 | 1039.5275 | 7514.9403 | -0.012162
36 |  | 53.2564 | 214.4935 | 4187 | 0.00096192 | 6.0337 | 6.0347 | -12.6423 | 1039.5864 | 7729.4339 | -0.012161
37 |  | 53.2564 | 214.4814 | 4187 | 0.00096187 | 6.0347 | 6.0356 | -12.6423 | 1039.6454 | 7943.9152 | -0.01216
38 |  | 53.2564 | 214.4692 | 4187 | 0.00096181 | 6.0356 | 6.0366 | -12.6423 | 1039.7043 | 8158.3845 | -0.01216
39 |  | 53.2564 | 214.4571 | 4187 | 0.00096176 | 6.0366 | 6.0375 | -12.6423 | 1039.7633 | 8372.8415 | -0.012159
40 |  | 53.2564 | 214.4449 | 4187 | 0.0009617 | 6.0375 | 6.0385 | -12.6423 | 1039.8222 | 8587.2864 | -0.012158
41 |  | 53.2564 | 214.4327 | 4187 | 0.00096165 | 6.0385 | 6.0395 | -12.6423 | 1039.8812 | 8801.7191 | -0.012157
42 |  | 53.2564 | 214.4206 | 4187 | 0.00096159 | 6.0395 | 6.0404 | -12.6423 | 1039.9401 | 9016.1397 | -0.012157
43 |  | 53.2564 | 214.4084 | 4187 | 0.00096154 | 6.0404 | 6.0414 | -12.6423 | 1039.9991 | 9230.5481 | -0.012156
44 |  | 53.2564 | 214.3963 | 4187 | 0.00096148 | 6.0414 | 6.0424 | -12.6423 | 1040.0581 | 9444.9444 | -0.012155
45 |  | 53.2564 | 214.3841 | 4187 | 0.00096143 | 6.0424 | 6.0433 | -12.6423 | 1040.117 | 9659.3285 | -0.012155
46 |  | 53.2564 | 214.372 | 4187 | 0.00096138 | 6.0433 | 6.0443 | -12.6423 | 1040.176 | 9873.7005 | -0.012154
47 |  | 53.2564 | 214.3598 | 4187 | 0.00096132 | 6.0443 | 6.0452 | -12.6423 | 1040.235 | 10088.0603 | -0.012153
48 |  | 53.2564 | 214.3476 | 4187 | 0.00096127 | 6.0452 | 6.0462 | -12.6423 | 1040.294 | 10302.4079 | -0.012153
49 |  | 53.2564 | 214.3355 | 4187 | 0.00096121 | 6.0462 | 6.0472 | -12.6423 | 1040.353 | 10516.7434 | -0.012152
50 |  | 53.2564 | 214.3233 | 4187 | 0.00096116 | 6.0472 | 6.0481 | -12.6423 | 1040.4119 | 10731.0667 | -0.012151
51 |  | 53.2564 | 214.3112 | 4187 | 0.0009611 | 6.0481 | 6.0491 | -12.6423 | 1040.4709 | 10945.3779 | -0.012151
52 |  | 53.2564 | 214.299 | 4187 | 0.00096105 | 6.0491 | 6.05 | -12.6423 | 1040.5299 | 11159.677 | -0.01215
53 |  | 53.2564 | 214.2869 | 4187 | 0.00096099 | 6.05 | 6.051 | -12.6423 | 1040.5889 | 11373.9639 | -0.012149
54 |  | 53.2564 | 214.2747 | 4187 | 0.00096094 | 6.051 | 6.052 | -12.6423 | 1040.6479 | 11588.2386 | -0.012149
55 |  | 53.2564 | 214.2626 | 4187 | 0.00096089 | 6.052 | 6.0529 | -12.6423 | 1040.7069 | 11802.5012 | -0.012148
56 |  | 53.2564 | 214.2504 | 4187 | 0.00096083 | 6.0529 | 6.0539 | -12.6423 | 1040.7659 | 12016.7516 | -0.012147
57 |  | 53.2564 | 214.2383 | 4187 | 0.00096078 | 6.0539 | 6.0549 | -12.6423 | 1040.825 | 12230.9899 | -0.012146
58 |  | 53.2564 | 214.2262 | 4187 | 0.00096072 | 6.0549 | 6.0558 | -12.6423 | 1040.884 | 12445.2161 | -0.012146
59 |  | 53.2564 | 214.214 | 4187 | 0.00096067 | 6.0558 | 6.0568 | -12.6423 | 1040.943 | 12659.4301 | -0.012145
60 |  | 53.2564 | 214.2019 | 4187 | 0.00096061 | 6.0568 | 6.0577 | -12.6423 | 1041.002 | 12873.6319 | -0.012144
61 |  | 53.2564 | 214.1897 | 4187 | 0.00096056 | 6.0577 | 6.0587 | -12.6423 | 1041.061 | 13087.8217 | -0.012144
62 |  | 53.2564 | 214.1776 | 4187 | 0.0009605 | 6.0587 | 6.0597 | -12.6423 | 1041.1201 | 13301.9992 | -0.012143
63 |  | 53.2564 | 214.1654 | 4187 | 0.00096045 | 6.0597 | 6.0606 | -12.6423 | 1041.1791 | 13516.1647 | -0.012142
64 |  | 53.2564 | 214.1533 | 4187 | 0.0009604 | 6.0606 | 6.0616 | -12.6423 | 1041.2381 | 13730.3179 | -0.012142
65 |  | 53.2564 | 214.1411 | 4187 | 0.00096034 | 6.0616 | 6.0625 | -12.6423 | 1041.2972 | 13944.4591 | -0.012141
66 |  | 53.2564 | 214.129 | 4187 | 0.00096029 | 6.0625 | 6.0635 | -12.6423 | 1041.3562 | 14158.5881 | -0.01214
67 |  | 53.2564 | 214.1169 | 4187 | 0.00096023 | 6.0635 | 6.0645 | -12.6423 | 1041.4152 | 14372.705 | -0.01214
68 |  | 53.2564 | 214.1047 | 4187 | 0.00096018 | 6.0645 | 6.0654 | -12.6423 | 1041.4743 | 14586.8097 | -0.012139
69 |  | 53.2564 | 214.0926 | 4187 | 0.00096012 | 6.0654 | 6.0664 | -12.6423 | 1041.5333 | 14800.9023 | -0.012138
70 |  | 53.2564 | 214.0804 | 4187 | 0.00096007 | 6.0664 | 6.0673 | -12.6423 | 1041.5924 | 15014.9827 | -0.012138
71 |  | 53.2564 | 214.0683 | 4187 | 0.00096001 | 6.0673 | 6.0683 | -12.6423 | 1041.6515 | 15229.051 | -0.012137
72 |  | 53.2564 | 214.0562 | 4187 | 0.00095996 | 6.0683 | 6.0693 | -12.6423 | 1041.7105 | 15443.1072 | -0.012136
73 |  | 53.2564 | 214.044 | 4187 | 0.00095991 | 6.0693 | 6.0702 | -12.6423 | 1041.7696 | 15657.1512 | -0.012135
74 |  | 53.2564 | 214.0319 | 4187 | 0.00095985 | 6.0702 | 6.0712 | -12.6423 | 1041.8286 | 15871.1831 | -0.012135
75 |  | 53.2564 | 214.0198 | 4187 | 0.0009598 | 6.0712 | 6.0721 | -12.6423 | 1041.8877 | 16085.2029 | -0.012134
76 |  | 53.2564 | 214.0076 | 4187 | 0.00095974 | 6.0721 | 6.0731 | -12.6423 | 1041.9468 | 16299.2105 | -0.012133
77 |  | 53.2564 | 213.9955 | 4187 | 0.00095969 | 6.0731 | 6.0741 | -12.6423 | 1042.0059 | 16513.206 | -0.012133
78 |  | 53.2564 | 213.9834 | 4187 | 0.00095963 | 6.0741 | 6.075 | -12.6423 | 1042.0649 | 16727.1894 | -0.012132
79 |  | 53.2564 | 213.9712 | 4187 | 0.00095958 | 6.075 | 6.076 | -12.6423 | 1042.124 | 16941.1606 | -0.012131
80 |  | 53.2564 | 213.9591 | 4187 | 0.00095952 | 6.076 | 6.0769 | -12.6423 | 1042.1831 | 17155.1197 | -0.012131
81 |  | 53.2564 | 213.947 | 4187 | 0.00095947 | 6.0769 | 6.0779 | -12.6423 | 1042.2422 | 17369.0667 | -0.01213
82 |  | 53.2564 | 213.9348 | 4187 | 0.00095942 | 6.0779 | 6.0789 | -12.6423 | 1042.3013 | 17583.0015 | -0.012129
83 |  | 53.2564 | 213.9227 | 4187 | 0.00095936 | 6.0789 | 6.0798 | -12.6423 | 1042.3604 | 17796.9243 | -0.012129
84 |  | 53.2564 | 213.9106 | 4187 | 0.00095931 | 6.0798 | 6.0808 | -12.6423 | 1042.4195 | 18010.8348 | -0.012128
85 |  | 53.2564 | 213.8985 | 4187 | 0.00095925 | 6.0808 | 6.0817 | -12.6423 | 1042.4786 | 18224.7333 | -0.012127
86 |  | 53.2564 | 213.8863 | 4187 | 0.0009592 | 6.0817 | 6.0827 | -12.6423 | 1042.5377 | 18438.6196 | -0.012126
87 |  | 53.2564 | 213.8742 | 4187 | 0.00095914 | 6.0827 | 6.0836 | -12.6423 | 1042.5968 | 18652.4938 | -0.012126
88 |  | 53.2564 | 213.8621 | 4187 | 0.00095909 | 6.0836 | 6.0846 | -12.6423 | 1042.6559 | 18866.3559 | -0.012125
89 |  | 53.2564 | 213.85 | 4187 | 0.00095903 | 6.0846 | 6.0856 | -12.6423 | 1042.7151 | 19080.2059 | -0.012124
90 |  | 53.2564 | 213.8378 | 4187 | 0.00095898 | 6.0856 | 6.0865 | -12.6423 | 1042.7742 | 19294.0437 | -0.012124
91 |  | 53.2564 | 213.8257 | 4187 | 0.00095893 | 6.0865 | 6.0875 | -12.6423 | 1042.8333 | 19507.8694 | -0.012123
92 |  | 53.2564 | 213.8136 | 4187 | 0.00095887 | 6.0875 | 6.0884 | -12.6423 | 1042.8924 | 19721.683 | -0.012122
93 |  | 53.2564 | 213.8015 | 4187 | 0.00095882 | 6.0884 | 6.0894 | -12.6423 | 1042.9516 | 19935.4844 | -0.012122
94 |  | 53.2564 | 213.7893 | 4187 | 0.00095876 | 6.0894 | 6.0904 | -12.6423 | 1043.0107 | 20149.2738 | -0.012121
95 |  | 53.2564 | 213.7772 | 4187 | 0.00095871 | 6.0904 | 6.0913 | -12.6423 | 1043.0698 | 20363.051 | -0.01212
96 |  | 53.2564 | 213.7651 | 4187 | 0.00095865 | 6.0913 | 6.0923 | -12.6423 | 1043.129 | 20576.8161 | -0.01212
97 |  | 53.2564 | 213.753 | 4187 | 0.0009586 | 6.0923 | 6.0932 | -12.6423 | 1043.1881 | 20790.5691 | -0.012119
98 |  | 53.2564 | 213.7409 | 4187 | 0.00095855 | 6.0932 | 6.0942 | -12.6423 | 1043.2473 | 21004.3099 | -0.012118
99 |  | 53.2564 | 213.7287 | 4187 | 0.00095849 | 6.0942 | 6.0952 | -12.6423 | 1043.3064 | 21218.0386 | -0.012118
100 |  | 53.2564 | 213.7166 | 4187 | 0.00095844 | 6.0952 | 6.0961 | -12.6423 | 1043.3656 | 21431.7553 | -0.012117
101 |  | 53.2564 | 213.7045 | 4187 | 0.00095838 | 6.0961 | 6.0971 | -12.6423 | 1043.4247 | 21645.4598 | -0.012116
102 |  | 53.2564 | 213.6924 | 4187 | 0.00095833 | 6.0971 | 6.098 | -12.6423 | 1043.4839 | 21859.1522 | -0.012116
103 |  | 53.2564 | 213.6803 | 4187 | 0.00095827 | 6.098 | 6.099 | -12.6423 | 1043.5431 | 22072.8324 | -0.012115
104 |  | 53.2564 | 213.6682 | 4187 | 0.00095822 | 6.099 | 6.0999 | -12.6423 | 1043.6022 | 22286.5006 | -0.012114
105 |  | 53.2564 | 213.656 | 4187 | 0.00095817 | 6.0999 | 6.1009 | -12.6423 | 1043.6614 | 22500.1566 | -0.012113
106 |  | 53.2564 | 213.6439 | 4187 | 0.00095811 | 6.1009 | 6.1019 | -12.6423 | 1043.7206 | 22713.8006 | -0.012113
107 |  | 53.2564 | 213.6318 | 4187 | 0.00095806 | 6.1019 | 6.1028 | -12.6423 | 1043.7798 | 22927.4324 | -0.012112
108 |  | 53.2564 | 213.6197 | 4187 | 0.000958 | 6.1028 | 6.1038 | -12.6423 | 1043.8389 | 23141.0521 | -0.012111
109 |  | 53.2564 | 213.6076 | 4187 | 0.00095795 | 6.1038 | 6.1047 | -12.6423 | 1043.8981 | 23354.6597 | -0.012111
110 |  | 53.2564 | 213.5955 | 4187 | 0.00095789 | 6.1047 | 6.1057 | -12.6423 | 1043.9573 | 23568.2552 | -0.01211
111 |  | 53.2564 | 213.5834 | 4187 | 0.00095784 | 6.1057 | 6.1067 | -12.6423 | 1044.0165 | 23781.8385 | -0.012109
112 |  | 53.2564 | 213.5713 | 4187 | 0.00095778 | 6.1067 | 6.1076 | -12.6423 | 1044.0757 | 23995.4098 | -0.012109
113 |  | 53.2564 | 213.5592 | 4187 | 0.00095773 | 6.1076 | 6.1086 | -12.6423 | 1044.1349 | 24208.969 | -0.012108
114 |  | 53.2564 | 213.547 | 4187 | 0.00095768 | 6.1086 | 6.1095 | -12.6423 | 1044.1941 | 24422.516 | -0.012107
115 |  | 53.2564 | 213.5349 | 4187 | 0.00095762 | 6.1095 | 6.1105 | -12.6423 | 1044.2533 | 24636.0509 | -0.012107
116 |  | 53.2564 | 213.5228 | 4187 | 0.00095757 | 6.1105 | 6.1114 | -12.6423 | 1044.3125 | 24849.5738 | -0.012106
117 |  | 53.2564 | 213.5107 | 4187 | 0.00095751 | 6.1114 | 6.1124 | -12.6423 | 1044.3717 | 25063.0845 | -0.012105
118 |  | 53.2564 | 213.4986 | 4187 | 0.00095746 | 6.1124 | 6.1134 | -12.6423 | 1044.4309 | 25276.5831 | -0.012105
119 |  | 53.2564 | 213.4865 | 4187 | 0.0009574 | 6.1134 | 6.1143 | -12.6423 | 1044.4901 | 25490.0696 | -0.012104
120 |  | 53.2564 | 213.4744 | 4187 | 0.00095735 | 6.1143 | 6.1153 | -12.6423 | 1044.5494 | 25703.5441 | -0.012103
121 |  | 53.2564 | 213.4623 | 4187 | 0.0009573 | 6.1153 | 6.1162 | -12.6423 | 1044.6086 | 25917.0064 | -0.012102
122 |  | 53.2564 | 213.4502 | 4187 | 0.00095724 | 6.1162 | 6.1172 | -12.6423 | 1044.6678 | 26130.4566 | -0.012102
123 |  | 53.2564 | 213.4381 | 4187 | 0.00095719 | 6.1172 | 6.1181 | -12.6423 | 1044.7271 | 26343.8947 | -0.012101
124 |  | 53.2564 | 213.426 | 4187 | 0.00095713 | 6.1181 | 6.1191 | -12.6423 | 1044.7863 | 26557.3207 | -0.0121
125 |  | 53.2564 | 213.4139 | 4187 | 0.00095708 | 6.1191 | 6.1201 | -12.6423 | 1044.8455 | 26770.7346 | -0.0121
126 |  | 53.2564 | 213.4018 | 4187 | 0.00095703 | 6.1201 | 6.121 | -12.6423 | 1044.9048 | 26984.1364 | -0.012099
127 |  | 53.2564 | 213.3897 | 4187 | 0.00095697 | 6.121 | 6.122 | -12.6423 | 1044.964 | 27197.5261 | -0.012098
128 |  | 53.2564 | 213.3776 | 4187 | 0.00095692 | 6.122 | 6.1229 | -12.6423 | 1045.0233 | 27410.9037 | -0.012098
129 |  | 53.2564 | 213.3655 | 4187 | 0.00095686 | 6.1229 | 6.1239 | -12.6423 | 1045.0825 | 27624.2692 | -0.012097
130 |  | 53.2564 | 213.3534 | 4187 | 0.00095681 | 6.1239 | 6.1248 | -12.6423 | 1045.1418 | 27837.6226 | -0.012096
131 |  | 53.2564 | 213.3413 | 4187 | 0.00095675 | 6.1248 | 6.1258 | -12.6423 | 1045.201 | 28050.964 | -0.012096
132 |  | 53.2564 | 213.3292 | 4187 | 0.0009567 | 6.1258 | 6.1268 | -12.6423 | 1045.2603 | 28264.2932 | -0.012095
133 |  | 53.2564 | 213.3171 | 4187 | 0.00095665 | 6.1268 | 6.1277 | -12.6423 | 1045.3196 | 28477.6103 | -0.012094
134 |  | 53.2564 | 213.305 | 4187 | 0.00095659 | 6.1277 | 6.1287 | -12.6423 | 1045.3788 | 28690.9153 | -0.012094
135 |  | 53.2564 | 213.2929 | 4187 | 0.00095654 | 6.1287 | 6.1296 | -12.6423 | 1045.4381 | 28904.2083 | -0.012093
136 |  | 53.2564 | 213.2808 | 4187 | 0.00095648 | 6.1296 | 6.1306 | -12.6423 | 1045.4974 | 29117.4891 | -0.012092
137 |  | 53.2564 | 213.2688 | 4187 | 0.00095643 | 6.1306 | 6.1315 | -12.6423 | 1045.5567 | 29330.7579 | -0.012091
138 |  | 53.2564 | 213.2567 | 4187 | 0.00095637 | 6.1315 | 6.1325 | -12.6423 | 1045.6159 | 29544.0145 | -0.012091
139 |  | 53.2564 | 213.2446 | 4187 | 0.00095632 | 6.1325 | 6.1334 | -12.6423 | 1045.6752 | 29757.2591 | -0.01209
140 |  | 53.2564 | 213.2325 | 4187 | 0.00095627 | 6.1334 | 6.1344 | -12.6423 | 1045.7345 | 29970.4916 | -0.012089
141 |  | 53.2564 | 213.2204 | 4187 | 0.00095621 | 6.1344 | 6.1354 | -12.6423 | 1045.7938 | 30183.712 | -0.012089
142 |  | 53.2564 | 213.2083 | 4187 | 0.00095616 | 6.1354 | 6.1363 | -12.6423 | 1045.8531 | 30396.9203 | -0.012088
143 |  | 53.2564 | 213.1962 | 4187 | 0.0009561 | 6.1363 | 6.1373 | -12.6423 | 1045.9124 | 30610.1165 | -0.012087
144 |  | 53.2564 | 213.1841 | 4187 | 0.00095605 | 6.1373 | 6.1382 | -12.6423 | 1045.9717 | 30823.3006 | -0.012087
145 |  | 53.2564 | 213.172 | 4187 | 0.00095599 | 6.1382 | 6.1392 | -12.6423 | 1046.031 | 31036.4727 | -0.012086
146 |  | 53.2564 | 213.16 | 4187 | 0.00095594 | 6.1392 | 6.1401 | -12.6423 | 1046.0903 | 31249.6326 | -0.012085
147 |  | 53.2564 | 213.1479 | 4187 | 0.00095589 | 6.1401 | 6.1411 | -12.6423 | 1046.1496 | 31462.7805 | -0.012085
148 |  | 53.2564 | 213.1358 | 4187 | 0.00095583 | 6.1411 | 6.1421 | -12.6423 | 1046.2089 | 31675.9163 | -0.012084
149 |  | 53.2564 | 213.1237 | 4187 | 0.00095578 | 6.1421 | 6.143 | -12.6423 | 1046.2683 | 31889.04 | -0.012083
150 |  | 53.2564 | 213.1116 | 4187 | 0.00095572 | 6.143 | 6.144 | -12.6423 | 1046.3276 | 32102.1516 | -0.012083
151 |  | 53.2564 | 213.0995 | 4187 | 0.00095567 | 6.144 | 6.1449 | -12.6423 | 1046.3869 | 32315.2511 | -0.012082
152 |  | 53.2564 | 213.0875 | 4187 | 0.00095562 | 6.1449 | 6.1459 | -12.6423 | 1046.4462 | 32528.3386 | -0.012081
153 |  | 53.2564 | 213.0754 | 4187 | 0.00095556 | 6.1459 | 6.1468 | -12.6423 | 1046.5056 | 32741.414 | -0.012081
154 |  | 53.2564 | 213.0633 | 4187 | 0.00095551 | 6.1468 | 6.1478 | -12.6423 | 1046.5649 | 32954.4772 | -0.01208
155 |  | 53.2564 | 213.0512 | 4187 | 0.00095545 | 6.1478 | 6.1487 | -12.6423 | 1046.6242 | 33167.5285 | -0.012079
156 |  | 53.2564 | 213.0391 | 4187 | 0.0009554 | 6.1487 | 6.1497 | -12.6423 | 1046.6836 | 33380.5676 | -0.012078
157 |  | 53.2564 | 213.0271 | 4187 | 0.00095534 | 6.1497 | 6.1507 | -12.6423 | 1046.7429 | 33593.5946 | -0.012078
158 |  | 53.2564 | 213.015 | 4187 | 0.00095529 | 6.1507 | 6.1516 | -12.6423 | 1046.8023 | 33806.6096 | -0.012077
159 |  | 53.2564 | 213.0029 | 4187 | 0.00095524 | 6.1516 | 6.1526 | -12.6423 | 1046.8616 | 34019.6125 | -0.012076
160 |  | 53.2564 | 212.9908 | 4187 | 0.00095518 | 6.1526 | 6.1535 | -12.6423 | 1046.921 | 34232.6033 | -0.012076
161 |  | 53.2564 | 212.9787 | 4187 | 0.00095513 | 6.1535 | 6.1545 | -12.6423 | 1046.9804 | 34445.5821 | -0.012075
162 |  | 53.2564 | 212.9667 | 4187 | 0.00095507 | 6.1545 | 6.1554 | -12.6423 | 1047.0397 | 34658.5488 | -0.012074
163 |  | 53.2564 | 212.9546 | 4187 | 0.00095502 | 6.1554 | 6.1564 | -12.6423 | 1047.0991 | 34871.5034 | -0.012074
164 |  | 53.2564 | 212.9425 | 4187 | 0.00095497 | 6.1564 | 6.1573 | -12.6423 | 1047.1585 | 35084.4459 | -0.012073
165 |  | 53.2564 | 212.9305 | 4187 | 0.00095491 | 6.1573 | 6.1583 | -12.6423 | 1047.2178 | 35297.3763 | -0.012072
166 |  | 53.2564 | 212.9184 | 4187 | 0.00095486 | 6.1583 | 6.1593 | -12.6423 | 1047.2772 | 35510.2947 | -0.012072
167 |  | 53.2564 | 212.9063 | 4187 | 0.0009548 | 6.1593 | 6.1602 | -12.6423 | 1047.3366 | 35723.201 | -0.012071
168 |  | 53.2564 | 212.8942 | 4187 | 0.00095475 | 6.1602 | 6.1612 | -12.6423 | 1047.396 | 35936.0953 | -0.01207
169 |  | 53.2564 | 212.8822 | 4187 | 0.00095469 | 6.1612 | 6.1621 | -12.6423 | 1047.4554 | 36148.9774 | -0.01207
170 |  | 53.2564 | 212.8701 | 4187 | 0.00095464 | 6.1621 | 6.1631 | -12.6423 | 1047.5147 | 36361.8475 | -0.012069
171 |  | 53.2564 | 212.858 | 4187 | 0.00095459 | 6.1631 | 6.164 | -12.6423 | 1047.5741 | 36574.7056 | -0.012068
172 |  | 53.2564 | 212.846 | 4187 | 0.00095453 | 6.164 | 6.165 | -12.6423 | 1047.6335 | 36787.5515 | -0.012068
173 |  | 53.2564 | 212.8339 | 4187 | 0.00095448 | 6.165 | 6.1659 | -12.6423 | 1047.6929 | 37000.3854 | -0.012067
174 |  | 53.2564 | 212.8218 | 4187 | 0.00095442 | 6.1659 | 6.1669 | -12.6423 | 1047.7523 | 37213.2072 | -0.012066
175 |  | 53.2564 | 212.8098 | 4187 | 0.00095437 | 6.1669 | 6.1678 | -12.6423 | 1047.8117 | 37426.017 | -0.012065
176 |  | 53.2564 | 212.7977 | 4187 | 0.00095432 | 6.1678 | 6.1688 | -12.6423 | 1047.8712 | 37638.8147 | -0.012065
177 |  | 53.2564 | 212.7856 | 4187 | 0.00095426 | 6.1688 | 6.1697 | -12.6423 | 1047.9306 | 37851.6003 | -0.012064
178 |  | 53.2564 | 212.7736 | 4187 | 0.00095421 | 6.1697 | 6.1707 | -12.6423 | 1047.99 | 38064.3739 | -0.012063
179 |  | 53.2564 | 212.7615 | 4187 | 0.00095415 | 6.1707 | 6.1717 | -12.6423 | 1048.0494 | 38277.1354 | -0.012063
180 |  | 53.2564 | 212.7494 | 4187 | 0.0009541 | 6.1717 | 6.1726 | -12.6423 | 1048.1088 | 38489.8848 | -0.012062
181 |  | 53.2564 | 212.7374 | 4187 | 0.00095405 | 6.1726 | 6.1736 | -12.6423 | 1048.1683 | 38702.6222 | -0.012061
182 |  | 53.2564 | 212.7253 | 4187 | 0.00095399 | 6.1736 | 6.1745 | -12.6423 | 1048.2277 | 38915.3475 | -0.012061
183 |  | 53.2564 | 212.7133 | 4187 | 0.00095394 | 6.1745 | 6.1755 | -12.6423 | 1048.2871 | 39128.0608 | -0.01206
184 |  | 53.2564 | 212.7012 | 4187 | 0.00095388 | 6.1755 | 6.1764 | -12.6423 | 1048.3466 | 39340.762 | -0.012059
185 |  | 53.2564 | 212.6891 | 4187 | 0.00095383 | 6.1764 | 6.1774 | -12.6423 | 1048.406 | 39553.4511 | -0.012059
186 |  | 53.2564 | 212.6771 | 4187 | 0.00095377 | 6.1774 | 6.1783 | -12.6423 | 1048.4654 | 39766.1282 | -0.012058
187 |  | 53.2564 | 212.665 | 4187 | 0.00095372 | 6.1783 | 6.1793 | -12.6423 | 1048.5249 | 39978.7932 | -0.012057
188 |  | 53.2564 | 212.653 | 4187 | 0.00095367 | 6.1793 | 6.1802 | -12.6423 | 1048.5843 | 40191.4461 | -0.012057
189 |  | 53.2564 | 212.6409 | 4187 | 0.00095361 | 6.1802 | 6.1812 | -12.6423 | 1048.6438 | 40404.0871 | -0.012056
190 |  | 53.2564 | 212.6288 | 4187 | 0.00095356 | 6.1812 | 6.1822 | -12.6423 | 1048.7032 | 40616.7159 | -0.012055
191 |  | 53.2564 | 212.6168 | 4187 | 0.0009535 | 6.1822 | 6.1831 | -12.6423 | 1048.7627 | 40829.3327 | -0.012055
192 |  | 53.2564 | 212.6047 | 4187 | 0.00095345 | 6.1831 | 6.1841 | -12.6423 | 1048.8222 | 41041.9374 | -0.012054
193 |  | 53.2564 | 212.5927 | 4187 | 0.0009534 | 6.1841 | 6.185 | -12.6423 | 1048.8816 | 41254.5301 | -0.012053
194 |  | 53.2564 | 212.5806 | 4187 | 0.00095334 | 6.185 | 6.186 | -12.6423 | 1048.9411 | 41467.1108 | -0.012052
195 |  | 53.2564 | 212.5686 | 4187 | 0.00095329 | 6.186 | 6.1869 | -12.6423 | 1049.0006 | 41679.6793 | -0.012052
196 |  | 53.2564 | 212.5565 | 4187 | 0.00095323 | 6.1869 | 6.1879 | -12.6423 | 1049.0601 | 41892.2359 | -0.012051
197 |  | 53.2564 | 212.5445 | 4187 | 0.00095318 | 6.1879 | 6.1888 | -12.6423 | 1049.1195 | 42104.7803 | -0.01205
198 |  | 53.2564 | 212.5324 | 4187 | 0.00095313 | 6.1888 | 6.1898 | -12.6423 | 1049.179 | 42317.3128 | -0.01205
199 |  | 53.2564 | 212.5204 | 4187 | 0.00095307 | 6.1898 | 6.1907 | -12.6423 | 1049.2385 | 42529.8331 | -0.012049
200 |  | 53.2564 | 212.5083 | 4187 | 0.00095302 | 6.1907 | 6.1917 | -12.6423 | 1049.298 | 42742.3415 | -0.012048
201 |  | 53.2564 | 212.4963 | 4187 | 0.00095296 | 6.1917 | 6.1926 | -12.6423 | 1049.3575 | 42954.8377 | -0.012048
202 |  | 53.2564 | 212.4842 | 4187 | 0.00095291 | 6.1926 | 6.1936 | -12.6423 | 1049.417 | 43167.322 | -0.012047
203 |  | 53.2564 | 212.4722 | 4187 | 0.00095286 | 6.1936 | 6.1945 | -12.6423 | 1049.4765 | 43379.7942 | -0.012046
204 |  | 53.2564 | 212.4601 | 4187 | 0.0009528 | 6.1945 | 6.1955 | -12.6423 | 1049.536 | 43592.2543 | -0.012046
205 |  | 53.2564 | 212.4481 | 4187 | 0.00095275 | 6.1955 | 6.1964 | -12.6423 | 1049.5955 | 43804.7024 | -0.012045
206 |  | 53.2564 | 212.436 | 4187 | 0.00095269 | 6.1964 | 6.1974 | -12.6423 | 1049.655 | 44017.1384 | -0.012044
207 |  | 53.2564 | 212.424 | 4187 | 0.00095264 | 6.1974 | 6.1984 | -12.6423 | 1049.7145 | 44229.5624 | -0.012044
208 |  | 53.2564 | 212.412 | 4187 | 0.00095259 | 6.1984 | 6.1993 | -12.6423 | 1049.7741 | 44441.9744 | -0.012043
209 |  | 53.2564 | 212.3999 | 4187 | 0.00095253 | 6.1993 | 6.2003 | -12.6423 | 1049.8336 | 44654.3743 | -0.012042
210 |  | 53.2564 | 212.3879 | 4187 | 0.00095248 | 6.2003 | 6.2012 | -12.6423 | 1049.8931 | 44866.7622 | -0.012042
211 |  | 53.2564 | 212.3758 | 4187 | 0.00095242 | 6.2012 | 6.2022 | -12.6423 | 1049.9526 | 45079.138 | -0.012041
212 |  | 53.2564 | 212.3638 | 4187 | 0.00095237 | 6.2022 | 6.2031 | -12.6423 | 1050.0122 | 45291.5018 | -0.01204
213 |  | 53.2564 | 212.3518 | 4187 | 0.00095232 | 6.2031 | 6.2041 | -12.6423 | 1050.0717 | 45503.8536 | -0.012039
214 |  | 53.2564 | 212.3397 | 4187 | 0.00095226 | 6.2041 | 6.205 | -12.6423 | 1050.1312 | 45716.1933 | -0.012039
215 |  | 53.2564 | 212.3277 | 4187 | 0.00095221 | 6.205 | 6.206 | -12.6423 | 1050.1908 | 45928.521 | -0.012038
216 |  | 53.2564 | 212.3156 | 4187 | 0.00095215 | 6.206 | 6.2069 | -12.6423 | 1050.2503 | 46140.8366 | -0.012037
217 |  | 53.2564 | 212.3036 | 4187 | 0.0009521 | 6.2069 | 6.2079 | -12.6423 | 1050.3099 | 46353.1402 | -0.012037
218 |  | 53.2564 | 212.2916 | 4187 | 0.00095205 | 6.2079 | 6.2088 | -12.6423 | 1050.3694 | 46565.4318 | -0.012036
219 |  | 53.2564 | 212.2795 | 4187 | 0.00095199 | 6.2088 | 6.2098 | -12.6423 | 1050.429 | 46777.7113 | -0.012035
220 |  | 53.2564 | 212.2675 | 4187 | 0.00095194 | 6.2098 | 6.2107 | -12.6423 | 1050.4885 | 46989.9788 | -0.012035
221 |  | 53.2564 | 212.2555 | 4187 | 0.00095188 | 6.2107 | 6.2117 | -12.6423 | 1050.5481 | 47202.2342 | -0.012034
222 |  | 53.2564 | 212.2434 | 4187 | 0.00095183 | 6.2117 | 6.2126 | -12.6423 | 1050.6077 | 47414.4777 | -0.012033
223 |  | 53.2564 | 212.2314 | 4187 | 0.00095178 | 6.2126 | 6.2136 | -12.6423 | 1050.6672 | 47626.709 | -0.012033
224 |  | 53.2564 | 212.2194 | 4187 | 0.00095172 | 6.2136 | 6.2145 | -12.6423 | 1050.7268 | 47838.9284 | -0.012032
225 |  | 53.2564 | 212.2073 | 4187 | 0.00095167 | 6.2145 | 6.2155 | -12.6423 | 1050.7864 | 48051.1357 | -0.012031
226 |  | 53.2564 | 212.1953 | 4187 | 0.00095161 | 6.2155 | 6.2164 | -12.6423 | 1050.846 | 48263.331 | -0.012031
227 |  | 53.2564 | 212.1833 | 4187 | 0.00095156 | 6.2164 | 6.2174 | -12.6423 | 1050.9055 | 48475.5143 | -0.01203
228 |  | 53.2564 | 212.1712 | 4187 | 0.00095151 | 6.2174 | 6.2183 | -12.6423 | 1050.9651 | 48687.6855 | -0.012029
229 |  | 53.2564 | 212.1592 | 4187 | 0.00095145 | 6.2183 | 6.2193 | -12.6423 | 1051.0247 | 48899.8447 | -0.012029
230 |  | 53.2564 | 212.1472 | 4187 | 0.0009514 | 6.2193 | 6.2202 | -12.6423 | 1051.0843 | 49111.9919 | -0.012028
231 |  | 53.2564 | 212.1351 | 4187 | 0.00095134 | 6.2202 | 6.2212 | -12.6423 | 1051.1439 | 49324.127 | -0.012027
232 |  | 53.2564 | 212.1231 | 4187 | 0.00095129 | 6.2212 | 6.2222 | -12.6423 | 1051.2035 | 49536.2501 | -0.012027
233 |  | 53.2564 | 212.1111 | 4187 | 0.00095124 | 6.2222 | 6.2231 | -12.6423 | 1051.2631 | 49748.3612 | -0.012026
234 |  | 53.2564 | 212.0991 | 4187 | 0.00095118 | 6.2231 | 6.2241 | -12.6423 | 1051.3227 | 49960.4603 | -0.012025
235 |  | 53.2564 | 212.087 | 4187 | 0.00095113 | 6.2241 | 6.225 | -12.6423 | 1051.3823 | 50172.5473 | -0.012024
236 |  | 53.2564 | 212.075 | 4187 | 0.00095107 | 6.225 | 6.226 | -12.6423 | 1051.4419 | 50384.6224 | -0.012024

## St323
|  |  | buis | verlies W/M | L /°C/sec
diam | wandikte |  | inhoud l/m |  | W/M
323.9 | 7.1 | 3.1416 | 75.3308 | 254.9432 | 4187
[8 empty] | J/sec/mtr | aantal mtr. | verlies
|  | buis | verlies W/M | L /°C/sec | verlies temp | begintemp | eindtemp | verlies | bij 1°C | totaal J/sec
|  | inhoud L |  | W/M | °C per M | °C | °C | per m°C | daling | aantal mtr
1 | 323.9 | 75.3308 | 254.9432 | 4187 | 0.00080829 | 6 | 6.0008 | -14.9967 | 1237.1771 | 254.9432 | -0.012122
2 |  | 75.3308 | 254.9311 | 4187 | 0.00080825 | 6.0008 | 6.0016 | -14.9967 | 1237.2359 | 509.8742 | -0.012121
3 |  | 75.3308 | 254.9189 | 4187 | 0.00080821 | 6.0016 | 6.0024 | -14.9967 | 1237.2947 | 764.7932 | -0.012121
4 |  | 75.3308 | 254.9068 | 4187 | 0.00080818 | 6.0024 | 6.0032 | -14.9967 | 1237.3536 | 1019.7 | -0.01212
5 |  | 75.3308 | 254.8947 | 4187 | 0.00080814 | 6.0032 | 6.004 | -14.9967 | 1237.4124 | 1274.5947 | -0.012119
6 |  | 75.3308 | 254.8826 | 4187 | 0.0008081 | 6.004 | 6.0048 | -14.9967 | 1237.4712 | 1529.4772 | -0.012119
7 |  | 75.3308 | 254.8705 | 4187 | 0.00080806 | 6.0048 | 6.0057 | -14.9967 | 1237.5301 | 1784.3477 | -0.012118
8 |  | 75.3308 | 254.8583 | 4187 | 0.00080802 | 6.0057 | 6.0065 | -14.9967 | 1237.5889 | 2039.206 | -0.012118
9 |  | 75.3308 | 254.8462 | 4187 | 0.00080798 | 6.0065 | 6.0073 | -14.9967 | 1237.6478 | 2294.0522 | -0.012117
10 |  | 75.3308 | 254.8341 | 4187 | 0.00080795 | 6.0073 | 6.0081 | -14.9967 | 1237.7066 | 2548.8863 | -0.012116
11 |  | 75.3308 | 254.822 | 4187 | 0.00080791 | 6.0081 | 6.0089 | -14.9967 | 1237.7655 | 2803.7083 | -0.012116
12 |  | 75.3308 | 254.8099 | 4187 | 0.00080787 | 6.0089 | 6.0097 | -14.9967 | 1237.8243 | 3058.5182 | -0.012115
13 |  | 75.3308 | 254.7978 | 4187 | 0.00080783 | 6.0097 | 6.0105 | -14.9967 | 1237.8832 | 3313.3159 | -0.012115
14 |  | 75.3308 | 254.7856 | 4187 | 0.00080779 | 6.0105 | 6.0113 | -14.9967 | 1237.942 | 3568.1016 | -0.012114
15 |  | 75.3308 | 254.7735 | 4187 | 0.00080775 | 6.0113 | 6.0121 | -14.9967 | 1238.0009 | 3822.8751 | -0.012114
16 |  | 75.3308 | 254.7614 | 4187 | 0.00080772 | 6.0121 | 6.0129 | -14.9967 | 1238.0598 | 4077.6365 | -0.012113
17 |  | 75.3308 | 254.7493 | 4187 | 0.00080768 | 6.0129 | 6.0137 | -14.9967 | 1238.1186 | 4332.3858 | -0.012112
18 |  | 75.3308 | 254.7372 | 4187 | 0.00080764 | 6.0137 | 6.0145 | -14.9967 | 1238.1775 | 4587.123 | -0.012112
19 |  | 75.3308 | 254.7251 | 4187 | 0.0008076 | 6.0145 | 6.0154 | -14.9967 | 1238.2364 | 4841.848 | -0.012111
20 |  | 75.3308 | 254.713 | 4187 | 0.00080756 | 6.0154 | 6.0162 | -14.9967 | 1238.2953 | 5096.561 | -0.012111
21 |  | 75.3308 | 254.7008 | 4187 | 0.00080752 | 6.0162 | 6.017 | -14.9967 | 1238.3541 | 5351.2619 | -0.01211
22 |  | 75.3308 | 254.6887 | 4187 | 0.00080749 | 6.017 | 6.0178 | -14.9967 | 1238.413 | 5605.9506 | -0.01211
23 |  | 75.3308 | 254.6766 | 4187 | 0.00080745 | 6.0178 | 6.0186 | -14.9967 | 1238.4719 | 5860.6272 | -0.012109
24 |  | 75.3308 | 254.6645 | 4187 | 0.00080741 | 6.0186 | 6.0194 | -14.9967 | 1238.5308 | 6115.2917 | -0.012108
25 |  | 75.3308 | 254.6524 | 4187 | 0.00080737 | 6.0194 | 6.0202 | -14.9967 | 1238.5897 | 6369.9442 | -0.012108
26 |  | 75.3308 | 254.6403 | 4187 | 0.00080733 | 6.0202 | 6.021 | -14.9967 | 1238.6486 | 6624.5845 | -0.012107
27 |  | 75.3308 | 254.6282 | 4187 | 0.00080729 | 6.021 | 6.0218 | -14.9967 | 1238.7075 | 6879.2127 | -0.012107
28 |  | 75.3308 | 254.6161 | 4187 | 0.00080725 | 6.0218 | 6.0226 | -14.9967 | 1238.7664 | 7133.8287 | -0.012106
29 |  | 75.3308 | 254.604 | 4187 | 0.00080722 | 6.0226 | 6.0234 | -14.9967 | 1238.8253 | 7388.4327 | -0.012106
30 |  | 75.3308 | 254.5919 | 4187 | 0.00080718 | 6.0234 | 6.0242 | -14.9967 | 1238.8842 | 7643.0246 | -0.012105
31 |  | 75.3308 | 254.5798 | 4187 | 0.00080714 | 6.0242 | 6.025 | -14.9967 | 1238.9431 | 7897.6044 | -0.012104
32 |  | 75.3308 | 254.5677 | 4187 | 0.0008071 | 6.025 | 6.0258 | -14.9967 | 1239.002 | 8152.172 | -0.012104
33 |  | 75.3308 | 254.5556 | 4187 | 0.00080706 | 6.0258 | 6.0267 | -14.9967 | 1239.0609 | 8406.7276 | -0.012103
34 |  | 75.3308 | 254.5435 | 4187 | 0.00080702 | 6.0267 | 6.0275 | -14.9967 | 1239.1198 | 8661.2711 | -0.012103
35 |  | 75.3308 | 254.5314 | 4187 | 0.00080699 | 6.0275 | 6.0283 | -14.9967 | 1239.1787 | 8915.8024 | -0.012102
36 |  | 75.3308 | 254.5193 | 4187 | 0.00080695 | 6.0283 | 6.0291 | -14.9967 | 1239.2377 | 9170.3217 | -0.012102
37 |  | 75.3308 | 254.5072 | 4187 | 0.00080691 | 6.0291 | 6.0299 | -14.9967 | 1239.2966 | 9424.8288 | -0.012101
38 |  | 75.3308 | 254.4951 | 4187 | 0.00080687 | 6.0299 | 6.0307 | -14.9967 | 1239.3555 | 9679.3239 | -0.0121
39 |  | 75.3308 | 254.483 | 4187 | 0.00080683 | 6.0307 | 6.0315 | -14.9967 | 1239.4144 | 9933.8069 | -0.0121
40 |  | 75.3308 | 254.4709 | 4187 | 0.00080679 | 6.0315 | 6.0323 | -14.9967 | 1239.4734 | 10188.2777 | -0.012099
41 |  | 75.3308 | 254.4588 | 4187 | 0.00080676 | 6.0323 | 6.0331 | -14.9967 | 1239.5323 | 10442.7365 | -0.012099
42 |  | 75.3308 | 254.4467 | 4187 | 0.00080672 | 6.0331 | 6.0339 | -14.9967 | 1239.5913 | 10697.1831 | -0.012098
43 |  | 75.3308 | 254.4346 | 4187 | 0.00080668 | 6.0339 | 6.0347 | -14.9967 | 1239.6502 | 10951.6177 | -0.012097
44 |  | 75.3308 | 254.4225 | 4187 | 0.00080664 | 6.0347 | 6.0355 | -14.9967 | 1239.7091 | 11206.0401 | -0.012097
45 |  | 75.3308 | 254.4104 | 4187 | 0.0008066 | 6.0355 | 6.0363 | -14.9967 | 1239.7681 | 11460.4505 | -0.012096
46 |  | 75.3308 | 254.3983 | 4187 | 0.00080656 | 6.0363 | 6.0371 | -14.9967 | 1239.827 | 11714.8488 | -0.012096
47 |  | 75.3308 | 254.3862 | 4187 | 0.00080653 | 6.0371 | 6.0379 | -14.9967 | 1239.886 | 11969.235 | -0.012095
48 |  | 75.3308 | 254.3741 | 4187 | 0.00080649 | 6.0379 | 6.0388 | -14.9967 | 1239.9449 | 12223.609 | -0.012095
49 |  | 75.3308 | 254.362 | 4187 | 0.00080645 | 6.0388 | 6.0396 | -14.9967 | 1240.0039 | 12477.971 | -0.012094
50 |  | 75.3308 | 254.3499 | 4187 | 0.00080641 | 6.0396 | 6.0404 | -14.9967 | 1240.0629 | 12732.3209 | -0.012093
51 |  | 75.3308 | 254.3378 | 4187 | 0.00080637 | 6.0404 | 6.0412 | -14.9967 | 1240.1218 | 12986.6587 | -0.012093
52 |  | 75.3308 | 254.3257 | 4187 | 0.00080633 | 6.0412 | 6.042 | -14.9967 | 1240.1808 | 13240.9844 | -0.012092
53 |  | 75.3308 | 254.3136 | 4187 | 0.0008063 | 6.042 | 6.0428 | -14.9967 | 1240.2398 | 13495.298 | -0.012092
54 |  | 75.3308 | 254.3015 | 4187 | 0.00080626 | 6.0428 | 6.0436 | -14.9967 | 1240.2987 | 13749.5995 | -0.012091
55 |  | 75.3308 | 254.2894 | 4187 | 0.00080622 | 6.0436 | 6.0444 | -14.9967 | 1240.3577 | 14003.889 | -0.012091
56 |  | 75.3308 | 254.2773 | 4187 | 0.00080618 | 6.0444 | 6.0452 | -14.9967 | 1240.4167 | 14258.1663 | -0.01209
57 |  | 75.3308 | 254.2652 | 4187 | 0.00080614 | 6.0452 | 6.046 | -14.9967 | 1240.4757 | 14512.4315 | -0.012089
58 |  | 75.3308 | 254.2532 | 4187 | 0.0008061 | 6.046 | 6.0468 | -14.9967 | 1240.5346 | 14766.6847 | -0.012089
59 |  | 75.3308 | 254.2411 | 4187 | 0.00080607 | 6.0468 | 6.0476 | -14.9967 | 1240.5936 | 15020.9258 | -0.012088
60 |  | 75.3308 | 254.229 | 4187 | 0.00080603 | 6.0476 | 6.0484 | -14.9967 | 1240.6526 | 15275.1547 | -0.012088
61 |  | 75.3308 | 254.2169 | 4187 | 0.00080599 | 6.0484 | 6.0492 | -14.9967 | 1240.7116 | 15529.3716 | -0.012087
62 |  | 75.3308 | 254.2048 | 4187 | 0.00080595 | 6.0492 | 6.05 | -14.9967 | 1240.7706 | 15783.5764 | -0.012087
63 |  | 75.3308 | 254.1927 | 4187 | 0.00080591 | 6.05 | 6.0508 | -14.9967 | 1240.8296 | 16037.7692 | -0.012086
64 |  | 75.3308 | 254.1806 | 4187 | 0.00080587 | 6.0508 | 6.0517 | -14.9967 | 1240.8886 | 16291.9498 | -0.012085
65 |  | 75.3308 | 254.1685 | 4187 | 0.00080584 | 6.0517 | 6.0525 | -14.9967 | 1240.9476 | 16546.1183 | -0.012085
66 |  | 75.3308 | 254.1565 | 4187 | 0.0008058 | 6.0525 | 6.0533 | -14.9967 | 1241.0066 | 16800.2748 | -0.012084
67 |  | 75.3308 | 254.1444 | 4187 | 0.00080576 | 6.0533 | 6.0541 | -14.9967 | 1241.0656 | 17054.4192 | -0.012084
68 |  | 75.3308 | 254.1323 | 4187 | 0.00080572 | 6.0541 | 6.0549 | -14.9967 | 1241.1246 | 17308.5515 | -0.012083
69 |  | 75.3308 | 254.1202 | 4187 | 0.00080568 | 6.0549 | 6.0557 | -14.9967 | 1241.1836 | 17562.6717 | -0.012083
70 |  | 75.3308 | 254.1081 | 4187 | 0.00080564 | 6.0557 | 6.0565 | -14.9967 | 1241.2427 | 17816.7798 | -0.012082
71 |  | 75.3308 | 254.096 | 4187 | 0.00080561 | 6.0565 | 6.0573 | -14.9967 | 1241.3017 | 18070.8759 | -0.012081
72 |  | 75.3308 | 254.084 | 4187 | 0.00080557 | 6.0573 | 6.0581 | -14.9967 | 1241.3607 | 18324.9598 | -0.012081
73 |  | 75.3308 | 254.0719 | 4187 | 0.00080553 | 6.0581 | 6.0589 | -14.9967 | 1241.4197 | 18579.0317 | -0.01208
74 |  | 75.3308 | 254.0598 | 4187 | 0.00080549 | 6.0589 | 6.0597 | -14.9967 | 1241.4788 | 18833.0915 | -0.01208
75 |  | 75.3308 | 254.0477 | 4187 | 0.00080545 | 6.0597 | 6.0605 | -14.9967 | 1241.5378 | 19087.1392 | -0.012079
76 |  | 75.3308 | 254.0356 | 4187 | 0.00080541 | 6.0605 | 6.0613 | -14.9967 | 1241.5968 | 19341.1749 | -0.012079
77 |  | 75.3308 | 254.0236 | 4187 | 0.00080538 | 6.0613 | 6.0621 | -14.9967 | 1241.6559 | 19595.1984 | -0.012078
78 |  | 75.3308 | 254.0115 | 4187 | 0.00080534 | 6.0621 | 6.0629 | -14.9967 | 1241.7149 | 19849.2099 | -0.012077
79 |  | 75.3308 | 253.9994 | 4187 | 0.0008053 | 6.0629 | 6.0637 | -14.9967 | 1241.7739 | 20103.2093 | -0.012077
80 |  | 75.3308 | 253.9873 | 4187 | 0.00080526 | 6.0637 | 6.0645 | -14.9967 | 1241.833 | 20357.1967 | -0.012076
81 |  | 75.3308 | 253.9753 | 4187 | 0.00080522 | 6.0645 | 6.0653 | -14.9967 | 1241.892 | 20611.1719 | -0.012076
82 |  | 75.3308 | 253.9632 | 4187 | 0.00080518 | 6.0653 | 6.0662 | -14.9967 | 1241.9511 | 20865.1351 | -0.012075
83 |  | 75.3308 | 253.9511 | 4187 | 0.00080515 | 6.0662 | 6.067 | -14.9967 | 1242.0101 | 21119.0862 | -0.012075
84 |  | 75.3308 | 253.939 | 4187 | 0.00080511 | 6.067 | 6.0678 | -14.9967 | 1242.0692 | 21373.0253 | -0.012074
85 |  | 75.3308 | 253.927 | 4187 | 0.00080507 | 6.0678 | 6.0686 | -14.9967 | 1242.1283 | 21626.9522 | -0.012073
86 |  | 75.3308 | 253.9149 | 4187 | 0.00080503 | 6.0686 | 6.0694 | -14.9967 | 1242.1873 | 21880.8671 | -0.012073
87 |  | 75.3308 | 253.9028 | 4187 | 0.00080499 | 6.0694 | 6.0702 | -14.9967 | 1242.2464 | 22134.7699 | -0.012072
88 |  | 75.3308 | 253.8907 | 4187 | 0.00080496 | 6.0702 | 6.071 | -14.9967 | 1242.3054 | 22388.6607 | -0.012072
89 |  | 75.3308 | 253.8787 | 4187 | 0.00080492 | 6.071 | 6.0718 | -14.9967 | 1242.3645 | 22642.5393 | -0.012071
90 |  | 75.3308 | 253.8666 | 4187 | 0.00080488 | 6.0718 | 6.0726 | -14.9967 | 1242.4236 | 22896.4059 | -0.01207
91 |  | 75.3308 | 253.8545 | 4187 | 0.00080484 | 6.0726 | 6.0734 | -14.9967 | 1242.4827 | 23150.2604 | -0.01207
92 |  | 75.3308 | 253.8425 | 4187 | 0.0008048 | 6.0734 | 6.0742 | -14.9967 | 1242.5417 | 23404.1029 | -0.012069
93 |  | 75.3308 | 253.8304 | 4187 | 0.00080476 | 6.0742 | 6.075 | -14.9967 | 1242.6008 | 23657.9333 | -0.012069
94 |  | 75.3308 | 253.8183 | 4187 | 0.00080473 | 6.075 | 6.0758 | -14.9967 | 1242.6599 | 23911.7516 | -0.012068
95 |  | 75.3308 | 253.8063 | 4187 | 0.00080469 | 6.0758 | 6.0766 | -14.9967 | 1242.719 | 24165.5579 | -0.012068
96 |  | 75.3308 | 253.7942 | 4187 | 0.00080465 | 6.0766 | 6.0774 | -14.9967 | 1242.7781 | 24419.3521 | -0.012067
97 |  | 75.3308 | 253.7821 | 4187 | 0.00080461 | 6.0774 | 6.0782 | -14.9967 | 1242.8372 | 24673.1342 | -0.012066
98 |  | 75.3308 | 253.7701 | 4187 | 0.00080457 | 6.0782 | 6.079 | -14.9967 | 1242.8963 | 24926.9042 | -0.012066
99 |  | 75.3308 | 253.758 | 4187 | 0.00080453 | 6.079 | 6.0798 | -14.9967 | 1242.9554 | 25180.6622 | -0.012065
100 |  | 75.3308 | 253.7459 | 4187 | 0.0008045 | 6.0798 | 6.0806 | -14.9967 | 1243.0145 | 25434.4081 | -0.012065
101 |  | 75.3308 | 253.7339 | 4187 | 0.00080446 | 6.0806 | 6.0814 | -14.9967 | 1243.0736 | 25688.142 | -0.012064
102 |  | 75.3308 | 253.7218 | 4187 | 0.00080442 | 6.0814 | 6.0822 | -14.9967 | 1243.1327 | 25941.8638 | -0.012064
103 |  | 75.3308 | 253.7097 | 4187 | 0.00080438 | 6.0822 | 6.0831 | -14.9967 | 1243.1918 | 26195.5735 | -0.012063
104 |  | 75.3308 | 253.6977 | 4187 | 0.00080434 | 6.0831 | 6.0839 | -14.9967 | 1243.2509 | 26449.2712 | -0.012062
105 |  | 75.3308 | 253.6856 | 4187 | 0.0008043 | 6.0839 | 6.0847 | -14.9967 | 1243.31 | 26702.9568 | -0.012062
106 |  | 75.3308 | 253.6735 | 4187 | 0.00080427 | 6.0847 | 6.0855 | -14.9967 | 1243.3691 | 26956.6303 | -0.012061
107 |  | 75.3308 | 253.6615 | 4187 | 0.00080423 | 6.0855 | 6.0863 | -14.9967 | 1243.4283 | 27210.2918 | -0.012061
108 |  | 75.3308 | 253.6494 | 4187 | 0.00080419 | 6.0863 | 6.0871 | -14.9967 | 1243.4874 | 27463.9412 | -0.01206
109 |  | 75.3308 | 253.6374 | 4187 | 0.00080415 | 6.0871 | 6.0879 | -14.9967 | 1243.5465 | 27717.5785 | -0.01206
110 |  | 75.3308 | 253.6253 | 4187 | 0.00080411 | 6.0879 | 6.0887 | -14.9967 | 1243.6056 | 27971.2038 | -0.012059
111 |  | 75.3308 | 253.6132 | 4187 | 0.00080408 | 6.0887 | 6.0895 | -14.9967 | 1243.6648 | 28224.8171 | -0.012058
112 |  | 75.3308 | 253.6012 | 4187 | 0.00080404 | 6.0895 | 6.0903 | -14.9967 | 1243.7239 | 28478.4183 | -0.012058
113 |  | 75.3308 | 253.5891 | 4187 | 0.000804 | 6.0903 | 6.0911 | -14.9967 | 1243.783 | 28732.0074 | -0.012057
114 |  | 75.3308 | 253.5771 | 4187 | 0.00080396 | 6.0911 | 6.0919 | -14.9967 | 1243.8422 | 28985.5844 | -0.012057
115 |  | 75.3308 | 253.565 | 4187 | 0.00080392 | 6.0919 | 6.0927 | -14.9967 | 1243.9013 | 29239.1495 | -0.012056
116 |  | 75.3308 | 253.553 | 4187 | 0.00080388 | 6.0927 | 6.0935 | -14.9967 | 1243.9605 | 29492.7024 | -0.012056
117 |  | 75.3308 | 253.5409 | 4187 | 0.00080385 | 6.0935 | 6.0943 | -14.9967 | 1244.0196 | 29746.2433 | -0.012055
118 |  | 75.3308 | 253.5288 | 4187 | 0.00080381 | 6.0943 | 6.0951 | -14.9967 | 1244.0788 | 29999.7721 | -0.012054
119 |  | 75.3308 | 253.5168 | 4187 | 0.00080377 | 6.0951 | 6.0959 | -14.9967 | 1244.1379 | 30253.2889 | -0.012054
120 |  | 75.3308 | 253.5047 | 4187 | 0.00080373 | 6.0959 | 6.0967 | -14.9967 | 1244.1971 | 30506.7937 | -0.012053
121 |  | 75.3308 | 253.4927 | 4187 | 0.00080369 | 6.0967 | 6.0975 | -14.9967 | 1244.2562 | 30760.2863 | -0.012053
122 |  | 75.3308 | 253.4806 | 4187 | 0.00080365 | 6.0975 | 6.0983 | -14.9967 | 1244.3154 | 31013.767 | -0.012052
123 |  | 75.3308 | 253.4686 | 4187 | 0.00080362 | 6.0983 | 6.0991 | -14.9967 | 1244.3746 | 31267.2355 | -0.012052
124 |  | 75.3308 | 253.4565 | 4187 | 0.00080358 | 6.0991 | 6.0999 | -14.9967 | 1244.4337 | 31520.6921 | -0.012051
125 |  | 75.3308 | 253.4445 | 4187 | 0.00080354 | 6.0999 | 6.1007 | -14.9967 | 1244.4929 | 31774.1365 | -0.01205
126 |  | 75.3308 | 253.4324 | 4187 | 0.0008035 | 6.1007 | 6.1015 | -14.9967 | 1244.5521 | 32027.569 | -0.01205
127 |  | 75.3308 | 253.4204 | 4187 | 0.00080346 | 6.1015 | 6.1023 | -14.9967 | 1244.6113 | 32280.9893 | -0.012049
128 |  | 75.3308 | 253.4083 | 4187 | 0.00080343 | 6.1023 | 6.1031 | -14.9967 | 1244.6704 | 32534.3977 | -0.012049
129 |  | 75.3308 | 253.3963 | 4187 | 0.00080339 | 6.1031 | 6.104 | -14.9967 | 1244.7296 | 32787.7939 | -0.012048
130 |  | 75.3308 | 253.3842 | 4187 | 0.00080335 | 6.104 | 6.1048 | -14.9967 | 1244.7888 | 33041.1782 | -0.012048
131 |  | 75.3308 | 253.3722 | 4187 | 0.00080331 | 6.1048 | 6.1056 | -14.9967 | 1244.848 | 33294.5503 | -0.012047
132 |  | 75.3308 | 253.3601 | 4187 | 0.00080327 | 6.1056 | 6.1064 | -14.9967 | 1244.9072 | 33547.9105 | -0.012046
133 |  | 75.3308 | 253.3481 | 4187 | 0.00080323 | 6.1064 | 6.1072 | -14.9967 | 1244.9664 | 33801.2586 | -0.012046
134 |  | 75.3308 | 253.336 | 4187 | 0.0008032 | 6.1072 | 6.108 | -14.9967 | 1245.0256 | 34054.5946 | -0.012045
135 |  | 75.3308 | 253.324 | 4187 | 0.00080316 | 6.108 | 6.1088 | -14.9967 | 1245.0848 | 34307.9186 | -0.012045
136 |  | 75.3308 | 253.3119 | 4187 | 0.00080312 | 6.1088 | 6.1096 | -14.9967 | 1245.144 | 34561.2305 | -0.012044
137 |  | 75.3308 | 253.2999 | 4187 | 0.00080308 | 6.1096 | 6.1104 | -14.9967 | 1245.2032 | 34814.5304 | -0.012044
138 |  | 75.3308 | 253.2879 | 4187 | 0.00080304 | 6.1104 | 6.1112 | -14.9967 | 1245.2624 | 35067.8183 | -0.012043
139 |  | 75.3308 | 253.2758 | 4187 | 0.00080301 | 6.1112 | 6.112 | -14.9967 | 1245.3216 | 35321.0941 | -0.012042
140 |  | 75.3308 | 253.2638 | 4187 | 0.00080297 | 6.112 | 6.1128 | -14.9967 | 1245.3808 | 35574.3579 | -0.012042
141 |  | 75.3308 | 253.2517 | 4187 | 0.00080293 | 6.1128 | 6.1136 | -14.9967 | 1245.44 | 35827.6096 | -0.012041
142 |  | 75.3308 | 253.2397 | 4187 | 0.00080289 | 6.1136 | 6.1144 | -14.9967 | 1245.4993 | 36080.8493 | -0.012041
143 |  | 75.3308 | 253.2277 | 4187 | 0.00080285 | 6.1144 | 6.1152 | -14.9967 | 1245.5585 | 36334.077 | -0.01204
144 |  | 75.3308 | 253.2156 | 4187 | 0.00080281 | 6.1152 | 6.116 | -14.9967 | 1245.6177 | 36587.2926 | -0.01204
145 |  | 75.3308 | 253.2036 | 4187 | 0.00080278 | 6.116 | 6.1168 | -14.9967 | 1245.6769 | 36840.4962 | -0.012039
146 |  | 75.3308 | 253.1915 | 4187 | 0.00080274 | 6.1168 | 6.1176 | -14.9967 | 1245.7362 | 37093.6877 | -0.012038
147 |  | 75.3308 | 253.1795 | 4187 | 0.0008027 | 6.1176 | 6.1184 | -14.9967 | 1245.7954 | 37346.8672 | -0.012038
148 |  | 75.3308 | 253.1675 | 4187 | 0.00080266 | 6.1184 | 6.1192 | -14.9967 | 1245.8546 | 37600.0347 | -0.012037
149 |  | 75.3308 | 253.1554 | 4187 | 0.00080262 | 6.1192 | 6.12 | -14.9967 | 1245.9139 | 37853.1901 | -0.012037
150 |  | 75.3308 | 253.1434 | 4187 | 0.00080259 | 6.12 | 6.1208 | -14.9967 | 1245.9731 | 38106.3335 | -0.012036
151 |  | 75.3308 | 253.1313 | 4187 | 0.00080255 | 6.1208 | 6.1216 | -14.9967 | 1246.0324 | 38359.4648 | -0.012036
152 |  | 75.3308 | 253.1193 | 4187 | 0.00080251 | 6.1216 | 6.1224 | -14.9967 | 1246.0916 | 38612.5841 | -0.012035
153 |  | 75.3308 | 253.1073 | 4187 | 0.00080247 | 6.1224 | 6.1232 | -14.9967 | 1246.1509 | 38865.6914 | -0.012034
154 |  | 75.3308 | 253.0952 | 4187 | 0.00080243 | 6.1232 | 6.124 | -14.9967 | 1246.2101 | 39118.7866 | -0.012034
155 |  | 75.3308 | 253.0832 | 4187 | 0.00080239 | 6.124 | 6.1248 | -14.9967 | 1246.2694 | 39371.8698 | -0.012033
156 |  | 75.3308 | 253.0712 | 4187 | 0.00080236 | 6.1248 | 6.1256 | -14.9967 | 1246.3286 | 39624.941 | -0.012033
157 |  | 75.3308 | 253.0591 | 4187 | 0.00080232 | 6.1256 | 6.1264 | -14.9967 | 1246.3879 | 39878.0002 | -0.012032
158 |  | 75.3308 | 253.0471 | 4187 | 0.00080228 | 6.1264 | 6.1272 | -14.9967 | 1246.4472 | 40131.0473 | -0.012032
159 |  | 75.3308 | 253.0351 | 4187 | 0.00080224 | 6.1272 | 6.128 | -14.9967 | 1246.5064 | 40384.0824 | -0.012031
160 |  | 75.3308 | 253.023 | 4187 | 0.0008022 | 6.128 | 6.1288 | -14.9967 | 1246.5657 | 40637.1054 | -0.01203
161 |  | 75.3308 | 253.011 | 4187 | 0.00080217 | 6.1288 | 6.1296 | -14.9967 | 1246.625 | 40890.1164 | -0.01203
162 |  | 75.3308 | 252.999 | 4187 | 0.00080213 | 6.1296 | 6.1304 | -14.9967 | 1246.6842 | 41143.1154 | -0.012029
163 |  | 75.3308 | 252.987 | 4187 | 0.00080209 | 6.1304 | 6.1312 | -14.9967 | 1246.7435 | 41396.1024 | -0.012029
164 |  | 75.3308 | 252.9749 | 4187 | 0.00080205 | 6.1312 | 6.132 | -14.9967 | 1246.8028 | 41649.0773 | -0.012028
165 |  | 75.3308 | 252.9629 | 4187 | 0.00080201 | 6.132 | 6.1328 | -14.9967 | 1246.8621 | 41902.0402 | -0.012028
166 |  | 75.3308 | 252.9509 | 4187 | 0.00080198 | 6.1328 | 6.1337 | -14.9967 | 1246.9214 | 42154.9911 | -0.012027
167 |  | 75.3308 | 252.9388 | 4187 | 0.00080194 | 6.1337 | 6.1345 | -14.9967 | 1246.9807 | 42407.9299 | -0.012026
168 |  | 75.3308 | 252.9268 | 4187 | 0.0008019 | 6.1345 | 6.1353 | -14.9967 | 1247.0399 | 42660.8567 | -0.012026
169 |  | 75.3308 | 252.9148 | 4187 | 0.00080186 | 6.1353 | 6.1361 | -14.9967 | 1247.0992 | 42913.7715 | -0.012025
170 |  | 75.3308 | 252.9028 | 4187 | 0.00080182 | 6.1361 | 6.1369 | -14.9967 | 1247.1585 | 43166.6743 | -0.012025
171 |  | 75.3308 | 252.8907 | 4187 | 0.00080178 | 6.1369 | 6.1377 | -14.9967 | 1247.2178 | 43419.5651 | -0.012024
172 |  | 75.3308 | 252.8787 | 4187 | 0.00080175 | 6.1377 | 6.1385 | -14.9967 | 1247.2771 | 43672.4438 | -0.012024
173 |  | 75.3308 | 252.8667 | 4187 | 0.00080171 | 6.1385 | 6.1393 | -14.9967 | 1247.3365 | 43925.3105 | -0.012023
174 |  | 75.3308 | 252.8547 | 4187 | 0.00080167 | 6.1393 | 6.1401 | -14.9967 | 1247.3958 | 44178.1652 | -0.012022
175 |  | 75.3308 | 252.8427 | 4187 | 0.00080163 | 6.1401 | 6.1409 | -14.9967 | 1247.4551 | 44431.0078 | -0.012022
176 |  | 75.3308 | 252.8306 | 4187 | 0.00080159 | 6.1409 | 6.1417 | -14.9967 | 1247.5144 | 44683.8384 | -0.012021
177 |  | 75.3308 | 252.8186 | 4187 | 0.00080156 | 6.1417 | 6.1425 | -14.9967 | 1247.5737 | 44936.657 | -0.012021
178 |  | 75.3308 | 252.8066 | 4187 | 0.00080152 | 6.1425 | 6.1433 | -14.9967 | 1247.633 | 45189.4636 | -0.01202
179 |  | 75.3308 | 252.7946 | 4187 | 0.00080148 | 6.1433 | 6.1441 | -14.9967 | 1247.6924 | 45442.2582 | -0.01202
180 |  | 75.3308 | 252.7825 | 4187 | 0.00080144 | 6.1441 | 6.1449 | -14.9967 | 1247.7517 | 45695.0408 | -0.012019
181 |  | 75.3308 | 252.7705 | 4187 | 0.0008014 | 6.1449 | 6.1457 | -14.9967 | 1247.811 | 45947.8113 | -0.012018
182 |  | 75.3308 | 252.7585 | 4187 | 0.00080137 | 6.1457 | 6.1465 | -14.9967 | 1247.8703 | 46200.5698 | -0.012018
183 |  | 75.3308 | 252.7465 | 4187 | 0.00080133 | 6.1465 | 6.1473 | -14.9967 | 1247.9297 | 46453.3163 | -0.012017
184 |  | 75.3308 | 252.7345 | 4187 | 0.00080129 | 6.1473 | 6.1481 | -14.9967 | 1247.989 | 46706.0508 | -0.012017
185 |  | 75.3308 | 252.7225 | 4187 | 0.00080125 | 6.1481 | 6.1489 | -14.9967 | 1248.0484 | 46958.7732 | -0.012016
186 |  | 75.3308 | 252.7104 | 4187 | 0.00080121 | 6.1489 | 6.1497 | -14.9967 | 1248.1077 | 47211.4837 | -0.012016
187 |  | 75.3308 | 252.6984 | 4187 | 0.00080117 | 6.1497 | 6.1505 | -14.9967 | 1248.167 | 47464.1821 | -0.012015
188 |  | 75.3308 | 252.6864 | 4187 | 0.00080114 | 6.1505 | 6.1513 | -14.9967 | 1248.2264 | 47716.8685 | -0.012014
189 |  | 75.3308 | 252.6744 | 4187 | 0.0008011 | 6.1513 | 6.1521 | -14.9967 | 1248.2857 | 47969.5429 | -0.012014
190 |  | 75.3308 | 252.6624 | 4187 | 0.00080106 | 6.1521 | 6.1529 | -14.9967 | 1248.3451 | 48222.2053 | -0.012013
191 |  | 75.3308 | 252.6504 | 4187 | 0.00080102 | 6.1529 | 6.1537 | -14.9967 | 1248.4045 | 48474.8557 | -0.012013
192 |  | 75.3308 | 252.6384 | 4187 | 0.00080098 | 6.1537 | 6.1545 | -14.9967 | 1248.4638 | 48727.494 | -0.012012
193 |  | 75.3308 | 252.6263 | 4187 | 0.00080095 | 6.1545 | 6.1553 | -14.9967 | 1248.5232 | 48980.1204 | -0.012012
194 |  | 75.3308 | 252.6143 | 4187 | 0.00080091 | 6.1553 | 6.1561 | -14.9967 | 1248.5825 | 49232.7347 | -0.012011
195 |  | 75.3308 | 252.6023 | 4187 | 0.00080087 | 6.1561 | 6.1569 | -14.9967 | 1248.6419 | 49485.337 | -0.01201
196 |  | 75.3308 | 252.5903 | 4187 | 0.00080083 | 6.1569 | 6.1577 | -14.9967 | 1248.7013 | 49737.9274 | -0.01201
197 |  | 75.3308 | 252.5783 | 4187 | 0.00080079 | 6.1577 | 6.1585 | -14.9967 | 1248.7607 | 49990.5057 | -0.012009
198 |  | 75.3308 | 252.5663 | 4187 | 0.00080076 | 6.1585 | 6.1593 | -14.9967 | 1248.82 | 50243.072 | -0.012009
199 |  | 75.3308 | 252.5543 | 4187 | 0.00080072 | 6.1593 | 6.1601 | -14.9967 | 1248.8794 | 50495.6262 | -0.012008
200 |  | 75.3308 | 252.5423 | 4187 | 0.00080068 | 6.1601 | 6.1609 | -14.9967 | 1248.9388 | 50748.1685 | -0.012008
201 |  | 75.3308 | 252.5303 | 4187 | 0.00080064 | 6.1609 | 6.1617 | -14.9967 | 1248.9982 | 51000.6988 | -0.012007
202 |  | 75.3308 | 252.5183 | 4187 | 0.0008006 | 6.1617 | 6.1625 | -14.9967 | 1249.0576 | 51253.2171 | -0.012006
203 |  | 75.3308 | 252.5063 | 4187 | 0.00080057 | 6.1625 | 6.1633 | -14.9967 | 1249.117 | 51505.7233 | -0.012006
204 |  | 75.3308 | 252.4943 | 4187 | 0.00080053 | 6.1633 | 6.1641 | -14.9967 | 1249.1764 | 51758.2176 | -0.012005
205 |  | 75.3308 | 252.4822 | 4187 | 0.00080049 | 6.1641 | 6.1649 | -14.9967 | 1249.2358 | 52010.6998 | -0.012005
206 |  | 75.3308 | 252.4702 | 4187 | 0.00080045 | 6.1649 | 6.1657 | -14.9967 | 1249.2952 | 52263.1701 | -0.012004
207 |  | 75.3308 | 252.4582 | 4187 | 0.00080041 | 6.1657 | 6.1665 | -14.9967 | 1249.3546 | 52515.6283 | -0.012004
208 |  | 75.3308 | 252.4462 | 4187 | 0.00080038 | 6.1665 | 6.1673 | -14.9967 | 1249.414 | 52768.0745 | -0.012003
209 |  | 75.3308 | 252.4342 | 4187 | 0.00080034 | 6.1673 | 6.1681 | -14.9967 | 1249.4734 | 53020.5088 | -0.012002
210 |  | 75.3308 | 252.4222 | 4187 | 0.0008003 | 6.1681 | 6.1689 | -14.9967 | 1249.5328 | 53272.931 | -0.012002
211 |  | 75.3308 | 252.4102 | 4187 | 0.00080026 | 6.1689 | 6.1697 | -14.9967 | 1249.5922 | 53525.3412 | -0.012001
212 |  | 75.3308 | 252.3982 | 4187 | 0.00080022 | 6.1697 | 6.1705 | -14.9967 | 1249.6516 | 53777.7395 | -0.012001
213 |  | 75.3308 | 252.3862 | 4187 | 0.00080018 | 6.1705 | 6.1713 | -14.9967 | 1249.711 | 54030.1257 | -0.012
214 |  | 75.3308 | 252.3742 | 4187 | 0.00080015 | 6.1713 | 6.1721 | -14.9967 | 1249.7705 | 54282.4999 | -0.012
215 |  | 75.3308 | 252.3622 | 4187 | 0.00080011 | 6.1721 | 6.1729 | -14.9967 | 1249.8299 | 54534.8621 | -0.011999
216 |  | 75.3308 | 252.3502 | 4187 | 0.00080007 | 6.1729 | 6.1737 | -14.9967 | 1249.8893 | 54787.2124 | -0.011998
217 |  | 75.3308 | 252.3382 | 4187 | 0.00080003 | 6.1737 | 6.1745 | -14.9967 | 1249.9487 | 55039.5506 | -0.011998
218 |  | 75.3308 | 252.3262 | 4187 | 0.00079999 | 6.1745 | 6.1753 | -14.9967 | 1250.0082 | 55291.8768 | -0.011997
219 |  | 75.3308 | 252.3142 | 4187 | 0.00079996 | 6.1753 | 6.1761 | -14.9967 | 1250.0676 | 55544.1911 | -0.011997
220 |  | 75.3308 | 252.3022 | 4187 | 0.00079992 | 6.1761 | 6.1769 | -14.9967 | 1250.127 | 55796.4933 | -0.011996
221 |  | 75.3308 | 252.2902 | 4187 | 0.00079988 | 6.1769 | 6.1777 | -14.9967 | 1250.1865 | 56048.7835 | -0.011996
222 |  | 75.3308 | 252.2782 | 4187 | 0.00079984 | 6.1777 | 6.1785 | -14.9967 | 1250.2459 | 56301.0618 | -0.011995
223 |  | 75.3308 | 252.2663 | 4187 | 0.0007998 | 6.1785 | 6.1793 | -14.9967 | 1250.3054 | 56553.328 | -0.011994
224 |  | 75.3308 | 252.2543 | 4187 | 0.00079977 | 6.1793 | 6.1801 | -14.9967 | 1250.3648 | 56805.5823 | -0.011994
225 |  | 75.3308 | 252.2423 | 4187 | 0.00079973 | 6.1801 | 6.1809 | -14.9967 | 1250.4243 | 57057.8245 | -0.011993
226 |  | 75.3308 | 252.2303 | 4187 | 0.00079969 | 6.1809 | 6.1817 | -14.9967 | 1250.4837 | 57310.0548 | -0.011993
227 |  | 75.3308 | 252.2183 | 4187 | 0.00079965 | 6.1817 | 6.1825 | -14.9967 | 1250.5432 | 57562.2731 | -0.011992
228 |  | 75.3308 | 252.2063 | 4187 | 0.00079961 | 6.1825 | 6.1833 | -14.9967 | 1250.6027 | 57814.4794 | -0.011992
229 |  | 75.3308 | 252.1943 | 4187 | 0.00079958 | 6.1833 | 6.1841 | -14.9967 | 1250.6621 | 58066.6737 | -0.011991
230 |  | 75.3308 | 252.1823 | 4187 | 0.00079954 | 6.1841 | 6.1849 | -14.9967 | 1250.7216 | 58318.856 | -0.01199
231 |  | 75.3308 | 252.1703 | 4187 | 0.0007995 | 6.1849 | 6.1857 | -14.9967 | 1250.7811 | 58571.0263 | -0.01199
232 |  | 75.3308 | 252.1583 | 4187 | 0.00079946 | 6.1857 | 6.1865 | -14.9967 | 1250.8405 | 58823.1846 | -0.011989
233 |  | 75.3308 | 252.1463 | 4187 | 0.00079942 | 6.1865 | 6.1873 | -14.9967 | 1250.9 | 59075.3309 | -0.011989
234 |  | 75.3308 | 252.1343 | 4187 | 0.00079939 | 6.1873 | 6.1881 | -14.9967 | 1250.9595 | 59327.4653 | -0.011988
235 |  | 75.3308 | 252.1224 | 4187 | 0.00079935 | 6.1881 | 6.1889 | -14.9967 | 1251.019 | 59579.5876 | -0.011988
236 |  | 75.3308 | 252.1104 | 4187 | 0.00079931 | 6.1889 | 6.1897 | -14.9967 | 1251.0785 | 59831.698 | -0.011987

## St355
|  |  | buis | verlies W/M | L /°C/sec
diam | wandikte |  | inhoud l/m |  | W/M
355.6 | 8 | 3.1416 | 90.5785 | 279.8172 | 4187
[8 empty] | J/sec/mtr | aantal mtr. | verlies
|  | buis | verlies W/M | L /°C/sec | verlies temp | begintemp | eindtemp | verlies | bij 1°C | totaal J/sec
|  | inhoud L |  | W/M | °C per M | °C | °C | per m°C | daling | aantal mtr
1 | 355.6 | 90.5785 | 279.8172 | 4187 | 0.00073781 | 6 | 6.0007 | -16.4598 | 1355.3575 | 279.8172 | -0.012144
2 |  | 90.5785 | 279.805 | 4187 | 0.00073778 | 6.0007 | 6.0015 | -16.4598 | 1355.4163 | 559.6222 | -0.012144
3 |  | 90.5785 | 279.7929 | 4187 | 0.00073775 | 6.0015 | 6.0022 | -16.4598 | 1355.4751 | 839.4151 | -0.012143
4 |  | 90.5785 | 279.7807 | 4187 | 0.00073772 | 6.0022 | 6.003 | -16.4598 | 1355.534 | 1119.1958 | -0.012143
5 |  | 90.5785 | 279.7686 | 4187 | 0.00073768 | 6.003 | 6.0037 | -16.4598 | 1355.5928 | 1398.9644 | -0.012142
6 |  | 90.5785 | 279.7564 | 4187 | 0.00073765 | 6.0037 | 6.0044 | -16.4598 | 1355.6516 | 1678.7208 | -0.012142
7 |  | 90.5785 | 279.7443 | 4187 | 0.00073762 | 6.0044 | 6.0052 | -16.4598 | 1355.7105 | 1958.4651 | -0.012141
8 |  | 90.5785 | 279.7322 | 4187 | 0.00073759 | 6.0052 | 6.0059 | -16.4598 | 1355.7693 | 2238.1973 | -0.012141
9 |  | 90.5785 | 279.72 | 4187 | 0.00073756 | 6.0059 | 6.0066 | -16.4598 | 1355.8282 | 2517.9173 | -0.01214
10 |  | 90.5785 | 279.7079 | 4187 | 0.00073752 | 6.0066 | 6.0074 | -16.4598 | 1355.887 | 2797.6252 | -0.01214
11 |  | 90.5785 | 279.6957 | 4187 | 0.00073749 | 6.0074 | 6.0081 | -16.4598 | 1355.9458 | 3077.321 | -0.012139
12 |  | 90.5785 | 279.6836 | 4187 | 0.00073746 | 6.0081 | 6.0089 | -16.4598 | 1356.0047 | 3357.0046 | -0.012138
13 |  | 90.5785 | 279.6715 | 4187 | 0.00073743 | 6.0089 | 6.0096 | -16.4598 | 1356.0636 | 3636.676 | -0.012138
14 |  | 90.5785 | 279.6593 | 4187 | 0.0007374 | 6.0096 | 6.0103 | -16.4598 | 1356.1224 | 3916.3354 | -0.012137
15 |  | 90.5785 | 279.6472 | 4187 | 0.00073736 | 6.0103 | 6.0111 | -16.4598 | 1356.1813 | 4195.9826 | -0.012137
16 |  | 90.5785 | 279.6351 | 4187 | 0.00073733 | 6.0111 | 6.0118 | -16.4598 | 1356.2401 | 4475.6176 | -0.012136
17 |  | 90.5785 | 279.6229 | 4187 | 0.0007373 | 6.0118 | 6.0125 | -16.4598 | 1356.299 | 4755.2405 | -0.012136
18 |  | 90.5785 | 279.6108 | 4187 | 0.00073727 | 6.0125 | 6.0133 | -16.4598 | 1356.3579 | 5034.8513 | -0.012135
19 |  | 90.5785 | 279.5986 | 4187 | 0.00073724 | 6.0133 | 6.014 | -16.4598 | 1356.4167 | 5314.45 | -0.012135
20 |  | 90.5785 | 279.5865 | 4187 | 0.0007372 | 6.014 | 6.0148 | -16.4598 | 1356.4756 | 5594.0365 | -0.012134
21 |  | 90.5785 | 279.5744 | 4187 | 0.00073717 | 6.0148 | 6.0155 | -16.4598 | 1356.5345 | 5873.6109 | -0.012134
22 |  | 90.5785 | 279.5622 | 4187 | 0.00073714 | 6.0155 | 6.0162 | -16.4598 | 1356.5934 | 6153.1731 | -0.012133
23 |  | 90.5785 | 279.5501 | 4187 | 0.00073711 | 6.0162 | 6.017 | -16.4598 | 1356.6522 | 6432.7232 | -0.012133
24 |  | 90.5785 | 279.538 | 4187 | 0.00073708 | 6.017 | 6.0177 | -16.4598 | 1356.7111 | 6712.2612 | -0.012132
25 |  | 90.5785 | 279.5258 | 4187 | 0.00073704 | 6.0177 | 6.0184 | -16.4598 | 1356.77 | 6991.787 | -0.012132
26 |  | 90.5785 | 279.5137 | 4187 | 0.00073701 | 6.0184 | 6.0192 | -16.4598 | 1356.8289 | 7271.3007 | -0.012131
27 |  | 90.5785 | 279.5016 | 4187 | 0.00073698 | 6.0192 | 6.0199 | -16.4598 | 1356.8878 | 7550.8023 | -0.012131
28 |  | 90.5785 | 279.4895 | 4187 | 0.00073695 | 6.0199 | 6.0206 | -16.4598 | 1356.9467 | 7830.2918 | -0.01213
29 |  | 90.5785 | 279.4773 | 4187 | 0.00073692 | 6.0206 | 6.0214 | -16.4598 | 1357.0056 | 8109.7691 | -0.01213
30 |  | 90.5785 | 279.4652 | 4187 | 0.00073688 | 6.0214 | 6.0221 | -16.4598 | 1357.0645 | 8389.2343 | -0.012129
31 |  | 90.5785 | 279.4531 | 4187 | 0.00073685 | 6.0221 | 6.0229 | -16.4598 | 1357.1234 | 8668.6874 | -0.012128
32 |  | 90.5785 | 279.4409 | 4187 | 0.00073682 | 6.0229 | 6.0236 | -16.4598 | 1357.1823 | 8948.1283 | -0.012128
33 |  | 90.5785 | 279.4288 | 4187 | 0.00073679 | 6.0236 | 6.0243 | -16.4598 | 1357.2412 | 9227.5571 | -0.012127
34 |  | 90.5785 | 279.4167 | 4187 | 0.00073676 | 6.0243 | 6.0251 | -16.4598 | 1357.3001 | 9506.9738 | -0.012127
35 |  | 90.5785 | 279.4046 | 4187 | 0.00073672 | 6.0251 | 6.0258 | -16.4598 | 1357.359 | 9786.3784 | -0.012126
36 |  | 90.5785 | 279.3924 | 4187 | 0.00073669 | 6.0258 | 6.0265 | -16.4598 | 1357.4179 | 10065.7708 | -0.012126
37 |  | 90.5785 | 279.3803 | 4187 | 0.00073666 | 6.0265 | 6.0273 | -16.4598 | 1357.4768 | 10345.1511 | -0.012125
38 |  | 90.5785 | 279.3682 | 4187 | 0.00073663 | 6.0273 | 6.028 | -16.4598 | 1357.5357 | 10624.5193 | -0.012125
39 |  | 90.5785 | 279.3561 | 4187 | 0.0007366 | 6.028 | 6.0288 | -16.4598 | 1357.5947 | 10903.8753 | -0.012124
40 |  | 90.5785 | 279.3439 | 4187 | 0.00073656 | 6.0288 | 6.0295 | -16.4598 | 1357.6536 | 11183.2192 | -0.012124
41 |  | 90.5785 | 279.3318 | 4187 | 0.00073653 | 6.0295 | 6.0302 | -16.4598 | 1357.7125 | 11462.551 | -0.012123
42 |  | 90.5785 | 279.3197 | 4187 | 0.0007365 | 6.0302 | 6.031 | -16.4598 | 1357.7714 | 11741.8707 | -0.012123
43 |  | 90.5785 | 279.3076 | 4187 | 0.00073647 | 6.031 | 6.0317 | -16.4598 | 1357.8304 | 12021.1783 | -0.012122
44 |  | 90.5785 | 279.2954 | 4187 | 0.00073644 | 6.0317 | 6.0324 | -16.4598 | 1357.8893 | 12300.4737 | -0.012122
45 |  | 90.5785 | 279.2833 | 4187 | 0.00073641 | 6.0324 | 6.0332 | -16.4598 | 1357.9482 | 12579.757 | -0.012121
46 |  | 90.5785 | 279.2712 | 4187 | 0.00073637 | 6.0332 | 6.0339 | -16.4598 | 1358.0072 | 12859.0282 | -0.012121
47 |  | 90.5785 | 279.2591 | 4187 | 0.00073634 | 6.0339 | 6.0346 | -16.4598 | 1358.0661 | 13138.2873 | -0.01212
48 |  | 90.5785 | 279.247 | 4187 | 0.00073631 | 6.0346 | 6.0354 | -16.4598 | 1358.1251 | 13417.5343 | -0.01212
49 |  | 90.5785 | 279.2348 | 4187 | 0.00073628 | 6.0354 | 6.0361 | -16.4598 | 1358.184 | 13696.7691 | -0.012119
50 |  | 90.5785 | 279.2227 | 4187 | 0.00073625 | 6.0361 | 6.0369 | -16.4598 | 1358.243 | 13975.9918 | -0.012118
51 |  | 90.5785 | 279.2106 | 4187 | 0.00073621 | 6.0369 | 6.0376 | -16.4598 | 1358.3019 | 14255.2024 | -0.012118
52 |  | 90.5785 | 279.1985 | 4187 | 0.00073618 | 6.0376 | 6.0383 | -16.4598 | 1358.3609 | 14534.4009 | -0.012117
53 |  | 90.5785 | 279.1864 | 4187 | 0.00073615 | 6.0383 | 6.0391 | -16.4598 | 1358.4198 | 14813.5872 | -0.012117
54 |  | 90.5785 | 279.1742 | 4187 | 0.00073612 | 6.0391 | 6.0398 | -16.4598 | 1358.4788 | 15092.7615 | -0.012116
55 |  | 90.5785 | 279.1621 | 4187 | 0.00073609 | 6.0398 | 6.0405 | -16.4598 | 1358.5377 | 15371.9236 | -0.012116
56 |  | 90.5785 | 279.15 | 4187 | 0.00073605 | 6.0405 | 6.0413 | -16.4598 | 1358.5967 | 15651.0736 | -0.012115
57 |  | 90.5785 | 279.1379 | 4187 | 0.00073602 | 6.0413 | 6.042 | -16.4598 | 1358.6557 | 15930.2115 | -0.012115
58 |  | 90.5785 | 279.1258 | 4187 | 0.00073599 | 6.042 | 6.0427 | -16.4598 | 1358.7146 | 16209.3373 | -0.012114
59 |  | 90.5785 | 279.1137 | 4187 | 0.00073596 | 6.0427 | 6.0435 | -16.4598 | 1358.7736 | 16488.451 | -0.012114
60 |  | 90.5785 | 279.1016 | 4187 | 0.00073593 | 6.0435 | 6.0442 | -16.4598 | 1358.8326 | 16767.5525 | -0.012113
61 |  | 90.5785 | 279.0894 | 4187 | 0.00073589 | 6.0442 | 6.0449 | -16.4598 | 1358.8916 | 17046.642 | -0.012113
62 |  | 90.5785 | 279.0773 | 4187 | 0.00073586 | 6.0449 | 6.0457 | -16.4598 | 1358.9505 | 17325.7193 | -0.012112
63 |  | 90.5785 | 279.0652 | 4187 | 0.00073583 | 6.0457 | 6.0464 | -16.4598 | 1359.0095 | 17604.7845 | -0.012112
64 |  | 90.5785 | 279.0531 | 4187 | 0.0007358 | 6.0464 | 6.0472 | -16.4598 | 1359.0685 | 17883.8376 | -0.012111
65 |  | 90.5785 | 279.041 | 4187 | 0.00073577 | 6.0472 | 6.0479 | -16.4598 | 1359.1275 | 18162.8786 | -0.012111
66 |  | 90.5785 | 279.0289 | 4187 | 0.00073573 | 6.0479 | 6.0486 | -16.4598 | 1359.1865 | 18441.9075 | -0.01211
67 |  | 90.5785 | 279.0168 | 4187 | 0.0007357 | 6.0486 | 6.0494 | -16.4598 | 1359.2455 | 18720.9242 | -0.01211
68 |  | 90.5785 | 279.0047 | 4187 | 0.00073567 | 6.0494 | 6.0501 | -16.4598 | 1359.3045 | 18999.9289 | -0.012109
69 |  | 90.5785 | 278.9926 | 4187 | 0.00073564 | 6.0501 | 6.0508 | -16.4598 | 1359.3635 | 19278.9215 | -0.012108
70 |  | 90.5785 | 278.9804 | 4187 | 0.00073561 | 6.0508 | 6.0516 | -16.4598 | 1359.4225 | 19557.9019 | -0.012108
71 |  | 90.5785 | 278.9683 | 4187 | 0.00073557 | 6.0516 | 6.0523 | -16.4598 | 1359.4815 | 19836.8702 | -0.012107
72 |  | 90.5785 | 278.9562 | 4187 | 0.00073554 | 6.0523 | 6.053 | -16.4598 | 1359.5405 | 20115.8265 | -0.012107
73 |  | 90.5785 | 278.9441 | 4187 | 0.00073551 | 6.053 | 6.0538 | -16.4598 | 1359.5995 | 20394.7706 | -0.012106
74 |  | 90.5785 | 278.932 | 4187 | 0.00073548 | 6.0538 | 6.0545 | -16.4598 | 1359.6585 | 20673.7026 | -0.012106
75 |  | 90.5785 | 278.9199 | 4187 | 0.00073545 | 6.0545 | 6.0552 | -16.4598 | 1359.7175 | 20952.6225 | -0.012105
76 |  | 90.5785 | 278.9078 | 4187 | 0.00073541 | 6.0552 | 6.056 | -16.4598 | 1359.7765 | 21231.5303 | -0.012105
77 |  | 90.5785 | 278.8957 | 4187 | 0.00073538 | 6.056 | 6.0567 | -16.4598 | 1359.8355 | 21510.426 | -0.012104
78 |  | 90.5785 | 278.8836 | 4187 | 0.00073535 | 6.0567 | 6.0575 | -16.4598 | 1359.8946 | 21789.3096 | -0.012104
79 |  | 90.5785 | 278.8715 | 4187 | 0.00073532 | 6.0575 | 6.0582 | -16.4598 | 1359.9536 | 22068.1811 | -0.012103
80 |  | 90.5785 | 278.8594 | 4187 | 0.00073529 | 6.0582 | 6.0589 | -16.4598 | 1360.0126 | 22347.0405 | -0.012103
81 |  | 90.5785 | 278.8473 | 4187 | 0.00073526 | 6.0589 | 6.0597 | -16.4598 | 1360.0716 | 22625.8878 | -0.012102
82 |  | 90.5785 | 278.8352 | 4187 | 0.00073522 | 6.0597 | 6.0604 | -16.4598 | 1360.1307 | 22904.723 | -0.012102
83 |  | 90.5785 | 278.8231 | 4187 | 0.00073519 | 6.0604 | 6.0611 | -16.4598 | 1360.1897 | 23183.546 | -0.012101
84 |  | 90.5785 | 278.811 | 4187 | 0.00073516 | 6.0611 | 6.0619 | -16.4598 | 1360.2487 | 23462.357 | -0.012101
85 |  | 90.5785 | 278.7989 | 4187 | 0.00073513 | 6.0619 | 6.0626 | -16.4598 | 1360.3078 | 23741.1559 | -0.0121
86 |  | 90.5785 | 278.7868 | 4187 | 0.0007351 | 6.0626 | 6.0633 | -16.4598 | 1360.3668 | 24019.9427 | -0.0121
87 |  | 90.5785 | 278.7747 | 4187 | 0.00073506 | 6.0633 | 6.0641 | -16.4598 | 1360.4259 | 24298.7174 | -0.012099
88 |  | 90.5785 | 278.7626 | 4187 | 0.00073503 | 6.0641 | 6.0648 | -16.4598 | 1360.4849 | 24577.48 | -0.012099
89 |  | 90.5785 | 278.7505 | 4187 | 0.000735 | 6.0648 | 6.0655 | -16.4598 | 1360.544 | 24856.2304 | -0.012098
90 |  | 90.5785 | 278.7384 | 4187 | 0.00073497 | 6.0655 | 6.0663 | -16.4598 | 1360.603 | 25134.9688 | -0.012097
91 |  | 90.5785 | 278.7263 | 4187 | 0.00073494 | 6.0663 | 6.067 | -16.4598 | 1360.6621 | 25413.6951 | -0.012097
92 |  | 90.5785 | 278.7142 | 4187 | 0.0007349 | 6.067 | 6.0677 | -16.4598 | 1360.7211 | 25692.4093 | -0.012096
93 |  | 90.5785 | 278.7021 | 4187 | 0.00073487 | 6.0677 | 6.0685 | -16.4598 | 1360.7802 | 25971.1114 | -0.012096
94 |  | 90.5785 | 278.69 | 4187 | 0.00073484 | 6.0685 | 6.0692 | -16.4598 | 1360.8392 | 26249.8014 | -0.012095
95 |  | 90.5785 | 278.6779 | 4187 | 0.00073481 | 6.0692 | 6.0699 | -16.4598 | 1360.8983 | 26528.4793 | -0.012095
96 |  | 90.5785 | 278.6658 | 4187 | 0.00073478 | 6.0699 | 6.0707 | -16.4598 | 1360.9574 | 26807.1451 | -0.012094
97 |  | 90.5785 | 278.6537 | 4187 | 0.00073474 | 6.0707 | 6.0714 | -16.4598 | 1361.0164 | 27085.7988 | -0.012094
98 |  | 90.5785 | 278.6416 | 4187 | 0.00073471 | 6.0714 | 6.0722 | -16.4598 | 1361.0755 | 27364.4404 | -0.012093
99 |  | 90.5785 | 278.6295 | 4187 | 0.00073468 | 6.0722 | 6.0729 | -16.4598 | 1361.1346 | 27643.07 | -0.012093
100 |  | 90.5785 | 278.6174 | 4187 | 0.00073465 | 6.0729 | 6.0736 | -16.4598 | 1361.1937 | 27921.6874 | -0.012092
101 |  | 90.5785 | 278.6053 | 4187 | 0.00073462 | 6.0736 | 6.0744 | -16.4598 | 1361.2527 | 28200.2927 | -0.012092
102 |  | 90.5785 | 278.5933 | 4187 | 0.00073459 | 6.0744 | 6.0751 | -16.4598 | 1361.3118 | 28478.886 | -0.012091
103 |  | 90.5785 | 278.5812 | 4187 | 0.00073455 | 6.0751 | 6.0758 | -16.4598 | 1361.3709 | 28757.4672 | -0.012091
104 |  | 90.5785 | 278.5691 | 4187 | 0.00073452 | 6.0758 | 6.0766 | -16.4598 | 1361.43 | 29036.0362 | -0.01209
105 |  | 90.5785 | 278.557 | 4187 | 0.00073449 | 6.0766 | 6.0773 | -16.4598 | 1361.4891 | 29314.5932 | -0.01209
106 |  | 90.5785 | 278.5449 | 4187 | 0.00073446 | 6.0773 | 6.078 | -16.4598 | 1361.5482 | 29593.1381 | -0.012089
107 |  | 90.5785 | 278.5328 | 4187 | 0.00073443 | 6.078 | 6.0788 | -16.4598 | 1361.6073 | 29871.6709 | -0.012089
108 |  | 90.5785 | 278.5207 | 4187 | 0.00073439 | 6.0788 | 6.0795 | -16.4598 | 1361.6664 | 30150.1916 | -0.012088
109 |  | 90.5785 | 278.5086 | 4187 | 0.00073436 | 6.0795 | 6.0802 | -16.4598 | 1361.7255 | 30428.7002 | -0.012087
110 |  | 90.5785 | 278.4965 | 4187 | 0.00073433 | 6.0802 | 6.081 | -16.4598 | 1361.7846 | 30707.1968 | -0.012087
111 |  | 90.5785 | 278.4844 | 4187 | 0.0007343 | 6.081 | 6.0817 | -16.4598 | 1361.8437 | 30985.6812 | -0.012086
112 |  | 90.5785 | 278.4724 | 4187 | 0.00073427 | 6.0817 | 6.0824 | -16.4598 | 1361.9028 | 31264.1536 | -0.012086
113 |  | 90.5785 | 278.4603 | 4187 | 0.00073423 | 6.0824 | 6.0832 | -16.4598 | 1361.9619 | 31542.6138 | -0.012085
114 |  | 90.5785 | 278.4482 | 4187 | 0.0007342 | 6.0832 | 6.0839 | -16.4598 | 1362.021 | 31821.062 | -0.012085
115 |  | 90.5785 | 278.4361 | 4187 | 0.00073417 | 6.0839 | 6.0846 | -16.4598 | 1362.0801 | 32099.4981 | -0.012084
116 |  | 90.5785 | 278.424 | 4187 | 0.00073414 | 6.0846 | 6.0854 | -16.4598 | 1362.1392 | 32377.9222 | -0.012084
117 |  | 90.5785 | 278.4119 | 4187 | 0.00073411 | 6.0854 | 6.0861 | -16.4598 | 1362.1984 | 32656.3341 | -0.012083
118 |  | 90.5785 | 278.3999 | 4187 | 0.00073408 | 6.0861 | 6.0868 | -16.4598 | 1362.2575 | 32934.734 | -0.012083
119 |  | 90.5785 | 278.3878 | 4187 | 0.00073404 | 6.0868 | 6.0876 | -16.4598 | 1362.3166 | 33213.1217 | -0.012082
120 |  | 90.5785 | 278.3757 | 4187 | 0.00073401 | 6.0876 | 6.0883 | -16.4598 | 1362.3757 | 33491.4974 | -0.012082
121 |  | 90.5785 | 278.3636 | 4187 | 0.00073398 | 6.0883 | 6.089 | -16.4598 | 1362.4349 | 33769.861 | -0.012081
122 |  | 90.5785 | 278.3515 | 4187 | 0.00073395 | 6.089 | 6.0898 | -16.4598 | 1362.494 | 34048.2126 | -0.012081
123 |  | 90.5785 | 278.3394 | 4187 | 0.00073392 | 6.0898 | 6.0905 | -16.4598 | 1362.5531 | 34326.552 | -0.01208
124 |  | 90.5785 | 278.3274 | 4187 | 0.00073388 | 6.0905 | 6.0912 | -16.4598 | 1362.6123 | 34604.8794 | -0.01208
125 |  | 90.5785 | 278.3153 | 4187 | 0.00073385 | 6.0912 | 6.092 | -16.4598 | 1362.6714 | 34883.1947 | -0.012079
126 |  | 90.5785 | 278.3032 | 4187 | 0.00073382 | 6.092 | 6.0927 | -16.4598 | 1362.7306 | 35161.4979 | -0.012079
127 |  | 90.5785 | 278.2911 | 4187 | 0.00073379 | 6.0927 | 6.0934 | -16.4598 | 1362.7897 | 35439.789 | -0.012078
128 |  | 90.5785 | 278.2791 | 4187 | 0.00073376 | 6.0934 | 6.0942 | -16.4598 | 1362.8489 | 35718.068 | -0.012078
129 |  | 90.5785 | 278.267 | 4187 | 0.00073373 | 6.0942 | 6.0949 | -16.4598 | 1362.908 | 35996.335 | -0.012077
130 |  | 90.5785 | 278.2549 | 4187 | 0.00073369 | 6.0949 | 6.0956 | -16.4598 | 1362.9672 | 36274.5899 | -0.012076
131 |  | 90.5785 | 278.2428 | 4187 | 0.00073366 | 6.0956 | 6.0964 | -16.4598 | 1363.0263 | 36552.8327 | -0.012076
132 |  | 90.5785 | 278.2307 | 4187 | 0.00073363 | 6.0964 | 6.0971 | -16.4598 | 1363.0855 | 36831.0635 | -0.012075
133 |  | 90.5785 | 278.2187 | 4187 | 0.0007336 | 6.0971 | 6.0978 | -16.4598 | 1363.1446 | 37109.2821 | -0.012075
134 |  | 90.5785 | 278.2066 | 4187 | 0.00073357 | 6.0978 | 6.0986 | -16.4598 | 1363.2038 | 37387.4887 | -0.012074
135 |  | 90.5785 | 278.1945 | 4187 | 0.00073353 | 6.0986 | 6.0993 | -16.4598 | 1363.263 | 37665.6833 | -0.012074
136 |  | 90.5785 | 278.1824 | 4187 | 0.0007335 | 6.0993 | 6.1 | -16.4598 | 1363.3221 | 37943.8657 | -0.012073
137 |  | 90.5785 | 278.1704 | 4187 | 0.00073347 | 6.1 | 6.1008 | -16.4598 | 1363.3813 | 38222.0361 | -0.012073
138 |  | 90.5785 | 278.1583 | 4187 | 0.00073344 | 6.1008 | 6.1015 | -16.4598 | 1363.4405 | 38500.1944 | -0.012072
139 |  | 90.5785 | 278.1462 | 4187 | 0.00073341 | 6.1015 | 6.1022 | -16.4598 | 1363.4997 | 38778.3406 | -0.012072
140 |  | 90.5785 | 278.1342 | 4187 | 0.00073338 | 6.1022 | 6.103 | -16.4598 | 1363.5588 | 39056.4748 | -0.012071
141 |  | 90.5785 | 278.1221 | 4187 | 0.00073334 | 6.103 | 6.1037 | -16.4598 | 1363.618 | 39334.5968 | -0.012071
142 |  | 90.5785 | 278.11 | 4187 | 0.00073331 | 6.1037 | 6.1044 | -16.4598 | 1363.6772 | 39612.7068 | -0.01207
143 |  | 90.5785 | 278.0979 | 4187 | 0.00073328 | 6.1044 | 6.1052 | -16.4598 | 1363.7364 | 39890.8048 | -0.01207
144 |  | 90.5785 | 278.0859 | 4187 | 0.00073325 | 6.1052 | 6.1059 | -16.4598 | 1363.7956 | 40168.8907 | -0.012069
145 |  | 90.5785 | 278.0738 | 4187 | 0.00073322 | 6.1059 | 6.1066 | -16.4598 | 1363.8548 | 40446.9645 | -0.012069
146 |  | 90.5785 | 278.0617 | 4187 | 0.00073318 | 6.1066 | 6.1074 | -16.4598 | 1363.914 | 40725.0262 | -0.012068
147 |  | 90.5785 | 278.0497 | 4187 | 0.00073315 | 6.1074 | 6.1081 | -16.4598 | 1363.9732 | 41003.0759 | -0.012068
148 |  | 90.5785 | 278.0376 | 4187 | 0.00073312 | 6.1081 | 6.1088 | -16.4598 | 1364.0324 | 41281.1135 | -0.012067
149 |  | 90.5785 | 278.0255 | 4187 | 0.00073309 | 6.1088 | 6.1096 | -16.4598 | 1364.0916 | 41559.139 | -0.012067
150 |  | 90.5785 | 278.0135 | 4187 | 0.00073306 | 6.1096 | 6.1103 | -16.4598 | 1364.1508 | 41837.1525 | -0.012066
151 |  | 90.5785 | 278.0014 | 4187 | 0.00073302 | 6.1103 | 6.111 | -16.4598 | 1364.21 | 42115.1539 | -0.012065
152 |  | 90.5785 | 277.9893 | 4187 | 0.00073299 | 6.111 | 6.1118 | -16.4598 | 1364.2692 | 42393.1432 | -0.012065
153 |  | 90.5785 | 277.9773 | 4187 | 0.00073296 | 6.1118 | 6.1125 | -16.4598 | 1364.3284 | 42671.1205 | -0.012064
154 |  | 90.5785 | 277.9652 | 4187 | 0.00073293 | 6.1125 | 6.1132 | -16.4598 | 1364.3876 | 42949.0857 | -0.012064
155 |  | 90.5785 | 277.9531 | 4187 | 0.0007329 | 6.1132 | 6.114 | -16.4598 | 1364.4468 | 43227.0388 | -0.012063
156 |  | 90.5785 | 277.9411 | 4187 | 0.00073287 | 6.114 | 6.1147 | -16.4598 | 1364.5061 | 43504.9799 | -0.012063
157 |  | 90.5785 | 277.929 | 4187 | 0.00073283 | 6.1147 | 6.1154 | -16.4598 | 1364.5653 | 43782.9089 | -0.012062
158 |  | 90.5785 | 277.917 | 4187 | 0.0007328 | 6.1154 | 6.1162 | -16.4598 | 1364.6245 | 44060.8259 | -0.012062
159 |  | 90.5785 | 277.9049 | 4187 | 0.00073277 | 6.1162 | 6.1169 | -16.4598 | 1364.6837 | 44338.7308 | -0.012061
160 |  | 90.5785 | 277.8928 | 4187 | 0.00073274 | 6.1169 | 6.1176 | -16.4598 | 1364.743 | 44616.6236 | -0.012061
161 |  | 90.5785 | 277.8808 | 4187 | 0.00073271 | 6.1176 | 6.1184 | -16.4598 | 1364.8022 | 44894.5044 | -0.01206
162 |  | 90.5785 | 277.8687 | 4187 | 0.00073268 | 6.1184 | 6.1191 | -16.4598 | 1364.8614 | 45172.3731 | -0.01206
163 |  | 90.5785 | 277.8566 | 4187 | 0.00073264 | 6.1191 | 6.1198 | -16.4598 | 1364.9207 | 45450.2297 | -0.012059
164 |  | 90.5785 | 277.8446 | 4187 | 0.00073261 | 6.1198 | 6.1206 | -16.4598 | 1364.9799 | 45728.0743 | -0.012059
165 |  | 90.5785 | 277.8325 | 4187 | 0.00073258 | 6.1206 | 6.1213 | -16.4598 | 1365.0392 | 46005.9068 | -0.012058
166 |  | 90.5785 | 277.8205 | 4187 | 0.00073255 | 6.1213 | 6.122 | -16.4598 | 1365.0984 | 46283.7273 | -0.012058
167 |  | 90.5785 | 277.8084 | 4187 | 0.00073252 | 6.122 | 6.1228 | -16.4598 | 1365.1577 | 46561.5357 | -0.012057
168 |  | 90.5785 | 277.7964 | 4187 | 0.00073248 | 6.1228 | 6.1235 | -16.4598 | 1365.2169 | 46839.3321 | -0.012057
169 |  | 90.5785 | 277.7843 | 4187 | 0.00073245 | 6.1235 | 6.1242 | -16.4598 | 1365.2762 | 47117.1164 | -0.012056
170 |  | 90.5785 | 277.7722 | 4187 | 0.00073242 | 6.1242 | 6.125 | -16.4598 | 1365.3354 | 47394.8886 | -0.012056
171 |  | 90.5785 | 277.7602 | 4187 | 0.00073239 | 6.125 | 6.1257 | -16.4598 | 1365.3947 | 47672.6488 | -0.012055
172 |  | 90.5785 | 277.7481 | 4187 | 0.00073236 | 6.1257 | 6.1264 | -16.4598 | 1365.4539 | 47950.397 | -0.012054
173 |  | 90.5785 | 277.7361 | 4187 | 0.00073233 | 6.1264 | 6.1272 | -16.4598 | 1365.5132 | 48228.133 | -0.012054
174 |  | 90.5785 | 277.724 | 4187 | 0.00073229 | 6.1272 | 6.1279 | -16.4598 | 1365.5725 | 48505.8571 | -0.012053
175 |  | 90.5785 | 277.712 | 4187 | 0.00073226 | 6.1279 | 6.1286 | -16.4598 | 1365.6317 | 48783.569 | -0.012053
176 |  | 90.5785 | 277.6999 | 4187 | 0.00073223 | 6.1286 | 6.1294 | -16.4598 | 1365.691 | 49061.269 | -0.012052
177 |  | 90.5785 | 277.6879 | 4187 | 0.0007322 | 6.1294 | 6.1301 | -16.4598 | 1365.7503 | 49338.9568 | -0.012052
178 |  | 90.5785 | 277.6758 | 4187 | 0.00073217 | 6.1301 | 6.1308 | -16.4598 | 1365.8096 | 49616.6327 | -0.012051
179 |  | 90.5785 | 277.6638 | 4187 | 0.00073213 | 6.1308 | 6.1316 | -16.4598 | 1365.8688 | 49894.2964 | -0.012051
180 |  | 90.5785 | 277.6517 | 4187 | 0.0007321 | 6.1316 | 6.1323 | -16.4598 | 1365.9281 | 50171.9481 | -0.01205
181 |  | 90.5785 | 277.6397 | 4187 | 0.00073207 | 6.1323 | 6.133 | -16.4598 | 1365.9874 | 50449.5878 | -0.01205
182 |  | 90.5785 | 277.6276 | 4187 | 0.00073204 | 6.133 | 6.1338 | -16.4598 | 1366.0467 | 50727.2154 | -0.012049
183 |  | 90.5785 | 277.6156 | 4187 | 0.00073201 | 6.1338 | 6.1345 | -16.4598 | 1366.106 | 51004.831 | -0.012049
184 |  | 90.5785 | 277.6035 | 4187 | 0.00073198 | 6.1345 | 6.1352 | -16.4598 | 1366.1653 | 51282.4345 | -0.012048
185 |  | 90.5785 | 277.5915 | 4187 | 0.00073194 | 6.1352 | 6.136 | -16.4598 | 1366.2246 | 51560.026 | -0.012048
186 |  | 90.5785 | 277.5794 | 4187 | 0.00073191 | 6.136 | 6.1367 | -16.4598 | 1366.2839 | 51837.6054 | -0.012047
187 |  | 90.5785 | 277.5674 | 4187 | 0.00073188 | 6.1367 | 6.1374 | -16.4598 | 1366.3432 | 52115.1728 | -0.012047
188 |  | 90.5785 | 277.5553 | 4187 | 0.00073185 | 6.1374 | 6.1381 | -16.4598 | 1366.4025 | 52392.7281 | -0.012046
189 |  | 90.5785 | 277.5433 | 4187 | 0.00073182 | 6.1381 | 6.1389 | -16.4598 | 1366.4618 | 52670.2714 | -0.012046
190 |  | 90.5785 | 277.5312 | 4187 | 0.00073179 | 6.1389 | 6.1396 | -16.4598 | 1366.5211 | 52947.8026 | -0.012045
191 |  | 90.5785 | 277.5192 | 4187 | 0.00073175 | 6.1396 | 6.1403 | -16.4598 | 1366.5804 | 53225.3218 | -0.012045
192 |  | 90.5785 | 277.5071 | 4187 | 0.00073172 | 6.1403 | 6.1411 | -16.4598 | 1366.6397 | 53502.8289 | -0.012044
193 |  | 90.5785 | 277.4951 | 4187 | 0.00073169 | 6.1411 | 6.1418 | -16.4598 | 1366.699 | 53780.324 | -0.012043
194 |  | 90.5785 | 277.4831 | 4187 | 0.00073166 | 6.1418 | 6.1425 | -16.4598 | 1366.7583 | 54057.8071 | -0.012043
195 |  | 90.5785 | 277.471 | 4187 | 0.00073163 | 6.1425 | 6.1433 | -16.4598 | 1366.8177 | 54335.2781 | -0.012042
196 |  | 90.5785 | 277.459 | 4187 | 0.00073159 | 6.1433 | 6.144 | -16.4598 | 1366.877 | 54612.7371 | -0.012042
197 |  | 90.5785 | 277.4469 | 4187 | 0.00073156 | 6.144 | 6.1447 | -16.4598 | 1366.9363 | 54890.184 | -0.012041
198 |  | 90.5785 | 277.4349 | 4187 | 0.00073153 | 6.1447 | 6.1455 | -16.4598 | 1366.9956 | 55167.6189 | -0.012041
199 |  | 90.5785 | 277.4228 | 4187 | 0.0007315 | 6.1455 | 6.1462 | -16.4598 | 1367.055 | 55445.0417 | -0.01204
200 |  | 90.5785 | 277.4108 | 4187 | 0.00073147 | 6.1462 | 6.1469 | -16.4598 | 1367.1143 | 55722.4526 | -0.01204
201 |  | 90.5785 | 277.3988 | 4187 | 0.00073144 | 6.1469 | 6.1477 | -16.4598 | 1367.1736 | 55999.8513 | -0.012039
202 |  | 90.5785 | 277.3867 | 4187 | 0.0007314 | 6.1477 | 6.1484 | -16.4598 | 1367.233 | 56277.2381 | -0.012039
203 |  | 90.5785 | 277.3747 | 4187 | 0.00073137 | 6.1484 | 6.1491 | -16.4598 | 1367.2923 | 56554.6127 | -0.012038
204 |  | 90.5785 | 277.3627 | 4187 | 0.00073134 | 6.1491 | 6.1499 | -16.4598 | 1367.3517 | 56831.9754 | -0.012038
205 |  | 90.5785 | 277.3506 | 4187 | 0.00073131 | 6.1499 | 6.1506 | -16.4598 | 1367.411 | 57109.326 | -0.012037
206 |  | 90.5785 | 277.3386 | 4187 | 0.00073128 | 6.1506 | 6.1513 | -16.4598 | 1367.4704 | 57386.6646 | -0.012037
207 |  | 90.5785 | 277.3265 | 4187 | 0.00073125 | 6.1513 | 6.152 | -16.4598 | 1367.5297 | 57663.9911 | -0.012036
208 |  | 90.5785 | 277.3145 | 4187 | 0.00073121 | 6.152 | 6.1528 | -16.4598 | 1367.5891 | 57941.3056 | -0.012036
209 |  | 90.5785 | 277.3025 | 4187 | 0.00073118 | 6.1528 | 6.1535 | -16.4598 | 1367.6484 | 58218.6081 | -0.012035
210 |  | 90.5785 | 277.2904 | 4187 | 0.00073115 | 6.1535 | 6.1542 | -16.4598 | 1367.7078 | 58495.8985 | -0.012035
211 |  | 90.5785 | 277.2784 | 4187 | 0.00073112 | 6.1542 | 6.155 | -16.4598 | 1367.7671 | 58773.1769 | -0.012034
212 |  | 90.5785 | 277.2664 | 4187 | 0.00073109 | 6.155 | 6.1557 | -16.4598 | 1367.8265 | 59050.4433 | -0.012034
213 |  | 90.5785 | 277.2543 | 4187 | 0.00073106 | 6.1557 | 6.1564 | -16.4598 | 1367.8859 | 59327.6976 | -0.012033
214 |  | 90.5785 | 277.2423 | 4187 | 0.00073102 | 6.1564 | 6.1572 | -16.4598 | 1367.9453 | 59604.9399 | -0.012033
215 |  | 90.5785 | 277.2303 | 4187 | 0.00073099 | 6.1572 | 6.1579 | -16.4598 | 1368.0046 | 59882.1702 | -0.012032
216 |  | 90.5785 | 277.2182 | 4187 | 0.00073096 | 6.1579 | 6.1586 | -16.4598 | 1368.064 | 60159.3884 | -0.012031
217 |  | 90.5785 | 277.2062 | 4187 | 0.00073093 | 6.1586 | 6.1594 | -16.4598 | 1368.1234 | 60436.5946 | -0.012031
218 |  | 90.5785 | 277.1942 | 4187 | 0.0007309 | 6.1594 | 6.1601 | -16.4598 | 1368.1828 | 60713.7888 | -0.01203
219 |  | 90.5785 | 277.1821 | 4187 | 0.00073086 | 6.1601 | 6.1608 | -16.4598 | 1368.2421 | 60990.9709 | -0.01203
220 |  | 90.5785 | 277.1701 | 4187 | 0.00073083 | 6.1608 | 6.1615 | -16.4598 | 1368.3015 | 61268.141 | -0.012029
221 |  | 90.5785 | 277.1581 | 4187 | 0.0007308 | 6.1615 | 6.1623 | -16.4598 | 1368.3609 | 61545.2991 | -0.012029
222 |  | 90.5785 | 277.1461 | 4187 | 0.00073077 | 6.1623 | 6.163 | -16.4598 | 1368.4203 | 61822.4452 | -0.012028
223 |  | 90.5785 | 277.134 | 4187 | 0.00073074 | 6.163 | 6.1637 | -16.4598 | 1368.4797 | 62099.5792 | -0.012028
224 |  | 90.5785 | 277.122 | 4187 | 0.00073071 | 6.1637 | 6.1645 | -16.4598 | 1368.5391 | 62376.7012 | -0.012027
225 |  | 90.5785 | 277.11 | 4187 | 0.00073067 | 6.1645 | 6.1652 | -16.4598 | 1368.5985 | 62653.8112 | -0.012027
226 |  | 90.5785 | 277.0979 | 4187 | 0.00073064 | 6.1652 | 6.1659 | -16.4598 | 1368.6579 | 62930.9091 | -0.012026
227 |  | 90.5785 | 277.0859 | 4187 | 0.00073061 | 6.1659 | 6.1667 | -16.4598 | 1368.7173 | 63207.995 | -0.012026
228 |  | 90.5785 | 277.0739 | 4187 | 0.00073058 | 6.1667 | 6.1674 | -16.4598 | 1368.7767 | 63485.0689 | -0.012025
229 |  | 90.5785 | 277.0619 | 4187 | 0.00073055 | 6.1674 | 6.1681 | -16.4598 | 1368.8361 | 63762.1308 | -0.012025
230 |  | 90.5785 | 277.0498 | 4187 | 0.00073052 | 6.1681 | 6.1689 | -16.4598 | 1368.8955 | 64039.1806 | -0.012024
231 |  | 90.5785 | 277.0378 | 4187 | 0.00073048 | 6.1689 | 6.1696 | -16.4598 | 1368.9549 | 64316.2184 | -0.012024
232 |  | 90.5785 | 277.0258 | 4187 | 0.00073045 | 6.1696 | 6.1703 | -16.4598 | 1369.0143 | 64593.2442 | -0.012023
233 |  | 90.5785 | 277.0138 | 4187 | 0.00073042 | 6.1703 | 6.171 | -16.4598 | 1369.0738 | 64870.258 | -0.012023
234 |  | 90.5785 | 277.0017 | 4187 | 0.00073039 | 6.171 | 6.1718 | -16.4598 | 1369.1332 | 65147.2597 | -0.012022
235 |  | 90.5785 | 276.9897 | 4187 | 0.00073036 | 6.1718 | 6.1725 | -16.4598 | 1369.1926 | 65424.2495 | -0.012022
236 |  | 90.5785 | 276.9777 | 4187 | 0.00073033 | 6.1725 | 6.1732 | -16.4598 | 1369.252 | 65701.2272 | -0.012021

## St406
|  |  | buis | verlies W/M | L /°C/sec
diam | wandikte |  | inhoud l/m |  | W/M
406.4 | 8.8 | 3.1416 | 118.7251 | 319.7282 | 4187
[8 empty] | J/sec/mtr | aantal mtr. | verlies
|  | buis | verlies W/M | L /°C/sec | verlies temp | begintemp | eindtemp | verlies | bij 1°C | totaal J/sec
|  | inhoud L |  | W/M | °C per M | °C | °C | per m°C | daling | aantal mtr
1 | 406.4 | 118.7251 | 319.7282 | 4187 | 0.00064318 | 6 | 6.0006 | -18.8075 | 1554.7639 | 319.7282 | -0.012097
2 |  | 118.7251 | 319.7161 | 4187 | 0.00064316 | 6.0006 | 6.0013 | -18.8075 | 1554.8227 | 639.4443 | -0.012096
3 |  | 118.7251 | 319.704 | 4187 | 0.00064314 | 6.0013 | 6.0019 | -18.8075 | 1554.8815 | 959.1482 | -0.012096
4 |  | 118.7251 | 319.6919 | 4187 | 0.00064311 | 6.0019 | 6.0026 | -18.8075 | 1554.9404 | 1278.8401 | -0.012095
5 |  | 118.7251 | 319.6798 | 4187 | 0.00064309 | 6.0026 | 6.0032 | -18.8075 | 1554.9992 | 1598.5199 | -0.012095
6 |  | 118.7251 | 319.6677 | 4187 | 0.00064306 | 6.0032 | 6.0039 | -18.8075 | 1555.058 | 1918.1876 | -0.012094
7 |  | 118.7251 | 319.6556 | 4187 | 0.00064304 | 6.0039 | 6.0045 | -18.8075 | 1555.1169 | 2237.8432 | -0.012094
8 |  | 118.7251 | 319.6435 | 4187 | 0.00064301 | 6.0045 | 6.0051 | -18.8075 | 1555.1757 | 2557.4867 | -0.012094
9 |  | 118.7251 | 319.6314 | 4187 | 0.00064299 | 6.0051 | 6.0058 | -18.8075 | 1555.2346 | 2877.1181 | -0.012093
10 |  | 118.7251 | 319.6193 | 4187 | 0.00064297 | 6.0058 | 6.0064 | -18.8075 | 1555.2934 | 3196.7375 | -0.012093
11 |  | 118.7251 | 319.6072 | 4187 | 0.00064294 | 6.0064 | 6.0071 | -18.8075 | 1555.3523 | 3516.3447 | -0.012092
12 |  | 118.7251 | 319.5951 | 4187 | 0.00064292 | 6.0071 | 6.0077 | -18.8075 | 1555.4111 | 3835.9398 | -0.012092
13 |  | 118.7251 | 319.583 | 4187 | 0.00064289 | 6.0077 | 6.0084 | -18.8075 | 1555.4699 | 4155.5229 | -0.012091
14 |  | 118.7251 | 319.571 | 4187 | 0.00064287 | 6.0084 | 6.009 | -18.8075 | 1555.5288 | 4475.0938 | -0.012091
15 |  | 118.7251 | 319.5589 | 4187 | 0.00064284 | 6.009 | 6.0096 | -18.8075 | 1555.5877 | 4794.6527 | -0.01209
16 |  | 118.7251 | 319.5468 | 4187 | 0.00064282 | 6.0096 | 6.0103 | -18.8075 | 1555.6465 | 5114.1994 | -0.01209
17 |  | 118.7251 | 319.5347 | 4187 | 0.0006428 | 6.0103 | 6.0109 | -18.8075 | 1555.7054 | 5433.7341 | -0.012089
18 |  | 118.7251 | 319.5226 | 4187 | 0.00064277 | 6.0109 | 6.0116 | -18.8075 | 1555.7642 | 5753.2567 | -0.012089
19 |  | 118.7251 | 319.5105 | 4187 | 0.00064275 | 6.0116 | 6.0122 | -18.8075 | 1555.8231 | 6072.7672 | -0.012088
20 |  | 118.7251 | 319.4984 | 4187 | 0.00064272 | 6.0122 | 6.0129 | -18.8075 | 1555.882 | 6392.2656 | -0.012088
21 |  | 118.7251 | 319.4863 | 4187 | 0.0006427 | 6.0129 | 6.0135 | -18.8075 | 1555.9408 | 6711.752 | -0.012088
22 |  | 118.7251 | 319.4742 | 4187 | 0.00064267 | 6.0135 | 6.0141 | -18.8075 | 1555.9997 | 7031.2262 | -0.012087
23 |  | 118.7251 | 319.4622 | 4187 | 0.00064265 | 6.0141 | 6.0148 | -18.8075 | 1556.0586 | 7350.6884 | -0.012087
24 |  | 118.7251 | 319.4501 | 4187 | 0.00064263 | 6.0148 | 6.0154 | -18.8075 | 1556.1174 | 7670.1384 | -0.012086
25 |  | 118.7251 | 319.438 | 4187 | 0.0006426 | 6.0154 | 6.0161 | -18.8075 | 1556.1763 | 7989.5764 | -0.012086
26 |  | 118.7251 | 319.4259 | 4187 | 0.00064258 | 6.0161 | 6.0167 | -18.8075 | 1556.2352 | 8309.0023 | -0.012085
27 |  | 118.7251 | 319.4138 | 4187 | 0.00064255 | 6.0167 | 6.0174 | -18.8075 | 1556.2941 | 8628.4161 | -0.012085
28 |  | 118.7251 | 319.4017 | 4187 | 0.00064253 | 6.0174 | 6.018 | -18.8075 | 1556.353 | 8947.8178 | -0.012084
29 |  | 118.7251 | 319.3896 | 4187 | 0.0006425 | 6.018 | 6.0186 | -18.8075 | 1556.4119 | 9267.2075 | -0.012084
30 |  | 118.7251 | 319.3776 | 4187 | 0.00064248 | 6.0186 | 6.0193 | -18.8075 | 1556.4707 | 9586.585 | -0.012083
31 |  | 118.7251 | 319.3655 | 4187 | 0.00064245 | 6.0193 | 6.0199 | -18.8075 | 1556.5296 | 9905.9505 | -0.012083
32 |  | 118.7251 | 319.3534 | 4187 | 0.00064243 | 6.0199 | 6.0206 | -18.8075 | 1556.5885 | 10225.3039 | -0.012083
33 |  | 118.7251 | 319.3413 | 4187 | 0.00064241 | 6.0206 | 6.0212 | -18.8075 | 1556.6474 | 10544.6452 | -0.012082
34 |  | 118.7251 | 319.3292 | 4187 | 0.00064238 | 6.0212 | 6.0219 | -18.8075 | 1556.7063 | 10863.9744 | -0.012082
35 |  | 118.7251 | 319.3171 | 4187 | 0.00064236 | 6.0219 | 6.0225 | -18.8075 | 1556.7652 | 11183.2916 | -0.012081
36 |  | 118.7251 | 319.3051 | 4187 | 0.00064233 | 6.0225 | 6.0231 | -18.8075 | 1556.8241 | 11502.5966 | -0.012081
37 |  | 118.7251 | 319.293 | 4187 | 0.00064231 | 6.0231 | 6.0238 | -18.8075 | 1556.883 | 11821.8896 | -0.01208
38 |  | 118.7251 | 319.2809 | 4187 | 0.00064228 | 6.0238 | 6.0244 | -18.8075 | 1556.9419 | 12141.1705 | -0.01208
39 |  | 118.7251 | 319.2688 | 4187 | 0.00064226 | 6.0244 | 6.0251 | -18.8075 | 1557.0008 | 12460.4393 | -0.012079
40 |  | 118.7251 | 319.2567 | 4187 | 0.00064224 | 6.0251 | 6.0257 | -18.8075 | 1557.0597 | 12779.6961 | -0.012079
41 |  | 118.7251 | 319.2447 | 4187 | 0.00064221 | 6.0257 | 6.0264 | -18.8075 | 1557.1187 | 13098.9407 | -0.012078
42 |  | 118.7251 | 319.2326 | 4187 | 0.00064219 | 6.0264 | 6.027 | -18.8075 | 1557.1776 | 13418.1733 | -0.012078
43 |  | 118.7251 | 319.2205 | 4187 | 0.00064216 | 6.027 | 6.0276 | -18.8075 | 1557.2365 | 13737.3938 | -0.012078
44 |  | 118.7251 | 319.2084 | 4187 | 0.00064214 | 6.0276 | 6.0283 | -18.8075 | 1557.2954 | 14056.6023 | -0.012077
45 |  | 118.7251 | 319.1964 | 4187 | 0.00064211 | 6.0283 | 6.0289 | -18.8075 | 1557.3543 | 14375.7986 | -0.012077
46 |  | 118.7251 | 319.1843 | 4187 | 0.00064209 | 6.0289 | 6.0296 | -18.8075 | 1557.4133 | 14694.9829 | -0.012076
47 |  | 118.7251 | 319.1722 | 4187 | 0.00064207 | 6.0296 | 6.0302 | -18.8075 | 1557.4722 | 15014.1551 | -0.012076
48 |  | 118.7251 | 319.1601 | 4187 | 0.00064204 | 6.0302 | 6.0308 | -18.8075 | 1557.5311 | 15333.3152 | -0.012075
49 |  | 118.7251 | 319.148 | 4187 | 0.00064202 | 6.0308 | 6.0315 | -18.8075 | 1557.59 | 15652.4633 | -0.012075
50 |  | 118.7251 | 319.136 | 4187 | 0.00064199 | 6.0315 | 6.0321 | -18.8075 | 1557.649 | 15971.5992 | -0.012074
51 |  | 118.7251 | 319.1239 | 4187 | 0.00064197 | 6.0321 | 6.0328 | -18.8075 | 1557.7079 | 16290.7231 | -0.012074
52 |  | 118.7251 | 319.1118 | 4187 | 0.00064194 | 6.0328 | 6.0334 | -18.8075 | 1557.7668 | 16609.835 | -0.012073
53 |  | 118.7251 | 319.0998 | 4187 | 0.00064192 | 6.0334 | 6.0341 | -18.8075 | 1557.8258 | 16928.9347 | -0.012073
54 |  | 118.7251 | 319.0877 | 4187 | 0.0006419 | 6.0341 | 6.0347 | -18.8075 | 1557.8847 | 17248.0224 | -0.012072
55 |  | 118.7251 | 319.0756 | 4187 | 0.00064187 | 6.0347 | 6.0353 | -18.8075 | 1557.9437 | 17567.098 | -0.012072
56 |  | 118.7251 | 319.0635 | 4187 | 0.00064185 | 6.0353 | 6.036 | -18.8075 | 1558.0026 | 17886.1615 | -0.012072
57 |  | 118.7251 | 319.0515 | 4187 | 0.00064182 | 6.036 | 6.0366 | -18.8075 | 1558.0616 | 18205.213 | -0.012071
58 |  | 118.7251 | 319.0394 | 4187 | 0.0006418 | 6.0366 | 6.0373 | -18.8075 | 1558.1205 | 18524.2524 | -0.012071
59 |  | 118.7251 | 319.0273 | 4187 | 0.00064177 | 6.0373 | 6.0379 | -18.8075 | 1558.1795 | 18843.2797 | -0.01207
60 |  | 118.7251 | 319.0153 | 4187 | 0.00064175 | 6.0379 | 6.0385 | -18.8075 | 1558.2384 | 19162.295 | -0.01207
61 |  | 118.7251 | 319.0032 | 4187 | 0.00064173 | 6.0385 | 6.0392 | -18.8075 | 1558.2974 | 19481.2981 | -0.012069
62 |  | 118.7251 | 318.9911 | 4187 | 0.0006417 | 6.0392 | 6.0398 | -18.8075 | 1558.3563 | 19800.2893 | -0.012069
63 |  | 118.7251 | 318.979 | 4187 | 0.00064168 | 6.0398 | 6.0405 | -18.8075 | 1558.4153 | 20119.2683 | -0.012068
64 |  | 118.7251 | 318.967 | 4187 | 0.00064165 | 6.0405 | 6.0411 | -18.8075 | 1558.4743 | 20438.2353 | -0.012068
65 |  | 118.7251 | 318.9549 | 4187 | 0.00064163 | 6.0411 | 6.0418 | -18.8075 | 1558.5332 | 20757.1902 | -0.012067
66 |  | 118.7251 | 318.9428 | 4187 | 0.0006416 | 6.0418 | 6.0424 | -18.8075 | 1558.5922 | 21076.133 | -0.012067
67 |  | 118.7251 | 318.9308 | 4187 | 0.00064158 | 6.0424 | 6.043 | -18.8075 | 1558.6512 | 21395.0638 | -0.012067
68 |  | 118.7251 | 318.9187 | 4187 | 0.00064156 | 6.043 | 6.0437 | -18.8075 | 1558.7101 | 21713.9825 | -0.012066
69 |  | 118.7251 | 318.9066 | 4187 | 0.00064153 | 6.0437 | 6.0443 | -18.8075 | 1558.7691 | 22032.8891 | -0.012066
70 |  | 118.7251 | 318.8946 | 4187 | 0.00064151 | 6.0443 | 6.045 | -18.8075 | 1558.8281 | 22351.7837 | -0.012065
71 |  | 118.7251 | 318.8825 | 4187 | 0.00064148 | 6.045 | 6.0456 | -18.8075 | 1558.8871 | 22670.6662 | -0.012065
72 |  | 118.7251 | 318.8704 | 4187 | 0.00064146 | 6.0456 | 6.0462 | -18.8075 | 1558.9461 | 22989.5367 | -0.012064
73 |  | 118.7251 | 318.8584 | 4187 | 0.00064143 | 6.0462 | 6.0469 | -18.8075 | 1559.005 | 23308.395 | -0.012064
74 |  | 118.7251 | 318.8463 | 4187 | 0.00064141 | 6.0469 | 6.0475 | -18.8075 | 1559.064 | 23627.2414 | -0.012063
75 |  | 118.7251 | 318.8343 | 4187 | 0.00064139 | 6.0475 | 6.0482 | -18.8075 | 1559.123 | 23946.0756 | -0.012063
76 |  | 118.7251 | 318.8222 | 4187 | 0.00064136 | 6.0482 | 6.0488 | -18.8075 | 1559.182 | 24264.8978 | -0.012062
77 |  | 118.7251 | 318.8101 | 4187 | 0.00064134 | 6.0488 | 6.0495 | -18.8075 | 1559.241 | 24583.7079 | -0.012062
78 |  | 118.7251 | 318.7981 | 4187 | 0.00064131 | 6.0495 | 6.0501 | -18.8075 | 1559.3 | 24902.506 | -0.012062
79 |  | 118.7251 | 318.786 | 4187 | 0.00064129 | 6.0501 | 6.0507 | -18.8075 | 1559.359 | 25221.292 | -0.012061
80 |  | 118.7251 | 318.7739 | 4187 | 0.00064126 | 6.0507 | 6.0514 | -18.8075 | 1559.418 | 25540.0659 | -0.012061
81 |  | 118.7251 | 318.7619 | 4187 | 0.00064124 | 6.0514 | 6.052 | -18.8075 | 1559.477 | 25858.8278 | -0.01206
82 |  | 118.7251 | 318.7498 | 4187 | 0.00064122 | 6.052 | 6.0527 | -18.8075 | 1559.536 | 26177.5776 | -0.01206
83 |  | 118.7251 | 318.7378 | 4187 | 0.00064119 | 6.0527 | 6.0533 | -18.8075 | 1559.595 | 26496.3154 | -0.012059
84 |  | 118.7251 | 318.7257 | 4187 | 0.00064117 | 6.0533 | 6.0539 | -18.8075 | 1559.654 | 26815.0411 | -0.012059
85 |  | 118.7251 | 318.7136 | 4187 | 0.00064114 | 6.0539 | 6.0546 | -18.8075 | 1559.713 | 27133.7548 | -0.012058
86 |  | 118.7251 | 318.7016 | 4187 | 0.00064112 | 6.0546 | 6.0552 | -18.8075 | 1559.772 | 27452.4563 | -0.012058
87 |  | 118.7251 | 318.6895 | 4187 | 0.0006411 | 6.0552 | 6.0559 | -18.8075 | 1559.8311 | 27771.1459 | -0.012057
88 |  | 118.7251 | 318.6775 | 4187 | 0.00064107 | 6.0559 | 6.0565 | -18.8075 | 1559.8901 | 28089.8233 | -0.012057
89 |  | 118.7251 | 318.6654 | 4187 | 0.00064105 | 6.0565 | 6.0571 | -18.8075 | 1559.9491 | 28408.4888 | -0.012057
90 |  | 118.7251 | 318.6534 | 4187 | 0.00064102 | 6.0571 | 6.0578 | -18.8075 | 1560.0081 | 28727.1421 | -0.012056
91 |  | 118.7251 | 318.6413 | 4187 | 0.000641 | 6.0578 | 6.0584 | -18.8075 | 1560.0671 | 29045.7834 | -0.012056
92 |  | 118.7251 | 318.6292 | 4187 | 0.00064097 | 6.0584 | 6.0591 | -18.8075 | 1560.1262 | 29364.4127 | -0.012055
93 |  | 118.7251 | 318.6172 | 4187 | 0.00064095 | 6.0591 | 6.0597 | -18.8075 | 1560.1852 | 29683.0298 | -0.012055
94 |  | 118.7251 | 318.6051 | 4187 | 0.00064093 | 6.0597 | 6.0604 | -18.8075 | 1560.2442 | 30001.635 | -0.012054
95 |  | 118.7251 | 318.5931 | 4187 | 0.0006409 | 6.0604 | 6.061 | -18.8075 | 1560.3033 | 30320.2281 | -0.012054
96 |  | 118.7251 | 318.581 | 4187 | 0.00064088 | 6.061 | 6.0616 | -18.8075 | 1560.3623 | 30638.8091 | -0.012053
97 |  | 118.7251 | 318.569 | 4187 | 0.00064085 | 6.0616 | 6.0623 | -18.8075 | 1560.4213 | 30957.3781 | -0.012053
98 |  | 118.7251 | 318.5569 | 4187 | 0.00064083 | 6.0623 | 6.0629 | -18.8075 | 1560.4804 | 31275.935 | -0.012052
99 |  | 118.7251 | 318.5449 | 4187 | 0.0006408 | 6.0629 | 6.0636 | -18.8075 | 1560.5394 | 31594.4799 | -0.012052
100 |  | 118.7251 | 318.5328 | 4187 | 0.00064078 | 6.0636 | 6.0642 | -18.8075 | 1560.5985 | 31913.0127 | -0.012051
101 |  | 118.7251 | 318.5208 | 4187 | 0.00064076 | 6.0642 | 6.0648 | -18.8075 | 1560.6575 | 32231.5334 | -0.012051
102 |  | 118.7251 | 318.5087 | 4187 | 0.00064073 | 6.0648 | 6.0655 | -18.8075 | 1560.7165 | 32550.0422 | -0.012051
103 |  | 118.7251 | 318.4967 | 4187 | 0.00064071 | 6.0655 | 6.0661 | -18.8075 | 1560.7756 | 32868.5388 | -0.01205
104 |  | 118.7251 | 318.4846 | 4187 | 0.00064068 | 6.0661 | 6.0668 | -18.8075 | 1560.8347 | 33187.0234 | -0.01205
105 |  | 118.7251 | 318.4726 | 4187 | 0.00064066 | 6.0668 | 6.0674 | -18.8075 | 1560.8937 | 33505.496 | -0.012049
106 |  | 118.7251 | 318.4605 | 4187 | 0.00064063 | 6.0674 | 6.068 | -18.8075 | 1560.9528 | 33823.9565 | -0.012049
107 |  | 118.7251 | 318.4485 | 4187 | 0.00064061 | 6.068 | 6.0687 | -18.8075 | 1561.0118 | 34142.405 | -0.012048
108 |  | 118.7251 | 318.4364 | 4187 | 0.00064059 | 6.0687 | 6.0693 | -18.8075 | 1561.0709 | 34460.8414 | -0.012048
109 |  | 118.7251 | 318.4244 | 4187 | 0.00064056 | 6.0693 | 6.07 | -18.8075 | 1561.13 | 34779.2658 | -0.012047
110 |  | 118.7251 | 318.4123 | 4187 | 0.00064054 | 6.07 | 6.0706 | -18.8075 | 1561.189 | 35097.6781 | -0.012047
111 |  | 118.7251 | 318.4003 | 4187 | 0.00064051 | 6.0706 | 6.0712 | -18.8075 | 1561.2481 | 35416.0784 | -0.012046
112 |  | 118.7251 | 318.3882 | 4187 | 0.00064049 | 6.0712 | 6.0719 | -18.8075 | 1561.3072 | 35734.4666 | -0.012046
113 |  | 118.7251 | 318.3762 | 4187 | 0.00064046 | 6.0719 | 6.0725 | -18.8075 | 1561.3662 | 36052.8428 | -0.012046
114 |  | 118.7251 | 318.3641 | 4187 | 0.00064044 | 6.0725 | 6.0732 | -18.8075 | 1561.4253 | 36371.2069 | -0.012045
115 |  | 118.7251 | 318.3521 | 4187 | 0.00064042 | 6.0732 | 6.0738 | -18.8075 | 1561.4844 | 36689.559 | -0.012045
116 |  | 118.7251 | 318.34 | 4187 | 0.00064039 | 6.0738 | 6.0744 | -18.8075 | 1561.5435 | 37007.8991 | -0.012044
117 |  | 118.7251 | 318.328 | 4187 | 0.00064037 | 6.0744 | 6.0751 | -18.8075 | 1561.6025 | 37326.2271 | -0.012044
118 |  | 118.7251 | 318.316 | 4187 | 0.00064034 | 6.0751 | 6.0757 | -18.8075 | 1561.6616 | 37644.543 | -0.012043
119 |  | 118.7251 | 318.3039 | 4187 | 0.00064032 | 6.0757 | 6.0764 | -18.8075 | 1561.7207 | 37962.8469 | -0.012043
120 |  | 118.7251 | 318.2919 | 4187 | 0.0006403 | 6.0764 | 6.077 | -18.8075 | 1561.7798 | 38281.1388 | -0.012042
121 |  | 118.7251 | 318.2798 | 4187 | 0.00064027 | 6.077 | 6.0776 | -18.8075 | 1561.8389 | 38599.4186 | -0.012042
122 |  | 118.7251 | 318.2678 | 4187 | 0.00064025 | 6.0776 | 6.0783 | -18.8075 | 1561.898 | 38917.6864 | -0.012041
123 |  | 118.7251 | 318.2557 | 4187 | 0.00064022 | 6.0783 | 6.0789 | -18.8075 | 1561.9571 | 39235.9422 | -0.012041
124 |  | 118.7251 | 318.2437 | 4187 | 0.0006402 | 6.0789 | 6.0796 | -18.8075 | 1562.0162 | 39554.1859 | -0.012041
125 |  | 118.7251 | 318.2317 | 4187 | 0.00064017 | 6.0796 | 6.0802 | -18.8075 | 1562.0753 | 39872.4176 | -0.01204
126 |  | 118.7251 | 318.2196 | 4187 | 0.00064015 | 6.0802 | 6.0808 | -18.8075 | 1562.1344 | 40190.6372 | -0.01204
127 |  | 118.7251 | 318.2076 | 4187 | 0.00064013 | 6.0808 | 6.0815 | -18.8075 | 1562.1935 | 40508.8448 | -0.012039
128 |  | 118.7251 | 318.1955 | 4187 | 0.0006401 | 6.0815 | 6.0821 | -18.8075 | 1562.2526 | 40827.0403 | -0.012039
129 |  | 118.7251 | 318.1835 | 4187 | 0.00064008 | 6.0821 | 6.0828 | -18.8075 | 1562.3117 | 41145.2238 | -0.012038
130 |  | 118.7251 | 318.1715 | 4187 | 0.00064005 | 6.0828 | 6.0834 | -18.8075 | 1562.3708 | 41463.3953 | -0.012038
131 |  | 118.7251 | 318.1594 | 4187 | 0.00064003 | 6.0834 | 6.0841 | -18.8075 | 1562.4299 | 41781.5547 | -0.012037
132 |  | 118.7251 | 318.1474 | 4187 | 0.00064 | 6.0841 | 6.0847 | -18.8075 | 1562.489 | 42099.7021 | -0.012037
133 |  | 118.7251 | 318.1354 | 4187 | 0.00063998 | 6.0847 | 6.0853 | -18.8075 | 1562.5482 | 42417.8375 | -0.012036
134 |  | 118.7251 | 318.1233 | 4187 | 0.00063996 | 6.0853 | 6.086 | -18.8075 | 1562.6073 | 42735.9608 | -0.012036
135 |  | 118.7251 | 318.1113 | 4187 | 0.00063993 | 6.086 | 6.0866 | -18.8075 | 1562.6664 | 43054.0721 | -0.012036
136 |  | 118.7251 | 318.0993 | 4187 | 0.00063991 | 6.0866 | 6.0873 | -18.8075 | 1562.7255 | 43372.1713 | -0.012035
137 |  | 118.7251 | 318.0872 | 4187 | 0.00063988 | 6.0873 | 6.0879 | -18.8075 | 1562.7847 | 43690.2586 | -0.012035
138 |  | 118.7251 | 318.0752 | 4187 | 0.00063986 | 6.0879 | 6.0885 | -18.8075 | 1562.8438 | 44008.3337 | -0.012034
139 |  | 118.7251 | 318.0631 | 4187 | 0.00063984 | 6.0885 | 6.0892 | -18.8075 | 1562.9029 | 44326.3969 | -0.012034
140 |  | 118.7251 | 318.0511 | 4187 | 0.00063981 | 6.0892 | 6.0898 | -18.8075 | 1562.9621 | 44644.448 | -0.012033
141 |  | 118.7251 | 318.0391 | 4187 | 0.00063979 | 6.0898 | 6.0904 | -18.8075 | 1563.0212 | 44962.4871 | -0.012033
142 |  | 118.7251 | 318.027 | 4187 | 0.00063976 | 6.0904 | 6.0911 | -18.8075 | 1563.0803 | 45280.5141 | -0.012032
143 |  | 118.7251 | 318.015 | 4187 | 0.00063974 | 6.0911 | 6.0917 | -18.8075 | 1563.1395 | 45598.5291 | -0.012032
144 |  | 118.7251 | 318.003 | 4187 | 0.00063971 | 6.0917 | 6.0924 | -18.8075 | 1563.1986 | 45916.5321 | -0.012031
145 |  | 118.7251 | 317.991 | 4187 | 0.00063969 | 6.0924 | 6.093 | -18.8075 | 1563.2578 | 46234.5231 | -0.012031
146 |  | 118.7251 | 317.9789 | 4187 | 0.00063967 | 6.093 | 6.0936 | -18.8075 | 1563.3169 | 46552.502 | -0.012031
147 |  | 118.7251 | 317.9669 | 4187 | 0.00063964 | 6.0936 | 6.0943 | -18.8075 | 1563.3761 | 46870.4689 | -0.01203
148 |  | 118.7251 | 317.9549 | 4187 | 0.00063962 | 6.0943 | 6.0949 | -18.8075 | 1563.4352 | 47188.4237 | -0.01203
149 |  | 118.7251 | 317.9428 | 4187 | 0.00063959 | 6.0949 | 6.0956 | -18.8075 | 1563.4944 | 47506.3666 | -0.012029
150 |  | 118.7251 | 317.9308 | 4187 | 0.00063957 | 6.0956 | 6.0962 | -18.8075 | 1563.5535 | 47824.2974 | -0.012029
151 |  | 118.7251 | 317.9188 | 4187 | 0.00063954 | 6.0962 | 6.0968 | -18.8075 | 1563.6127 | 48142.2162 | -0.012028
152 |  | 118.7251 | 317.9067 | 4187 | 0.00063952 | 6.0968 | 6.0975 | -18.8075 | 1563.6718 | 48460.1229 | -0.012028
153 |  | 118.7251 | 317.8947 | 4187 | 0.0006395 | 6.0975 | 6.0981 | -18.8075 | 1563.731 | 48778.0176 | -0.012027
154 |  | 118.7251 | 317.8827 | 4187 | 0.00063947 | 6.0981 | 6.0988 | -18.8075 | 1563.7902 | 49095.9003 | -0.012027
155 |  | 118.7251 | 317.8707 | 4187 | 0.00063945 | 6.0988 | 6.0994 | -18.8075 | 1563.8493 | 49413.771 | -0.012026
156 |  | 118.7251 | 317.8586 | 4187 | 0.00063942 | 6.0994 | 6.1 | -18.8075 | 1563.9085 | 49731.6296 | -0.012026
157 |  | 118.7251 | 317.8466 | 4187 | 0.0006394 | 6.1 | 6.1007 | -18.8075 | 1563.9677 | 50049.4762 | -0.012026
158 |  | 118.7251 | 317.8346 | 4187 | 0.00063938 | 6.1007 | 6.1013 | -18.8075 | 1564.0268 | 50367.3108 | -0.012025
159 |  | 118.7251 | 317.8226 | 4187 | 0.00063935 | 6.1013 | 6.102 | -18.8075 | 1564.086 | 50685.1334 | -0.012025
160 |  | 118.7251 | 317.8105 | 4187 | 0.00063933 | 6.102 | 6.1026 | -18.8075 | 1564.1452 | 51002.9439 | -0.012024
161 |  | 118.7251 | 317.7985 | 4187 | 0.0006393 | 6.1026 | 6.1032 | -18.8075 | 1564.2044 | 51320.7424 | -0.012024
162 |  | 118.7251 | 317.7865 | 4187 | 0.00063928 | 6.1032 | 6.1039 | -18.8075 | 1564.2636 | 51638.5289 | -0.012023
163 |  | 118.7251 | 317.7745 | 4187 | 0.00063925 | 6.1039 | 6.1045 | -18.8075 | 1564.3227 | 51956.3033 | -0.012023
164 |  | 118.7251 | 317.7624 | 4187 | 0.00063923 | 6.1045 | 6.1052 | -18.8075 | 1564.3819 | 52274.0658 | -0.012022
165 |  | 118.7251 | 317.7504 | 4187 | 0.00063921 | 6.1052 | 6.1058 | -18.8075 | 1564.4411 | 52591.8162 | -0.012022
166 |  | 118.7251 | 317.7384 | 4187 | 0.00063918 | 6.1058 | 6.1064 | -18.8075 | 1564.5003 | 52909.5546 | -0.012021
167 |  | 118.7251 | 317.7264 | 4187 | 0.00063916 | 6.1064 | 6.1071 | -18.8075 | 1564.5595 | 53227.281 | -0.012021
168 |  | 118.7251 | 317.7144 | 4187 | 0.00063913 | 6.1071 | 6.1077 | -18.8075 | 1564.6187 | 53544.9953 | -0.012021
169 |  | 118.7251 | 317.7023 | 4187 | 0.00063911 | 6.1077 | 6.1084 | -18.8075 | 1564.6779 | 53862.6977 | -0.01202
170 |  | 118.7251 | 317.6903 | 4187 | 0.00063908 | 6.1084 | 6.109 | -18.8075 | 1564.7371 | 54180.388 | -0.01202
171 |  | 118.7251 | 317.6783 | 4187 | 0.00063906 | 6.109 | 6.1096 | -18.8075 | 1564.7963 | 54498.0663 | -0.012019
172 |  | 118.7251 | 317.6663 | 4187 | 0.00063904 | 6.1096 | 6.1103 | -18.8075 | 1564.8555 | 54815.7325 | -0.012019
173 |  | 118.7251 | 317.6543 | 4187 | 0.00063901 | 6.1103 | 6.1109 | -18.8075 | 1564.9147 | 55133.3868 | -0.012018
174 |  | 118.7251 | 317.6422 | 4187 | 0.00063899 | 6.1109 | 6.1115 | -18.8075 | 1564.9739 | 55451.029 | -0.012018
175 |  | 118.7251 | 317.6302 | 4187 | 0.00063896 | 6.1115 | 6.1122 | -18.8075 | 1565.0331 | 55768.6593 | -0.012017
176 |  | 118.7251 | 317.6182 | 4187 | 0.00063894 | 6.1122 | 6.1128 | -18.8075 | 1565.0924 | 56086.2775 | -0.012017
177 |  | 118.7251 | 317.6062 | 4187 | 0.00063892 | 6.1128 | 6.1135 | -18.8075 | 1565.1516 | 56403.8836 | -0.012016
178 |  | 118.7251 | 317.5942 | 4187 | 0.00063889 | 6.1135 | 6.1141 | -18.8075 | 1565.2108 | 56721.4778 | -0.012016
179 |  | 118.7251 | 317.5822 | 4187 | 0.00063887 | 6.1141 | 6.1147 | -18.8075 | 1565.27 | 57039.06 | -0.012016
180 |  | 118.7251 | 317.5701 | 4187 | 0.00063884 | 6.1147 | 6.1154 | -18.8075 | 1565.3292 | 57356.6301 | -0.012015
181 |  | 118.7251 | 317.5581 | 4187 | 0.00063882 | 6.1154 | 6.116 | -18.8075 | 1565.3885 | 57674.1882 | -0.012015
182 |  | 118.7251 | 317.5461 | 4187 | 0.00063879 | 6.116 | 6.1167 | -18.8075 | 1565.4477 | 57991.7343 | -0.012014
183 |  | 118.7251 | 317.5341 | 4187 | 0.00063877 | 6.1167 | 6.1173 | -18.8075 | 1565.5069 | 58309.2684 | -0.012014
184 |  | 118.7251 | 317.5221 | 4187 | 0.00063875 | 6.1173 | 6.1179 | -18.8075 | 1565.5662 | 58626.7905 | -0.012013
185 |  | 118.7251 | 317.5101 | 4187 | 0.00063872 | 6.1179 | 6.1186 | -18.8075 | 1565.6254 | 58944.3006 | -0.012013
186 |  | 118.7251 | 317.4981 | 4187 | 0.0006387 | 6.1186 | 6.1192 | -18.8075 | 1565.6846 | 59261.7986 | -0.012012
187 |  | 118.7251 | 317.486 | 4187 | 0.00063867 | 6.1192 | 6.1199 | -18.8075 | 1565.7439 | 59579.2847 | -0.012012
188 |  | 118.7251 | 317.474 | 4187 | 0.00063865 | 6.1199 | 6.1205 | -18.8075 | 1565.8031 | 59896.7587 | -0.012011
189 |  | 118.7251 | 317.462 | 4187 | 0.00063863 | 6.1205 | 6.1211 | -18.8075 | 1565.8624 | 60214.2207 | -0.012011
190 |  | 118.7251 | 317.45 | 4187 | 0.0006386 | 6.1211 | 6.1218 | -18.8075 | 1565.9216 | 60531.6707 | -0.012011
191 |  | 118.7251 | 317.438 | 4187 | 0.00063858 | 6.1218 | 6.1224 | -18.8075 | 1565.9808 | 60849.1087 | -0.01201
192 |  | 118.7251 | 317.426 | 4187 | 0.00063855 | 6.1224 | 6.123 | -18.8075 | 1566.0401 | 61166.5347 | -0.01201
193 |  | 118.7251 | 317.414 | 4187 | 0.00063853 | 6.123 | 6.1237 | -18.8075 | 1566.0993 | 61483.9487 | -0.012009
194 |  | 118.7251 | 317.402 | 4187 | 0.0006385 | 6.1237 | 6.1243 | -18.8075 | 1566.1586 | 61801.3506 | -0.012009
195 |  | 118.7251 | 317.39 | 4187 | 0.00063848 | 6.1243 | 6.125 | -18.8075 | 1566.2179 | 62118.7406 | -0.012008
196 |  | 118.7251 | 317.378 | 4187 | 0.00063846 | 6.125 | 6.1256 | -18.8075 | 1566.2771 | 62436.1186 | -0.012008
197 |  | 118.7251 | 317.3659 | 4187 | 0.00063843 | 6.1256 | 6.1262 | -18.8075 | 1566.3364 | 62753.4845 | -0.012007
198 |  | 118.7251 | 317.3539 | 4187 | 0.00063841 | 6.1262 | 6.1269 | -18.8075 | 1566.3956 | 63070.8384 | -0.012007
199 |  | 118.7251 | 317.3419 | 4187 | 0.00063838 | 6.1269 | 6.1275 | -18.8075 | 1566.4549 | 63388.1804 | -0.012006
200 |  | 118.7251 | 317.3299 | 4187 | 0.00063836 | 6.1275 | 6.1282 | -18.8075 | 1566.5142 | 63705.5103 | -0.012006
201 |  | 118.7251 | 317.3179 | 4187 | 0.00063834 | 6.1282 | 6.1288 | -18.8075 | 1566.5734 | 64022.8282 | -0.012006
202 |  | 118.7251 | 317.3059 | 4187 | 0.00063831 | 6.1288 | 6.1294 | -18.8075 | 1566.6327 | 64340.1341 | -0.012005
203 |  | 118.7251 | 317.2939 | 4187 | 0.00063829 | 6.1294 | 6.1301 | -18.8075 | 1566.692 | 64657.428 | -0.012005
204 |  | 118.7251 | 317.2819 | 4187 | 0.00063826 | 6.1301 | 6.1307 | -18.8075 | 1566.7513 | 64974.7099 | -0.012004
205 |  | 118.7251 | 317.2699 | 4187 | 0.00063824 | 6.1307 | 6.1313 | -18.8075 | 1566.8106 | 65291.9798 | -0.012004
206 |  | 118.7251 | 317.2579 | 4187 | 0.00063822 | 6.1313 | 6.132 | -18.8075 | 1566.8698 | 65609.2377 | -0.012003
207 |  | 118.7251 | 317.2459 | 4187 | 0.00063819 | 6.132 | 6.1326 | -18.8075 | 1566.9291 | 65926.4836 | -0.012003
208 |  | 118.7251 | 317.2339 | 4187 | 0.00063817 | 6.1326 | 6.1333 | -18.8075 | 1566.9884 | 66243.7175 | -0.012002
209 |  | 118.7251 | 317.2219 | 4187 | 0.00063814 | 6.1333 | 6.1339 | -18.8075 | 1567.0477 | 66560.9394 | -0.012002
210 |  | 118.7251 | 317.2099 | 4187 | 0.00063812 | 6.1339 | 6.1345 | -18.8075 | 1567.107 | 66878.1493 | -0.012001
211 |  | 118.7251 | 317.1979 | 4187 | 0.00063809 | 6.1345 | 6.1352 | -18.8075 | 1567.1663 | 67195.3471 | -0.012001
212 |  | 118.7251 | 317.1859 | 4187 | 0.00063807 | 6.1352 | 6.1358 | -18.8075 | 1567.2256 | 67512.533 | -0.012001
213 |  | 118.7251 | 317.1739 | 4187 | 0.00063805 | 6.1358 | 6.1365 | -18.8075 | 1567.2849 | 67829.7069 | -0.012
214 |  | 118.7251 | 317.1619 | 4187 | 0.00063802 | 6.1365 | 6.1371 | -18.8075 | 1567.3442 | 68146.8688 | -0.012
215 |  | 118.7251 | 317.1499 | 4187 | 0.000638 | 6.1371 | 6.1377 | -18.8075 | 1567.4035 | 68464.0187 | -0.011999
216 |  | 118.7251 | 317.1379 | 4187 | 0.00063797 | 6.1377 | 6.1384 | -18.8075 | 1567.4628 | 68781.1565 | -0.011999
217 |  | 118.7251 | 317.1259 | 4187 | 0.00063795 | 6.1384 | 6.139 | -18.8075 | 1567.5221 | 69098.2824 | -0.011998
218 |  | 118.7251 | 317.1139 | 4187 | 0.00063793 | 6.139 | 6.1396 | -18.8075 | 1567.5814 | 69415.3963 | -0.011998
219 |  | 118.7251 | 317.1019 | 4187 | 0.0006379 | 6.1396 | 6.1403 | -18.8075 | 1567.6407 | 69732.4982 | -0.011997
220 |  | 118.7251 | 317.0899 | 4187 | 0.00063788 | 6.1403 | 6.1409 | -18.8075 | 1567.7 | 70049.5881 | -0.011997
221 |  | 118.7251 | 317.0779 | 4187 | 0.00063785 | 6.1409 | 6.1416 | -18.8075 | 1567.7593 | 70366.666 | -0.011996
222 |  | 118.7251 | 317.0659 | 4187 | 0.00063783 | 6.1416 | 6.1422 | -18.8075 | 1567.8186 | 70683.7319 | -0.011996
223 |  | 118.7251 | 317.0539 | 4187 | 0.0006378 | 6.1422 | 6.1428 | -18.8075 | 1567.878 | 71000.7858 | -0.011996
224 |  | 118.7251 | 317.0419 | 4187 | 0.00063778 | 6.1428 | 6.1435 | -18.8075 | 1567.9373 | 71317.8277 | -0.011995
225 |  | 118.7251 | 317.0299 | 4187 | 0.00063776 | 6.1435 | 6.1441 | -18.8075 | 1567.9966 | 71634.8576 | -0.011995
226 |  | 118.7251 | 317.0179 | 4187 | 0.00063773 | 6.1441 | 6.1447 | -18.8075 | 1568.0559 | 71951.8755 | -0.011994
227 |  | 118.7251 | 317.0059 | 4187 | 0.00063771 | 6.1447 | 6.1454 | -18.8075 | 1568.1153 | 72268.8814 | -0.011994
228 |  | 118.7251 | 316.9939 | 4187 | 0.00063768 | 6.1454 | 6.146 | -18.8075 | 1568.1746 | 72585.8753 | -0.011993
229 |  | 118.7251 | 316.9819 | 4187 | 0.00063766 | 6.146 | 6.1467 | -18.8075 | 1568.2339 | 72902.8573 | -0.011993
230 |  | 118.7251 | 316.9699 | 4187 | 0.00063764 | 6.1467 | 6.1473 | -18.8075 | 1568.2933 | 73219.8272 | -0.011992
231 |  | 118.7251 | 316.9579 | 4187 | 0.00063761 | 6.1473 | 6.1479 | -18.8075 | 1568.3526 | 73536.7852 | -0.011992
232 |  | 118.7251 | 316.946 | 4187 | 0.00063759 | 6.1479 | 6.1486 | -18.8075 | 1568.4119 | 73853.7311 | -0.011991
233 |  | 118.7251 | 316.934 | 4187 | 0.00063756 | 6.1486 | 6.1492 | -18.8075 | 1568.4713 | 74170.6651 | -0.011991
234 |  | 118.7251 | 316.922 | 4187 | 0.00063754 | 6.1492 | 6.1498 | -18.8075 | 1568.5306 | 74487.5871 | -0.011991
235 |  | 118.7251 | 316.91 | 4187 | 0.00063752 | 6.1498 | 6.1505 | -18.8075 | 1568.59 | 74804.497 | -0.01199
236 |  | 118.7251 | 316.898 | 4187 | 0.00063749 | 6.1505 | 6.1511 | -18.8075 | 1568.6493 | 75121.395 | -0.01199

## St457
|  |  | buis | verlies W/M | L /°C/sec
diam | wandikte |  | inhoud l/m |  | W/M
457 | 10 | 3.1416 | 149.9867 | 359.4095 | 4187
[8 empty] | J/sec/mtr | aantal mtr. | verlies
|  | buis | verlies W/M | L /°C/sec | verlies temp | begintemp | eindtemp | verlies | bij 1°C | totaal J/sec
|  | inhoud L |  | W/M | °C per M | °C | °C | per m°C | daling | aantal mtr
1 | 457 | 149.9867 | 359.4095 | 4187 | 0.00057231 | 6 | 6.0006 | -21.1417 | 1747.2946 | 359.4095 | -0.0121
2 |  | 149.9867 | 359.3974 | 4187 | 0.00057229 | 6.0006 | 6.0011 | -21.1417 | 1747.3534 | 718.8069 | -0.012099
3 |  | 149.9867 | 359.3853 | 4187 | 0.00057227 | 6.0011 | 6.0017 | -21.1417 | 1747.4123 | 1078.1923 | -0.012099
4 |  | 149.9867 | 359.3732 | 4187 | 0.00057226 | 6.0017 | 6.0023 | -21.1417 | 1747.4711 | 1437.5655 | -0.012098
5 |  | 149.9867 | 359.3611 | 4187 | 0.00057224 | 6.0023 | 6.0029 | -21.1417 | 1747.5299 | 1796.9266 | -0.012098
6 |  | 149.9867 | 359.349 | 4187 | 0.00057222 | 6.0029 | 6.0034 | -21.1417 | 1747.5887 | 2156.2757 | -0.012098
7 |  | 149.9867 | 359.3369 | 4187 | 0.0005722 | 6.0034 | 6.004 | -21.1417 | 1747.6476 | 2515.6126 | -0.012097
8 |  | 149.9867 | 359.3248 | 4187 | 0.00057218 | 6.004 | 6.0046 | -21.1417 | 1747.7064 | 2874.9374 | -0.012097
9 |  | 149.9867 | 359.3127 | 4187 | 0.00057216 | 6.0046 | 6.0052 | -21.1417 | 1747.7653 | 3234.2502 | -0.012096
10 |  | 149.9867 | 359.3006 | 4187 | 0.00057214 | 6.0052 | 6.0057 | -21.1417 | 1747.8241 | 3593.5508 | -0.012096
11 |  | 149.9867 | 359.2885 | 4187 | 0.00057212 | 6.0057 | 6.0063 | -21.1417 | 1747.8829 | 3952.8394 | -0.012096
12 |  | 149.9867 | 359.2765 | 4187 | 0.0005721 | 6.0063 | 6.0069 | -21.1417 | 1747.9418 | 4312.1158 | -0.012095
13 |  | 149.9867 | 359.2644 | 4187 | 0.00057208 | 6.0069 | 6.0074 | -21.1417 | 1748.0006 | 4671.3802 | -0.012095
14 |  | 149.9867 | 359.2523 | 4187 | 0.00057206 | 6.0074 | 6.008 | -21.1417 | 1748.0595 | 5030.6324 | -0.012094
15 |  | 149.9867 | 359.2402 | 4187 | 0.00057204 | 6.008 | 6.0086 | -21.1417 | 1748.1183 | 5389.8726 | -0.012094
16 |  | 149.9867 | 359.2281 | 4187 | 0.00057202 | 6.0086 | 6.0092 | -21.1417 | 1748.1772 | 5749.1007 | -0.012094
17 |  | 149.9867 | 359.216 | 4187 | 0.00057201 | 6.0092 | 6.0097 | -21.1417 | 1748.236 | 6108.3166 | -0.012093
18 |  | 149.9867 | 359.2039 | 4187 | 0.00057199 | 6.0097 | 6.0103 | -21.1417 | 1748.2949 | 6467.5205 | -0.012093
19 |  | 149.9867 | 359.1918 | 4187 | 0.00057197 | 6.0103 | 6.0109 | -21.1417 | 1748.3538 | 6826.7123 | -0.012092
20 |  | 149.9867 | 359.1797 | 4187 | 0.00057195 | 6.0109 | 6.0114 | -21.1417 | 1748.4126 | 7185.892 | -0.012092
21 |  | 149.9867 | 359.1676 | 4187 | 0.00057193 | 6.0114 | 6.012 | -21.1417 | 1748.4715 | 7545.0596 | -0.012092
22 |  | 149.9867 | 359.1555 | 4187 | 0.00057191 | 6.012 | 6.0126 | -21.1417 | 1748.5303 | 7904.2151 | -0.012091
23 |  | 149.9867 | 359.1434 | 4187 | 0.00057189 | 6.0126 | 6.0132 | -21.1417 | 1748.5892 | 8263.3586 | -0.012091
24 |  | 149.9867 | 359.1313 | 4187 | 0.00057187 | 6.0132 | 6.0137 | -21.1417 | 1748.6481 | 8622.4899 | -0.01209
25 |  | 149.9867 | 359.1192 | 4187 | 0.00057185 | 6.0137 | 6.0143 | -21.1417 | 1748.707 | 8981.6091 | -0.01209
26 |  | 149.9867 | 359.1072 | 4187 | 0.00057183 | 6.0143 | 6.0149 | -21.1417 | 1748.7658 | 9340.7163 | -0.01209
27 |  | 149.9867 | 359.0951 | 4187 | 0.00057181 | 6.0149 | 6.0154 | -21.1417 | 1748.8247 | 9699.8114 | -0.012089
28 |  | 149.9867 | 359.083 | 4187 | 0.00057179 | 6.0154 | 6.016 | -21.1417 | 1748.8836 | 10058.8943 | -0.012089
29 |  | 149.9867 | 359.0709 | 4187 | 0.00057177 | 6.016 | 6.0166 | -21.1417 | 1748.9425 | 10417.9652 | -0.012088
30 |  | 149.9867 | 359.0588 | 4187 | 0.00057175 | 6.0166 | 6.0172 | -21.1417 | 1749.0013 | 10777.024 | -0.012088
31 |  | 149.9867 | 359.0467 | 4187 | 0.00057174 | 6.0172 | 6.0177 | -21.1417 | 1749.0602 | 11136.0707 | -0.012087
32 |  | 149.9867 | 359.0346 | 4187 | 0.00057172 | 6.0177 | 6.0183 | -21.1417 | 1749.1191 | 11495.1054 | -0.012087
33 |  | 149.9867 | 359.0225 | 4187 | 0.0005717 | 6.0183 | 6.0189 | -21.1417 | 1749.178 | 11854.1279 | -0.012087
34 |  | 149.9867 | 359.0104 | 4187 | 0.00057168 | 6.0189 | 6.0194 | -21.1417 | 1749.2369 | 12213.1383 | -0.012086
35 |  | 149.9867 | 358.9984 | 4187 | 0.00057166 | 6.0194 | 6.02 | -21.1417 | 1749.2958 | 12572.1367 | -0.012086
36 |  | 149.9867 | 358.9863 | 4187 | 0.00057164 | 6.02 | 6.0206 | -21.1417 | 1749.3547 | 12931.123 | -0.012085
37 |  | 149.9867 | 358.9742 | 4187 | 0.00057162 | 6.0206 | 6.0212 | -21.1417 | 1749.4136 | 13290.0972 | -0.012085
38 |  | 149.9867 | 358.9621 | 4187 | 0.0005716 | 6.0212 | 6.0217 | -21.1417 | 1749.4725 | 13649.0593 | -0.012085
39 |  | 149.9867 | 358.95 | 4187 | 0.00057158 | 6.0217 | 6.0223 | -21.1417 | 1749.5314 | 14008.0093 | -0.012084
40 |  | 149.9867 | 358.9379 | 4187 | 0.00057156 | 6.0223 | 6.0229 | -21.1417 | 1749.5903 | 14366.9472 | -0.012084
41 |  | 149.9867 | 358.9259 | 4187 | 0.00057154 | 6.0229 | 6.0234 | -21.1417 | 1749.6492 | 14725.8731 | -0.012083
42 |  | 149.9867 | 358.9138 | 4187 | 0.00057152 | 6.0234 | 6.024 | -21.1417 | 1749.7081 | 15084.7869 | -0.012083
43 |  | 149.9867 | 358.9017 | 4187 | 0.0005715 | 6.024 | 6.0246 | -21.1417 | 1749.767 | 15443.6886 | -0.012083
44 |  | 149.9867 | 358.8896 | 4187 | 0.00057149 | 6.0246 | 6.0252 | -21.1417 | 1749.8259 | 15802.5782 | -0.012082
45 |  | 149.9867 | 358.8775 | 4187 | 0.00057147 | 6.0252 | 6.0257 | -21.1417 | 1749.8848 | 16161.4557 | -0.012082
46 |  | 149.9867 | 358.8654 | 4187 | 0.00057145 | 6.0257 | 6.0263 | -21.1417 | 1749.9437 | 16520.3211 | -0.012081
47 |  | 149.9867 | 358.8534 | 4187 | 0.00057143 | 6.0263 | 6.0269 | -21.1417 | 1750.0026 | 16879.1745 | -0.012081
48 |  | 149.9867 | 358.8413 | 4187 | 0.00057141 | 6.0269 | 6.0274 | -21.1417 | 1750.0615 | 17238.0158 | -0.012081
49 |  | 149.9867 | 358.8292 | 4187 | 0.00057139 | 6.0274 | 6.028 | -21.1417 | 1750.1205 | 17596.845 | -0.01208
50 |  | 149.9867 | 358.8171 | 4187 | 0.00057137 | 6.028 | 6.0286 | -21.1417 | 1750.1794 | 17955.6621 | -0.01208
51 |  | 149.9867 | 358.805 | 4187 | 0.00057135 | 6.0286 | 6.0292 | -21.1417 | 1750.2383 | 18314.4671 | -0.012079
52 |  | 149.9867 | 358.793 | 4187 | 0.00057133 | 6.0292 | 6.0297 | -21.1417 | 1750.2972 | 18673.2601 | -0.012079
53 |  | 149.9867 | 358.7809 | 4187 | 0.00057131 | 6.0297 | 6.0303 | -21.1417 | 1750.3562 | 19032.041 | -0.012079
54 |  | 149.9867 | 358.7688 | 4187 | 0.00057129 | 6.0303 | 6.0309 | -21.1417 | 1750.4151 | 19390.8098 | -0.012078
55 |  | 149.9867 | 358.7567 | 4187 | 0.00057127 | 6.0309 | 6.0314 | -21.1417 | 1750.474 | 19749.5665 | -0.012078
56 |  | 149.9867 | 358.7446 | 4187 | 0.00057125 | 6.0314 | 6.032 | -21.1417 | 1750.5329 | 20108.3111 | -0.012077
57 |  | 149.9867 | 358.7326 | 4187 | 0.00057124 | 6.032 | 6.0326 | -21.1417 | 1750.5919 | 20467.0437 | -0.012077
58 |  | 149.9867 | 358.7205 | 4187 | 0.00057122 | 6.0326 | 6.0332 | -21.1417 | 1750.6508 | 20825.7642 | -0.012077
59 |  | 149.9867 | 358.7084 | 4187 | 0.0005712 | 6.0332 | 6.0337 | -21.1417 | 1750.7098 | 21184.4726 | -0.012076
60 |  | 149.9867 | 358.6963 | 4187 | 0.00057118 | 6.0337 | 6.0343 | -21.1417 | 1750.7687 | 21543.1689 | -0.012076
61 |  | 149.9867 | 358.6843 | 4187 | 0.00057116 | 6.0343 | 6.0349 | -21.1417 | 1750.8276 | 21901.8532 | -0.012075
62 |  | 149.9867 | 358.6722 | 4187 | 0.00057114 | 6.0349 | 6.0354 | -21.1417 | 1750.8866 | 22260.5254 | -0.012075
63 |  | 149.9867 | 358.6601 | 4187 | 0.00057112 | 6.0354 | 6.036 | -21.1417 | 1750.9455 | 22619.1855 | -0.012074
64 |  | 149.9867 | 358.648 | 4187 | 0.0005711 | 6.036 | 6.0366 | -21.1417 | 1751.0045 | 22977.8335 | -0.012074
65 |  | 149.9867 | 358.636 | 4187 | 0.00057108 | 6.0366 | 6.0372 | -21.1417 | 1751.0634 | 23336.4695 | -0.012074
66 |  | 149.9867 | 358.6239 | 4187 | 0.00057106 | 6.0372 | 6.0377 | -21.1417 | 1751.1224 | 23695.0934 | -0.012073
67 |  | 149.9867 | 358.6118 | 4187 | 0.00057104 | 6.0377 | 6.0383 | -21.1417 | 1751.1813 | 24053.7052 | -0.012073
68 |  | 149.9867 | 358.5997 | 4187 | 0.00057102 | 6.0383 | 6.0389 | -21.1417 | 1751.2403 | 24412.305 | -0.012072
69 |  | 149.9867 | 358.5877 | 4187 | 0.000571 | 6.0389 | 6.0394 | -21.1417 | 1751.2992 | 24770.8926 | -0.012072
70 |  | 149.9867 | 358.5756 | 4187 | 0.00057099 | 6.0394 | 6.04 | -21.1417 | 1751.3582 | 25129.4682 | -0.012072
71 |  | 149.9867 | 358.5635 | 4187 | 0.00057097 | 6.04 | 6.0406 | -21.1417 | 1751.4172 | 25488.0318 | -0.012071
72 |  | 149.9867 | 358.5515 | 4187 | 0.00057095 | 6.0406 | 6.0412 | -21.1417 | 1751.4761 | 25846.5832 | -0.012071
73 |  | 149.9867 | 358.5394 | 4187 | 0.00057093 | 6.0412 | 6.0417 | -21.1417 | 1751.5351 | 26205.1226 | -0.01207
74 |  | 149.9867 | 358.5273 | 4187 | 0.00057091 | 6.0417 | 6.0423 | -21.1417 | 1751.5941 | 26563.6499 | -0.01207
75 |  | 149.9867 | 358.5152 | 4187 | 0.00057089 | 6.0423 | 6.0429 | -21.1417 | 1751.653 | 26922.1652 | -0.01207
76 |  | 149.9867 | 358.5032 | 4187 | 0.00057087 | 6.0429 | 6.0434 | -21.1417 | 1751.712 | 27280.6684 | -0.012069
77 |  | 149.9867 | 358.4911 | 4187 | 0.00057085 | 6.0434 | 6.044 | -21.1417 | 1751.771 | 27639.1595 | -0.012069
78 |  | 149.9867 | 358.479 | 4187 | 0.00057083 | 6.044 | 6.0446 | -21.1417 | 1751.83 | 27997.6385 | -0.012068
79 |  | 149.9867 | 358.467 | 4187 | 0.00057081 | 6.0446 | 6.0452 | -21.1417 | 1751.8889 | 28356.1055 | -0.012068
80 |  | 149.9867 | 358.4549 | 4187 | 0.00057079 | 6.0452 | 6.0457 | -21.1417 | 1751.9479 | 28714.5604 | -0.012068
81 |  | 149.9867 | 358.4428 | 4187 | 0.00057077 | 6.0457 | 6.0463 | -21.1417 | 1752.0069 | 29073.0032 | -0.012067
82 |  | 149.9867 | 358.4308 | 4187 | 0.00057075 | 6.0463 | 6.0469 | -21.1417 | 1752.0659 | 29431.434 | -0.012067
83 |  | 149.9867 | 358.4187 | 4187 | 0.00057074 | 6.0469 | 6.0474 | -21.1417 | 1752.1249 | 29789.8527 | -0.012066
84 |  | 149.9867 | 358.4066 | 4187 | 0.00057072 | 6.0474 | 6.048 | -21.1417 | 1752.1839 | 30148.2593 | -0.012066
85 |  | 149.9867 | 358.3946 | 4187 | 0.0005707 | 6.048 | 6.0486 | -21.1417 | 1752.2429 | 30506.6539 | -0.012066
86 |  | 149.9867 | 358.3825 | 4187 | 0.00057068 | 6.0486 | 6.0491 | -21.1417 | 1752.3018 | 30865.0364 | -0.012065
87 |  | 149.9867 | 358.3704 | 4187 | 0.00057066 | 6.0491 | 6.0497 | -21.1417 | 1752.3608 | 31223.4068 | -0.012065
88 |  | 149.9867 | 358.3584 | 4187 | 0.00057064 | 6.0497 | 6.0503 | -21.1417 | 1752.4198 | 31581.7652 | -0.012064
89 |  | 149.9867 | 358.3463 | 4187 | 0.00057062 | 6.0503 | 6.0509 | -21.1417 | 1752.4788 | 31940.1115 | -0.012064
90 |  | 149.9867 | 358.3342 | 4187 | 0.0005706 | 6.0509 | 6.0514 | -21.1417 | 1752.5378 | 32298.4457 | -0.012063
91 |  | 149.9867 | 358.3222 | 4187 | 0.00057058 | 6.0514 | 6.052 | -21.1417 | 1752.5968 | 32656.7679 | -0.012063
92 |  | 149.9867 | 358.3101 | 4187 | 0.00057056 | 6.052 | 6.0526 | -21.1417 | 1752.6558 | 33015.078 | -0.012063
93 |  | 149.9867 | 358.2981 | 4187 | 0.00057054 | 6.0526 | 6.0531 | -21.1417 | 1752.7148 | 33373.3761 | -0.012062
94 |  | 149.9867 | 358.286 | 4187 | 0.00057052 | 6.0531 | 6.0537 | -21.1417 | 1752.7739 | 33731.6621 | -0.012062
95 |  | 149.9867 | 358.2739 | 4187 | 0.00057051 | 6.0537 | 6.0543 | -21.1417 | 1752.8329 | 34089.936 | -0.012061
96 |  | 149.9867 | 358.2619 | 4187 | 0.00057049 | 6.0543 | 6.0549 | -21.1417 | 1752.8919 | 34448.1979 | -0.012061
97 |  | 149.9867 | 358.2498 | 4187 | 0.00057047 | 6.0549 | 6.0554 | -21.1417 | 1752.9509 | 34806.4477 | -0.012061
98 |  | 149.9867 | 358.2377 | 4187 | 0.00057045 | 6.0554 | 6.056 | -21.1417 | 1753.0099 | 35164.6855 | -0.01206
99 |  | 149.9867 | 358.2257 | 4187 | 0.00057043 | 6.056 | 6.0566 | -21.1417 | 1753.0689 | 35522.9111 | -0.01206
100 |  | 149.9867 | 358.2136 | 4187 | 0.00057041 | 6.0566 | 6.0571 | -21.1417 | 1753.1279 | 35881.1248 | -0.012059
101 |  | 149.9867 | 358.2016 | 4187 | 0.00057039 | 6.0571 | 6.0577 | -21.1417 | 1753.187 | 36239.3263 | -0.012059
102 |  | 149.9867 | 358.1895 | 4187 | 0.00057037 | 6.0577 | 6.0583 | -21.1417 | 1753.246 | 36597.5159 | -0.012059
103 |  | 149.9867 | 358.1775 | 4187 | 0.00057035 | 6.0583 | 6.0588 | -21.1417 | 1753.305 | 36955.6933 | -0.012058
104 |  | 149.9867 | 358.1654 | 4187 | 0.00057033 | 6.0588 | 6.0594 | -21.1417 | 1753.364 | 37313.8587 | -0.012058
105 |  | 149.9867 | 358.1533 | 4187 | 0.00057031 | 6.0594 | 6.06 | -21.1417 | 1753.4231 | 37672.012 | -0.012057
106 |  | 149.9867 | 358.1413 | 4187 | 0.00057029 | 6.06 | 6.0606 | -21.1417 | 1753.4821 | 38030.1533 | -0.012057
107 |  | 149.9867 | 358.1292 | 4187 | 0.00057027 | 6.0606 | 6.0611 | -21.1417 | 1753.5411 | 38388.2825 | -0.012057
108 |  | 149.9867 | 358.1172 | 4187 | 0.00057026 | 6.0611 | 6.0617 | -21.1417 | 1753.6002 | 38746.3997 | -0.012056
109 |  | 149.9867 | 358.1051 | 4187 | 0.00057024 | 6.0617 | 6.0623 | -21.1417 | 1753.6592 | 39104.5048 | -0.012056
110 |  | 149.9867 | 358.0931 | 4187 | 0.00057022 | 6.0623 | 6.0628 | -21.1417 | 1753.7182 | 39462.5979 | -0.012055
111 |  | 149.9867 | 358.081 | 4187 | 0.0005702 | 6.0628 | 6.0634 | -21.1417 | 1753.7773 | 39820.6789 | -0.012055
112 |  | 149.9867 | 358.0689 | 4187 | 0.00057018 | 6.0634 | 6.064 | -21.1417 | 1753.8363 | 40178.7478 | -0.012055
113 |  | 149.9867 | 358.0569 | 4187 | 0.00057016 | 6.064 | 6.0645 | -21.1417 | 1753.8954 | 40536.8047 | -0.012054
114 |  | 149.9867 | 358.0448 | 4187 | 0.00057014 | 6.0645 | 6.0651 | -21.1417 | 1753.9544 | 40894.8495 | -0.012054
115 |  | 149.9867 | 358.0328 | 4187 | 0.00057012 | 6.0651 | 6.0657 | -21.1417 | 1754.0135 | 41252.8823 | -0.012053
116 |  | 149.9867 | 358.0207 | 4187 | 0.0005701 | 6.0657 | 6.0663 | -21.1417 | 1754.0725 | 41610.903 | -0.012053
117 |  | 149.9867 | 358.0087 | 4187 | 0.00057008 | 6.0663 | 6.0668 | -21.1417 | 1754.1316 | 41968.9117 | -0.012053
118 |  | 149.9867 | 357.9966 | 4187 | 0.00057006 | 6.0668 | 6.0674 | -21.1417 | 1754.1906 | 42326.9083 | -0.012052
119 |  | 149.9867 | 357.9846 | 4187 | 0.00057004 | 6.0674 | 6.068 | -21.1417 | 1754.2497 | 42684.8929 | -0.012052
120 |  | 149.9867 | 357.9725 | 4187 | 0.00057003 | 6.068 | 6.0685 | -21.1417 | 1754.3088 | 43042.8654 | -0.012051
121 |  | 149.9867 | 357.9605 | 4187 | 0.00057001 | 6.0685 | 6.0691 | -21.1417 | 1754.3678 | 43400.8259 | -0.012051
122 |  | 149.9867 | 357.9484 | 4187 | 0.00056999 | 6.0691 | 6.0697 | -21.1417 | 1754.4269 | 43758.7743 | -0.012051
123 |  | 149.9867 | 357.9364 | 4187 | 0.00056997 | 6.0697 | 6.0703 | -21.1417 | 1754.4859 | 44116.7106 | -0.01205
124 |  | 149.9867 | 357.9243 | 4187 | 0.00056995 | 6.0703 | 6.0708 | -21.1417 | 1754.545 | 44474.635 | -0.01205
125 |  | 149.9867 | 357.9123 | 4187 | 0.00056993 | 6.0708 | 6.0714 | -21.1417 | 1754.6041 | 44832.5472 | -0.012049
126 |  | 149.9867 | 357.9002 | 4187 | 0.00056991 | 6.0714 | 6.072 | -21.1417 | 1754.6632 | 45190.4474 | -0.012049
127 |  | 149.9867 | 357.8882 | 4187 | 0.00056989 | 6.072 | 6.0725 | -21.1417 | 1754.7222 | 45548.3356 | -0.012048
128 |  | 149.9867 | 357.8761 | 4187 | 0.00056987 | 6.0725 | 6.0731 | -21.1417 | 1754.7813 | 45906.2117 | -0.012048
129 |  | 149.9867 | 357.8641 | 4187 | 0.00056985 | 6.0731 | 6.0737 | -21.1417 | 1754.8404 | 46264.0758 | -0.012048
130 |  | 149.9867 | 357.852 | 4187 | 0.00056983 | 6.0737 | 6.0742 | -21.1417 | 1754.8995 | 46621.9278 | -0.012047
131 |  | 149.9867 | 357.84 | 4187 | 0.00056981 | 6.0742 | 6.0748 | -21.1417 | 1754.9585 | 46979.7678 | -0.012047
132 |  | 149.9867 | 357.8279 | 4187 | 0.00056979 | 6.0748 | 6.0754 | -21.1417 | 1755.0176 | 47337.5957 | -0.012046
133 |  | 149.9867 | 357.8159 | 4187 | 0.00056978 | 6.0754 | 6.0759 | -21.1417 | 1755.0767 | 47695.4116 | -0.012046
134 |  | 149.9867 | 357.8038 | 4187 | 0.00056976 | 6.0759 | 6.0765 | -21.1417 | 1755.1358 | 48053.2154 | -0.012046
135 |  | 149.9867 | 357.7918 | 4187 | 0.00056974 | 6.0765 | 6.0771 | -21.1417 | 1755.1949 | 48411.0072 | -0.012045
136 |  | 149.9867 | 357.7797 | 4187 | 0.00056972 | 6.0771 | 6.0777 | -21.1417 | 1755.254 | 48768.787 | -0.012045
137 |  | 149.9867 | 357.7677 | 4187 | 0.0005697 | 6.0777 | 6.0782 | -21.1417 | 1755.3131 | 49126.5547 | -0.012044
138 |  | 149.9867 | 357.7557 | 4187 | 0.00056968 | 6.0782 | 6.0788 | -21.1417 | 1755.3722 | 49484.3103 | -0.012044
139 |  | 149.9867 | 357.7436 | 4187 | 0.00056966 | 6.0788 | 6.0794 | -21.1417 | 1755.4313 | 49842.0539 | -0.012044
140 |  | 149.9867 | 357.7316 | 4187 | 0.00056964 | 6.0794 | 6.0799 | -21.1417 | 1755.4904 | 50199.7855 | -0.012043
141 |  | 149.9867 | 357.7195 | 4187 | 0.00056962 | 6.0799 | 6.0805 | -21.1417 | 1755.5495 | 50557.505 | -0.012043
142 |  | 149.9867 | 357.7075 | 4187 | 0.0005696 | 6.0805 | 6.0811 | -21.1417 | 1755.6086 | 50915.2125 | -0.012042
143 |  | 149.9867 | 357.6954 | 4187 | 0.00056958 | 6.0811 | 6.0816 | -21.1417 | 1755.6677 | 51272.9079 | -0.012042
144 |  | 149.9867 | 357.6834 | 4187 | 0.00056956 | 6.0816 | 6.0822 | -21.1417 | 1755.7268 | 51630.5913 | -0.012042
145 |  | 149.9867 | 357.6714 | 4187 | 0.00056955 | 6.0822 | 6.0828 | -21.1417 | 1755.7859 | 51988.2627 | -0.012041
146 |  | 149.9867 | 357.6593 | 4187 | 0.00056953 | 6.0828 | 6.0834 | -21.1417 | 1755.845 | 52345.922 | -0.012041
147 |  | 149.9867 | 357.6473 | 4187 | 0.00056951 | 6.0834 | 6.0839 | -21.1417 | 1755.9041 | 52703.5693 | -0.01204
148 |  | 149.9867 | 357.6352 | 4187 | 0.00056949 | 6.0839 | 6.0845 | -21.1417 | 1755.9632 | 53061.2045 | -0.01204
149 |  | 149.9867 | 357.6232 | 4187 | 0.00056947 | 6.0845 | 6.0851 | -21.1417 | 1756.0224 | 53418.8277 | -0.01204
150 |  | 149.9867 | 357.6112 | 4187 | 0.00056945 | 6.0851 | 6.0856 | -21.1417 | 1756.0815 | 53776.4389 | -0.012039
151 |  | 149.9867 | 357.5991 | 4187 | 0.00056943 | 6.0856 | 6.0862 | -21.1417 | 1756.1406 | 54134.038 | -0.012039
152 |  | 149.9867 | 357.5871 | 4187 | 0.00056941 | 6.0862 | 6.0868 | -21.1417 | 1756.1997 | 54491.6251 | -0.012038
153 |  | 149.9867 | 357.575 | 4187 | 0.00056939 | 6.0868 | 6.0873 | -21.1417 | 1756.2588 | 54849.2001 | -0.012038
154 |  | 149.9867 | 357.563 | 4187 | 0.00056937 | 6.0873 | 6.0879 | -21.1417 | 1756.318 | 55206.7631 | -0.012038
155 |  | 149.9867 | 357.551 | 4187 | 0.00056935 | 6.0879 | 6.0885 | -21.1417 | 1756.3771 | 55564.3141 | -0.012037
156 |  | 149.9867 | 357.5389 | 4187 | 0.00056933 | 6.0885 | 6.089 | -21.1417 | 1756.4362 | 55921.853 | -0.012037
157 |  | 149.9867 | 357.5269 | 4187 | 0.00056932 | 6.089 | 6.0896 | -21.1417 | 1756.4954 | 56279.3799 | -0.012036
158 |  | 149.9867 | 357.5149 | 4187 | 0.0005693 | 6.0896 | 6.0902 | -21.1417 | 1756.5545 | 56636.8947 | -0.012036
159 |  | 149.9867 | 357.5028 | 4187 | 0.00056928 | 6.0902 | 6.0908 | -21.1417 | 1756.6136 | 56994.3975 | -0.012036
160 |  | 149.9867 | 357.4908 | 4187 | 0.00056926 | 6.0908 | 6.0913 | -21.1417 | 1756.6728 | 57351.8883 | -0.012035
161 |  | 149.9867 | 357.4787 | 4187 | 0.00056924 | 6.0913 | 6.0919 | -21.1417 | 1756.7319 | 57709.3671 | -0.012035
162 |  | 149.9867 | 357.4667 | 4187 | 0.00056922 | 6.0919 | 6.0925 | -21.1417 | 1756.7911 | 58066.8338 | -0.012034
163 |  | 149.9867 | 357.4547 | 4187 | 0.0005692 | 6.0925 | 6.093 | -21.1417 | 1756.8502 | 58424.2884 | -0.012034
164 |  | 149.9867 | 357.4426 | 4187 | 0.00056918 | 6.093 | 6.0936 | -21.1417 | 1756.9094 | 58781.7311 | -0.012033
165 |  | 149.9867 | 357.4306 | 4187 | 0.00056916 | 6.0936 | 6.0942 | -21.1417 | 1756.9685 | 59139.1617 | -0.012033
166 |  | 149.9867 | 357.4186 | 4187 | 0.00056914 | 6.0942 | 6.0947 | -21.1417 | 1757.0277 | 59496.5803 | -0.012033
167 |  | 149.9867 | 357.4065 | 4187 | 0.00056912 | 6.0947 | 6.0953 | -21.1417 | 1757.0868 | 59853.9868 | -0.012032
168 |  | 149.9867 | 357.3945 | 4187 | 0.0005691 | 6.0953 | 6.0959 | -21.1417 | 1757.146 | 60211.3813 | -0.012032
169 |  | 149.9867 | 357.3825 | 4187 | 0.00056909 | 6.0959 | 6.0964 | -21.1417 | 1757.2051 | 60568.7638 | -0.012031
170 |  | 149.9867 | 357.3704 | 4187 | 0.00056907 | 6.0964 | 6.097 | -21.1417 | 1757.2643 | 60926.1343 | -0.012031
171 |  | 149.9867 | 357.3584 | 4187 | 0.00056905 | 6.097 | 6.0976 | -21.1417 | 1757.3234 | 61283.4927 | -0.012031
172 |  | 149.9867 | 357.3464 | 4187 | 0.00056903 | 6.0976 | 6.0982 | -21.1417 | 1757.3826 | 61640.8391 | -0.01203
173 |  | 149.9867 | 357.3344 | 4187 | 0.00056901 | 6.0982 | 6.0987 | -21.1417 | 1757.4418 | 61998.1734 | -0.01203
174 |  | 149.9867 | 357.3223 | 4187 | 0.00056899 | 6.0987 | 6.0993 | -21.1417 | 1757.5009 | 62355.4957 | -0.012029
175 |  | 149.9867 | 357.3103 | 4187 | 0.00056897 | 6.0993 | 6.0999 | -21.1417 | 1757.5601 | 62712.806 | -0.012029
176 |  | 149.9867 | 357.2983 | 4187 | 0.00056895 | 6.0999 | 6.1004 | -21.1417 | 1757.6193 | 63070.1043 | -0.012029
177 |  | 149.9867 | 357.2862 | 4187 | 0.00056893 | 6.1004 | 6.101 | -21.1417 | 1757.6784 | 63427.3905 | -0.012028
178 |  | 149.9867 | 357.2742 | 4187 | 0.00056891 | 6.101 | 6.1016 | -21.1417 | 1757.7376 | 63784.6647 | -0.012028
179 |  | 149.9867 | 357.2622 | 4187 | 0.00056889 | 6.1016 | 6.1021 | -21.1417 | 1757.7968 | 64141.9269 | -0.012027
180 |  | 149.9867 | 357.2502 | 4187 | 0.00056887 | 6.1021 | 6.1027 | -21.1417 | 1757.856 | 64499.1771 | -0.012027
181 |  | 149.9867 | 357.2381 | 4187 | 0.00056886 | 6.1027 | 6.1033 | -21.1417 | 1757.9152 | 64856.4152 | -0.012027
182 |  | 149.9867 | 357.2261 | 4187 | 0.00056884 | 6.1033 | 6.1038 | -21.1417 | 1757.9743 | 65213.6413 | -0.012026
183 |  | 149.9867 | 357.2141 | 4187 | 0.00056882 | 6.1038 | 6.1044 | -21.1417 | 1758.0335 | 65570.8554 | -0.012026
184 |  | 149.9867 | 357.202 | 4187 | 0.0005688 | 6.1044 | 6.105 | -21.1417 | 1758.0927 | 65928.0574 | -0.012025
185 |  | 149.9867 | 357.19 | 4187 | 0.00056878 | 6.105 | 6.1056 | -21.1417 | 1758.1519 | 66285.2475 | -0.012025
186 |  | 149.9867 | 357.178 | 4187 | 0.00056876 | 6.1056 | 6.1061 | -21.1417 | 1758.2111 | 66642.4255 | -0.012025
187 |  | 149.9867 | 357.166 | 4187 | 0.00056874 | 6.1061 | 6.1067 | -21.1417 | 1758.2703 | 66999.5914 | -0.012024
188 |  | 149.9867 | 357.154 | 4187 | 0.00056872 | 6.1067 | 6.1073 | -21.1417 | 1758.3295 | 67356.7454 | -0.012024
189 |  | 149.9867 | 357.1419 | 4187 | 0.0005687 | 6.1073 | 6.1078 | -21.1417 | 1758.3887 | 67713.8873 | -0.012023
190 |  | 149.9867 | 357.1299 | 4187 | 0.00056868 | 6.1078 | 6.1084 | -21.1417 | 1758.4479 | 68071.0172 | -0.012023
191 |  | 149.9867 | 357.1179 | 4187 | 0.00056866 | 6.1084 | 6.109 | -21.1417 | 1758.5071 | 68428.1351 | -0.012023
192 |  | 149.9867 | 357.1059 | 4187 | 0.00056865 | 6.109 | 6.1095 | -21.1417 | 1758.5663 | 68785.241 | -0.012022
193 |  | 149.9867 | 357.0938 | 4187 | 0.00056863 | 6.1095 | 6.1101 | -21.1417 | 1758.6255 | 69142.3348 | -0.012022
194 |  | 149.9867 | 357.0818 | 4187 | 0.00056861 | 6.1101 | 6.1107 | -21.1417 | 1758.6847 | 69499.4166 | -0.012021
195 |  | 149.9867 | 357.0698 | 4187 | 0.00056859 | 6.1107 | 6.1112 | -21.1417 | 1758.7439 | 69856.4864 | -0.012021
196 |  | 149.9867 | 357.0578 | 4187 | 0.00056857 | 6.1112 | 6.1118 | -21.1417 | 1758.8031 | 70213.5442 | -0.012021
197 |  | 149.9867 | 357.0458 | 4187 | 0.00056855 | 6.1118 | 6.1124 | -21.1417 | 1758.8623 | 70570.5899 | -0.01202
198 |  | 149.9867 | 357.0337 | 4187 | 0.00056853 | 6.1124 | 6.1129 | -21.1417 | 1758.9215 | 70927.6237 | -0.01202
199 |  | 149.9867 | 357.0217 | 4187 | 0.00056851 | 6.1129 | 6.1135 | -21.1417 | 1758.9808 | 71284.6454 | -0.012019
200 |  | 149.9867 | 357.0097 | 4187 | 0.00056849 | 6.1135 | 6.1141 | -21.1417 | 1759.04 | 71641.6551 | -0.012019
201 |  | 149.9867 | 356.9977 | 4187 | 0.00056847 | 6.1141 | 6.1146 | -21.1417 | 1759.0992 | 71998.6527 | -0.012019
202 |  | 149.9867 | 356.9857 | 4187 | 0.00056845 | 6.1146 | 6.1152 | -21.1417 | 1759.1584 | 72355.6384 | -0.012018
203 |  | 149.9867 | 356.9736 | 4187 | 0.00056843 | 6.1152 | 6.1158 | -21.1417 | 1759.2176 | 72712.612 | -0.012018
204 |  | 149.9867 | 356.9616 | 4187 | 0.00056842 | 6.1158 | 6.1164 | -21.1417 | 1759.2769 | 73069.5736 | -0.012017
205 |  | 149.9867 | 356.9496 | 4187 | 0.0005684 | 6.1164 | 6.1169 | -21.1417 | 1759.3361 | 73426.5232 | -0.012017
206 |  | 149.9867 | 356.9376 | 4187 | 0.00056838 | 6.1169 | 6.1175 | -21.1417 | 1759.3953 | 73783.4608 | -0.012016
207 |  | 149.9867 | 356.9256 | 4187 | 0.00056836 | 6.1175 | 6.1181 | -21.1417 | 1759.4546 | 74140.3864 | -0.012016
208 |  | 149.9867 | 356.9136 | 4187 | 0.00056834 | 6.1181 | 6.1186 | -21.1417 | 1759.5138 | 74497.2999 | -0.012016
209 |  | 149.9867 | 356.9015 | 4187 | 0.00056832 | 6.1186 | 6.1192 | -21.1417 | 1759.573 | 74854.2015 | -0.012015
210 |  | 149.9867 | 356.8895 | 4187 | 0.0005683 | 6.1192 | 6.1198 | -21.1417 | 1759.6323 | 75211.091 | -0.012015
211 |  | 149.9867 | 356.8775 | 4187 | 0.00056828 | 6.1198 | 6.1203 | -21.1417 | 1759.6915 | 75567.9685 | -0.012014
212 |  | 149.9867 | 356.8655 | 4187 | 0.00056826 | 6.1203 | 6.1209 | -21.1417 | 1759.7508 | 75924.834 | -0.012014
213 |  | 149.9867 | 356.8535 | 4187 | 0.00056824 | 6.1209 | 6.1215 | -21.1417 | 1759.81 | 76281.6875 | -0.012014
214 |  | 149.9867 | 356.8415 | 4187 | 0.00056822 | 6.1215 | 6.122 | -21.1417 | 1759.8693 | 76638.5289 | -0.012013
215 |  | 149.9867 | 356.8295 | 4187 | 0.0005682 | 6.122 | 6.1226 | -21.1417 | 1759.9285 | 76995.3584 | -0.012013
216 |  | 149.9867 | 356.8174 | 4187 | 0.00056819 | 6.1226 | 6.1232 | -21.1417 | 1759.9878 | 77352.1758 | -0.012012
217 |  | 149.9867 | 356.8054 | 4187 | 0.00056817 | 6.1232 | 6.1237 | -21.1417 | 1760.047 | 77708.9813 | -0.012012
218 |  | 149.9867 | 356.7934 | 4187 | 0.00056815 | 6.1237 | 6.1243 | -21.1417 | 1760.1063 | 78065.7747 | -0.012012
219 |  | 149.9867 | 356.7814 | 4187 | 0.00056813 | 6.1243 | 6.1249 | -21.1417 | 1760.1655 | 78422.5561 | -0.012011
220 |  | 149.9867 | 356.7694 | 4187 | 0.00056811 | 6.1249 | 6.1254 | -21.1417 | 1760.2248 | 78779.3255 | -0.012011
221 |  | 149.9867 | 356.7574 | 4187 | 0.00056809 | 6.1254 | 6.126 | -21.1417 | 1760.284 | 79136.0828 | -0.01201
222 |  | 149.9867 | 356.7454 | 4187 | 0.00056807 | 6.126 | 6.1266 | -21.1417 | 1760.3433 | 79492.8282 | -0.01201
223 |  | 149.9867 | 356.7334 | 4187 | 0.00056805 | 6.1266 | 6.1272 | -21.1417 | 1760.4026 | 79849.5616 | -0.01201
224 |  | 149.9867 | 356.7213 | 4187 | 0.00056803 | 6.1272 | 6.1277 | -21.1417 | 1760.4618 | 80206.2829 | -0.012009
225 |  | 149.9867 | 356.7093 | 4187 | 0.00056801 | 6.1277 | 6.1283 | -21.1417 | 1760.5211 | 80562.9923 | -0.012009
226 |  | 149.9867 | 356.6973 | 4187 | 0.00056799 | 6.1283 | 6.1289 | -21.1417 | 1760.5804 | 80919.6896 | -0.012008
227 |  | 149.9867 | 356.6853 | 4187 | 0.00056798 | 6.1289 | 6.1294 | -21.1417 | 1760.6396 | 81276.3749 | -0.012008
228 |  | 149.9867 | 356.6733 | 4187 | 0.00056796 | 6.1294 | 6.13 | -21.1417 | 1760.6989 | 81633.0482 | -0.012008
229 |  | 149.9867 | 356.6613 | 4187 | 0.00056794 | 6.13 | 6.1306 | -21.1417 | 1760.7582 | 81989.7095 | -0.012007
230 |  | 149.9867 | 356.6493 | 4187 | 0.00056792 | 6.1306 | 6.1311 | -21.1417 | 1760.8175 | 82346.3588 | -0.012007
231 |  | 149.9867 | 356.6373 | 4187 | 0.0005679 | 6.1311 | 6.1317 | -21.1417 | 1760.8768 | 82702.9961 | -0.012006
232 |  | 149.9867 | 356.6253 | 4187 | 0.00056788 | 6.1317 | 6.1323 | -21.1417 | 1760.936 | 83059.6214 | -0.012006
233 |  | 149.9867 | 356.6133 | 4187 | 0.00056786 | 6.1323 | 6.1328 | -21.1417 | 1760.9953 | 83416.2347 | -0.012006
234 |  | 149.9867 | 356.6013 | 4187 | 0.00056784 | 6.1328 | 6.1334 | -21.1417 | 1761.0546 | 83772.836 | -0.012005
235 |  | 149.9867 | 356.5893 | 4187 | 0.00056782 | 6.1334 | 6.134 | -21.1417 | 1761.1139 | 84129.4253 | -0.012005
236 |  | 149.9867 | 356.5773 | 4187 | 0.0005678 | 6.134 | 6.1345 | -21.1417 | 1761.1732 | 84486.0025 | -0.012004

## St508
|  |  | buis | verlies W/M | L /°C/sec
diam | wandikte |  | inhoud l/m |  | W/M
508 | 11 | 3.1416 | 185.5079 | 399.4077 | 4187
[8 empty] | J/sec/mtr | aantal mtr. | verlies
|  | buis | verlies W/M | L /°C/sec | verlies temp | begintemp | eindtemp | verlies | bij 1°C | totaal J/sec
|  | inhoud L |  | W/M | °C per M | °C | °C | per m°C | daling | aantal mtr
1 | 508 | 185.5079 | 399.4077 | 4187 | 0.00051422 | 6 | 6.0005 | -23.4946 | 1944.6837 | 399.4077 | -0.012081
2 |  | 185.5079 | 399.3956 | 4187 | 0.00051421 | 6.0005 | 6.001 | -23.4946 | 1944.7425 | 798.8033 | -0.012081
3 |  | 185.5079 | 399.3835 | 4187 | 0.00051419 | 6.001 | 6.0015 | -23.4946 | 1944.8014 | 1198.1868 | -0.012081
4 |  | 185.5079 | 399.3714 | 4187 | 0.00051418 | 6.0015 | 6.0021 | -23.4946 | 1944.8602 | 1597.5582 | -0.01208
5 |  | 185.5079 | 399.3593 | 4187 | 0.00051416 | 6.0021 | 6.0026 | -23.4946 | 1944.919 | 1996.9175 | -0.01208
6 |  | 185.5079 | 399.3473 | 4187 | 0.00051414 | 6.0026 | 6.0031 | -23.4946 | 1944.9779 | 2396.2648 | -0.01208
7 |  | 185.5079 | 399.3352 | 4187 | 0.00051413 | 6.0031 | 6.0036 | -23.4946 | 1945.0367 | 2795.6 | -0.012079
8 |  | 185.5079 | 399.3231 | 4187 | 0.00051411 | 6.0036 | 6.0041 | -23.4946 | 1945.0955 | 3194.9231 | -0.012079
9 |  | 185.5079 | 399.311 | 4187 | 0.0005141 | 6.0041 | 6.0046 | -23.4946 | 1945.1544 | 3594.2341 | -0.012079
10 |  | 185.5079 | 399.299 | 4187 | 0.00051408 | 6.0046 | 6.0051 | -23.4946 | 1945.2132 | 3993.5331 | -0.012078
11 |  | 185.5079 | 399.2869 | 4187 | 0.00051407 | 6.0051 | 6.0057 | -23.4946 | 1945.2721 | 4392.82 | -0.012078
12 |  | 185.5079 | 399.2748 | 4187 | 0.00051405 | 6.0057 | 6.0062 | -23.4946 | 1945.3309 | 4792.0948 | -0.012077
13 |  | 185.5079 | 399.2627 | 4187 | 0.00051404 | 6.0062 | 6.0067 | -23.4946 | 1945.3897 | 5191.3575 | -0.012077
14 |  | 185.5079 | 399.2506 | 4187 | 0.00051402 | 6.0067 | 6.0072 | -23.4946 | 1945.4486 | 5590.6081 | -0.012077
15 |  | 185.5079 | 399.2386 | 4187 | 0.000514 | 6.0072 | 6.0077 | -23.4946 | 1945.5074 | 5989.8467 | -0.012076
16 |  | 185.5079 | 399.2265 | 4187 | 0.00051399 | 6.0077 | 6.0082 | -23.4946 | 1945.5663 | 6389.0732 | -0.012076
17 |  | 185.5079 | 399.2144 | 4187 | 0.00051397 | 6.0082 | 6.0087 | -23.4946 | 1945.6251 | 6788.2876 | -0.012076
18 |  | 185.5079 | 399.2023 | 4187 | 0.00051396 | 6.0087 | 6.0093 | -23.4946 | 1945.684 | 7187.4899 | -0.012075
19 |  | 185.5079 | 399.1903 | 4187 | 0.00051394 | 6.0093 | 6.0098 | -23.4946 | 1945.7428 | 7586.6802 | -0.012075
20 |  | 185.5079 | 399.1782 | 4187 | 0.00051393 | 6.0098 | 6.0103 | -23.4946 | 1945.8017 | 7985.8584 | -0.012074
21 |  | 185.5079 | 399.1661 | 4187 | 0.00051391 | 6.0103 | 6.0108 | -23.4946 | 1945.8606 | 8385.0245 | -0.012074
22 |  | 185.5079 | 399.154 | 4187 | 0.0005139 | 6.0108 | 6.0113 | -23.4946 | 1945.9194 | 8784.1785 | -0.012074
23 |  | 185.5079 | 399.142 | 4187 | 0.00051388 | 6.0113 | 6.0118 | -23.4946 | 1945.9783 | 9183.3205 | -0.012073
24 |  | 185.5079 | 399.1299 | 4187 | 0.00051386 | 6.0118 | 6.0123 | -23.4946 | 1946.0372 | 9582.4504 | -0.012073
25 |  | 185.5079 | 399.1178 | 4187 | 0.00051385 | 6.0123 | 6.0129 | -23.4946 | 1946.096 | 9981.5682 | -0.012073
26 |  | 185.5079 | 399.1057 | 4187 | 0.00051383 | 6.0129 | 6.0134 | -23.4946 | 1946.1549 | 10380.6739 | -0.012072
27 |  | 185.5079 | 399.0937 | 4187 | 0.00051382 | 6.0134 | 6.0139 | -23.4946 | 1946.2138 | 10779.7676 | -0.012072
28 |  | 185.5079 | 399.0816 | 4187 | 0.0005138 | 6.0139 | 6.0144 | -23.4946 | 1946.2726 | 11178.8492 | -0.012072
29 |  | 185.5079 | 399.0695 | 4187 | 0.00051379 | 6.0144 | 6.0149 | -23.4946 | 1946.3315 | 11577.9187 | -0.012071
30 |  | 185.5079 | 399.0575 | 4187 | 0.00051377 | 6.0149 | 6.0154 | -23.4946 | 1946.3904 | 11976.9762 | -0.012071
31 |  | 185.5079 | 399.0454 | 4187 | 0.00051376 | 6.0154 | 6.0159 | -23.4946 | 1946.4493 | 12376.0216 | -0.01207
32 |  | 185.5079 | 399.0333 | 4187 | 0.00051374 | 6.0159 | 6.0164 | -23.4946 | 1946.5081 | 12775.0549 | -0.01207
33 |  | 185.5079 | 399.0212 | 4187 | 0.00051372 | 6.0164 | 6.017 | -23.4946 | 1946.567 | 13174.0762 | -0.01207
34 |  | 185.5079 | 399.0092 | 4187 | 0.00051371 | 6.017 | 6.0175 | -23.4946 | 1946.6259 | 13573.0853 | -0.012069
35 |  | 185.5079 | 398.9971 | 4187 | 0.00051369 | 6.0175 | 6.018 | -23.4946 | 1946.6848 | 13972.0824 | -0.012069
36 |  | 185.5079 | 398.985 | 4187 | 0.00051368 | 6.018 | 6.0185 | -23.4946 | 1946.7437 | 14371.0675 | -0.012069
37 |  | 185.5079 | 398.973 | 4187 | 0.00051366 | 6.0185 | 6.019 | -23.4946 | 1946.8026 | 14770.0405 | -0.012068
38 |  | 185.5079 | 398.9609 | 4187 | 0.00051365 | 6.019 | 6.0195 | -23.4946 | 1946.8614 | 15169.0014 | -0.012068
39 |  | 185.5079 | 398.9488 | 4187 | 0.00051363 | 6.0195 | 6.02 | -23.4946 | 1946.9203 | 15567.9502 | -0.012068
40 |  | 185.5079 | 398.9368 | 4187 | 0.00051362 | 6.02 | 6.0206 | -23.4946 | 1946.9792 | 15966.887 | -0.012067
41 |  | 185.5079 | 398.9247 | 4187 | 0.0005136 | 6.0206 | 6.0211 | -23.4946 | 1947.0381 | 16365.8117 | -0.012067
42 |  | 185.5079 | 398.9126 | 4187 | 0.00051359 | 6.0211 | 6.0216 | -23.4946 | 1947.097 | 16764.7243 | -0.012066
43 |  | 185.5079 | 398.9006 | 4187 | 0.00051357 | 6.0216 | 6.0221 | -23.4946 | 1947.1559 | 17163.6248 | -0.012066
44 |  | 185.5079 | 398.8885 | 4187 | 0.00051355 | 6.0221 | 6.0226 | -23.4946 | 1947.2148 | 17562.5133 | -0.012066
45 |  | 185.5079 | 398.8764 | 4187 | 0.00051354 | 6.0226 | 6.0231 | -23.4946 | 1947.2737 | 17961.3898 | -0.012065
46 |  | 185.5079 | 398.8644 | 4187 | 0.00051352 | 6.0231 | 6.0236 | -23.4946 | 1947.3326 | 18360.2542 | -0.012065
47 |  | 185.5079 | 398.8523 | 4187 | 0.00051351 | 6.0236 | 6.0242 | -23.4946 | 1947.3915 | 18759.1065 | -0.012065
48 |  | 185.5079 | 398.8402 | 4187 | 0.00051349 | 6.0242 | 6.0247 | -23.4946 | 1947.4504 | 19157.9467 | -0.012064
49 |  | 185.5079 | 398.8282 | 4187 | 0.00051348 | 6.0247 | 6.0252 | -23.4946 | 1947.5093 | 19556.7749 | -0.012064
50 |  | 185.5079 | 398.8161 | 4187 | 0.00051346 | 6.0252 | 6.0257 | -23.4946 | 1947.5683 | 19955.591 | -0.012064
51 |  | 185.5079 | 398.804 | 4187 | 0.00051345 | 6.0257 | 6.0262 | -23.4946 | 1947.6272 | 20354.395 | -0.012063
52 |  | 185.5079 | 398.792 | 4187 | 0.00051343 | 6.0262 | 6.0267 | -23.4946 | 1947.6861 | 20753.187 | -0.012063
53 |  | 185.5079 | 398.7799 | 4187 | 0.00051341 | 6.0267 | 6.0272 | -23.4946 | 1947.745 | 21151.9669 | -0.012062
54 |  | 185.5079 | 398.7679 | 4187 | 0.0005134 | 6.0272 | 6.0277 | -23.4946 | 1947.8039 | 21550.7348 | -0.012062
55 |  | 185.5079 | 398.7558 | 4187 | 0.00051338 | 6.0277 | 6.0283 | -23.4946 | 1947.8628 | 21949.4906 | -0.012062
56 |  | 185.5079 | 398.7437 | 4187 | 0.00051337 | 6.0283 | 6.0288 | -23.4946 | 1947.9218 | 22348.2343 | -0.012061
57 |  | 185.5079 | 398.7317 | 4187 | 0.00051335 | 6.0288 | 6.0293 | -23.4946 | 1947.9807 | 22746.966 | -0.012061
58 |  | 185.5079 | 398.7196 | 4187 | 0.00051334 | 6.0293 | 6.0298 | -23.4946 | 1948.0396 | 23145.6856 | -0.012061
59 |  | 185.5079 | 398.7076 | 4187 | 0.00051332 | 6.0298 | 6.0303 | -23.4946 | 1948.0985 | 23544.3932 | -0.01206
60 |  | 185.5079 | 398.6955 | 4187 | 0.00051331 | 6.0303 | 6.0308 | -23.4946 | 1948.1575 | 23943.0887 | -0.01206
61 |  | 185.5079 | 398.6834 | 4187 | 0.00051329 | 6.0308 | 6.0313 | -23.4946 | 1948.2164 | 24341.7721 | -0.01206
62 |  | 185.5079 | 398.6714 | 4187 | 0.00051327 | 6.0313 | 6.0319 | -23.4946 | 1948.2753 | 24740.4435 | -0.012059
63 |  | 185.5079 | 398.6593 | 4187 | 0.00051326 | 6.0319 | 6.0324 | -23.4946 | 1948.3343 | 25139.1028 | -0.012059
64 |  | 185.5079 | 398.6473 | 4187 | 0.00051324 | 6.0324 | 6.0329 | -23.4946 | 1948.3932 | 25537.75 | -0.012058
65 |  | 185.5079 | 398.6352 | 4187 | 0.00051323 | 6.0329 | 6.0334 | -23.4946 | 1948.4521 | 25936.3852 | -0.012058
66 |  | 185.5079 | 398.6231 | 4187 | 0.00051321 | 6.0334 | 6.0339 | -23.4946 | 1948.5111 | 26335.0084 | -0.012058
67 |  | 185.5079 | 398.6111 | 4187 | 0.0005132 | 6.0339 | 6.0344 | -23.4946 | 1948.57 | 26733.6194 | -0.012057
68 |  | 185.5079 | 398.599 | 4187 | 0.00051318 | 6.0344 | 6.0349 | -23.4946 | 1948.629 | 27132.2185 | -0.012057
69 |  | 185.5079 | 398.587 | 4187 | 0.00051317 | 6.0349 | 6.0354 | -23.4946 | 1948.6879 | 27530.8054 | -0.012057
70 |  | 185.5079 | 398.5749 | 4187 | 0.00051315 | 6.0354 | 6.036 | -23.4946 | 1948.7468 | 27929.3803 | -0.012056
71 |  | 185.5079 | 398.5629 | 4187 | 0.00051313 | 6.036 | 6.0365 | -23.4946 | 1948.8058 | 28327.9432 | -0.012056
72 |  | 185.5079 | 398.5508 | 4187 | 0.00051312 | 6.0365 | 6.037 | -23.4946 | 1948.8647 | 28726.494 | -0.012056
73 |  | 185.5079 | 398.5387 | 4187 | 0.0005131 | 6.037 | 6.0375 | -23.4946 | 1948.9237 | 29125.0327 | -0.012055
74 |  | 185.5079 | 398.5267 | 4187 | 0.00051309 | 6.0375 | 6.038 | -23.4946 | 1948.9826 | 29523.5594 | -0.012055
75 |  | 185.5079 | 398.5146 | 4187 | 0.00051307 | 6.038 | 6.0385 | -23.4946 | 1949.0416 | 29922.074 | -0.012054
76 |  | 185.5079 | 398.5026 | 4187 | 0.00051306 | 6.0385 | 6.039 | -23.4946 | 1949.1006 | 30320.5766 | -0.012054
77 |  | 185.5079 | 398.4905 | 4187 | 0.00051304 | 6.039 | 6.0395 | -23.4946 | 1949.1595 | 30719.0671 | -0.012054
78 |  | 185.5079 | 398.4785 | 4187 | 0.00051303 | 6.0395 | 6.0401 | -23.4946 | 1949.2185 | 31117.5456 | -0.012053
79 |  | 185.5079 | 398.4664 | 4187 | 0.00051301 | 6.0401 | 6.0406 | -23.4946 | 1949.2774 | 31516.012 | -0.012053
80 |  | 185.5079 | 398.4544 | 4187 | 0.000513 | 6.0406 | 6.0411 | -23.4946 | 1949.3364 | 31914.4664 | -0.012053
81 |  | 185.5079 | 398.4423 | 4187 | 0.00051298 | 6.0411 | 6.0416 | -23.4946 | 1949.3954 | 32312.9087 | -0.012052
82 |  | 185.5079 | 398.4303 | 4187 | 0.00051296 | 6.0416 | 6.0421 | -23.4946 | 1949.4543 | 32711.339 | -0.012052
83 |  | 185.5079 | 398.4182 | 4187 | 0.00051295 | 6.0421 | 6.0426 | -23.4946 | 1949.5133 | 33109.7572 | -0.012052
84 |  | 185.5079 | 398.4062 | 4187 | 0.00051293 | 6.0426 | 6.0431 | -23.4946 | 1949.5723 | 33508.1633 | -0.012051
85 |  | 185.5079 | 398.3941 | 4187 | 0.00051292 | 6.0431 | 6.0437 | -23.4946 | 1949.6313 | 33906.5574 | -0.012051
86 |  | 185.5079 | 398.3821 | 4187 | 0.0005129 | 6.0437 | 6.0442 | -23.4946 | 1949.6902 | 34304.9395 | -0.01205
87 |  | 185.5079 | 398.37 | 4187 | 0.00051289 | 6.0442 | 6.0447 | -23.4946 | 1949.7492 | 34703.3095 | -0.01205
88 |  | 185.5079 | 398.358 | 4187 | 0.00051287 | 6.0447 | 6.0452 | -23.4946 | 1949.8082 | 35101.6674 | -0.01205
89 |  | 185.5079 | 398.3459 | 4187 | 0.00051286 | 6.0452 | 6.0457 | -23.4946 | 1949.8672 | 35500.0133 | -0.012049
90 |  | 185.5079 | 398.3339 | 4187 | 0.00051284 | 6.0457 | 6.0462 | -23.4946 | 1949.9261 | 35898.3472 | -0.012049
91 |  | 185.5079 | 398.3218 | 4187 | 0.00051282 | 6.0462 | 6.0467 | -23.4946 | 1949.9851 | 36296.669 | -0.012049
92 |  | 185.5079 | 398.3098 | 4187 | 0.00051281 | 6.0467 | 6.0472 | -23.4946 | 1950.0441 | 36694.9788 | -0.012048
93 |  | 185.5079 | 398.2977 | 4187 | 0.00051279 | 6.0472 | 6.0478 | -23.4946 | 1950.1031 | 37093.2765 | -0.012048
94 |  | 185.5079 | 398.2857 | 4187 | 0.00051278 | 6.0478 | 6.0483 | -23.4946 | 1950.1621 | 37491.5621 | -0.012047
95 |  | 185.5079 | 398.2736 | 4187 | 0.00051276 | 6.0483 | 6.0488 | -23.4946 | 1950.2211 | 37889.8357 | -0.012047
96 |  | 185.5079 | 398.2616 | 4187 | 0.00051275 | 6.0488 | 6.0493 | -23.4946 | 1950.2801 | 38288.0973 | -0.012047
97 |  | 185.5079 | 398.2495 | 4187 | 0.00051273 | 6.0493 | 6.0498 | -23.4946 | 1950.3391 | 38686.3468 | -0.012046
98 |  | 185.5079 | 398.2375 | 4187 | 0.00051272 | 6.0498 | 6.0503 | -23.4946 | 1950.3981 | 39084.5843 | -0.012046
99 |  | 185.5079 | 398.2254 | 4187 | 0.0005127 | 6.0503 | 6.0508 | -23.4946 | 1950.4571 | 39482.8097 | -0.012046
100 |  | 185.5079 | 398.2134 | 4187 | 0.00051268 | 6.0508 | 6.0513 | -23.4946 | 1950.5161 | 39881.0231 | -0.012045
101 |  | 185.5079 | 398.2013 | 4187 | 0.00051267 | 6.0513 | 6.0519 | -23.4946 | 1950.5751 | 40279.2244 | -0.012045
102 |  | 185.5079 | 398.1893 | 4187 | 0.00051265 | 6.0519 | 6.0524 | -23.4946 | 1950.6341 | 40677.4137 | -0.012045
103 |  | 185.5079 | 398.1772 | 4187 | 0.00051264 | 6.0524 | 6.0529 | -23.4946 | 1950.6931 | 41075.591 | -0.012044
104 |  | 185.5079 | 398.1652 | 4187 | 0.00051262 | 6.0529 | 6.0534 | -23.4946 | 1950.7521 | 41473.7562 | -0.012044
105 |  | 185.5079 | 398.1532 | 4187 | 0.00051261 | 6.0534 | 6.0539 | -23.4946 | 1950.8111 | 41871.9093 | -0.012043
106 |  | 185.5079 | 398.1411 | 4187 | 0.00051259 | 6.0539 | 6.0544 | -23.4946 | 1950.8701 | 42270.0504 | -0.012043
107 |  | 185.5079 | 398.1291 | 4187 | 0.00051258 | 6.0544 | 6.0549 | -23.4946 | 1950.9291 | 42668.1795 | -0.012043
108 |  | 185.5079 | 398.117 | 4187 | 0.00051256 | 6.0549 | 6.0554 | -23.4946 | 1950.9881 | 43066.2965 | -0.012042
109 |  | 185.5079 | 398.105 | 4187 | 0.00051255 | 6.0554 | 6.056 | -23.4946 | 1951.0471 | 43464.4015 | -0.012042
110 |  | 185.5079 | 398.0929 | 4187 | 0.00051253 | 6.056 | 6.0565 | -23.4946 | 1951.1062 | 43862.4945 | -0.012042
111 |  | 185.5079 | 398.0809 | 4187 | 0.00051251 | 6.0565 | 6.057 | -23.4946 | 1951.1652 | 44260.5754 | -0.012041
112 |  | 185.5079 | 398.0689 | 4187 | 0.0005125 | 6.057 | 6.0575 | -23.4946 | 1951.2242 | 44658.6442 | -0.012041
113 |  | 185.5079 | 398.0568 | 4187 | 0.00051248 | 6.0575 | 6.058 | -23.4946 | 1951.2832 | 45056.7011 | -0.012041
114 |  | 185.5079 | 398.0448 | 4187 | 0.00051247 | 6.058 | 6.0585 | -23.4946 | 1951.3423 | 45454.7458 | -0.01204
115 |  | 185.5079 | 398.0327 | 4187 | 0.00051245 | 6.0585 | 6.059 | -23.4946 | 1951.4013 | 45852.7786 | -0.01204
116 |  | 185.5079 | 398.0207 | 4187 | 0.00051244 | 6.059 | 6.0595 | -23.4946 | 1951.4603 | 46250.7993 | -0.012039
117 |  | 185.5079 | 398.0087 | 4187 | 0.00051242 | 6.0595 | 6.0601 | -23.4946 | 1951.5193 | 46648.8079 | -0.012039
118 |  | 185.5079 | 397.9966 | 4187 | 0.00051241 | 6.0601 | 6.0606 | -23.4946 | 1951.5784 | 47046.8046 | -0.012039
119 |  | 185.5079 | 397.9846 | 4187 | 0.00051239 | 6.0606 | 6.0611 | -23.4946 | 1951.6374 | 47444.7891 | -0.012038
120 |  | 185.5079 | 397.9725 | 4187 | 0.00051237 | 6.0611 | 6.0616 | -23.4946 | 1951.6964 | 47842.7617 | -0.012038
121 |  | 185.5079 | 397.9605 | 4187 | 0.00051236 | 6.0616 | 6.0621 | -23.4946 | 1951.7555 | 48240.7222 | -0.012038
122 |  | 185.5079 | 397.9485 | 4187 | 0.00051234 | 6.0621 | 6.0626 | -23.4946 | 1951.8145 | 48638.6707 | -0.012037
123 |  | 185.5079 | 397.9364 | 4187 | 0.00051233 | 6.0626 | 6.0631 | -23.4946 | 1951.8736 | 49036.6071 | -0.012037
124 |  | 185.5079 | 397.9244 | 4187 | 0.00051231 | 6.0631 | 6.0636 | -23.4946 | 1951.9326 | 49434.5315 | -0.012037
125 |  | 185.5079 | 397.9124 | 4187 | 0.0005123 | 6.0636 | 6.0642 | -23.4946 | 1951.9916 | 49832.4438 | -0.012036
126 |  | 185.5079 | 397.9003 | 4187 | 0.00051228 | 6.0642 | 6.0647 | -23.4946 | 1952.0507 | 50230.3442 | -0.012036
127 |  | 185.5079 | 397.8883 | 4187 | 0.00051227 | 6.0647 | 6.0652 | -23.4946 | 1952.1097 | 50628.2324 | -0.012035
128 |  | 185.5079 | 397.8762 | 4187 | 0.00051225 | 6.0652 | 6.0657 | -23.4946 | 1952.1688 | 51026.1087 | -0.012035
129 |  | 185.5079 | 397.8642 | 4187 | 0.00051224 | 6.0657 | 6.0662 | -23.4946 | 1952.2278 | 51423.9729 | -0.012035
130 |  | 185.5079 | 397.8522 | 4187 | 0.00051222 | 6.0662 | 6.0667 | -23.4946 | 1952.2869 | 51821.8251 | -0.012034
131 |  | 185.5079 | 397.8401 | 4187 | 0.0005122 | 6.0667 | 6.0672 | -23.4946 | 1952.346 | 52219.6652 | -0.012034
132 |  | 185.5079 | 397.8281 | 4187 | 0.00051219 | 6.0672 | 6.0677 | -23.4946 | 1952.405 | 52617.4933 | -0.012034
133 |  | 185.5079 | 397.8161 | 4187 | 0.00051217 | 6.0677 | 6.0683 | -23.4946 | 1952.4641 | 53015.3094 | -0.012033
134 |  | 185.5079 | 397.804 | 4187 | 0.00051216 | 6.0683 | 6.0688 | -23.4946 | 1952.5231 | 53413.1135 | -0.012033
135 |  | 185.5079 | 397.792 | 4187 | 0.00051214 | 6.0688 | 6.0693 | -23.4946 | 1952.5822 | 53810.9055 | -0.012033
136 |  | 185.5079 | 397.78 | 4187 | 0.00051213 | 6.0693 | 6.0698 | -23.4946 | 1952.6413 | 54208.6855 | -0.012032
137 |  | 185.5079 | 397.7679 | 4187 | 0.00051211 | 6.0698 | 6.0703 | -23.4946 | 1952.7003 | 54606.4534 | -0.012032
138 |  | 185.5079 | 397.7559 | 4187 | 0.0005121 | 6.0703 | 6.0708 | -23.4946 | 1952.7594 | 55004.2093 | -0.012031
139 |  | 185.5079 | 397.7439 | 4187 | 0.00051208 | 6.0708 | 6.0713 | -23.4946 | 1952.8185 | 55401.9532 | -0.012031
140 |  | 185.5079 | 397.7319 | 4187 | 0.00051206 | 6.0713 | 6.0718 | -23.4946 | 1952.8775 | 55799.6851 | -0.012031
141 |  | 185.5079 | 397.7198 | 4187 | 0.00051205 | 6.0718 | 6.0724 | -23.4946 | 1952.9366 | 56197.4049 | -0.01203
142 |  | 185.5079 | 397.7078 | 4187 | 0.00051203 | 6.0724 | 6.0729 | -23.4946 | 1952.9957 | 56595.1127 | -0.01203
143 |  | 185.5079 | 397.6958 | 4187 | 0.00051202 | 6.0729 | 6.0734 | -23.4946 | 1953.0548 | 56992.8084 | -0.01203
144 |  | 185.5079 | 397.6837 | 4187 | 0.000512 | 6.0734 | 6.0739 | -23.4946 | 1953.1138 | 57390.4922 | -0.012029
145 |  | 185.5079 | 397.6717 | 4187 | 0.00051199 | 6.0739 | 6.0744 | -23.4946 | 1953.1729 | 57788.1639 | -0.012029
146 |  | 185.5079 | 397.6597 | 4187 | 0.00051197 | 6.0744 | 6.0749 | -23.4946 | 1953.232 | 58185.8235 | -0.012029
147 |  | 185.5079 | 397.6476 | 4187 | 0.00051196 | 6.0749 | 6.0754 | -23.4946 | 1953.2911 | 58583.4712 | -0.012028
148 |  | 185.5079 | 397.6356 | 4187 | 0.00051194 | 6.0754 | 6.0759 | -23.4946 | 1953.3502 | 58981.1068 | -0.012028
149 |  | 185.5079 | 397.6236 | 4187 | 0.00051193 | 6.0759 | 6.0764 | -23.4946 | 1953.4093 | 59378.7304 | -0.012027
150 |  | 185.5079 | 397.6116 | 4187 | 0.00051191 | 6.0764 | 6.077 | -23.4946 | 1953.4683 | 59776.3419 | -0.012027
151 |  | 185.5079 | 397.5995 | 4187 | 0.00051189 | 6.077 | 6.0775 | -23.4946 | 1953.5274 | 60173.9415 | -0.012027
152 |  | 185.5079 | 397.5875 | 4187 | 0.00051188 | 6.0775 | 6.078 | -23.4946 | 1953.5865 | 60571.529 | -0.012026
153 |  | 185.5079 | 397.5755 | 4187 | 0.00051186 | 6.078 | 6.0785 | -23.4946 | 1953.6456 | 60969.1045 | -0.012026
154 |  | 185.5079 | 397.5635 | 4187 | 0.00051185 | 6.0785 | 6.079 | -23.4946 | 1953.7047 | 61366.6679 | -0.012026
155 |  | 185.5079 | 397.5514 | 4187 | 0.00051183 | 6.079 | 6.0795 | -23.4946 | 1953.7638 | 61764.2194 | -0.012025
156 |  | 185.5079 | 397.5394 | 4187 | 0.00051182 | 6.0795 | 6.08 | -23.4946 | 1953.8229 | 62161.7588 | -0.012025
157 |  | 185.5079 | 397.5274 | 4187 | 0.0005118 | 6.08 | 6.0805 | -23.4946 | 1953.882 | 62559.2861 | -0.012025
158 |  | 185.5079 | 397.5154 | 4187 | 0.00051179 | 6.0805 | 6.0811 | -23.4946 | 1953.9411 | 62956.8015 | -0.012024
159 |  | 185.5079 | 397.5033 | 4187 | 0.00051177 | 6.0811 | 6.0816 | -23.4946 | 1954.0002 | 63354.3048 | -0.012024
160 |  | 185.5079 | 397.4913 | 4187 | 0.00051176 | 6.0816 | 6.0821 | -23.4946 | 1954.0593 | 63751.7961 | -0.012023
161 |  | 185.5079 | 397.4793 | 4187 | 0.00051174 | 6.0821 | 6.0826 | -23.4946 | 1954.1184 | 64149.2754 | -0.012023
162 |  | 185.5079 | 397.4673 | 4187 | 0.00051172 | 6.0826 | 6.0831 | -23.4946 | 1954.1776 | 64546.7427 | -0.012023
163 |  | 185.5079 | 397.4552 | 4187 | 0.00051171 | 6.0831 | 6.0836 | -23.4946 | 1954.2367 | 64944.1979 | -0.012022
164 |  | 185.5079 | 397.4432 | 4187 | 0.00051169 | 6.0836 | 6.0841 | -23.4946 | 1954.2958 | 65341.6411 | -0.012022
165 |  | 185.5079 | 397.4312 | 4187 | 0.00051168 | 6.0841 | 6.0846 | -23.4946 | 1954.3549 | 65739.0723 | -0.012022
166 |  | 185.5079 | 397.4192 | 4187 | 0.00051166 | 6.0846 | 6.0851 | -23.4946 | 1954.414 | 66136.4915 | -0.012021
167 |  | 185.5079 | 397.4071 | 4187 | 0.00051165 | 6.0851 | 6.0857 | -23.4946 | 1954.4731 | 66533.8986 | -0.012021
168 |  | 185.5079 | 397.3951 | 4187 | 0.00051163 | 6.0857 | 6.0862 | -23.4946 | 1954.5323 | 66931.2938 | -0.012021
169 |  | 185.5079 | 397.3831 | 4187 | 0.00051162 | 6.0862 | 6.0867 | -23.4946 | 1954.5914 | 67328.6769 | -0.01202
170 |  | 185.5079 | 397.3711 | 4187 | 0.0005116 | 6.0867 | 6.0872 | -23.4946 | 1954.6505 | 67726.048 | -0.01202
171 |  | 185.5079 | 397.3591 | 4187 | 0.00051158 | 6.0872 | 6.0877 | -23.4946 | 1954.7096 | 68123.407 | -0.012019
172 |  | 185.5079 | 397.347 | 4187 | 0.00051157 | 6.0877 | 6.0882 | -23.4946 | 1954.7688 | 68520.7541 | -0.012019
173 |  | 185.5079 | 397.335 | 4187 | 0.00051155 | 6.0882 | 6.0887 | -23.4946 | 1954.8279 | 68918.0891 | -0.012019
174 |  | 185.5079 | 397.323 | 4187 | 0.00051154 | 6.0887 | 6.0892 | -23.4946 | 1954.887 | 69315.4121 | -0.012018
175 |  | 185.5079 | 397.311 | 4187 | 0.00051152 | 6.0892 | 6.0898 | -23.4946 | 1954.9462 | 69712.7231 | -0.012018
176 |  | 185.5079 | 397.299 | 4187 | 0.00051151 | 6.0898 | 6.0903 | -23.4946 | 1955.0053 | 70110.0221 | -0.012018
177 |  | 185.5079 | 397.287 | 4187 | 0.00051149 | 6.0903 | 6.0908 | -23.4946 | 1955.0644 | 70507.309 | -0.012017
178 |  | 185.5079 | 397.2749 | 4187 | 0.00051148 | 6.0908 | 6.0913 | -23.4946 | 1955.1236 | 70904.584 | -0.012017
179 |  | 185.5079 | 397.2629 | 4187 | 0.00051146 | 6.0913 | 6.0918 | -23.4946 | 1955.1827 | 71301.8469 | -0.012017
180 |  | 185.5079 | 397.2509 | 4187 | 0.00051145 | 6.0918 | 6.0923 | -23.4946 | 1955.2418 | 71699.0978 | -0.012016
181 |  | 185.5079 | 397.2389 | 4187 | 0.00051143 | 6.0923 | 6.0928 | -23.4946 | 1955.301 | 72096.3367 | -0.012016
182 |  | 185.5079 | 397.2269 | 4187 | 0.00051141 | 6.0928 | 6.0933 | -23.4946 | 1955.3601 | 72493.5636 | -0.012015
183 |  | 185.5079 | 397.2149 | 4187 | 0.0005114 | 6.0933 | 6.0938 | -23.4946 | 1955.4193 | 72890.7784 | -0.012015
184 |  | 185.5079 | 397.2028 | 4187 | 0.00051138 | 6.0938 | 6.0944 | -23.4946 | 1955.4784 | 73287.9813 | -0.012015
185 |  | 185.5079 | 397.1908 | 4187 | 0.00051137 | 6.0944 | 6.0949 | -23.4946 | 1955.5376 | 73685.1721 | -0.012014
186 |  | 185.5079 | 397.1788 | 4187 | 0.00051135 | 6.0949 | 6.0954 | -23.4946 | 1955.5967 | 74082.3509 | -0.012014
187 |  | 185.5079 | 397.1668 | 4187 | 0.00051134 | 6.0954 | 6.0959 | -23.4946 | 1955.6559 | 74479.5177 | -0.012014
188 |  | 185.5079 | 397.1548 | 4187 | 0.00051132 | 6.0959 | 6.0964 | -23.4946 | 1955.7151 | 74876.6725 | -0.012013
189 |  | 185.5079 | 397.1428 | 4187 | 0.00051131 | 6.0964 | 6.0969 | -23.4946 | 1955.7742 | 75273.8153 | -0.012013
190 |  | 185.5079 | 397.1308 | 4187 | 0.00051129 | 6.0969 | 6.0974 | -23.4946 | 1955.8334 | 75670.946 | -0.012013
191 |  | 185.5079 | 397.1187 | 4187 | 0.00051128 | 6.0974 | 6.0979 | -23.4946 | 1955.8925 | 76068.0648 | -0.012012
192 |  | 185.5079 | 397.1067 | 4187 | 0.00051126 | 6.0979 | 6.0984 | -23.4946 | 1955.9517 | 76465.1715 | -0.012012
193 |  | 185.5079 | 397.0947 | 4187 | 0.00051124 | 6.0984 | 6.099 | -23.4946 | 1956.0109 | 76862.2663 | -0.012011
194 |  | 185.5079 | 397.0827 | 4187 | 0.00051123 | 6.099 | 6.0995 | -23.4946 | 1956.07 | 77259.349 | -0.012011
195 |  | 185.5079 | 397.0707 | 4187 | 0.00051121 | 6.0995 | 6.1 | -23.4946 | 1956.1292 | 77656.4197 | -0.012011
196 |  | 185.5079 | 397.0587 | 4187 | 0.0005112 | 6.1 | 6.1005 | -23.4946 | 1956.1884 | 78053.4784 | -0.01201
197 |  | 185.5079 | 397.0467 | 4187 | 0.00051118 | 6.1005 | 6.101 | -23.4946 | 1956.2476 | 78450.525 | -0.01201
198 |  | 185.5079 | 397.0347 | 4187 | 0.00051117 | 6.101 | 6.1015 | -23.4946 | 1956.3067 | 78847.5597 | -0.01201
199 |  | 185.5079 | 397.0227 | 4187 | 0.00051115 | 6.1015 | 6.102 | -23.4946 | 1956.3659 | 79244.5824 | -0.012009
200 |  | 185.5079 | 397.0107 | 4187 | 0.00051114 | 6.102 | 6.1025 | -23.4946 | 1956.4251 | 79641.593 | -0.012009
201 |  | 185.5079 | 396.9986 | 4187 | 0.00051112 | 6.1025 | 6.103 | -23.4946 | 1956.4843 | 80038.5917 | -0.012009
202 |  | 185.5079 | 396.9866 | 4187 | 0.00051111 | 6.103 | 6.1036 | -23.4946 | 1956.5434 | 80435.5783 | -0.012008
203 |  | 185.5079 | 396.9746 | 4187 | 0.00051109 | 6.1036 | 6.1041 | -23.4946 | 1956.6026 | 80832.5529 | -0.012008
204 |  | 185.5079 | 396.9626 | 4187 | 0.00051107 | 6.1041 | 6.1046 | -23.4946 | 1956.6618 | 81229.5155 | -0.012007
205 |  | 185.5079 | 396.9506 | 4187 | 0.00051106 | 6.1046 | 6.1051 | -23.4946 | 1956.721 | 81626.4662 | -0.012007
206 |  | 185.5079 | 396.9386 | 4187 | 0.00051104 | 6.1051 | 6.1056 | -23.4946 | 1956.7802 | 82023.4048 | -0.012007
207 |  | 185.5079 | 396.9266 | 4187 | 0.00051103 | 6.1056 | 6.1061 | -23.4946 | 1956.8394 | 82420.3314 | -0.012006
208 |  | 185.5079 | 396.9146 | 4187 | 0.00051101 | 6.1061 | 6.1066 | -23.4946 | 1956.8986 | 82817.2459 | -0.012006
209 |  | 185.5079 | 396.9026 | 4187 | 0.000511 | 6.1066 | 6.1071 | -23.4946 | 1956.9578 | 83214.1485 | -0.012006
210 |  | 185.5079 | 396.8906 | 4187 | 0.00051098 | 6.1071 | 6.1076 | -23.4946 | 1957.017 | 83611.0391 | -0.012005
211 |  | 185.5079 | 396.8786 | 4187 | 0.00051097 | 6.1076 | 6.1082 | -23.4946 | 1957.0762 | 84007.9177 | -0.012005
212 |  | 185.5079 | 396.8666 | 4187 | 0.00051095 | 6.1082 | 6.1087 | -23.4946 | 1957.1354 | 84404.7842 | -0.012005
213 |  | 185.5079 | 396.8546 | 4187 | 0.00051094 | 6.1087 | 6.1092 | -23.4946 | 1957.1946 | 84801.6388 | -0.012004
214 |  | 185.5079 | 396.8426 | 4187 | 0.00051092 | 6.1092 | 6.1097 | -23.4946 | 1957.2538 | 85198.4814 | -0.012004
215 |  | 185.5079 | 396.8306 | 4187 | 0.0005109 | 6.1097 | 6.1102 | -23.4946 | 1957.313 | 85595.3119 | -0.012003
216 |  | 185.5079 | 396.8186 | 4187 | 0.00051089 | 6.1102 | 6.1107 | -23.4946 | 1957.3722 | 85992.1305 | -0.012003
217 |  | 185.5079 | 396.8065 | 4187 | 0.00051087 | 6.1107 | 6.1112 | -23.4946 | 1957.4314 | 86388.937 | -0.012003
218 |  | 185.5079 | 396.7945 | 4187 | 0.00051086 | 6.1112 | 6.1117 | -23.4946 | 1957.4906 | 86785.7316 | -0.012002
219 |  | 185.5079 | 396.7825 | 4187 | 0.00051084 | 6.1117 | 6.1122 | -23.4946 | 1957.5498 | 87182.5141 | -0.012002
220 |  | 185.5079 | 396.7705 | 4187 | 0.00051083 | 6.1122 | 6.1128 | -23.4946 | 1957.609 | 87579.2847 | -0.012002
221 |  | 185.5079 | 396.7585 | 4187 | 0.00051081 | 6.1128 | 6.1133 | -23.4946 | 1957.6682 | 87976.0432 | -0.012001
222 |  | 185.5079 | 396.7465 | 4187 | 0.0005108 | 6.1133 | 6.1138 | -23.4946 | 1957.7275 | 88372.7897 | -0.012001
223 |  | 185.5079 | 396.7345 | 4187 | 0.00051078 | 6.1138 | 6.1143 | -23.4946 | 1957.7867 | 88769.5243 | -0.012001
224 |  | 185.5079 | 396.7225 | 4187 | 0.00051077 | 6.1143 | 6.1148 | -23.4946 | 1957.8459 | 89166.2468 | -0.012
225 |  | 185.5079 | 396.7105 | 4187 | 0.00051075 | 6.1148 | 6.1153 | -23.4946 | 1957.9051 | 89562.9573 | -0.012
226 |  | 185.5079 | 396.6985 | 4187 | 0.00051073 | 6.1153 | 6.1158 | -23.4946 | 1957.9644 | 89959.6559 | -0.011999
227 |  | 185.5079 | 396.6865 | 4187 | 0.00051072 | 6.1158 | 6.1163 | -23.4946 | 1958.0236 | 90356.3424 | -0.011999
228 |  | 185.5079 | 396.6745 | 4187 | 0.0005107 | 6.1163 | 6.1168 | -23.4946 | 1958.0828 | 90753.017 | -0.011999
229 |  | 185.5079 | 396.6625 | 4187 | 0.00051069 | 6.1168 | 6.1174 | -23.4946 | 1958.142 | 91149.6795 | -0.011998
230 |  | 185.5079 | 396.6505 | 4187 | 0.00051067 | 6.1174 | 6.1179 | -23.4946 | 1958.2013 | 91546.33 | -0.011998
231 |  | 185.5079 | 396.6385 | 4187 | 0.00051066 | 6.1179 | 6.1184 | -23.4946 | 1958.2605 | 91942.9686 | -0.011998
232 |  | 185.5079 | 396.6265 | 4187 | 0.00051064 | 6.1184 | 6.1189 | -23.4946 | 1958.3197 | 92339.5951 | -0.011997
233 |  | 185.5079 | 396.6145 | 4187 | 0.00051063 | 6.1189 | 6.1194 | -23.4946 | 1958.379 | 92736.2097 | -0.011997
234 |  | 185.5079 | 396.6026 | 4187 | 0.00051061 | 6.1194 | 6.1199 | -23.4946 | 1958.4382 | 93132.8122 | -0.011997
235 |  | 185.5079 | 396.5906 | 4187 | 0.0005106 | 6.1199 | 6.1204 | -23.4946 | 1958.4975 | 93529.4028 | -0.011996
236 |  | 185.5079 | 396.5786 | 4187 | 0.00051058 | 6.1204 | 6.1209 | -23.4946 | 1958.5567 | 93925.9813 | -0.011996

## St559
|  |  | buis | verlies W/M | L /°C/sec
diam | wandikte |  | inhoud l/m |  | W/M
559 | 12.5 | 3.1416 | 223.961 | 439.3028 | 4187
[8 empty] | J/sec/mtr | aantal mtr. | verlies
|  | buis | verlies W/M | L /°C/sec | verlies temp | begintemp | eindtemp | verlies | bij 1°C | totaal J/sec
|  | inhoud L |  | W/M | °C per M | °C | °C | per m°C | daling | aantal mtr
1 | 559 | 223.961 | 439.3028 | 4187 | 0.00046848 | 6 | 6.0005 | -25.8413 | 2134.5746 | 439.3028 | -0.012106
2 |  | 223.961 | 439.2907 | 4187 | 0.00046846 | 6.0005 | 6.0009 | -25.8413 | 2134.6335 | 878.5936 | -0.012106
3 |  | 223.961 | 439.2786 | 4187 | 0.00046845 | 6.0009 | 6.0014 | -25.8413 | 2134.6923 | 1317.8722 | -0.012105
4 |  | 223.961 | 439.2665 | 4187 | 0.00046844 | 6.0014 | 6.0019 | -25.8413 | 2134.7511 | 1757.1387 | -0.012105
5 |  | 223.961 | 439.2544 | 4187 | 0.00046843 | 6.0019 | 6.0023 | -25.8413 | 2134.8099 | 2196.3932 | -0.012105
6 |  | 223.961 | 439.2423 | 4187 | 0.00046841 | 6.0023 | 6.0028 | -25.8413 | 2134.8688 | 2635.6355 | -0.012104
7 |  | 223.961 | 439.2302 | 4187 | 0.0004684 | 6.0028 | 6.0033 | -25.8413 | 2134.9276 | 3074.8657 | -0.012104
8 |  | 223.961 | 439.2181 | 4187 | 0.00046839 | 6.0033 | 6.0037 | -25.8413 | 2134.9864 | 3514.0838 | -0.012104
9 |  | 223.961 | 439.206 | 4187 | 0.00046837 | 6.0037 | 6.0042 | -25.8413 | 2135.0453 | 3953.2898 | -0.012103
10 |  | 223.961 | 439.1939 | 4187 | 0.00046836 | 6.0042 | 6.0047 | -25.8413 | 2135.1041 | 4392.4837 | -0.012103
11 |  | 223.961 | 439.1818 | 4187 | 0.00046835 | 6.0047 | 6.0052 | -25.8413 | 2135.163 | 4831.6655 | -0.012103
12 |  | 223.961 | 439.1697 | 4187 | 0.00046834 | 6.0052 | 6.0056 | -25.8413 | 2135.2218 | 5270.8352 | -0.012102
13 |  | 223.961 | 439.1576 | 4187 | 0.00046832 | 6.0056 | 6.0061 | -25.8413 | 2135.2806 | 5709.9928 | -0.012102
14 |  | 223.961 | 439.1455 | 4187 | 0.00046831 | 6.0061 | 6.0066 | -25.8413 | 2135.3395 | 6149.1383 | -0.012102
15 |  | 223.961 | 439.1334 | 4187 | 0.0004683 | 6.0066 | 6.007 | -25.8413 | 2135.3983 | 6588.2716 | -0.012101
16 |  | 223.961 | 439.1213 | 4187 | 0.00046828 | 6.007 | 6.0075 | -25.8413 | 2135.4572 | 7027.3929 | -0.012101
17 |  | 223.961 | 439.1092 | 4187 | 0.00046827 | 6.0075 | 6.008 | -25.8413 | 2135.516 | 7466.5021 | -0.012101
18 |  | 223.961 | 439.0971 | 4187 | 0.00046826 | 6.008 | 6.0084 | -25.8413 | 2135.5749 | 7905.5992 | -0.0121
19 |  | 223.961 | 439.085 | 4187 | 0.00046825 | 6.0084 | 6.0089 | -25.8413 | 2135.6337 | 8344.6842 | -0.0121
20 |  | 223.961 | 439.0729 | 4187 | 0.00046823 | 6.0089 | 6.0094 | -25.8413 | 2135.6926 | 8783.7571 | -0.0121
21 |  | 223.961 | 439.0608 | 4187 | 0.00046822 | 6.0094 | 6.0098 | -25.8413 | 2135.7514 | 9222.8179 | -0.012099
22 |  | 223.961 | 439.0487 | 4187 | 0.00046821 | 6.0098 | 6.0103 | -25.8413 | 2135.8103 | 9661.8665 | -0.012099
23 |  | 223.961 | 439.0366 | 4187 | 0.00046819 | 6.0103 | 6.0108 | -25.8413 | 2135.8692 | 10100.9031 | -0.012099
24 |  | 223.961 | 439.0245 | 4187 | 0.00046818 | 6.0108 | 6.0112 | -25.8413 | 2135.928 | 10539.9276 | -0.012098
25 |  | 223.961 | 439.0124 | 4187 | 0.00046817 | 6.0112 | 6.0117 | -25.8413 | 2135.9869 | 10978.94 | -0.012098
26 |  | 223.961 | 439.0003 | 4187 | 0.00046815 | 6.0117 | 6.0122 | -25.8413 | 2136.0457 | 11417.9403 | -0.012098
27 |  | 223.961 | 438.9882 | 4187 | 0.00046814 | 6.0122 | 6.0126 | -25.8413 | 2136.1046 | 11856.9285 | -0.012097
28 |  | 223.961 | 438.9761 | 4187 | 0.00046813 | 6.0126 | 6.0131 | -25.8413 | 2136.1635 | 12295.9046 | -0.012097
29 |  | 223.961 | 438.964 | 4187 | 0.00046812 | 6.0131 | 6.0136 | -25.8413 | 2136.2223 | 12734.8686 | -0.012097
30 |  | 223.961 | 438.9519 | 4187 | 0.0004681 | 6.0136 | 6.014 | -25.8413 | 2136.2812 | 13173.8205 | -0.012096
31 |  | 223.961 | 438.9398 | 4187 | 0.00046809 | 6.014 | 6.0145 | -25.8413 | 2136.3401 | 13612.7603 | -0.012096
32 |  | 223.961 | 438.9277 | 4187 | 0.00046808 | 6.0145 | 6.015 | -25.8413 | 2136.399 | 14051.688 | -0.012096
33 |  | 223.961 | 438.9156 | 4187 | 0.00046806 | 6.015 | 6.0155 | -25.8413 | 2136.4578 | 14490.6036 | -0.012095
34 |  | 223.961 | 438.9035 | 4187 | 0.00046805 | 6.0155 | 6.0159 | -25.8413 | 2136.5167 | 14929.5071 | -0.012095
35 |  | 223.961 | 438.8914 | 4187 | 0.00046804 | 6.0159 | 6.0164 | -25.8413 | 2136.5756 | 15368.3985 | -0.012095
36 |  | 223.961 | 438.8793 | 4187 | 0.00046803 | 6.0164 | 6.0169 | -25.8413 | 2136.6345 | 15807.2779 | -0.012094
37 |  | 223.961 | 438.8672 | 4187 | 0.00046801 | 6.0169 | 6.0173 | -25.8413 | 2136.6934 | 16246.1451 | -0.012094
38 |  | 223.961 | 438.8551 | 4187 | 0.000468 | 6.0173 | 6.0178 | -25.8413 | 2136.7522 | 16685.0002 | -0.012094
39 |  | 223.961 | 438.843 | 4187 | 0.00046799 | 6.0178 | 6.0183 | -25.8413 | 2136.8111 | 17123.8433 | -0.012093
40 |  | 223.961 | 438.831 | 4187 | 0.00046797 | 6.0183 | 6.0187 | -25.8413 | 2136.87 | 17562.6742 | -0.012093
41 |  | 223.961 | 438.8189 | 4187 | 0.00046796 | 6.0187 | 6.0192 | -25.8413 | 2136.9289 | 18001.4931 | -0.012093
42 |  | 223.961 | 438.8068 | 4187 | 0.00046795 | 6.0192 | 6.0197 | -25.8413 | 2136.9878 | 18440.2999 | -0.012092
43 |  | 223.961 | 438.7947 | 4187 | 0.00046794 | 6.0197 | 6.0201 | -25.8413 | 2137.0467 | 18879.0945 | -0.012092
44 |  | 223.961 | 438.7826 | 4187 | 0.00046792 | 6.0201 | 6.0206 | -25.8413 | 2137.1056 | 19317.8771 | -0.012092
45 |  | 223.961 | 438.7705 | 4187 | 0.00046791 | 6.0206 | 6.0211 | -25.8413 | 2137.1645 | 19756.6476 | -0.012091
46 |  | 223.961 | 438.7584 | 4187 | 0.0004679 | 6.0211 | 6.0215 | -25.8413 | 2137.2234 | 20195.406 | -0.012091
47 |  | 223.961 | 438.7463 | 4187 | 0.00046788 | 6.0215 | 6.022 | -25.8413 | 2137.2823 | 20634.1523 | -0.012091
48 |  | 223.961 | 438.7342 | 4187 | 0.00046787 | 6.022 | 6.0225 | -25.8413 | 2137.3412 | 21072.8865 | -0.01209
49 |  | 223.961 | 438.7221 | 4187 | 0.00046786 | 6.0225 | 6.0229 | -25.8413 | 2137.4001 | 21511.6087 | -0.01209
50 |  | 223.961 | 438.71 | 4187 | 0.00046785 | 6.0229 | 6.0234 | -25.8413 | 2137.459 | 21950.3187 | -0.01209
51 |  | 223.961 | 438.6979 | 4187 | 0.00046783 | 6.0234 | 6.0239 | -25.8413 | 2137.5179 | 22389.0166 | -0.012089
52 |  | 223.961 | 438.6859 | 4187 | 0.00046782 | 6.0239 | 6.0243 | -25.8413 | 2137.5768 | 22827.7025 | -0.012089
53 |  | 223.961 | 438.6738 | 4187 | 0.00046781 | 6.0243 | 6.0248 | -25.8413 | 2137.6357 | 23266.3763 | -0.012089
54 |  | 223.961 | 438.6617 | 4187 | 0.00046779 | 6.0248 | 6.0253 | -25.8413 | 2137.6946 | 23705.0379 | -0.012088
55 |  | 223.961 | 438.6496 | 4187 | 0.00046778 | 6.0253 | 6.0257 | -25.8413 | 2137.7535 | 24143.6875 | -0.012088
56 |  | 223.961 | 438.6375 | 4187 | 0.00046777 | 6.0257 | 6.0262 | -25.8413 | 2137.8124 | 24582.325 | -0.012088
57 |  | 223.961 | 438.6254 | 4187 | 0.00046775 | 6.0262 | 6.0267 | -25.8413 | 2137.8713 | 25020.9505 | -0.012087
58 |  | 223.961 | 438.6133 | 4187 | 0.00046774 | 6.0267 | 6.0272 | -25.8413 | 2137.9303 | 25459.5638 | -0.012087
59 |  | 223.961 | 438.6012 | 4187 | 0.00046773 | 6.0272 | 6.0276 | -25.8413 | 2137.9892 | 25898.165 | -0.012087
60 |  | 223.961 | 438.5892 | 4187 | 0.00046772 | 6.0276 | 6.0281 | -25.8413 | 2138.0481 | 26336.7542 | -0.012086
61 |  | 223.961 | 438.5771 | 4187 | 0.0004677 | 6.0281 | 6.0286 | -25.8413 | 2138.107 | 26775.3312 | -0.012086
62 |  | 223.961 | 438.565 | 4187 | 0.00046769 | 6.0286 | 6.029 | -25.8413 | 2138.1659 | 27213.8962 | -0.012086
63 |  | 223.961 | 438.5529 | 4187 | 0.00046768 | 6.029 | 6.0295 | -25.8413 | 2138.2249 | 27652.4491 | -0.012085
64 |  | 223.961 | 438.5408 | 4187 | 0.00046766 | 6.0295 | 6.03 | -25.8413 | 2138.2838 | 28090.9899 | -0.012085
65 |  | 223.961 | 438.5287 | 4187 | 0.00046765 | 6.03 | 6.0304 | -25.8413 | 2138.3427 | 28529.5187 | -0.012085
66 |  | 223.961 | 438.5166 | 4187 | 0.00046764 | 6.0304 | 6.0309 | -25.8413 | 2138.4016 | 28968.0353 | -0.012084
67 |  | 223.961 | 438.5046 | 4187 | 0.00046763 | 6.0309 | 6.0314 | -25.8413 | 2138.4606 | 29406.5398 | -0.012084
68 |  | 223.961 | 438.4925 | 4187 | 0.00046761 | 6.0314 | 6.0318 | -25.8413 | 2138.5195 | 29845.0323 | -0.012084
69 |  | 223.961 | 438.4804 | 4187 | 0.0004676 | 6.0318 | 6.0323 | -25.8413 | 2138.5784 | 30283.5127 | -0.012083
70 |  | 223.961 | 438.4683 | 4187 | 0.00046759 | 6.0323 | 6.0328 | -25.8413 | 2138.6374 | 30721.981 | -0.012083
71 |  | 223.961 | 438.4562 | 4187 | 0.00046757 | 6.0328 | 6.0332 | -25.8413 | 2138.6963 | 31160.4372 | -0.012083
72 |  | 223.961 | 438.4441 | 4187 | 0.00046756 | 6.0332 | 6.0337 | -25.8413 | 2138.7552 | 31598.8814 | -0.012082
73 |  | 223.961 | 438.4321 | 4187 | 0.00046755 | 6.0337 | 6.0342 | -25.8413 | 2138.8142 | 32037.3134 | -0.012082
74 |  | 223.961 | 438.42 | 4187 | 0.00046754 | 6.0342 | 6.0346 | -25.8413 | 2138.8731 | 32475.7334 | -0.012082
75 |  | 223.961 | 438.4079 | 4187 | 0.00046752 | 6.0346 | 6.0351 | -25.8413 | 2138.9321 | 32914.1413 | -0.012081
76 |  | 223.961 | 438.3958 | 4187 | 0.00046751 | 6.0351 | 6.0356 | -25.8413 | 2138.991 | 33352.5371 | -0.012081
77 |  | 223.961 | 438.3837 | 4187 | 0.0004675 | 6.0356 | 6.036 | -25.8413 | 2139.05 | 33790.9208 | -0.012081
78 |  | 223.961 | 438.3716 | 4187 | 0.00046748 | 6.036 | 6.0365 | -25.8413 | 2139.1089 | 34229.2925 | -0.01208
79 |  | 223.961 | 438.3596 | 4187 | 0.00046747 | 6.0365 | 6.037 | -25.8413 | 2139.1679 | 34667.6521 | -0.01208
80 |  | 223.961 | 438.3475 | 4187 | 0.00046746 | 6.037 | 6.0374 | -25.8413 | 2139.2268 | 35105.9995 | -0.01208
81 |  | 223.961 | 438.3354 | 4187 | 0.00046745 | 6.0374 | 6.0379 | -25.8413 | 2139.2858 | 35544.3349 | -0.012079
82 |  | 223.961 | 438.3233 | 4187 | 0.00046743 | 6.0379 | 6.0384 | -25.8413 | 2139.3447 | 35982.6583 | -0.012079
83 |  | 223.961 | 438.3113 | 4187 | 0.00046742 | 6.0384 | 6.0388 | -25.8413 | 2139.4037 | 36420.9695 | -0.012079
84 |  | 223.961 | 438.2992 | 4187 | 0.00046741 | 6.0388 | 6.0393 | -25.8413 | 2139.4626 | 36859.2687 | -0.012078
85 |  | 223.961 | 438.2871 | 4187 | 0.00046739 | 6.0393 | 6.0398 | -25.8413 | 2139.5216 | 37297.5558 | -0.012078
86 |  | 223.961 | 438.275 | 4187 | 0.00046738 | 6.0398 | 6.0402 | -25.8413 | 2139.5806 | 37735.8308 | -0.012078
87 |  | 223.961 | 438.2629 | 4187 | 0.00046737 | 6.0402 | 6.0407 | -25.8413 | 2139.6395 | 38174.0937 | -0.012077
88 |  | 223.961 | 438.2509 | 4187 | 0.00046736 | 6.0407 | 6.0412 | -25.8413 | 2139.6985 | 38612.3446 | -0.012077
89 |  | 223.961 | 438.2388 | 4187 | 0.00046734 | 6.0412 | 6.0416 | -25.8413 | 2139.7575 | 39050.5834 | -0.012077
90 |  | 223.961 | 438.2267 | 4187 | 0.00046733 | 6.0416 | 6.0421 | -25.8413 | 2139.8164 | 39488.8101 | -0.012076
91 |  | 223.961 | 438.2146 | 4187 | 0.00046732 | 6.0421 | 6.0426 | -25.8413 | 2139.8754 | 39927.0247 | -0.012076
92 |  | 223.961 | 438.2026 | 4187 | 0.0004673 | 6.0426 | 6.043 | -25.8413 | 2139.9344 | 40365.2273 | -0.012076
93 |  | 223.961 | 438.1905 | 4187 | 0.00046729 | 6.043 | 6.0435 | -25.8413 | 2139.9933 | 40803.4178 | -0.012075
94 |  | 223.961 | 438.1784 | 4187 | 0.00046728 | 6.0435 | 6.044 | -25.8413 | 2140.0523 | 41241.5962 | -0.012075
95 |  | 223.961 | 438.1663 | 4187 | 0.00046727 | 6.044 | 6.0444 | -25.8413 | 2140.1113 | 41679.7625 | -0.012075
96 |  | 223.961 | 438.1543 | 4187 | 0.00046725 | 6.0444 | 6.0449 | -25.8413 | 2140.1703 | 42117.9167 | -0.012074
97 |  | 223.961 | 438.1422 | 4187 | 0.00046724 | 6.0449 | 6.0454 | -25.8413 | 2140.2292 | 42556.0589 | -0.012074
98 |  | 223.961 | 438.1301 | 4187 | 0.00046723 | 6.0454 | 6.0458 | -25.8413 | 2140.2882 | 42994.189 | -0.012074
99 |  | 223.961 | 438.118 | 4187 | 0.00046721 | 6.0458 | 6.0463 | -25.8413 | 2140.3472 | 43432.307 | -0.012073
100 |  | 223.961 | 438.106 | 4187 | 0.0004672 | 6.0463 | 6.0468 | -25.8413 | 2140.4062 | 43870.413 | -0.012073
101 |  | 223.961 | 438.0939 | 4187 | 0.00046719 | 6.0468 | 6.0473 | -25.8413 | 2140.4652 | 44308.5069 | -0.012073
102 |  | 223.961 | 438.0818 | 4187 | 0.00046718 | 6.0473 | 6.0477 | -25.8413 | 2140.5242 | 44746.5887 | -0.012072
103 |  | 223.961 | 438.0697 | 4187 | 0.00046716 | 6.0477 | 6.0482 | -25.8413 | 2140.5832 | 45184.6584 | -0.012072
104 |  | 223.961 | 438.0577 | 4187 | 0.00046715 | 6.0482 | 6.0487 | -25.8413 | 2140.6421 | 45622.7161 | -0.012072
105 |  | 223.961 | 438.0456 | 4187 | 0.00046714 | 6.0487 | 6.0491 | -25.8413 | 2140.7011 | 46060.7617 | -0.012071
106 |  | 223.961 | 438.0335 | 4187 | 0.00046712 | 6.0491 | 6.0496 | -25.8413 | 2140.7601 | 46498.7952 | -0.012071
107 |  | 223.961 | 438.0215 | 4187 | 0.00046711 | 6.0496 | 6.0501 | -25.8413 | 2140.8191 | 46936.8167 | -0.012071
108 |  | 223.961 | 438.0094 | 4187 | 0.0004671 | 6.0501 | 6.0505 | -25.8413 | 2140.8781 | 47374.8261 | -0.01207
109 |  | 223.961 | 437.9973 | 4187 | 0.00046709 | 6.0505 | 6.051 | -25.8413 | 2140.9371 | 47812.8234 | -0.01207
110 |  | 223.961 | 437.9852 | 4187 | 0.00046707 | 6.051 | 6.0515 | -25.8413 | 2140.9961 | 48250.8086 | -0.01207
111 |  | 223.961 | 437.9732 | 4187 | 0.00046706 | 6.0515 | 6.0519 | -25.8413 | 2141.0551 | 48688.7818 | -0.012069
112 |  | 223.961 | 437.9611 | 4187 | 0.00046705 | 6.0519 | 6.0524 | -25.8413 | 2141.1141 | 49126.7429 | -0.012069
113 |  | 223.961 | 437.949 | 4187 | 0.00046703 | 6.0524 | 6.0529 | -25.8413 | 2141.1731 | 49564.6919 | -0.012069
114 |  | 223.961 | 437.937 | 4187 | 0.00046702 | 6.0529 | 6.0533 | -25.8413 | 2141.2321 | 50002.6289 | -0.012068
115 |  | 223.961 | 437.9249 | 4187 | 0.00046701 | 6.0533 | 6.0538 | -25.8413 | 2141.2911 | 50440.5538 | -0.012068
116 |  | 223.961 | 437.9128 | 4187 | 0.000467 | 6.0538 | 6.0543 | -25.8413 | 2141.3502 | 50878.4666 | -0.012068
117 |  | 223.961 | 437.9008 | 4187 | 0.00046698 | 6.0543 | 6.0547 | -25.8413 | 2141.4092 | 51316.3674 | -0.012067
118 |  | 223.961 | 437.8887 | 4187 | 0.00046697 | 6.0547 | 6.0552 | -25.8413 | 2141.4682 | 51754.256 | -0.012067
119 |  | 223.961 | 437.8766 | 4187 | 0.00046696 | 6.0552 | 6.0557 | -25.8413 | 2141.5272 | 52192.1327 | -0.012067
120 |  | 223.961 | 437.8646 | 4187 | 0.00046694 | 6.0557 | 6.0561 | -25.8413 | 2141.5862 | 52629.9972 | -0.012066
121 |  | 223.961 | 437.8525 | 4187 | 0.00046693 | 6.0561 | 6.0566 | -25.8413 | 2141.6452 | 53067.8497 | -0.012066
122 |  | 223.961 | 437.8404 | 4187 | 0.00046692 | 6.0566 | 6.0571 | -25.8413 | 2141.7043 | 53505.6901 | -0.012066
123 |  | 223.961 | 437.8284 | 4187 | 0.00046691 | 6.0571 | 6.0575 | -25.8413 | 2141.7633 | 53943.5185 | -0.012065
124 |  | 223.961 | 437.8163 | 4187 | 0.00046689 | 6.0575 | 6.058 | -25.8413 | 2141.8223 | 54381.3348 | -0.012065
125 |  | 223.961 | 437.8042 | 4187 | 0.00046688 | 6.058 | 6.0585 | -25.8413 | 2141.8813 | 54819.139 | -0.012065
126 |  | 223.961 | 437.7922 | 4187 | 0.00046687 | 6.0585 | 6.0589 | -25.8413 | 2141.9404 | 55256.9312 | -0.012064
127 |  | 223.961 | 437.7801 | 4187 | 0.00046685 | 6.0589 | 6.0594 | -25.8413 | 2141.9994 | 55694.7113 | -0.012064
128 |  | 223.961 | 437.768 | 4187 | 0.00046684 | 6.0594 | 6.0599 | -25.8413 | 2142.0584 | 56132.4793 | -0.012064
129 |  | 223.961 | 437.756 | 4187 | 0.00046683 | 6.0599 | 6.0603 | -25.8413 | 2142.1174 | 56570.2353 | -0.012063
130 |  | 223.961 | 437.7439 | 4187 | 0.00046681 | 6.0603 | 6.0608 | -25.8413 | 2142.1765 | 57007.9792 | -0.012063
131 |  | 223.961 | 437.7318 | 4187 | 0.0004668 | 6.0608 | 6.0613 | -25.8413 | 2142.2355 | 57445.7111 | -0.012063
132 |  | 223.961 | 437.7198 | 4187 | 0.00046679 | 6.0613 | 6.0617 | -25.8413 | 2142.2945 | 57883.4308 | -0.012062
133 |  | 223.961 | 437.7077 | 4187 | 0.00046678 | 6.0617 | 6.0622 | -25.8413 | 2142.3536 | 58321.1386 | -0.012062
134 |  | 223.961 | 437.6957 | 4187 | 0.00046676 | 6.0622 | 6.0627 | -25.8413 | 2142.4126 | 58758.8342 | -0.012062
135 |  | 223.961 | 437.6836 | 4187 | 0.00046675 | 6.0627 | 6.0631 | -25.8413 | 2142.4717 | 59196.5178 | -0.012061
136 |  | 223.961 | 437.6715 | 4187 | 0.00046674 | 6.0631 | 6.0636 | -25.8413 | 2142.5307 | 59634.1893 | -0.012061
137 |  | 223.961 | 437.6595 | 4187 | 0.00046672 | 6.0636 | 6.0641 | -25.8413 | 2142.5897 | 60071.8488 | -0.012061
138 |  | 223.961 | 437.6474 | 4187 | 0.00046671 | 6.0641 | 6.0645 | -25.8413 | 2142.6488 | 60509.4962 | -0.01206
139 |  | 223.961 | 437.6354 | 4187 | 0.0004667 | 6.0645 | 6.065 | -25.8413 | 2142.7078 | 60947.1316 | -0.01206
140 |  | 223.961 | 437.6233 | 4187 | 0.00046669 | 6.065 | 6.0655 | -25.8413 | 2142.7669 | 61384.7549 | -0.01206
141 |  | 223.961 | 437.6112 | 4187 | 0.00046667 | 6.0655 | 6.0659 | -25.8413 | 2142.8259 | 61822.3661 | -0.012059
142 |  | 223.961 | 437.5992 | 4187 | 0.00046666 | 6.0659 | 6.0664 | -25.8413 | 2142.885 | 62259.9653 | -0.012059
143 |  | 223.961 | 437.5871 | 4187 | 0.00046665 | 6.0664 | 6.0669 | -25.8413 | 2142.9441 | 62697.5524 | -0.012059
144 |  | 223.961 | 437.5751 | 4187 | 0.00046663 | 6.0669 | 6.0673 | -25.8413 | 2143.0031 | 63135.1274 | -0.012058
145 |  | 223.961 | 437.563 | 4187 | 0.00046662 | 6.0673 | 6.0678 | -25.8413 | 2143.0622 | 63572.6904 | -0.012058
146 |  | 223.961 | 437.5509 | 4187 | 0.00046661 | 6.0678 | 6.0683 | -25.8413 | 2143.1212 | 64010.2414 | -0.012058
147 |  | 223.961 | 437.5389 | 4187 | 0.0004666 | 6.0683 | 6.0687 | -25.8413 | 2143.1803 | 64447.7803 | -0.012057
148 |  | 223.961 | 437.5268 | 4187 | 0.00046658 | 6.0687 | 6.0692 | -25.8413 | 2143.2393 | 64885.3071 | -0.012057
149 |  | 223.961 | 437.5148 | 4187 | 0.00046657 | 6.0692 | 6.0697 | -25.8413 | 2143.2984 | 65322.8218 | -0.012057
150 |  | 223.961 | 437.5027 | 4187 | 0.00046656 | 6.0697 | 6.0701 | -25.8413 | 2143.3575 | 65760.3246 | -0.012056
151 |  | 223.961 | 437.4907 | 4187 | 0.00046654 | 6.0701 | 6.0706 | -25.8413 | 2143.4165 | 66197.8152 | -0.012056
152 |  | 223.961 | 437.4786 | 4187 | 0.00046653 | 6.0706 | 6.0711 | -25.8413 | 2143.4756 | 66635.2938 | -0.012056
153 |  | 223.961 | 437.4665 | 4187 | 0.00046652 | 6.0711 | 6.0715 | -25.8413 | 2143.5347 | 67072.7603 | -0.012055
154 |  | 223.961 | 437.4545 | 4187 | 0.00046651 | 6.0715 | 6.072 | -25.8413 | 2143.5938 | 67510.2148 | -0.012055
155 |  | 223.961 | 437.4424 | 4187 | 0.00046649 | 6.072 | 6.0725 | -25.8413 | 2143.6528 | 67947.6573 | -0.012055
156 |  | 223.961 | 437.4304 | 4187 | 0.00046648 | 6.0725 | 6.0729 | -25.8413 | 2143.7119 | 68385.0876 | -0.012054
157 |  | 223.961 | 437.4183 | 4187 | 0.00046647 | 6.0729 | 6.0734 | -25.8413 | 2143.771 | 68822.506 | -0.012054
158 |  | 223.961 | 437.4063 | 4187 | 0.00046645 | 6.0734 | 6.0739 | -25.8413 | 2143.8301 | 69259.9122 | -0.012054
159 |  | 223.961 | 437.3942 | 4187 | 0.00046644 | 6.0739 | 6.0743 | -25.8413 | 2143.8891 | 69697.3064 | -0.012053
160 |  | 223.961 | 437.3822 | 4187 | 0.00046643 | 6.0743 | 6.0748 | -25.8413 | 2143.9482 | 70134.6886 | -0.012053
161 |  | 223.961 | 437.3701 | 4187 | 0.00046642 | 6.0748 | 6.0753 | -25.8413 | 2144.0073 | 70572.0587 | -0.012053
162 |  | 223.961 | 437.3581 | 4187 | 0.0004664 | 6.0753 | 6.0757 | -25.8413 | 2144.0664 | 71009.4168 | -0.012052
163 |  | 223.961 | 437.346 | 4187 | 0.00046639 | 6.0757 | 6.0762 | -25.8413 | 2144.1255 | 71446.7628 | -0.012052
164 |  | 223.961 | 437.3339 | 4187 | 0.00046638 | 6.0762 | 6.0767 | -25.8413 | 2144.1846 | 71884.0967 | -0.012052
165 |  | 223.961 | 437.3219 | 4187 | 0.00046636 | 6.0767 | 6.0771 | -25.8413 | 2144.2437 | 72321.4186 | -0.012051
166 |  | 223.961 | 437.3098 | 4187 | 0.00046635 | 6.0771 | 6.0776 | -25.8413 | 2144.3027 | 72758.7284 | -0.012051
167 |  | 223.961 | 437.2978 | 4187 | 0.00046634 | 6.0776 | 6.0781 | -25.8413 | 2144.3618 | 73196.0262 | -0.012051
168 |  | 223.961 | 437.2857 | 4187 | 0.00046633 | 6.0781 | 6.0785 | -25.8413 | 2144.4209 | 73633.312 | -0.01205
169 |  | 223.961 | 437.2737 | 4187 | 0.00046631 | 6.0785 | 6.079 | -25.8413 | 2144.48 | 74070.5857 | -0.01205
170 |  | 223.961 | 437.2616 | 4187 | 0.0004663 | 6.079 | 6.0795 | -25.8413 | 2144.5391 | 74507.8473 | -0.01205
171 |  | 223.961 | 437.2496 | 4187 | 0.00046629 | 6.0795 | 6.0799 | -25.8413 | 2144.5982 | 74945.0969 | -0.01205
172 |  | 223.961 | 437.2375 | 4187 | 0.00046627 | 6.0799 | 6.0804 | -25.8413 | 2144.6573 | 75382.3345 | -0.012049
173 |  | 223.961 | 437.2255 | 4187 | 0.00046626 | 6.0804 | 6.0809 | -25.8413 | 2144.7164 | 75819.5599 | -0.012049
174 |  | 223.961 | 437.2134 | 4187 | 0.00046625 | 6.0809 | 6.0813 | -25.8413 | 2144.7755 | 76256.7734 | -0.012049
175 |  | 223.961 | 437.2014 | 4187 | 0.00046624 | 6.0813 | 6.0818 | -25.8413 | 2144.8346 | 76693.9748 | -0.012048
176 |  | 223.961 | 437.1893 | 4187 | 0.00046622 | 6.0818 | 6.0823 | -25.8413 | 2144.8938 | 77131.1641 | -0.012048
177 |  | 223.961 | 437.1773 | 4187 | 0.00046621 | 6.0823 | 6.0827 | -25.8413 | 2144.9529 | 77568.3414 | -0.012048
178 |  | 223.961 | 437.1653 | 4187 | 0.0004662 | 6.0827 | 6.0832 | -25.8413 | 2145.012 | 78005.5067 | -0.012047
179 |  | 223.961 | 437.1532 | 4187 | 0.00046619 | 6.0832 | 6.0837 | -25.8413 | 2145.0711 | 78442.6599 | -0.012047
180 |  | 223.961 | 437.1412 | 4187 | 0.00046617 | 6.0837 | 6.0841 | -25.8413 | 2145.1302 | 78879.8011 | -0.012047
181 |  | 223.961 | 437.1291 | 4187 | 0.00046616 | 6.0841 | 6.0846 | -25.8413 | 2145.1893 | 79316.9302 | -0.012046
182 |  | 223.961 | 437.1171 | 4187 | 0.00046615 | 6.0846 | 6.0851 | -25.8413 | 2145.2484 | 79754.0472 | -0.012046
183 |  | 223.961 | 437.105 | 4187 | 0.00046613 | 6.0851 | 6.0855 | -25.8413 | 2145.3076 | 80191.1523 | -0.012046
184 |  | 223.961 | 437.093 | 4187 | 0.00046612 | 6.0855 | 6.086 | -25.8413 | 2145.3667 | 80628.2452 | -0.012045
185 |  | 223.961 | 437.0809 | 4187 | 0.00046611 | 6.086 | 6.0864 | -25.8413 | 2145.4258 | 81065.3262 | -0.012045
186 |  | 223.961 | 437.0689 | 4187 | 0.0004661 | 6.0864 | 6.0869 | -25.8413 | 2145.4849 | 81502.395 | -0.012045
187 |  | 223.961 | 437.0568 | 4187 | 0.00046608 | 6.0869 | 6.0874 | -25.8413 | 2145.544 | 81939.4519 | -0.012044
188 |  | 223.961 | 437.0448 | 4187 | 0.00046607 | 6.0874 | 6.0878 | -25.8413 | 2145.6032 | 82376.4967 | -0.012044
189 |  | 223.961 | 437.0328 | 4187 | 0.00046606 | 6.0878 | 6.0883 | -25.8413 | 2145.6623 | 82813.5294 | -0.012044
190 |  | 223.961 | 437.0207 | 4187 | 0.00046604 | 6.0883 | 6.0888 | -25.8413 | 2145.7214 | 83250.5501 | -0.012043
191 |  | 223.961 | 437.0087 | 4187 | 0.00046603 | 6.0888 | 6.0892 | -25.8413 | 2145.7806 | 83687.5588 | -0.012043
192 |  | 223.961 | 436.9966 | 4187 | 0.00046602 | 6.0892 | 6.0897 | -25.8413 | 2145.8397 | 84124.5554 | -0.012043
193 |  | 223.961 | 436.9846 | 4187 | 0.00046601 | 6.0897 | 6.0902 | -25.8413 | 2145.8988 | 84561.54 | -0.012042
194 |  | 223.961 | 436.9725 | 4187 | 0.00046599 | 6.0902 | 6.0906 | -25.8413 | 2145.958 | 84998.5125 | -0.012042
195 |  | 223.961 | 436.9605 | 4187 | 0.00046598 | 6.0906 | 6.0911 | -25.8413 | 2146.0171 | 85435.473 | -0.012042
196 |  | 223.961 | 436.9485 | 4187 | 0.00046597 | 6.0911 | 6.0916 | -25.8413 | 2146.0763 | 85872.4215 | -0.012041
197 |  | 223.961 | 436.9364 | 4187 | 0.00046595 | 6.0916 | 6.092 | -25.8413 | 2146.1354 | 86309.3579 | -0.012041
198 |  | 223.961 | 436.9244 | 4187 | 0.00046594 | 6.092 | 6.0925 | -25.8413 | 2146.1945 | 86746.2823 | -0.012041
199 |  | 223.961 | 436.9123 | 4187 | 0.00046593 | 6.0925 | 6.093 | -25.8413 | 2146.2537 | 87183.1946 | -0.01204
200 |  | 223.961 | 436.9003 | 4187 | 0.00046592 | 6.093 | 6.0934 | -25.8413 | 2146.3128 | 87620.0949 | -0.01204
201 |  | 223.961 | 436.8883 | 4187 | 0.0004659 | 6.0934 | 6.0939 | -25.8413 | 2146.372 | 88056.9832 | -0.01204
202 |  | 223.961 | 436.8762 | 4187 | 0.00046589 | 6.0939 | 6.0944 | -25.8413 | 2146.4311 | 88493.8594 | -0.012039
203 |  | 223.961 | 436.8642 | 4187 | 0.00046588 | 6.0944 | 6.0948 | -25.8413 | 2146.4903 | 88930.7235 | -0.012039
204 |  | 223.961 | 436.8521 | 4187 | 0.00046586 | 6.0948 | 6.0953 | -25.8413 | 2146.5494 | 89367.5757 | -0.012039
205 |  | 223.961 | 436.8401 | 4187 | 0.00046585 | 6.0953 | 6.0958 | -25.8413 | 2146.6086 | 89804.4158 | -0.012038
206 |  | 223.961 | 436.8281 | 4187 | 0.00046584 | 6.0958 | 6.0962 | -25.8413 | 2146.6677 | 90241.2438 | -0.012038
207 |  | 223.961 | 436.816 | 4187 | 0.00046583 | 6.0962 | 6.0967 | -25.8413 | 2146.7269 | 90678.0599 | -0.012038
208 |  | 223.961 | 436.804 | 4187 | 0.00046581 | 6.0967 | 6.0972 | -25.8413 | 2146.7861 | 91114.8638 | -0.012037
209 |  | 223.961 | 436.7919 | 4187 | 0.0004658 | 6.0972 | 6.0976 | -25.8413 | 2146.8452 | 91551.6558 | -0.012037
210 |  | 223.961 | 436.7799 | 4187 | 0.00046579 | 6.0976 | 6.0981 | -25.8413 | 2146.9044 | 91988.4357 | -0.012037
211 |  | 223.961 | 436.7679 | 4187 | 0.00046577 | 6.0981 | 6.0986 | -25.8413 | 2146.9636 | 92425.2036 | -0.012036
212 |  | 223.961 | 436.7558 | 4187 | 0.00046576 | 6.0986 | 6.099 | -25.8413 | 2147.0227 | 92861.9594 | -0.012036
213 |  | 223.961 | 436.7438 | 4187 | 0.00046575 | 6.099 | 6.0995 | -25.8413 | 2147.0819 | 93298.7032 | -0.012036
214 |  | 223.961 | 436.7318 | 4187 | 0.00046574 | 6.0995 | 6.1 | -25.8413 | 2147.1411 | 93735.435 | -0.012035
215 |  | 223.961 | 436.7197 | 4187 | 0.00046572 | 6.1 | 6.1004 | -25.8413 | 2147.2002 | 94172.1547 | -0.012035
216 |  | 223.961 | 436.7077 | 4187 | 0.00046571 | 6.1004 | 6.1009 | -25.8413 | 2147.2594 | 94608.8624 | -0.012035
217 |  | 223.961 | 436.6957 | 4187 | 0.0004657 | 6.1009 | 6.1014 | -25.8413 | 2147.3186 | 95045.558 | -0.012034
218 |  | 223.961 | 436.6836 | 4187 | 0.00046568 | 6.1014 | 6.1018 | -25.8413 | 2147.3778 | 95482.2417 | -0.012034
219 |  | 223.961 | 436.6716 | 4187 | 0.00046567 | 6.1018 | 6.1023 | -25.8413 | 2147.4369 | 95918.9133 | -0.012034
220 |  | 223.961 | 436.6596 | 4187 | 0.00046566 | 6.1023 | 6.1028 | -25.8413 | 2147.4961 | 96355.5728 | -0.012033
221 |  | 223.961 | 436.6475 | 4187 | 0.00046565 | 6.1028 | 6.1032 | -25.8413 | 2147.5553 | 96792.2203 | -0.012033
222 |  | 223.961 | 436.6355 | 4187 | 0.00046563 | 6.1032 | 6.1037 | -25.8413 | 2147.6145 | 97228.8558 | -0.012033
223 |  | 223.961 | 436.6235 | 4187 | 0.00046562 | 6.1037 | 6.1042 | -25.8413 | 2147.6737 | 97665.4793 | -0.012032
224 |  | 223.961 | 436.6114 | 4187 | 0.00046561 | 6.1042 | 6.1046 | -25.8413 | 2147.7328 | 98102.0907 | -0.012032
225 |  | 223.961 | 436.5994 | 4187 | 0.00046559 | 6.1046 | 6.1051 | -25.8413 | 2147.792 | 98538.6901 | -0.012032
226 |  | 223.961 | 436.5874 | 4187 | 0.00046558 | 6.1051 | 6.1055 | -25.8413 | 2147.8512 | 98975.2775 | -0.012031
227 |  | 223.961 | 436.5753 | 4187 | 0.00046557 | 6.1055 | 6.106 | -25.8413 | 2147.9104 | 99411.8528 | -0.012031
228 |  | 223.961 | 436.5633 | 4187 | 0.00046556 | 6.106 | 6.1065 | -25.8413 | 2147.9696 | 99848.4161 | -0.012031
229 |  | 223.961 | 436.5513 | 4187 | 0.00046554 | 6.1065 | 6.1069 | -25.8413 | 2148.0288 | 100284.9674 | -0.01203
230 |  | 223.961 | 436.5392 | 4187 | 0.00046553 | 6.1069 | 6.1074 | -25.8413 | 2148.088 | 100721.5066 | -0.01203
231 |  | 223.961 | 436.5272 | 4187 | 0.00046552 | 6.1074 | 6.1079 | -25.8413 | 2148.1472 | 101158.0338 | -0.01203
232 |  | 223.961 | 436.5152 | 4187 | 0.0004655 | 6.1079 | 6.1083 | -25.8413 | 2148.2064 | 101594.549 | -0.012029
233 |  | 223.961 | 436.5032 | 4187 | 0.00046549 | 6.1083 | 6.1088 | -25.8413 | 2148.2656 | 102031.0521 | -0.012029
234 |  | 223.961 | 436.4911 | 4187 | 0.00046548 | 6.1088 | 6.1093 | -25.8413 | 2148.3248 | 102467.5433 | -0.012029
235 |  | 223.961 | 436.4791 | 4187 | 0.00046547 | 6.1093 | 6.1097 | -25.8413 | 2148.384 | 102904.0224 | -0.012028
236 |  | 223.961 | 436.4671 | 4187 | 0.00046545 | 6.1097 | 6.1102 | -25.8413 | 2148.4432 | 103340.4894 | -0.012028

## St610
|  |  | buis | verlies W/M | L /°C/sec
diam | wandikte |  | inhoud l/m |  | W/M
610 | 12.5 | 3.1416 | 268.7829 | 479.4216 | 4187
[8 empty] | J/sec/mtr | aantal mtr. | verlies
|  | buis | verlies W/M | L /°C/sec | verlies temp | begintemp | eindtemp | verlies | bij 1°C | totaal J/sec
|  | inhoud L |  | W/M | °C per M | °C | °C | per m°C | daling | aantal mtr
1 | 610 | 268.7829 | 479.4216 | 4187 | 0.000426 | 6 | 6.0004 | -28.2013 | 2347.3995 | 479.4216 | -0.012014
2 |  | 268.7829 | 479.4095 | 4187 | 0.00042599 | 6.0004 | 6.0009 | -28.2013 | 2347.4584 | 958.8311 | -0.012014
3 |  | 268.7829 | 479.3975 | 4187 | 0.00042598 | 6.0009 | 6.0013 | -28.2013 | 2347.5172 | 1438.2286 | -0.012013
4 |  | 268.7829 | 479.3855 | 4187 | 0.00042597 | 6.0013 | 6.0017 | -28.2013 | 2347.576 | 1917.6141 | -0.012013
5 |  | 268.7829 | 479.3735 | 4187 | 0.00042596 | 6.0017 | 6.0021 | -28.2013 | 2347.6349 | 2396.9876 | -0.012013
6 |  | 268.7829 | 479.3615 | 4187 | 0.00042595 | 6.0021 | 6.0026 | -28.2013 | 2347.6937 | 2876.3491 | -0.012012
7 |  | 268.7829 | 479.3495 | 4187 | 0.00042594 | 6.0026 | 6.003 | -28.2013 | 2347.7525 | 3355.6986 | -0.012012
8 |  | 268.7829 | 479.3375 | 4187 | 0.00042593 | 6.003 | 6.0034 | -28.2013 | 2347.8114 | 3835.0361 | -0.012012
9 |  | 268.7829 | 479.3255 | 4187 | 0.00042592 | 6.0034 | 6.0038 | -28.2013 | 2347.8702 | 4314.3615 | -0.012011
10 |  | 268.7829 | 479.3134 | 4187 | 0.00042591 | 6.0038 | 6.0043 | -28.2013 | 2347.929 | 4793.675 | -0.012011
11 |  | 268.7829 | 479.3014 | 4187 | 0.0004259 | 6.0043 | 6.0047 | -28.2013 | 2347.9879 | 5272.9764 | -0.012011
12 |  | 268.7829 | 479.2894 | 4187 | 0.00042589 | 6.0047 | 6.0051 | -28.2013 | 2348.0467 | 5752.2658 | -0.012011
13 |  | 268.7829 | 479.2774 | 4187 | 0.00042588 | 6.0051 | 6.0055 | -28.2013 | 2348.1055 | 6231.5432 | -0.01201
14 |  | 268.7829 | 479.2654 | 4187 | 0.00042586 | 6.0055 | 6.006 | -28.2013 | 2348.1644 | 6710.8086 | -0.01201
15 |  | 268.7829 | 479.2534 | 4187 | 0.00042585 | 6.006 | 6.0064 | -28.2013 | 2348.2232 | 7190.062 | -0.01201
16 |  | 268.7829 | 479.2414 | 4187 | 0.00042584 | 6.0064 | 6.0068 | -28.2013 | 2348.2821 | 7669.3034 | -0.012009
17 |  | 268.7829 | 479.2294 | 4187 | 0.00042583 | 6.0068 | 6.0072 | -28.2013 | 2348.3409 | 8148.5328 | -0.012009
18 |  | 268.7829 | 479.2174 | 4187 | 0.00042582 | 6.0072 | 6.0077 | -28.2013 | 2348.3998 | 8627.7502 | -0.012009
19 |  | 268.7829 | 479.2054 | 4187 | 0.00042581 | 6.0077 | 6.0081 | -28.2013 | 2348.4586 | 9106.9555 | -0.012008
20 |  | 268.7829 | 479.1933 | 4187 | 0.0004258 | 6.0081 | 6.0085 | -28.2013 | 2348.5175 | 9586.1489 | -0.012008
21 |  | 268.7829 | 479.1813 | 4187 | 0.00042579 | 6.0085 | 6.0089 | -28.2013 | 2348.5763 | 10065.3302 | -0.012008
22 |  | 268.7829 | 479.1693 | 4187 | 0.00042578 | 6.0089 | 6.0094 | -28.2013 | 2348.6352 | 10544.4995 | -0.012008
23 |  | 268.7829 | 479.1573 | 4187 | 0.00042577 | 6.0094 | 6.0098 | -28.2013 | 2348.694 | 11023.6568 | -0.012007
24 |  | 268.7829 | 479.1453 | 4187 | 0.00042576 | 6.0098 | 6.0102 | -28.2013 | 2348.7529 | 11502.8022 | -0.012007
25 |  | 268.7829 | 479.1333 | 4187 | 0.00042575 | 6.0102 | 6.0106 | -28.2013 | 2348.8118 | 11981.9355 | -0.012007
26 |  | 268.7829 | 479.1213 | 4187 | 0.00042574 | 6.0106 | 6.0111 | -28.2013 | 2348.8706 | 12461.0568 | -0.012006
27 |  | 268.7829 | 479.1093 | 4187 | 0.00042573 | 6.0111 | 6.0115 | -28.2013 | 2348.9295 | 12940.1661 | -0.012006
28 |  | 268.7829 | 479.0973 | 4187 | 0.00042572 | 6.0115 | 6.0119 | -28.2013 | 2348.9883 | 13419.2634 | -0.012006
29 |  | 268.7829 | 479.0853 | 4187 | 0.0004257 | 6.0119 | 6.0123 | -28.2013 | 2349.0472 | 13898.3486 | -0.012005
30 |  | 268.7829 | 479.0733 | 4187 | 0.00042569 | 6.0123 | 6.0128 | -28.2013 | 2349.1061 | 14377.4219 | -0.012005
31 |  | 268.7829 | 479.0613 | 4187 | 0.00042568 | 6.0128 | 6.0132 | -28.2013 | 2349.1649 | 14856.4832 | -0.012005
32 |  | 268.7829 | 479.0493 | 4187 | 0.00042567 | 6.0132 | 6.0136 | -28.2013 | 2349.2238 | 15335.5325 | -0.012005
33 |  | 268.7829 | 479.0373 | 4187 | 0.00042566 | 6.0136 | 6.0141 | -28.2013 | 2349.2827 | 15814.5697 | -0.012004
34 |  | 268.7829 | 479.0253 | 4187 | 0.00042565 | 6.0141 | 6.0145 | -28.2013 | 2349.3416 | 16293.595 | -0.012004
35 |  | 268.7829 | 479.0133 | 4187 | 0.00042564 | 6.0145 | 6.0149 | -28.2013 | 2349.4004 | 16772.6082 | -0.012004
36 |  | 268.7829 | 479.0013 | 4187 | 0.00042563 | 6.0149 | 6.0153 | -28.2013 | 2349.4593 | 17251.6095 | -0.012003
37 |  | 268.7829 | 478.9892 | 4187 | 0.00042562 | 6.0153 | 6.0158 | -28.2013 | 2349.5182 | 17730.5987 | -0.012003
38 |  | 268.7829 | 478.9772 | 4187 | 0.00042561 | 6.0158 | 6.0162 | -28.2013 | 2349.5771 | 18209.576 | -0.012003
39 |  | 268.7829 | 478.9652 | 4187 | 0.0004256 | 6.0162 | 6.0166 | -28.2013 | 2349.6359 | 18688.5412 | -0.012002
40 |  | 268.7829 | 478.9532 | 4187 | 0.00042559 | 6.0166 | 6.017 | -28.2013 | 2349.6948 | 19167.4945 | -0.012002
41 |  | 268.7829 | 478.9412 | 4187 | 0.00042558 | 6.017 | 6.0175 | -28.2013 | 2349.7537 | 19646.4357 | -0.012002
42 |  | 268.7829 | 478.9292 | 4187 | 0.00042557 | 6.0175 | 6.0179 | -28.2013 | 2349.8126 | 20125.3649 | -0.012001
43 |  | 268.7829 | 478.9172 | 4187 | 0.00042556 | 6.0179 | 6.0183 | -28.2013 | 2349.8715 | 20604.2822 | -0.012001
44 |  | 268.7829 | 478.9052 | 4187 | 0.00042554 | 6.0183 | 6.0187 | -28.2013 | 2349.9304 | 21083.1874 | -0.012001
45 |  | 268.7829 | 478.8932 | 4187 | 0.00042553 | 6.0187 | 6.0192 | -28.2013 | 2349.9892 | 21562.0806 | -0.012001
46 |  | 268.7829 | 478.8812 | 4187 | 0.00042552 | 6.0192 | 6.0196 | -28.2013 | 2350.0481 | 22040.9619 | -0.012
47 |  | 268.7829 | 478.8692 | 4187 | 0.00042551 | 6.0196 | 6.02 | -28.2013 | 2350.107 | 22519.8311 | -0.012
48 |  | 268.7829 | 478.8572 | 4187 | 0.0004255 | 6.02 | 6.0204 | -28.2013 | 2350.1659 | 22998.6883 | -0.012
49 |  | 268.7829 | 478.8452 | 4187 | 0.00042549 | 6.0204 | 6.0209 | -28.2013 | 2350.2248 | 23477.5336 | -0.011999
50 |  | 268.7829 | 478.8332 | 4187 | 0.00042548 | 6.0209 | 6.0213 | -28.2013 | 2350.2837 | 23956.3668 | -0.011999
51 |  | 268.7829 | 478.8212 | 4187 | 0.00042547 | 6.0213 | 6.0217 | -28.2013 | 2350.3426 | 24435.188 | -0.011999
52 |  | 268.7829 | 478.8092 | 4187 | 0.00042546 | 6.0217 | 6.0221 | -28.2013 | 2350.4015 | 24913.9973 | -0.011998
53 |  | 268.7829 | 478.7972 | 4187 | 0.00042545 | 6.0221 | 6.0226 | -28.2013 | 2350.4604 | 25392.7945 | -0.011998
54 |  | 268.7829 | 478.7852 | 4187 | 0.00042544 | 6.0226 | 6.023 | -28.2013 | 2350.5193 | 25871.5797 | -0.011998
55 |  | 268.7829 | 478.7732 | 4187 | 0.00042543 | 6.023 | 6.0234 | -28.2013 | 2350.5782 | 26350.353 | -0.011998
56 |  | 268.7829 | 478.7612 | 4187 | 0.00042542 | 6.0234 | 6.0238 | -28.2013 | 2350.6371 | 26829.1142 | -0.011997
57 |  | 268.7829 | 478.7492 | 4187 | 0.00042541 | 6.0238 | 6.0243 | -28.2013 | 2350.696 | 27307.8635 | -0.011997
58 |  | 268.7829 | 478.7372 | 4187 | 0.0004254 | 6.0243 | 6.0247 | -28.2013 | 2350.7549 | 27786.6007 | -0.011997
59 |  | 268.7829 | 478.7253 | 4187 | 0.00042538 | 6.0247 | 6.0251 | -28.2013 | 2350.8138 | 28265.326 | -0.011996
60 |  | 268.7829 | 478.7133 | 4187 | 0.00042537 | 6.0251 | 6.0255 | -28.2013 | 2350.8727 | 28744.0392 | -0.011996
61 |  | 268.7829 | 478.7013 | 4187 | 0.00042536 | 6.0255 | 6.026 | -28.2013 | 2350.9317 | 29222.7405 | -0.011996
62 |  | 268.7829 | 478.6893 | 4187 | 0.00042535 | 6.026 | 6.0264 | -28.2013 | 2350.9906 | 29701.4298 | -0.011995
63 |  | 268.7829 | 478.6773 | 4187 | 0.00042534 | 6.0264 | 6.0268 | -28.2013 | 2351.0495 | 30180.107 | -0.011995
64 |  | 268.7829 | 478.6653 | 4187 | 0.00042533 | 6.0268 | 6.0272 | -28.2013 | 2351.1084 | 30658.7723 | -0.011995
65 |  | 268.7829 | 478.6533 | 4187 | 0.00042532 | 6.0272 | 6.0277 | -28.2013 | 2351.1673 | 31137.4256 | -0.011995
66 |  | 268.7829 | 478.6413 | 4187 | 0.00042531 | 6.0277 | 6.0281 | -28.2013 | 2351.2262 | 31616.0669 | -0.011994
67 |  | 268.7829 | 478.6293 | 4187 | 0.0004253 | 6.0281 | 6.0285 | -28.2013 | 2351.2852 | 32094.6962 | -0.011994
68 |  | 268.7829 | 478.6173 | 4187 | 0.00042529 | 6.0285 | 6.0289 | -28.2013 | 2351.3441 | 32573.3134 | -0.011994
69 |  | 268.7829 | 478.6053 | 4187 | 0.00042528 | 6.0289 | 6.0294 | -28.2013 | 2351.403 | 33051.9187 | -0.011993
70 |  | 268.7829 | 478.5933 | 4187 | 0.00042527 | 6.0294 | 6.0298 | -28.2013 | 2351.4619 | 33530.5121 | -0.011993
71 |  | 268.7829 | 478.5813 | 4187 | 0.00042526 | 6.0298 | 6.0302 | -28.2013 | 2351.5209 | 34009.0934 | -0.011993
72 |  | 268.7829 | 478.5693 | 4187 | 0.00042525 | 6.0302 | 6.0306 | -28.2013 | 2351.5798 | 34487.6627 | -0.011992
73 |  | 268.7829 | 478.5573 | 4187 | 0.00042524 | 6.0306 | 6.0311 | -28.2013 | 2351.6387 | 34966.22 | -0.011992
74 |  | 268.7829 | 478.5453 | 4187 | 0.00042522 | 6.0311 | 6.0315 | -28.2013 | 2351.6976 | 35444.7654 | -0.011992
75 |  | 268.7829 | 478.5333 | 4187 | 0.00042521 | 6.0315 | 6.0319 | -28.2013 | 2351.7566 | 35923.2987 | -0.011992
76 |  | 268.7829 | 478.5214 | 4187 | 0.0004252 | 6.0319 | 6.0323 | -28.2013 | 2351.8155 | 36401.8201 | -0.011991
77 |  | 268.7829 | 478.5094 | 4187 | 0.00042519 | 6.0323 | 6.0328 | -28.2013 | 2351.8745 | 36880.3294 | -0.011991
78 |  | 268.7829 | 478.4974 | 4187 | 0.00042518 | 6.0328 | 6.0332 | -28.2013 | 2351.9334 | 37358.8268 | -0.011991
79 |  | 268.7829 | 478.4854 | 4187 | 0.00042517 | 6.0332 | 6.0336 | -28.2013 | 2351.9923 | 37837.3122 | -0.01199
80 |  | 268.7829 | 478.4734 | 4187 | 0.00042516 | 6.0336 | 6.034 | -28.2013 | 2352.0513 | 38315.7856 | -0.01199
81 |  | 268.7829 | 478.4614 | 4187 | 0.00042515 | 6.034 | 6.0345 | -28.2013 | 2352.1102 | 38794.247 | -0.01199
82 |  | 268.7829 | 478.4494 | 4187 | 0.00042514 | 6.0345 | 6.0349 | -28.2013 | 2352.1692 | 39272.6964 | -0.011989
83 |  | 268.7829 | 478.4374 | 4187 | 0.00042513 | 6.0349 | 6.0353 | -28.2013 | 2352.2281 | 39751.1338 | -0.011989
84 |  | 268.7829 | 478.4254 | 4187 | 0.00042512 | 6.0353 | 6.0357 | -28.2013 | 2352.287 | 40229.5592 | -0.011989
85 |  | 268.7829 | 478.4134 | 4187 | 0.00042511 | 6.0357 | 6.0362 | -28.2013 | 2352.346 | 40707.9727 | -0.011989
86 |  | 268.7829 | 478.4015 | 4187 | 0.0004251 | 6.0362 | 6.0366 | -28.2013 | 2352.4049 | 41186.3741 | -0.011988
87 |  | 268.7829 | 478.3895 | 4187 | 0.00042509 | 6.0366 | 6.037 | -28.2013 | 2352.4639 | 41664.7636 | -0.011988
88 |  | 268.7829 | 478.3775 | 4187 | 0.00042508 | 6.037 | 6.0374 | -28.2013 | 2352.5228 | 42143.1411 | -0.011988
89 |  | 268.7829 | 478.3655 | 4187 | 0.00042506 | 6.0374 | 6.0379 | -28.2013 | 2352.5818 | 42621.5066 | -0.011987
90 |  | 268.7829 | 478.3535 | 4187 | 0.00042505 | 6.0379 | 6.0383 | -28.2013 | 2352.6407 | 43099.8601 | -0.011987
91 |  | 268.7829 | 478.3415 | 4187 | 0.00042504 | 6.0383 | 6.0387 | -28.2013 | 2352.6997 | 43578.2016 | -0.011987
92 |  | 268.7829 | 478.3295 | 4187 | 0.00042503 | 6.0387 | 6.0391 | -28.2013 | 2352.7587 | 44056.5311 | -0.011986
93 |  | 268.7829 | 478.3175 | 4187 | 0.00042502 | 6.0391 | 6.0396 | -28.2013 | 2352.8176 | 44534.8487 | -0.011986
94 |  | 268.7829 | 478.3056 | 4187 | 0.00042501 | 6.0396 | 6.04 | -28.2013 | 2352.8766 | 45013.1542 | -0.011986
95 |  | 268.7829 | 478.2936 | 4187 | 0.000425 | 6.04 | 6.0404 | -28.2013 | 2352.9355 | 45491.4478 | -0.011986
96 |  | 268.7829 | 478.2816 | 4187 | 0.00042499 | 6.0404 | 6.0408 | -28.2013 | 2352.9945 | 45969.7294 | -0.011985
97 |  | 268.7829 | 478.2696 | 4187 | 0.00042498 | 6.0408 | 6.0413 | -28.2013 | 2353.0535 | 46447.999 | -0.011985
98 |  | 268.7829 | 478.2576 | 4187 | 0.00042497 | 6.0413 | 6.0417 | -28.2013 | 2353.1124 | 46926.2566 | -0.011985
99 |  | 268.7829 | 478.2456 | 4187 | 0.00042496 | 6.0417 | 6.0421 | -28.2013 | 2353.1714 | 47404.5022 | -0.011984
100 |  | 268.7829 | 478.2336 | 4187 | 0.00042495 | 6.0421 | 6.0425 | -28.2013 | 2353.2304 | 47882.7359 | -0.011984
101 |  | 268.7829 | 478.2217 | 4187 | 0.00042494 | 6.0425 | 6.043 | -28.2013 | 2353.2893 | 48360.9575 | -0.011984
102 |  | 268.7829 | 478.2097 | 4187 | 0.00042493 | 6.043 | 6.0434 | -28.2013 | 2353.3483 | 48839.1672 | -0.011983
103 |  | 268.7829 | 478.1977 | 4187 | 0.00042492 | 6.0434 | 6.0438 | -28.2013 | 2353.4073 | 49317.3649 | -0.011983
104 |  | 268.7829 | 478.1857 | 4187 | 0.00042491 | 6.0438 | 6.0442 | -28.2013 | 2353.4663 | 49795.5506 | -0.011983
105 |  | 268.7829 | 478.1737 | 4187 | 0.00042489 | 6.0442 | 6.0447 | -28.2013 | 2353.5252 | 50273.7244 | -0.011983
106 |  | 268.7829 | 478.1617 | 4187 | 0.00042488 | 6.0447 | 6.0451 | -28.2013 | 2353.5842 | 50751.8861 | -0.011982
107 |  | 268.7829 | 478.1498 | 4187 | 0.00042487 | 6.0451 | 6.0455 | -28.2013 | 2353.6432 | 51230.0359 | -0.011982
108 |  | 268.7829 | 478.1378 | 4187 | 0.00042486 | 6.0455 | 6.0459 | -28.2013 | 2353.7022 | 51708.1737 | -0.011982
109 |  | 268.7829 | 478.1258 | 4187 | 0.00042485 | 6.0459 | 6.0464 | -28.2013 | 2353.7612 | 52186.2995 | -0.011981
110 |  | 268.7829 | 478.1138 | 4187 | 0.00042484 | 6.0464 | 6.0468 | -28.2013 | 2353.8202 | 52664.4133 | -0.011981
111 |  | 268.7829 | 478.1018 | 4187 | 0.00042483 | 6.0468 | 6.0472 | -28.2013 | 2353.8791 | 53142.5151 | -0.011981
112 |  | 268.7829 | 478.0899 | 4187 | 0.00042482 | 6.0472 | 6.0476 | -28.2013 | 2353.9381 | 53620.605 | -0.01198
113 |  | 268.7829 | 478.0779 | 4187 | 0.00042481 | 6.0476 | 6.0481 | -28.2013 | 2353.9971 | 54098.6828 | -0.01198
114 |  | 268.7829 | 478.0659 | 4187 | 0.0004248 | 6.0481 | 6.0485 | -28.2013 | 2354.0561 | 54576.7487 | -0.01198
115 |  | 268.7829 | 478.0539 | 4187 | 0.00042479 | 6.0485 | 6.0489 | -28.2013 | 2354.1151 | 55054.8027 | -0.01198
116 |  | 268.7829 | 478.0419 | 4187 | 0.00042478 | 6.0489 | 6.0493 | -28.2013 | 2354.1741 | 55532.8446 | -0.011979
117 |  | 268.7829 | 478.03 | 4187 | 0.00042477 | 6.0493 | 6.0498 | -28.2013 | 2354.2331 | 56010.8746 | -0.011979
118 |  | 268.7829 | 478.018 | 4187 | 0.00042476 | 6.0498 | 6.0502 | -28.2013 | 2354.2921 | 56488.8925 | -0.011979
119 |  | 268.7829 | 478.006 | 4187 | 0.00042475 | 6.0502 | 6.0506 | -28.2013 | 2354.3511 | 56966.8985 | -0.011978
120 |  | 268.7829 | 477.994 | 4187 | 0.00042473 | 6.0506 | 6.051 | -28.2013 | 2354.4101 | 57444.8926 | -0.011978
121 |  | 268.7829 | 477.982 | 4187 | 0.00042472 | 6.051 | 6.0515 | -28.2013 | 2354.4691 | 57922.8746 | -0.011978
122 |  | 268.7829 | 477.9701 | 4187 | 0.00042471 | 6.0515 | 6.0519 | -28.2013 | 2354.5281 | 58400.8447 | -0.011977
123 |  | 268.7829 | 477.9581 | 4187 | 0.0004247 | 6.0519 | 6.0523 | -28.2013 | 2354.5871 | 58878.8028 | -0.011977
124 |  | 268.7829 | 477.9461 | 4187 | 0.00042469 | 6.0523 | 6.0527 | -28.2013 | 2354.6461 | 59356.7489 | -0.011977
125 |  | 268.7829 | 477.9341 | 4187 | 0.00042468 | 6.0527 | 6.0532 | -28.2013 | 2354.7051 | 59834.683 | -0.011977
126 |  | 268.7829 | 477.9222 | 4187 | 0.00042467 | 6.0532 | 6.0536 | -28.2013 | 2354.7641 | 60312.6052 | -0.011976
127 |  | 268.7829 | 477.9102 | 4187 | 0.00042466 | 6.0536 | 6.054 | -28.2013 | 2354.8231 | 60790.5153 | -0.011976
128 |  | 268.7829 | 477.8982 | 4187 | 0.00042465 | 6.054 | 6.0544 | -28.2013 | 2354.8821 | 61268.4136 | -0.011976
129 |  | 268.7829 | 477.8862 | 4187 | 0.00042464 | 6.0544 | 6.0549 | -28.2013 | 2354.9411 | 61746.2998 | -0.011975
130 |  | 268.7829 | 477.8743 | 4187 | 0.00042463 | 6.0549 | 6.0553 | -28.2013 | 2355.0002 | 62224.174 | -0.011975
131 |  | 268.7829 | 477.8623 | 4187 | 0.00042462 | 6.0553 | 6.0557 | -28.2013 | 2355.0592 | 62702.0363 | -0.011975
132 |  | 268.7829 | 477.8503 | 4187 | 0.00042461 | 6.0557 | 6.0561 | -28.2013 | 2355.1182 | 63179.8866 | -0.011974
133 |  | 268.7829 | 477.8383 | 4187 | 0.0004246 | 6.0561 | 6.0566 | -28.2013 | 2355.1772 | 63657.725 | -0.011974
134 |  | 268.7829 | 477.8264 | 4187 | 0.00042459 | 6.0566 | 6.057 | -28.2013 | 2355.2362 | 64135.5513 | -0.011974
135 |  | 268.7829 | 477.8144 | 4187 | 0.00042458 | 6.057 | 6.0574 | -28.2013 | 2355.2952 | 64613.3657 | -0.011974
136 |  | 268.7829 | 477.8024 | 4187 | 0.00042456 | 6.0574 | 6.0578 | -28.2013 | 2355.3543 | 65091.1681 | -0.011973
137 |  | 268.7829 | 477.7904 | 4187 | 0.00042455 | 6.0578 | 6.0583 | -28.2013 | 2355.4133 | 65568.9585 | -0.011973
138 |  | 268.7829 | 477.7785 | 4187 | 0.00042454 | 6.0583 | 6.0587 | -28.2013 | 2355.4723 | 66046.737 | -0.011973
139 |  | 268.7829 | 477.7665 | 4187 | 0.00042453 | 6.0587 | 6.0591 | -28.2013 | 2355.5313 | 66524.5035 | -0.011972
140 |  | 268.7829 | 477.7545 | 4187 | 0.00042452 | 6.0591 | 6.0595 | -28.2013 | 2355.5904 | 67002.258 | -0.011972
141 |  | 268.7829 | 477.7425 | 4187 | 0.00042451 | 6.0595 | 6.06 | -28.2013 | 2355.6494 | 67480.0006 | -0.011972
142 |  | 268.7829 | 477.7306 | 4187 | 0.0004245 | 6.06 | 6.0604 | -28.2013 | 2355.7084 | 67957.7311 | -0.011971
143 |  | 268.7829 | 477.7186 | 4187 | 0.00042449 | 6.0604 | 6.0608 | -28.2013 | 2355.7675 | 68435.4497 | -0.011971
144 |  | 268.7829 | 477.7066 | 4187 | 0.00042448 | 6.0608 | 6.0612 | -28.2013 | 2355.8265 | 68913.1564 | -0.011971
145 |  | 268.7829 | 477.6947 | 4187 | 0.00042447 | 6.0612 | 6.0617 | -28.2013 | 2355.8855 | 69390.851 | -0.011971
146 |  | 268.7829 | 477.6827 | 4187 | 0.00042446 | 6.0617 | 6.0621 | -28.2013 | 2355.9446 | 69868.5337 | -0.01197
147 |  | 268.7829 | 477.6707 | 4187 | 0.00042445 | 6.0621 | 6.0625 | -28.2013 | 2356.0036 | 70346.2044 | -0.01197
148 |  | 268.7829 | 477.6588 | 4187 | 0.00042444 | 6.0625 | 6.0629 | -28.2013 | 2356.0627 | 70823.8632 | -0.01197
149 |  | 268.7829 | 477.6468 | 4187 | 0.00042443 | 6.0629 | 6.0634 | -28.2013 | 2356.1217 | 71301.51 | -0.011969
150 |  | 268.7829 | 477.6348 | 4187 | 0.00042442 | 6.0634 | 6.0638 | -28.2013 | 2356.1807 | 71779.1448 | -0.011969
151 |  | 268.7829 | 477.6228 | 4187 | 0.00042441 | 6.0638 | 6.0642 | -28.2013 | 2356.2398 | 72256.7676 | -0.011969
152 |  | 268.7829 | 477.6109 | 4187 | 0.00042439 | 6.0642 | 6.0646 | -28.2013 | 2356.2988 | 72734.3785 | -0.011968
153 |  | 268.7829 | 477.5989 | 4187 | 0.00042438 | 6.0646 | 6.0651 | -28.2013 | 2356.3579 | 73211.9774 | -0.011968
154 |  | 268.7829 | 477.5869 | 4187 | 0.00042437 | 6.0651 | 6.0655 | -28.2013 | 2356.4169 | 73689.5643 | -0.011968
155 |  | 268.7829 | 477.575 | 4187 | 0.00042436 | 6.0655 | 6.0659 | -28.2013 | 2356.476 | 74167.1393 | -0.011968
156 |  | 268.7829 | 477.563 | 4187 | 0.00042435 | 6.0659 | 6.0663 | -28.2013 | 2356.535 | 74644.7023 | -0.011967
157 |  | 268.7829 | 477.551 | 4187 | 0.00042434 | 6.0663 | 6.0668 | -28.2013 | 2356.5941 | 75122.2533 | -0.011967
158 |  | 268.7829 | 477.5391 | 4187 | 0.00042433 | 6.0668 | 6.0672 | -28.2013 | 2356.6531 | 75599.7924 | -0.011967
159 |  | 268.7829 | 477.5271 | 4187 | 0.00042432 | 6.0672 | 6.0676 | -28.2013 | 2356.7122 | 76077.3195 | -0.011966
160 |  | 268.7829 | 477.5151 | 4187 | 0.00042431 | 6.0676 | 6.068 | -28.2013 | 2356.7713 | 76554.8346 | -0.011966
161 |  | 268.7829 | 477.5032 | 4187 | 0.0004243 | 6.068 | 6.0684 | -28.2013 | 2356.8303 | 77032.3378 | -0.011966
162 |  | 268.7829 | 477.4912 | 4187 | 0.00042429 | 6.0684 | 6.0689 | -28.2013 | 2356.8894 | 77509.829 | -0.011965
163 |  | 268.7829 | 477.4792 | 4187 | 0.00042428 | 6.0689 | 6.0693 | -28.2013 | 2356.9484 | 77987.3083 | -0.011965
164 |  | 268.7829 | 477.4673 | 4187 | 0.00042427 | 6.0693 | 6.0697 | -28.2013 | 2357.0075 | 78464.7755 | -0.011965
165 |  | 268.7829 | 477.4553 | 4187 | 0.00042426 | 6.0697 | 6.0701 | -28.2013 | 2357.0666 | 78942.2308 | -0.011965
166 |  | 268.7829 | 477.4433 | 4187 | 0.00042425 | 6.0701 | 6.0706 | -28.2013 | 2357.1256 | 79419.6742 | -0.011964
167 |  | 268.7829 | 477.4314 | 4187 | 0.00042423 | 6.0706 | 6.071 | -28.2013 | 2357.1847 | 79897.1056 | -0.011964
168 |  | 268.7829 | 477.4194 | 4187 | 0.00042422 | 6.071 | 6.0714 | -28.2013 | 2357.2438 | 80374.525 | -0.011964
169 |  | 268.7829 | 477.4075 | 4187 | 0.00042421 | 6.0714 | 6.0718 | -28.2013 | 2357.3029 | 80851.9324 | -0.011963
170 |  | 268.7829 | 477.3955 | 4187 | 0.0004242 | 6.0718 | 6.0723 | -28.2013 | 2357.3619 | 81329.3279 | -0.011963
171 |  | 268.7829 | 477.3835 | 4187 | 0.00042419 | 6.0723 | 6.0727 | -28.2013 | 2357.421 | 81806.7114 | -0.011963
172 |  | 268.7829 | 477.3716 | 4187 | 0.00042418 | 6.0727 | 6.0731 | -28.2013 | 2357.4801 | 82284.083 | -0.011962
173 |  | 268.7829 | 477.3596 | 4187 | 0.00042417 | 6.0731 | 6.0735 | -28.2013 | 2357.5392 | 82761.4426 | -0.011962
174 |  | 268.7829 | 477.3476 | 4187 | 0.00042416 | 6.0735 | 6.074 | -28.2013 | 2357.5982 | 83238.7902 | -0.011962
175 |  | 268.7829 | 477.3357 | 4187 | 0.00042415 | 6.074 | 6.0744 | -28.2013 | 2357.6573 | 83716.1259 | -0.011962
176 |  | 268.7829 | 477.3237 | 4187 | 0.00042414 | 6.0744 | 6.0748 | -28.2013 | 2357.7164 | 84193.4496 | -0.011961
177 |  | 268.7829 | 477.3118 | 4187 | 0.00042413 | 6.0748 | 6.0752 | -28.2013 | 2357.7755 | 84670.7614 | -0.011961
178 |  | 268.7829 | 477.2998 | 4187 | 0.00042412 | 6.0752 | 6.0757 | -28.2013 | 2357.8346 | 85148.0612 | -0.011961
179 |  | 268.7829 | 477.2878 | 4187 | 0.00042411 | 6.0757 | 6.0761 | -28.2013 | 2357.8937 | 85625.349 | -0.01196
180 |  | 268.7829 | 477.2759 | 4187 | 0.0004241 | 6.0761 | 6.0765 | -28.2013 | 2357.9527 | 86102.6249 | -0.01196
181 |  | 268.7829 | 477.2639 | 4187 | 0.00042409 | 6.0765 | 6.0769 | -28.2013 | 2358.0118 | 86579.8888 | -0.01196
182 |  | 268.7829 | 477.2519 | 4187 | 0.00042408 | 6.0769 | 6.0774 | -28.2013 | 2358.0709 | 87057.1407 | -0.011959
183 |  | 268.7829 | 477.24 | 4187 | 0.00042406 | 6.0774 | 6.0778 | -28.2013 | 2358.13 | 87534.3807 | -0.011959
184 |  | 268.7829 | 477.228 | 4187 | 0.00042405 | 6.0778 | 6.0782 | -28.2013 | 2358.1891 | 88011.6087 | -0.011959
185 |  | 268.7829 | 477.2161 | 4187 | 0.00042404 | 6.0782 | 6.0786 | -28.2013 | 2358.2482 | 88488.8248 | -0.011959
186 |  | 268.7829 | 477.2041 | 4187 | 0.00042403 | 6.0786 | 6.0791 | -28.2013 | 2358.3073 | 88966.0289 | -0.011958
187 |  | 268.7829 | 477.1922 | 4187 | 0.00042402 | 6.0791 | 6.0795 | -28.2013 | 2358.3664 | 89443.2211 | -0.011958
188 |  | 268.7829 | 477.1802 | 4187 | 0.00042401 | 6.0795 | 6.0799 | -28.2013 | 2358.4255 | 89920.4013 | -0.011958
189 |  | 268.7829 | 477.1682 | 4187 | 0.000424 | 6.0799 | 6.0803 | -28.2013 | 2358.4846 | 90397.5695 | -0.011957
190 |  | 268.7829 | 477.1563 | 4187 | 0.00042399 | 6.0803 | 6.0807 | -28.2013 | 2358.5437 | 90874.7258 | -0.011957
191 |  | 268.7829 | 477.1443 | 4187 | 0.00042398 | 6.0807 | 6.0812 | -28.2013 | 2358.6028 | 91351.8701 | -0.011957
192 |  | 268.7829 | 477.1324 | 4187 | 0.00042397 | 6.0812 | 6.0816 | -28.2013 | 2358.6619 | 91829.0025 | -0.011956
193 |  | 268.7829 | 477.1204 | 4187 | 0.00042396 | 6.0816 | 6.082 | -28.2013 | 2358.721 | 92306.1229 | -0.011956
194 |  | 268.7829 | 477.1085 | 4187 | 0.00042395 | 6.082 | 6.0824 | -28.2013 | 2358.7801 | 92783.2314 | -0.011956
195 |  | 268.7829 | 477.0965 | 4187 | 0.00042394 | 6.0824 | 6.0829 | -28.2013 | 2358.8392 | 93260.3279 | -0.011956
196 |  | 268.7829 | 477.0845 | 4187 | 0.00042393 | 6.0829 | 6.0833 | -28.2013 | 2358.8984 | 93737.4124 | -0.011955
197 |  | 268.7829 | 477.0726 | 4187 | 0.00042392 | 6.0833 | 6.0837 | -28.2013 | 2358.9575 | 94214.485 | -0.011955
198 |  | 268.7829 | 477.0606 | 4187 | 0.00042391 | 6.0837 | 6.0841 | -28.2013 | 2359.0166 | 94691.5456 | -0.011955
199 |  | 268.7829 | 477.0487 | 4187 | 0.00042389 | 6.0841 | 6.0846 | -28.2013 | 2359.0757 | 95168.5943 | -0.011954
200 |  | 268.7829 | 477.0367 | 4187 | 0.00042388 | 6.0846 | 6.085 | -28.2013 | 2359.1348 | 95645.631 | -0.011954
201 |  | 268.7829 | 477.0248 | 4187 | 0.00042387 | 6.085 | 6.0854 | -28.2013 | 2359.1939 | 96122.6558 | -0.011954
202 |  | 268.7829 | 477.0128 | 4187 | 0.00042386 | 6.0854 | 6.0858 | -28.2013 | 2359.2531 | 96599.6686 | -0.011953
203 |  | 268.7829 | 477.0009 | 4187 | 0.00042385 | 6.0858 | 6.0863 | -28.2013 | 2359.3122 | 97076.6695 | -0.011953
204 |  | 268.7829 | 476.9889 | 4187 | 0.00042384 | 6.0863 | 6.0867 | -28.2013 | 2359.3713 | 97553.6584 | -0.011953
205 |  | 268.7829 | 476.977 | 4187 | 0.00042383 | 6.0867 | 6.0871 | -28.2013 | 2359.4304 | 98030.6354 | -0.011953
206 |  | 268.7829 | 476.965 | 4187 | 0.00042382 | 6.0871 | 6.0875 | -28.2013 | 2359.4895 | 98507.6004 | -0.011952
207 |  | 268.7829 | 476.9531 | 4187 | 0.00042381 | 6.0875 | 6.088 | -28.2013 | 2359.5487 | 98984.5534 | -0.011952
208 |  | 268.7829 | 476.9411 | 4187 | 0.0004238 | 6.088 | 6.0884 | -28.2013 | 2359.6078 | 99461.4945 | -0.011952
209 |  | 268.7829 | 476.9291 | 4187 | 0.00042379 | 6.0884 | 6.0888 | -28.2013 | 2359.6669 | 99938.4237 | -0.011951
210 |  | 268.7829 | 476.9172 | 4187 | 0.00042378 | 6.0888 | 6.0892 | -28.2013 | 2359.7261 | 100415.3409 | -0.011951
211 |  | 268.7829 | 476.9052 | 4187 | 0.00042377 | 6.0892 | 6.0897 | -28.2013 | 2359.7852 | 100892.2461 | -0.011951
212 |  | 268.7829 | 476.8933 | 4187 | 0.00042376 | 6.0897 | 6.0901 | -28.2013 | 2359.8443 | 101369.1394 | -0.01195
213 |  | 268.7829 | 476.8813 | 4187 | 0.00042375 | 6.0901 | 6.0905 | -28.2013 | 2359.9035 | 101846.0208 | -0.01195
214 |  | 268.7829 | 476.8694 | 4187 | 0.00042374 | 6.0905 | 6.0909 | -28.2013 | 2359.9626 | 102322.8902 | -0.01195
215 |  | 268.7829 | 476.8574 | 4187 | 0.00042372 | 6.0909 | 6.0913 | -28.2013 | 2360.0218 | 102799.7476 | -0.01195
216 |  | 268.7829 | 476.8455 | 4187 | 0.00042371 | 6.0913 | 6.0918 | -28.2013 | 2360.0809 | 103276.5931 | -0.011949
217 |  | 268.7829 | 476.8335 | 4187 | 0.0004237 | 6.0918 | 6.0922 | -28.2013 | 2360.14 | 103753.4266 | -0.011949
218 |  | 268.7829 | 476.8216 | 4187 | 0.00042369 | 6.0922 | 6.0926 | -28.2013 | 2360.1992 | 104230.2482 | -0.011949
219 |  | 268.7829 | 476.8096 | 4187 | 0.00042368 | 6.0926 | 6.093 | -28.2013 | 2360.2583 | 104707.0579 | -0.011948
220 |  | 268.7829 | 476.7977 | 4187 | 0.00042367 | 6.093 | 6.0935 | -28.2013 | 2360.3175 | 105183.8556 | -0.011948
221 |  | 268.7829 | 476.7858 | 4187 | 0.00042366 | 6.0935 | 6.0939 | -28.2013 | 2360.3766 | 105660.6413 | -0.011948
222 |  | 268.7829 | 476.7738 | 4187 | 0.00042365 | 6.0939 | 6.0943 | -28.2013 | 2360.4358 | 106137.4151 | -0.011947
223 |  | 268.7829 | 476.7619 | 4187 | 0.00042364 | 6.0943 | 6.0947 | -28.2013 | 2360.4949 | 106614.177 | -0.011947
224 |  | 268.7829 | 476.7499 | 4187 | 0.00042363 | 6.0947 | 6.0952 | -28.2013 | 2360.5541 | 107090.9269 | -0.011947
225 |  | 268.7829 | 476.738 | 4187 | 0.00042362 | 6.0952 | 6.0956 | -28.2013 | 2360.6132 | 107567.6649 | -0.011947
226 |  | 268.7829 | 476.726 | 4187 | 0.00042361 | 6.0956 | 6.096 | -28.2013 | 2360.6724 | 108044.3909 | -0.011946
227 |  | 268.7829 | 476.7141 | 4187 | 0.0004236 | 6.096 | 6.0964 | -28.2013 | 2360.7315 | 108521.105 | -0.011946
228 |  | 268.7829 | 476.7021 | 4187 | 0.00042359 | 6.0964 | 6.0969 | -28.2013 | 2360.7907 | 108997.8071 | -0.011946
229 |  | 268.7829 | 476.6902 | 4187 | 0.00042358 | 6.0969 | 6.0973 | -28.2013 | 2360.8499 | 109474.4973 | -0.011945
230 |  | 268.7829 | 476.6782 | 4187 | 0.00042357 | 6.0973 | 6.0977 | -28.2013 | 2360.909 | 109951.1755 | -0.011945
231 |  | 268.7829 | 476.6663 | 4187 | 0.00042356 | 6.0977 | 6.0981 | -28.2013 | 2360.9682 | 110427.8418 | -0.011945
232 |  | 268.7829 | 476.6543 | 4187 | 0.00042354 | 6.0981 | 6.0985 | -28.2013 | 2361.0274 | 110904.4961 | -0.011944
233 |  | 268.7829 | 476.6424 | 4187 | 0.00042353 | 6.0985 | 6.099 | -28.2013 | 2361.0865 | 111381.1385 | -0.011944
234 |  | 268.7829 | 476.6305 | 4187 | 0.00042352 | 6.099 | 6.0994 | -28.2013 | 2361.1457 | 111857.769 | -0.011944
235 |  | 268.7829 | 476.6185 | 4187 | 0.00042351 | 6.0994 | 6.0998 | -28.2013 | 2361.2049 | 112334.3875 | -0.011944
236 |  | 268.7829 | 476.6066 | 4187 | 0.0004235 | 6.0998 | 6.1002 | -28.2013 | 2361.264 | 112810.9941 | -0.011943

## Cu19
|  |  | buis | verlies W/M | L /°C/sec
diam | wandikte |  | inhoud l/m |  | W/M
19.1 | 1 | 3.1416 | 0.22966 | 15.0484 | 4187
[8 empty] | J/sec/mtr | aantal mtr. | verlies
|  | buis | verlies W/M | L /°C/sec | verlies temp | begintemp | eindtemp | verlies | bij 1°C | totaal J/sec
|  | inhoud L |  | W/M | °C per M | °C | °C | per m°C | daling | aantal mtr
1 | 19.1 | 0.22966 | 15.0484 | 4187 | 0.01565 | 6 | 6.0156 | -0.8852 | 63.8992 | 15.0484 | -0.013853
2 |  | 0.22966 | 15.0345 | 4187 | 0.015635 | 6.0156 | 6.0313 | -0.8852 | 63.9581 | 30.0829 | -0.01384
3 |  | 0.22966 | 15.0207 | 4187 | 0.015621 | 6.0313 | 6.0469 | -0.8852 | 64.017 | 45.1036 | -0.013828
4 |  | 0.22966 | 15.0068 | 4187 | 0.015606 | 6.0469 | 6.0625 | -0.8852 | 64.076 | 60.1104 | -0.013815
5 |  | 0.22966 | 14.993 | 4187 | 0.015592 | 6.0625 | 6.0781 | -0.8852 | 64.1351 | 75.1034 | -0.013802
6 |  | 0.22966 | 14.9792 | 4187 | 0.015578 | 6.0781 | 6.0937 | -0.8852 | 64.1942 | 90.0827 | -0.013789
7 |  | 0.22966 | 14.9654 | 4187 | 0.015563 | 6.0937 | 6.1092 | -0.8852 | 64.2533 | 105.0481 | -0.013777
8 |  | 0.22966 | 14.9517 | 4187 | 0.015549 | 6.1092 | 6.1248 | -0.8852 | 64.3125 | 119.9998 | -0.013764
9 |  | 0.22966 | 14.9379 | 4187 | 0.015535 | 6.1248 | 6.1403 | -0.8852 | 64.3718 | 134.9377 | -0.013751
10 |  | 0.22966 | 14.9241 | 4187 | 0.01552 | 6.1403 | 6.1558 | -0.8852 | 64.4311 | 149.8618 | -0.013739
11 |  | 0.22966 | 14.9104 | 4187 | 0.015506 | 6.1558 | 6.1714 | -0.8852 | 64.4905 | 164.7722 | -0.013726
12 |  | 0.22966 | 14.8967 | 4187 | 0.015492 | 6.1714 | 6.1868 | -0.8852 | 64.5499 | 179.6689 | -0.013713
13 |  | 0.22966 | 14.883 | 4187 | 0.015478 | 6.1868 | 6.2023 | -0.8852 | 64.6094 | 194.5519 | -0.013701
14 |  | 0.22966 | 14.8693 | 4187 | 0.015463 | 6.2023 | 6.2178 | -0.8852 | 64.6689 | 209.4211 | -0.013688
15 |  | 0.22966 | 14.8556 | 4187 | 0.015449 | 6.2178 | 6.2332 | -0.8852 | 64.7285 | 224.2767 | -0.013676
16 |  | 0.22966 | 14.8419 | 4187 | 0.015435 | 6.2332 | 6.2487 | -0.8852 | 64.7881 | 239.1186 | -0.013663
17 |  | 0.22966 | 14.8282 | 4187 | 0.015421 | 6.2487 | 6.2641 | -0.8852 | 64.8478 | 253.9469 | -0.01365
18 |  | 0.22966 | 14.8146 | 4187 | 0.015407 | 6.2641 | 6.2795 | -0.8852 | 64.9076 | 268.7615 | -0.013638
19 |  | 0.22966 | 14.801 | 4187 | 0.015392 | 6.2795 | 6.2949 | -0.8852 | 64.9674 | 283.5624 | -0.013625
20 |  | 0.22966 | 14.7873 | 4187 | 0.015378 | 6.2949 | 6.3103 | -0.8852 | 65.0272 | 298.3497 | -0.013613
21 |  | 0.22966 | 14.7737 | 4187 | 0.015364 | 6.3103 | 6.3256 | -0.8852 | 65.0872 | 313.1235 | -0.0136
22 |  | 0.22966 | 14.7601 | 4187 | 0.01535 | 6.3256 | 6.341 | -0.8852 | 65.1471 | 327.8836 | -0.013588
23 |  | 0.22966 | 14.7465 | 4187 | 0.015336 | 6.341 | 6.3563 | -0.8852 | 65.2072 | 342.6301 | -0.013575
24 |  | 0.22966 | 14.733 | 4187 | 0.015322 | 6.3563 | 6.3716 | -0.8852 | 65.2672 | 357.3631 | -0.013563
25 |  | 0.22966 | 14.7194 | 4187 | 0.015308 | 6.3716 | 6.3869 | -0.8852 | 65.3274 | 372.0824 | -0.01355
26 |  | 0.22966 | 14.7058 | 4187 | 0.015293 | 6.3869 | 6.4022 | -0.8852 | 65.3876 | 386.7883 | -0.013538
27 |  | 0.22966 | 14.6923 | 4187 | 0.015279 | 6.4022 | 6.4175 | -0.8852 | 65.4478 | 401.4806 | -0.013525
28 |  | 0.22966 | 14.6788 | 4187 | 0.015265 | 6.4175 | 6.4328 | -0.8852 | 65.5081 | 416.1594 | -0.013513
29 |  | 0.22966 | 14.6653 | 4187 | 0.015251 | 6.4328 | 6.448 | -0.8852 | 65.5685 | 430.8246 | -0.0135
30 |  | 0.22966 | 14.6518 | 4187 | 0.015237 | 6.448 | 6.4633 | -0.8852 | 65.6289 | 445.4764 | -0.013488
31 |  | 0.22966 | 14.6383 | 4187 | 0.015223 | 6.4633 | 6.4785 | -0.8852 | 65.6894 | 460.1147 | -0.013476
32 |  | 0.22966 | 14.6248 | 4187 | 0.015209 | 6.4785 | 6.4937 | -0.8852 | 65.7499 | 474.7395 | -0.013463
33 |  | 0.22966 | 14.6113 | 4187 | 0.015195 | 6.4937 | 6.5089 | -0.8852 | 65.8105 | 489.3508 | -0.013451
34 |  | 0.22966 | 14.5979 | 4187 | 0.015181 | 6.5089 | 6.5241 | -0.8852 | 65.8711 | 503.9487 | -0.013438
35 |  | 0.22966 | 14.5844 | 4187 | 0.015167 | 6.5241 | 6.5393 | -0.8852 | 65.9318 | 518.5331 | -0.013426
36 |  | 0.22966 | 14.571 | 4187 | 0.015153 | 6.5393 | 6.5544 | -0.8852 | 65.9926 | 533.1042 | -0.013414
37 |  | 0.22966 | 14.5576 | 4187 | 0.015139 | 6.5544 | 6.5695 | -0.8852 | 66.0534 | 547.6618 | -0.013401
38 |  | 0.22966 | 14.5442 | 4187 | 0.015125 | 6.5695 | 6.5847 | -0.8852 | 66.1142 | 562.206 | -0.013389
39 |  | 0.22966 | 14.5308 | 4187 | 0.015111 | 6.5847 | 6.5998 | -0.8852 | 66.1752 | 576.7368 | -0.013377
40 |  | 0.22966 | 14.5174 | 4187 | 0.015098 | 6.5998 | 6.6149 | -0.8852 | 66.2361 | 591.2542 | -0.013364
41 |  | 0.22966 | 14.5041 | 4187 | 0.015084 | 6.6149 | 6.63 | -0.8852 | 66.2972 | 605.7583 | -0.013352
42 |  | 0.22966 | 14.4907 | 4187 | 0.01507 | 6.63 | 6.645 | -0.8852 | 66.3582 | 620.2491 | -0.01334
43 |  | 0.22966 | 14.4774 | 4187 | 0.015056 | 6.645 | 6.6601 | -0.8852 | 66.4194 | 634.7264 | -0.013327
44 |  | 0.22966 | 14.4641 | 4187 | 0.015042 | 6.6601 | 6.6751 | -0.8852 | 66.4806 | 649.1905 | -0.013315
45 |  | 0.22966 | 14.4507 | 4187 | 0.015028 | 6.6751 | 6.6902 | -0.8852 | 66.5418 | 663.6412 | -0.013303
46 |  | 0.22966 | 14.4374 | 4187 | 0.015014 | 6.6902 | 6.7052 | -0.8852 | 66.6032 | 678.0787 | -0.013291
47 |  | 0.22966 | 14.4242 | 4187 | 0.015 | 6.7052 | 6.7202 | -0.8852 | 66.6645 | 692.5028 | -0.013278
48 |  | 0.22966 | 14.4109 | 4187 | 0.014987 | 6.7202 | 6.7352 | -0.8852 | 66.726 | 706.9137 | -0.013266
49 |  | 0.22966 | 14.3976 | 4187 | 0.014973 | 6.7352 | 6.7501 | -0.8852 | 66.7874 | 721.3113 | -0.013254
50 |  | 0.22966 | 14.3844 | 4187 | 0.014959 | 6.7501 | 6.7651 | -0.8852 | 66.849 | 735.6957 | -0.013242
51 |  | 0.22966 | 14.3711 | 4187 | 0.014945 | 6.7651 | 6.78 | -0.8852 | 66.9106 | 750.0668 | -0.01323
52 |  | 0.22966 | 14.3579 | 4187 | 0.014932 | 6.78 | 6.795 | -0.8852 | 66.9722 | 764.4247 | -0.013217
53 |  | 0.22966 | 14.3447 | 4187 | 0.014918 | 6.795 | 6.8099 | -0.8852 | 67.0339 | 778.7693 | -0.013205
54 |  | 0.22966 | 14.3315 | 4187 | 0.014904 | 6.8099 | 6.8248 | -0.8852 | 67.0957 | 793.1008 | -0.013193
55 |  | 0.22966 | 14.3183 | 4187 | 0.01489 | 6.8248 | 6.8397 | -0.8852 | 67.1575 | 807.419 | -0.013181
56 |  | 0.22966 | 14.3051 | 4187 | 0.014877 | 6.8397 | 6.8546 | -0.8852 | 67.2194 | 821.7241 | -0.013169
57 |  | 0.22966 | 14.2919 | 4187 | 0.014863 | 6.8546 | 6.8694 | -0.8852 | 67.2813 | 836.016 | -0.013157
58 |  | 0.22966 | 14.2788 | 4187 | 0.014849 | 6.8694 | 6.8843 | -0.8852 | 67.3433 | 850.2948 | -0.013145
59 |  | 0.22966 | 14.2656 | 4187 | 0.014836 | 6.8843 | 6.8991 | -0.8852 | 67.4054 | 864.5604 | -0.013132
60 |  | 0.22966 | 14.2525 | 4187 | 0.014822 | 6.8991 | 6.9139 | -0.8852 | 67.4675 | 878.8129 | -0.01312
61 |  | 0.22966 | 14.2394 | 4187 | 0.014808 | 6.9139 | 6.9287 | -0.8852 | 67.5297 | 893.0522 | -0.013108
62 |  | 0.22966 | 14.2263 | 4187 | 0.014795 | 6.9287 | 6.9435 | -0.8852 | 67.5919 | 907.2785 | -0.013096
63 |  | 0.22966 | 14.2132 | 4187 | 0.014781 | 6.9435 | 6.9583 | -0.8852 | 67.6542 | 921.4917 | -0.013084
64 |  | 0.22966 | 14.2001 | 4187 | 0.014767 | 6.9583 | 6.9731 | -0.8852 | 67.7165 | 935.6917 | -0.013072
65 |  | 0.22966 | 14.187 | 4187 | 0.014754 | 6.9731 | 6.9878 | -0.8852 | 67.7789 | 949.8787 | -0.01306
66 |  | 0.22966 | 14.1739 | 4187 | 0.01474 | 6.9878 | 7.0026 | -0.8852 | 67.8413 | 964.0527 | -0.013048
67 |  | 0.22966 | 14.1609 | 4187 | 0.014727 | 7.0026 | 7.0173 | -0.8852 | 67.9039 | 978.2136 | -0.013036
68 |  | 0.22966 | 14.1479 | 4187 | 0.014713 | 7.0173 | 7.032 | -0.8852 | 67.9664 | 992.3614 | -0.013024
69 |  | 0.22966 | 14.1348 | 4187 | 0.0147 | 7.032 | 7.0467 | -0.8852 | 68.0291 | 1006.4962 | -0.013012
70 |  | 0.22966 | 14.1218 | 4187 | 0.014686 | 7.0467 | 7.0614 | -0.8852 | 68.0917 | 1020.6181 | -0.013
71 |  | 0.22966 | 14.1088 | 4187 | 0.014673 | 7.0614 | 7.0761 | -0.8852 | 68.1545 | 1034.7269 | -0.012988
72 |  | 0.22966 | 14.0958 | 4187 | 0.014659 | 7.0761 | 7.0907 | -0.8852 | 68.2173 | 1048.8227 | -0.012976
73 |  | 0.22966 | 14.0829 | 4187 | 0.014646 | 7.0907 | 7.1054 | -0.8852 | 68.2801 | 1062.9056 | -0.012964
74 |  | 0.22966 | 14.0699 | 4187 | 0.014632 | 7.1054 | 7.12 | -0.8852 | 68.343 | 1076.9755 | -0.012952
75 |  | 0.22966 | 14.0569 | 4187 | 0.014619 | 7.12 | 7.1346 | -0.8852 | 68.406 | 1091.0324 | -0.01294
76 |  | 0.22966 | 14.044 | 4187 | 0.014605 | 7.1346 | 7.1492 | -0.8852 | 68.469 | 1105.0764 | -0.012928
77 |  | 0.22966 | 14.0311 | 4187 | 0.014592 | 7.1492 | 7.1638 | -0.8852 | 68.5321 | 1119.1075 | -0.012917
78 |  | 0.22966 | 14.0182 | 4187 | 0.014578 | 7.1638 | 7.1784 | -0.8852 | 68.5953 | 1133.1256 | -0.012905
79 |  | 0.22966 | 14.0052 | 4187 | 0.014565 | 7.1784 | 7.193 | -0.8852 | 68.6585 | 1147.1309 | -0.012893
80 |  | 0.22966 | 13.9924 | 4187 | 0.014551 | 7.193 | 7.2075 | -0.8852 | 68.7218 | 1161.1232 | -0.012881
81 |  | 0.22966 | 13.9795 | 4187 | 0.014538 | 7.2075 | 7.2221 | -0.8852 | 68.7851 | 1175.1027 | -0.012869
82 |  | 0.22966 | 13.9666 | 4187 | 0.014525 | 7.2221 | 7.2366 | -0.8852 | 68.8485 | 1189.0693 | -0.012857
83 |  | 0.22966 | 13.9537 | 4187 | 0.014511 | 7.2366 | 7.2511 | -0.8852 | 68.9119 | 1203.0231 | -0.012845
84 |  | 0.22966 | 13.9409 | 4187 | 0.014498 | 7.2511 | 7.2656 | -0.8852 | 68.9754 | 1216.964 | -0.012834
85 |  | 0.22966 | 13.9281 | 4187 | 0.014485 | 7.2656 | 7.2801 | -0.8852 | 69.0389 | 1230.892 | -0.012822
86 |  | 0.22966 | 13.9152 | 4187 | 0.014471 | 7.2801 | 7.2945 | -0.8852 | 69.1026 | 1244.8073 | -0.01281
87 |  | 0.22966 | 13.9024 | 4187 | 0.014458 | 7.2945 | 7.309 | -0.8852 | 69.1662 | 1258.7097 | -0.012798
88 |  | 0.22966 | 13.8896 | 4187 | 0.014445 | 7.309 | 7.3234 | -0.8852 | 69.23 | 1272.5994 | -0.012786
89 |  | 0.22966 | 13.8769 | 4187 | 0.014431 | 7.3234 | 7.3379 | -0.8852 | 69.2937 | 1286.4762 | -0.012775
90 |  | 0.22966 | 13.8641 | 4187 | 0.014418 | 7.3379 | 7.3523 | -0.8852 | 69.3576 | 1300.3403 | -0.012763
91 |  | 0.22966 | 13.8513 | 4187 | 0.014405 | 7.3523 | 7.3667 | -0.8852 | 69.4215 | 1314.1916 | -0.012751
92 |  | 0.22966 | 13.8386 | 4187 | 0.014391 | 7.3667 | 7.3811 | -0.8852 | 69.4855 | 1328.0302 | -0.012739
93 |  | 0.22966 | 13.8258 | 4187 | 0.014378 | 7.3811 | 7.3955 | -0.8852 | 69.5495 | 1341.856 | -0.012728
94 |  | 0.22966 | 13.8131 | 4187 | 0.014365 | 7.3955 | 7.4098 | -0.8852 | 69.6136 | 1355.6691 | -0.012716
95 |  | 0.22966 | 13.8004 | 4187 | 0.014352 | 7.4098 | 7.4242 | -0.8852 | 69.6777 | 1369.4695 | -0.012704
96 |  | 0.22966 | 13.7877 | 4187 | 0.014339 | 7.4242 | 7.4385 | -0.8852 | 69.7419 | 1383.2572 | -0.012692
97 |  | 0.22966 | 13.775 | 4187 | 0.014325 | 7.4385 | 7.4529 | -0.8852 | 69.8062 | 1397.0322 | -0.012681
98 |  | 0.22966 | 13.7623 | 4187 | 0.014312 | 7.4529 | 7.4672 | -0.8852 | 69.8705 | 1410.7945 | -0.012669
99 |  | 0.22966 | 13.7496 | 4187 | 0.014299 | 7.4672 | 7.4815 | -0.8852 | 69.9349 | 1424.5441 | -0.012657
100 |  | 0.22966 | 13.737 | 4187 | 0.014286 | 7.4815 | 7.4957 | -0.8852 | 69.9993 | 1438.2811 | -0.012646
101 |  | 0.22966 | 13.7243 | 4187 | 0.014273 | 7.4957 | 7.51 | -0.8852 | 70.0638 | 1452.0054 | -0.012634
102 |  | 0.22966 | 13.7117 | 4187 | 0.01426 | 7.51 | 7.5243 | -0.8852 | 70.1284 | 1465.7171 | -0.012623
103 |  | 0.22966 | 13.6991 | 4187 | 0.014246 | 7.5243 | 7.5385 | -0.8852 | 70.193 | 1479.4162 | -0.012611
104 |  | 0.22966 | 13.6865 | 4187 | 0.014233 | 7.5385 | 7.5528 | -0.8852 | 70.2577 | 1493.1026 | -0.012599
105 |  | 0.22966 | 13.6739 | 4187 | 0.01422 | 7.5528 | 7.567 | -0.8852 | 70.3224 | 1506.7765 | -0.012588
106 |  | 0.22966 | 13.6613 | 4187 | 0.014207 | 7.567 | 7.5812 | -0.8852 | 70.3872 | 1520.4378 | -0.012576
107 |  | 0.22966 | 13.6487 | 4187 | 0.014194 | 7.5812 | 7.5954 | -0.8852 | 70.4521 | 1534.0865 | -0.012565
108 |  | 0.22966 | 13.6361 | 4187 | 0.014181 | 7.5954 | 7.6096 | -0.8852 | 70.517 | 1547.7226 | -0.012553
109 |  | 0.22966 | 13.6236 | 4187 | 0.014168 | 7.6096 | 7.6237 | -0.8852 | 70.582 | 1561.3462 | -0.012541
110 |  | 0.22966 | 13.611 | 4187 | 0.014155 | 7.6237 | 7.6379 | -0.8852 | 70.647 | 1574.9573 | -0.01253
111 |  | 0.22966 | 13.5985 | 4187 | 0.014142 | 7.6379 | 7.652 | -0.8852 | 70.7121 | 1588.5558 | -0.012518
112 |  | 0.22966 | 13.586 | 4187 | 0.014129 | 7.652 | 7.6662 | -0.8852 | 70.7772 | 1602.1418 | -0.012507
113 |  | 0.22966 | 13.5735 | 4187 | 0.014116 | 7.6662 | 7.6803 | -0.8852 | 70.8425 | 1615.7153 | -0.012495
114 |  | 0.22966 | 13.561 | 4187 | 0.014103 | 7.6803 | 7.6944 | -0.8852 | 70.9077 | 1629.2762 | -0.012484
115 |  | 0.22966 | 13.5485 | 4187 | 0.01409 | 7.6944 | 7.7085 | -0.8852 | 70.9731 | 1642.8248 | -0.012472
116 |  | 0.22966 | 13.536 | 4187 | 0.014077 | 7.7085 | 7.7225 | -0.8852 | 71.0385 | 1656.3608 | -0.012461
117 |  | 0.22966 | 13.5236 | 4187 | 0.014064 | 7.7225 | 7.7366 | -0.8852 | 71.1039 | 1669.8844 | -0.012449
118 |  | 0.22966 | 13.5111 | 4187 | 0.014051 | 7.7366 | 7.7507 | -0.8852 | 71.1694 | 1683.3955 | -0.012438
119 |  | 0.22966 | 13.4987 | 4187 | 0.014038 | 7.7507 | 7.7647 | -0.8852 | 71.235 | 1696.8942 | -0.012426
120 |  | 0.22966 | 13.4863 | 4187 | 0.014025 | 7.7647 | 7.7787 | -0.8852 | 71.3006 | 1710.3804 | -0.012415
121 |  | 0.22966 | 13.4738 | 4187 | 0.014012 | 7.7787 | 7.7927 | -0.8852 | 71.3663 | 1723.8543 | -0.012404
122 |  | 0.22966 | 13.4614 | 4187 | 0.013999 | 7.7927 | 7.8067 | -0.8852 | 71.4321 | 1737.3157 | -0.012392
123 |  | 0.22966 | 13.4491 | 4187 | 0.013986 | 7.8067 | 7.8207 | -0.8852 | 71.4979 | 1750.7648 | -0.012381
124 |  | 0.22966 | 13.4367 | 4187 | 0.013974 | 7.8207 | 7.8347 | -0.8852 | 71.5638 | 1764.2015 | -0.012369
125 |  | 0.22966 | 13.4243 | 4187 | 0.013961 | 7.8347 | 7.8487 | -0.8852 | 71.6297 | 1777.6258 | -0.012358
126 |  | 0.22966 | 13.4119 | 4187 | 0.013948 | 7.8487 | 7.8626 | -0.8852 | 71.6957 | 1791.0377 | -0.012347
127 |  | 0.22966 | 13.3996 | 4187 | 0.013935 | 7.8626 | 7.8765 | -0.8852 | 71.7618 | 1804.4373 | -0.012335
128 |  | 0.22966 | 13.3873 | 4187 | 0.013922 | 7.8765 | 7.8905 | -0.8852 | 71.8279 | 1817.8246 | -0.012324
129 |  | 0.22966 | 13.3749 | 4187 | 0.013909 | 7.8905 | 7.9044 | -0.8852 | 71.8941 | 1831.1995 | -0.012313
130 |  | 0.22966 | 13.3626 | 4187 | 0.013897 | 7.9044 | 7.9183 | -0.8852 | 71.9604 | 1844.5621 | -0.012301
131 |  | 0.22966 | 13.3503 | 4187 | 0.013884 | 7.9183 | 7.9321 | -0.8852 | 72.0267 | 1857.9125 | -0.01229
132 |  | 0.22966 | 13.338 | 4187 | 0.013871 | 7.9321 | 7.946 | -0.8852 | 72.093 | 1871.2505 | -0.012279
133 |  | 0.22966 | 13.3258 | 4187 | 0.013858 | 7.946 | 7.9599 | -0.8852 | 72.1595 | 1884.5762 | -0.012267
134 |  | 0.22966 | 13.3135 | 4187 | 0.013845 | 7.9599 | 7.9737 | -0.8852 | 72.2259 | 1897.8897 | -0.012256
135 |  | 0.22966 | 13.3012 | 4187 | 0.013833 | 7.9737 | 7.9876 | -0.8852 | 72.2925 | 1911.191 | -0.012245
136 |  | 0.22966 | 13.289 | 4187 | 0.01382 | 7.9876 | 8.0014 | -0.8852 | 72.3591 | 1924.48 | -0.012233
137 |  | 0.22966 | 13.2768 | 4187 | 0.013807 | 8.0014 | 8.0152 | -0.8852 | 72.4258 | 1937.7567 | -0.012222
138 |  | 0.22966 | 13.2645 | 4187 | 0.013795 | 8.0152 | 8.029 | -0.8852 | 72.4925 | 1951.0212 | -0.012211
139 |  | 0.22966 | 13.2523 | 4187 | 0.013782 | 8.029 | 8.0428 | -0.8852 | 72.5593 | 1964.2736 | -0.0122
140 |  | 0.22966 | 13.2401 | 4187 | 0.013769 | 8.0428 | 8.0565 | -0.8852 | 72.6262 | 1977.5137 | -0.012188
141 |  | 0.22966 | 13.2279 | 4187 | 0.013756 | 8.0565 | 8.0703 | -0.8852 | 72.6931 | 1990.7416 | -0.012177
142 |  | 0.22966 | 13.2158 | 4187 | 0.013744 | 8.0703 | 8.084 | -0.8852 | 72.7601 | 2003.9574 | -0.012166
143 |  | 0.22966 | 13.2036 | 4187 | 0.013731 | 8.084 | 8.0978 | -0.8852 | 72.8271 | 2017.161 | -0.012155
144 |  | 0.22966 | 13.1914 | 4187 | 0.013719 | 8.0978 | 8.1115 | -0.8852 | 72.8942 | 2030.3524 | -0.012144
145 |  | 0.22966 | 13.1793 | 4187 | 0.013706 | 8.1115 | 8.1252 | -0.8852 | 72.9614 | 2043.5317 | -0.012132
146 |  | 0.22966 | 13.1672 | 4187 | 0.013693 | 8.1252 | 8.1389 | -0.8852 | 73.0286 | 2056.6988 | -0.012121
147 |  | 0.22966 | 13.155 | 4187 | 0.013681 | 8.1389 | 8.1526 | -0.8852 | 73.0959 | 2069.8539 | -0.01211
148 |  | 0.22966 | 13.1429 | 4187 | 0.013668 | 8.1526 | 8.1662 | -0.8852 | 73.1632 | 2082.9968 | -0.012099
149 |  | 0.22966 | 13.1308 | 4187 | 0.013655 | 8.1662 | 8.1799 | -0.8852 | 73.2307 | 2096.1276 | -0.012088
150 |  | 0.22966 | 13.1187 | 4187 | 0.013643 | 8.1799 | 8.1935 | -0.8852 | 73.2981 | 2109.2464 | -0.012077
151 |  | 0.22966 | 13.1067 | 4187 | 0.01363 | 8.1935 | 8.2072 | -0.8852 | 73.3657 | 2122.353 | -0.012066
152 |  | 0.22966 | 13.0946 | 4187 | 0.013618 | 8.2072 | 8.2208 | -0.8852 | 73.4333 | 2135.4476 | -0.012054
153 |  | 0.22966 | 13.0825 | 4187 | 0.013605 | 8.2208 | 8.2344 | -0.8852 | 73.5009 | 2148.5302 | -0.012043
154 |  | 0.22966 | 13.0705 | 4187 | 0.013593 | 8.2344 | 8.248 | -0.8852 | 73.5687 | 2161.6007 | -0.012032
155 |  | 0.22966 | 13.0585 | 4187 | 0.01358 | 8.248 | 8.2615 | -0.8852 | 73.6364 | 2174.6592 | -0.012021
156 |  | 0.22966 | 13.0464 | 4187 | 0.013568 | 8.2615 | 8.2751 | -0.8852 | 73.7043 | 2187.7056 | -0.01201
157 |  | 0.22966 | 13.0344 | 4187 | 0.013555 | 8.2751 | 8.2887 | -0.8852 | 73.7722 | 2200.74 | -0.011999
158 |  | 0.22966 | 13.0224 | 4187 | 0.013543 | 8.2887 | 8.3022 | -0.8852 | 73.8402 | 2213.7625 | -0.011988
159 |  | 0.22966 | 13.0105 | 4187 | 0.01353 | 8.3022 | 8.3157 | -0.8852 | 73.9082 | 2226.7729 | -0.011977
160 |  | 0.22966 | 12.9985 | 4187 | 0.013518 | 8.3157 | 8.3293 | -0.8852 | 73.9763 | 2239.7714 | -0.011966
161 |  | 0.22966 | 12.9865 | 4187 | 0.013505 | 8.3293 | 8.3428 | -0.8852 | 74.0445 | 2252.7579 | -0.011955
162 |  | 0.22966 | 12.9746 | 4187 | 0.013493 | 8.3428 | 8.3563 | -0.8852 | 74.1127 | 2265.7325 | -0.011944
163 |  | 0.22966 | 12.9626 | 4187 | 0.013481 | 8.3563 | 8.3697 | -0.8852 | 74.181 | 2278.6951 | -0.011933
164 |  | 0.22966 | 12.9507 | 4187 | 0.013468 | 8.3697 | 8.3832 | -0.8852 | 74.2493 | 2291.6458 | -0.011922
165 |  | 0.22966 | 12.9388 | 4187 | 0.013456 | 8.3832 | 8.3967 | -0.8852 | 74.3178 | 2304.5845 | -0.011911
166 |  | 0.22966 | 12.9268 | 4187 | 0.013443 | 8.3967 | 8.4101 | -0.8852 | 74.3862 | 2317.5113 | -0.0119
167 |  | 0.22966 | 12.9149 | 4187 | 0.013431 | 8.4101 | 8.4235 | -0.8852 | 74.4548 | 2330.4263 | -0.011889
168 |  | 0.22966 | 12.9031 | 4187 | 0.013419 | 8.4235 | 8.437 | -0.8852 | 74.5234 | 2343.3293 | -0.011878
169 |  | 0.22966 | 12.8912 | 4187 | 0.013406 | 8.437 | 8.4504 | -0.8852 | 74.5921 | 2356.2205 | -0.011867
170 |  | 0.22966 | 12.8793 | 4187 | 0.013394 | 8.4504 | 8.4638 | -0.8852 | 74.6608 | 2369.0998 | -0.011856
171 |  | 0.22966 | 12.8675 | 4187 | 0.013382 | 8.4638 | 8.4771 | -0.8852 | 74.7296 | 2381.9673 | -0.011845
172 |  | 0.22966 | 12.8556 | 4187 | 0.013369 | 8.4771 | 8.4905 | -0.8852 | 74.7984 | 2394.8229 | -0.011834
173 |  | 0.22966 | 12.8438 | 4187 | 0.013357 | 8.4905 | 8.5039 | -0.8852 | 74.8674 | 2407.6667 | -0.011824
174 |  | 0.22966 | 12.8319 | 4187 | 0.013345 | 8.5039 | 8.5172 | -0.8852 | 74.9363 | 2420.4986 | -0.011813
175 |  | 0.22966 | 12.8201 | 4187 | 0.013332 | 8.5172 | 8.5305 | -0.8852 | 75.0054 | 2433.3187 | -0.011802
176 |  | 0.22966 | 12.8083 | 4187 | 0.01332 | 8.5305 | 8.5439 | -0.8852 | 75.0745 | 2446.1271 | -0.011791
177 |  | 0.22966 | 12.7965 | 4187 | 0.013308 | 8.5439 | 8.5572 | -0.8852 | 75.1437 | 2458.9236 | -0.01178
178 |  | 0.22966 | 12.7848 | 4187 | 0.013296 | 8.5572 | 8.5705 | -0.8852 | 75.2129 | 2471.7084 | -0.011769
179 |  | 0.22966 | 12.773 | 4187 | 0.013283 | 8.5705 | 8.5838 | -0.8852 | 75.2822 | 2484.4814 | -0.011758
180 |  | 0.22966 | 12.7612 | 4187 | 0.013271 | 8.5838 | 8.597 | -0.8852 | 75.3516 | 2497.2426 | -0.011748
181 |  | 0.22966 | 12.7495 | 4187 | 0.013259 | 8.597 | 8.6103 | -0.8852 | 75.421 | 2509.9921 | -0.011737
182 |  | 0.22966 | 12.7378 | 4187 | 0.013247 | 8.6103 | 8.6235 | -0.8852 | 75.4905 | 2522.7299 | -0.011726
183 |  | 0.22966 | 12.726 | 4187 | 0.013235 | 8.6235 | 8.6368 | -0.8852 | 75.5601 | 2535.4559 | -0.011715
184 |  | 0.22966 | 12.7143 | 4187 | 0.013222 | 8.6368 | 8.65 | -0.8852 | 75.6297 | 2548.1702 | -0.011704
185 |  | 0.22966 | 12.7026 | 4187 | 0.01321 | 8.65 | 8.6632 | -0.8852 | 75.6994 | 2560.8728 | -0.011694
186 |  | 0.22966 | 12.6909 | 4187 | 0.013198 | 8.6632 | 8.6764 | -0.8852 | 75.7691 | 2573.5637 | -0.011683
187 |  | 0.22966 | 12.6792 | 4187 | 0.013186 | 8.6764 | 8.6896 | -0.8852 | 75.8389 | 2586.2429 | -0.011672
188 |  | 0.22966 | 12.6676 | 4187 | 0.013174 | 8.6896 | 8.7028 | -0.8852 | 75.9088 | 2598.9105 | -0.011661
189 |  | 0.22966 | 12.6559 | 4187 | 0.013162 | 8.7028 | 8.7159 | -0.8852 | 75.9788 | 2611.5664 | -0.011651
190 |  | 0.22966 | 12.6442 | 4187 | 0.013149 | 8.7159 | 8.7291 | -0.8852 | 76.0488 | 2624.2106 | -0.01164
191 |  | 0.22966 | 12.6326 | 4187 | 0.013137 | 8.7291 | 8.7422 | -0.8852 | 76.1188 | 2636.8432 | -0.011629
192 |  | 0.22966 | 12.621 | 4187 | 0.013125 | 8.7422 | 8.7553 | -0.8852 | 76.189 | 2649.4642 | -0.011618
193 |  | 0.22966 | 12.6094 | 4187 | 0.013113 | 8.7553 | 8.7684 | -0.8852 | 76.2592 | 2662.0736 | -0.011608
194 |  | 0.22966 | 12.5977 | 4187 | 0.013101 | 8.7684 | 8.7815 | -0.8852 | 76.3294 | 2674.6713 | -0.011597
195 |  | 0.22966 | 12.5862 | 4187 | 0.013089 | 8.7815 | 8.7946 | -0.8852 | 76.3998 | 2687.2575 | -0.011586
196 |  | 0.22966 | 12.5746 | 4187 | 0.013077 | 8.7946 | 8.8077 | -0.8852 | 76.4702 | 2699.832 | -0.011576
197 |  | 0.22966 | 12.563 | 4187 | 0.013065 | 8.8077 | 8.8208 | -0.8852 | 76.5406 | 2712.395 | -0.011565
198 |  | 0.22966 | 12.5514 | 4187 | 0.013053 | 8.8208 | 8.8338 | -0.8852 | 76.6112 | 2724.9465 | -0.011554
199 |  | 0.22966 | 12.5399 | 4187 | 0.013041 | 8.8338 | 8.8469 | -0.8852 | 76.6817 | 2737.4863 | -0.011544
200 |  | 0.22966 | 12.5283 | 4187 | 0.013029 | 8.8469 | 8.8599 | -0.8852 | 76.7524 | 2750.0147 | -0.011533
201 |  | 0.22966 | 12.5168 | 4187 | 0.013017 | 8.8599 | 8.8729 | -0.8852 | 76.8231 | 2762.5314 | -0.011523
202 |  | 0.22966 | 12.5053 | 4187 | 0.013005 | 8.8729 | 8.8859 | -0.8852 | 76.8939 | 2775.0367 | -0.011512
203 |  | 0.22966 | 12.4938 | 4187 | 0.012993 | 8.8859 | 8.8989 | -0.8852 | 76.9648 | 2787.5305 | -0.011501
204 |  | 0.22966 | 12.4823 | 4187 | 0.012981 | 8.8989 | 8.9119 | -0.8852 | 77.0357 | 2800.0127 | -0.011491
205 |  | 0.22966 | 12.4708 | 4187 | 0.012969 | 8.9119 | 8.9249 | -0.8852 | 77.1067 | 2812.4835 | -0.01148
206 |  | 0.22966 | 12.4593 | 4187 | 0.012957 | 8.9249 | 8.9378 | -0.8852 | 77.1777 | 2824.9428 | -0.01147
207 |  | 0.22966 | 12.4478 | 4187 | 0.012945 | 8.9378 | 8.9508 | -0.8852 | 77.2488 | 2837.3906 | -0.011459
208 |  | 0.22966 | 12.4364 | 4187 | 0.012933 | 8.9508 | 8.9637 | -0.8852 | 77.32 | 2849.827 | -0.011449
209 |  | 0.22966 | 12.4249 | 4187 | 0.012921 | 8.9637 | 8.9766 | -0.8852 | 77.3912 | 2862.2519 | -0.011438
210 |  | 0.22966 | 12.4135 | 4187 | 0.012909 | 8.9766 | 8.9895 | -0.8852 | 77.4625 | 2874.6654 | -0.011427
211 |  | 0.22966 | 12.402 | 4187 | 0.012898 | 8.9895 | 9.0024 | -0.8852 | 77.5339 | 2887.0674 | -0.011417
212 |  | 0.22966 | 12.3906 | 4187 | 0.012886 | 9.0024 | 9.0153 | -0.8852 | 77.6054 | 2899.458 | -0.011406
213 |  | 0.22966 | 12.3792 | 4187 | 0.012874 | 9.0153 | 9.0282 | -0.8852 | 77.6769 | 2911.8372 | -0.011396
214 |  | 0.22966 | 12.3678 | 4187 | 0.012862 | 9.0282 | 9.041 | -0.8852 | 77.7484 | 2924.2051 | -0.011385
215 |  | 0.22966 | 12.3564 | 4187 | 0.01285 | 9.041 | 9.0539 | -0.8852 | 77.8201 | 2936.5615 | -0.011375
216 |  | 0.22966 | 12.3451 | 4187 | 0.012838 | 9.0539 | 9.0667 | -0.8852 | 77.8918 | 2948.9066 | -0.011364
217 |  | 0.22966 | 12.3337 | 4187 | 0.012827 | 9.0667 | 9.0796 | -0.8852 | 77.9636 | 2961.2403 | -0.011354
218 |  | 0.22966 | 12.3223 | 4187 | 0.012815 | 9.0796 | 9.0924 | -0.8852 | 78.0354 | 2973.5626 | -0.011344
219 |  | 0.22966 | 12.311 | 4187 | 0.012803 | 9.0924 | 9.1052 | -0.8852 | 78.1073 | 2985.8736 | -0.011333
220 |  | 0.22966 | 12.2997 | 4187 | 0.012791 | 9.1052 | 9.118 | -0.8852 | 78.1793 | 2998.1733 | -0.011323
221 |  | 0.22966 | 12.2883 | 4187 | 0.012779 | 9.118 | 9.1307 | -0.8852 | 78.2513 | 3010.4617 | -0.011312
222 |  | 0.22966 | 12.277 | 4187 | 0.012768 | 9.1307 | 9.1435 | -0.8852 | 78.3234 | 3022.7387 | -0.011302
223 |  | 0.22966 | 12.2657 | 4187 | 0.012756 | 9.1435 | 9.1563 | -0.8852 | 78.3956 | 3035.0044 | -0.011291
224 |  | 0.22966 | 12.2544 | 4187 | 0.012744 | 9.1563 | 9.169 | -0.8852 | 78.4678 | 3047.2589 | -0.011281
225 |  | 0.22966 | 12.2432 | 4187 | 0.012732 | 9.169 | 9.1817 | -0.8852 | 78.5401 | 3059.502 | -0.011271
226 |  | 0.22966 | 12.2319 | 4187 | 0.012721 | 9.1817 | 9.1945 | -0.8852 | 78.6125 | 3071.7339 | -0.01126
227 |  | 0.22966 | 12.2206 | 4187 | 0.012709 | 9.1945 | 9.2072 | -0.8852 | 78.6849 | 3083.9545 | -0.01125
228 |  | 0.22966 | 12.2094 | 4187 | 0.012697 | 9.2072 | 9.2199 | -0.8852 | 78.7574 | 3096.1639 | -0.01124
229 |  | 0.22966 | 12.1981 | 4187 | 0.012686 | 9.2199 | 9.2326 | -0.8852 | 78.83 | 3108.3621 | -0.011229
230 |  | 0.22966 | 12.1869 | 4187 | 0.012674 | 9.2326 | 9.2452 | -0.8852 | 78.9026 | 3120.549 | -0.011219
231 |  | 0.22966 | 12.1757 | 4187 | 0.012662 | 9.2452 | 9.2579 | -0.8852 | 78.9753 | 3132.7247 | -0.011209
232 |  | 0.22966 | 12.1645 | 4187 | 0.012651 | 9.2579 | 9.2705 | -0.8852 | 79.0481 | 3144.8892 | -0.011198
233 |  | 0.22966 | 12.1533 | 4187 | 0.012639 | 9.2705 | 9.2832 | -0.8852 | 79.1209 | 3157.0424 | -0.011188
234 |  | 0.22966 | 12.1421 | 4187 | 0.012627 | 9.2832 | 9.2958 | -0.8852 | 79.1938 | 3169.1845 | -0.011178
235 |  | 0.22966 | 12.1309 | 4187 | 0.012616 | 9.2958 | 9.3084 | -0.8852 | 79.2668 | 3181.3155 | -0.011167
236 |  | 0.22966 | 12.1198 | 4187 | 0.012604 | 9.3084 | 9.321 | -0.8852 | 79.3398 | 3193.4352 | -0.011157

## Cu25
|  |  | buis | verlies W/M | L /°C/sec
diam | wandikte |  | inhoud l/m |  | W/M
25.4 | 1.2 | 3.1416 | 0.41548 | 20.0155 | 4187
[8 empty] | J/sec/mtr | aantal mtr. | verlies
|  | buis | verlies W/M | L /°C/sec | verlies temp | begintemp | eindtemp | verlies | bij 1°C | totaal J/sec
|  | inhoud L |  | W/M | °C per M | °C | °C | per m°C | daling | aantal mtr
1 | 25.4 | 0.41548 | 20.0155 | 4187 | 0.011506 | 6 | 6.0115 | -1.1774 | 86.9123 | 20.0155 | -0.013547
2 |  | 0.41548 | 20.002 | 4187 | 0.011498 | 6.0115 | 6.023 | -1.1774 | 86.9712 | 40.0175 | -0.013538
3 |  | 0.41548 | 19.9884 | 4187 | 0.01149 | 6.023 | 6.0345 | -1.1774 | 87.0301 | 60.006 | -0.013528
4 |  | 0.41548 | 19.9749 | 4187 | 0.011483 | 6.0345 | 6.046 | -1.1774 | 87.089 | 79.9809 | -0.013519
5 |  | 0.41548 | 19.9614 | 4187 | 0.011475 | 6.046 | 6.0575 | -1.1774 | 87.148 | 99.9423 | -0.01351
6 |  | 0.41548 | 19.9479 | 4187 | 0.011467 | 6.0575 | 6.0689 | -1.1774 | 87.207 | 119.8902 | -0.013501
7 |  | 0.41548 | 19.9344 | 4187 | 0.011459 | 6.0689 | 6.0804 | -1.1774 | 87.2661 | 139.8246 | -0.013492
8 |  | 0.41548 | 19.9209 | 4187 | 0.011451 | 6.0804 | 6.0918 | -1.1774 | 87.3252 | 159.7455 | -0.013483
9 |  | 0.41548 | 19.9074 | 4187 | 0.011444 | 6.0918 | 6.1033 | -1.1774 | 87.3844 | 179.6529 | -0.013474
10 |  | 0.41548 | 19.8939 | 4187 | 0.011436 | 6.1033 | 6.1147 | -1.1774 | 87.4435 | 199.5468 | -0.013465
11 |  | 0.41548 | 19.8805 | 4187 | 0.011428 | 6.1147 | 6.1261 | -1.1774 | 87.5028 | 219.4273 | -0.013455
12 |  | 0.41548 | 19.867 | 4187 | 0.01142 | 6.1261 | 6.1376 | -1.1774 | 87.562 | 239.2943 | -0.013446
13 |  | 0.41548 | 19.8536 | 4187 | 0.011413 | 6.1376 | 6.149 | -1.1774 | 87.6213 | 259.1479 | -0.013437
14 |  | 0.41548 | 19.8401 | 4187 | 0.011405 | 6.149 | 6.1604 | -1.1774 | 87.6807 | 278.988 | -0.013428
15 |  | 0.41548 | 19.8267 | 4187 | 0.011397 | 6.1604 | 6.1718 | -1.1774 | 87.7401 | 298.8147 | -0.013419
16 |  | 0.41548 | 19.8133 | 4187 | 0.01139 | 6.1718 | 6.1832 | -1.1774 | 87.7995 | 318.628 | -0.01341
17 |  | 0.41548 | 19.7999 | 4187 | 0.011382 | 6.1832 | 6.1945 | -1.1774 | 87.8589 | 338.4279 | -0.013401
18 |  | 0.41548 | 19.7865 | 4187 | 0.011374 | 6.1945 | 6.2059 | -1.1774 | 87.9184 | 358.2144 | -0.013392
19 |  | 0.41548 | 19.7731 | 4187 | 0.011366 | 6.2059 | 6.2173 | -1.1774 | 87.978 | 377.9875 | -0.013383
20 |  | 0.41548 | 19.7597 | 4187 | 0.011359 | 6.2173 | 6.2286 | -1.1774 | 88.0376 | 397.7472 | -0.013374
21 |  | 0.41548 | 19.7463 | 4187 | 0.011351 | 6.2286 | 6.24 | -1.1774 | 88.0972 | 417.4935 | -0.013365
22 |  | 0.41548 | 19.733 | 4187 | 0.011343 | 6.24 | 6.2513 | -1.1774 | 88.1569 | 437.2265 | -0.013356
23 |  | 0.41548 | 19.7196 | 4187 | 0.011336 | 6.2513 | 6.2627 | -1.1774 | 88.2166 | 456.9461 | -0.013347
24 |  | 0.41548 | 19.7063 | 4187 | 0.011328 | 6.2627 | 6.274 | -1.1774 | 88.2763 | 476.6523 | -0.013337
25 |  | 0.41548 | 19.6929 | 4187 | 0.01132 | 6.274 | 6.2853 | -1.1774 | 88.3361 | 496.3452 | -0.013328
26 |  | 0.41548 | 19.6796 | 4187 | 0.011313 | 6.2853 | 6.2966 | -1.1774 | 88.3959 | 516.0248 | -0.013319
27 |  | 0.41548 | 19.6663 | 4187 | 0.011305 | 6.2966 | 6.3079 | -1.1774 | 88.4558 | 535.6911 | -0.01331
28 |  | 0.41548 | 19.653 | 4187 | 0.011297 | 6.3079 | 6.3192 | -1.1774 | 88.5157 | 555.3441 | -0.013301
29 |  | 0.41548 | 19.6397 | 4187 | 0.01129 | 6.3192 | 6.3305 | -1.1774 | 88.5757 | 574.9838 | -0.013292
30 |  | 0.41548 | 19.6264 | 4187 | 0.011282 | 6.3305 | 6.3418 | -1.1774 | 88.6357 | 594.6101 | -0.013283
31 |  | 0.41548 | 19.6131 | 4187 | 0.011275 | 6.3418 | 6.3531 | -1.1774 | 88.6957 | 614.2232 | -0.013274
32 |  | 0.41548 | 19.5998 | 4187 | 0.011267 | 6.3531 | 6.3644 | -1.1774 | 88.7558 | 633.823 | -0.013265
33 |  | 0.41548 | 19.5866 | 4187 | 0.011259 | 6.3644 | 6.3756 | -1.1774 | 88.8159 | 653.4096 | -0.013256
34 |  | 0.41548 | 19.5733 | 4187 | 0.011252 | 6.3756 | 6.3869 | -1.1774 | 88.876 | 672.9829 | -0.013247
35 |  | 0.41548 | 19.56 | 4187 | 0.011244 | 6.3869 | 6.3981 | -1.1774 | 88.9362 | 692.5429 | -0.013239
36 |  | 0.41548 | 19.5468 | 4187 | 0.011236 | 6.3981 | 6.4093 | -1.1774 | 88.9964 | 712.0897 | -0.01323
37 |  | 0.41548 | 19.5336 | 4187 | 0.011229 | 6.4093 | 6.4206 | -1.1774 | 89.0567 | 731.6233 | -0.013221
38 |  | 0.41548 | 19.5204 | 4187 | 0.011221 | 6.4206 | 6.4318 | -1.1774 | 89.117 | 751.1437 | -0.013212
39 |  | 0.41548 | 19.5071 | 4187 | 0.011214 | 6.4318 | 6.443 | -1.1774 | 89.1774 | 770.6508 | -0.013203
40 |  | 0.41548 | 19.4939 | 4187 | 0.011206 | 6.443 | 6.4542 | -1.1774 | 89.2378 | 790.1448 | -0.013194
41 |  | 0.41548 | 19.4807 | 4187 | 0.011198 | 6.4542 | 6.4654 | -1.1774 | 89.2982 | 809.6255 | -0.013185
42 |  | 0.41548 | 19.4676 | 4187 | 0.011191 | 6.4654 | 6.4766 | -1.1774 | 89.3587 | 829.0931 | -0.013176
43 |  | 0.41548 | 19.4544 | 4187 | 0.011183 | 6.4766 | 6.4878 | -1.1774 | 89.4192 | 848.5475 | -0.013167
44 |  | 0.41548 | 19.4412 | 4187 | 0.011176 | 6.4878 | 6.499 | -1.1774 | 89.4798 | 867.9887 | -0.013158
45 |  | 0.41548 | 19.4281 | 4187 | 0.011168 | 6.499 | 6.5101 | -1.1774 | 89.5404 | 887.4168 | -0.013149
46 |  | 0.41548 | 19.4149 | 4187 | 0.011161 | 6.5101 | 6.5213 | -1.1774 | 89.601 | 906.8317 | -0.01314
47 |  | 0.41548 | 19.4018 | 4187 | 0.011153 | 6.5213 | 6.5324 | -1.1774 | 89.6617 | 926.2334 | -0.013131
48 |  | 0.41548 | 19.3886 | 4187 | 0.011145 | 6.5324 | 6.5436 | -1.1774 | 89.7224 | 945.6221 | -0.013123
49 |  | 0.41548 | 19.3755 | 4187 | 0.011138 | 6.5436 | 6.5547 | -1.1774 | 89.7832 | 964.9976 | -0.013114
50 |  | 0.41548 | 19.3624 | 4187 | 0.01113 | 6.5547 | 6.5659 | -1.1774 | 89.844 | 984.36 | -0.013105
51 |  | 0.41548 | 19.3493 | 4187 | 0.011123 | 6.5659 | 6.577 | -1.1774 | 89.9049 | 1003.7093 | -0.013096
52 |  | 0.41548 | 19.3362 | 4187 | 0.011115 | 6.577 | 6.5881 | -1.1774 | 89.9658 | 1023.0455 | -0.013087
53 |  | 0.41548 | 19.3231 | 4187 | 0.011108 | 6.5881 | 6.5992 | -1.1774 | 90.0267 | 1042.3686 | -0.013078
54 |  | 0.41548 | 19.31 | 4187 | 0.0111 | 6.5992 | 6.6103 | -1.1774 | 90.0877 | 1061.6787 | -0.013069
55 |  | 0.41548 | 19.297 | 4187 | 0.011093 | 6.6103 | 6.6214 | -1.1774 | 90.1487 | 1080.9757 | -0.01306
56 |  | 0.41548 | 19.2839 | 4187 | 0.011085 | 6.6214 | 6.6325 | -1.1774 | 90.2097 | 1100.2596 | -0.013052
57 |  | 0.41548 | 19.2709 | 4187 | 0.011078 | 6.6325 | 6.6436 | -1.1774 | 90.2708 | 1119.5304 | -0.013043
58 |  | 0.41548 | 19.2578 | 4187 | 0.01107 | 6.6436 | 6.6546 | -1.1774 | 90.332 | 1138.7882 | -0.013034
59 |  | 0.41548 | 19.2448 | 4187 | 0.011063 | 6.6546 | 6.6657 | -1.1774 | 90.3931 | 1158.033 | -0.013025
60 |  | 0.41548 | 19.2318 | 4187 | 0.011055 | 6.6657 | 6.6767 | -1.1774 | 90.4544 | 1177.2648 | -0.013016
61 |  | 0.41548 | 19.2187 | 4187 | 0.011048 | 6.6767 | 6.6878 | -1.1774 | 90.5156 | 1196.4835 | -0.013008
62 |  | 0.41548 | 19.2057 | 4187 | 0.01104 | 6.6878 | 6.6988 | -1.1774 | 90.5769 | 1215.6893 | -0.012999
63 |  | 0.41548 | 19.1927 | 4187 | 0.011033 | 6.6988 | 6.7099 | -1.1774 | 90.6383 | 1234.882 | -0.01299
64 |  | 0.41548 | 19.1797 | 4187 | 0.011025 | 6.7099 | 6.7209 | -1.1774 | 90.6997 | 1254.0617 | -0.012981
65 |  | 0.41548 | 19.1668 | 4187 | 0.011018 | 6.7209 | 6.7319 | -1.1774 | 90.7611 | 1273.2285 | -0.012972
66 |  | 0.41548 | 19.1538 | 4187 | 0.01101 | 6.7319 | 6.7429 | -1.1774 | 90.8226 | 1292.3823 | -0.012964
67 |  | 0.41548 | 19.1408 | 4187 | 0.011003 | 6.7429 | 6.7539 | -1.1774 | 90.8841 | 1311.5231 | -0.012955
68 |  | 0.41548 | 19.1279 | 4187 | 0.010996 | 6.7539 | 6.7649 | -1.1774 | 90.9456 | 1330.651 | -0.012946
69 |  | 0.41548 | 19.1149 | 4187 | 0.010988 | 6.7649 | 6.7759 | -1.1774 | 91.0072 | 1349.7659 | -0.012937
70 |  | 0.41548 | 19.102 | 4187 | 0.010981 | 6.7759 | 6.7869 | -1.1774 | 91.0689 | 1368.8679 | -0.012929
71 |  | 0.41548 | 19.0891 | 4187 | 0.010973 | 6.7869 | 6.7979 | -1.1774 | 91.1305 | 1387.957 | -0.01292
72 |  | 0.41548 | 19.0761 | 4187 | 0.010966 | 6.7979 | 6.8088 | -1.1774 | 91.1923 | 1407.0331 | -0.012911
73 |  | 0.41548 | 19.0632 | 4187 | 0.010958 | 6.8088 | 6.8198 | -1.1774 | 91.254 | 1426.0963 | -0.012902
74 |  | 0.41548 | 19.0503 | 4187 | 0.010951 | 6.8198 | 6.8307 | -1.1774 | 91.3158 | 1445.1467 | -0.012894
75 |  | 0.41548 | 19.0374 | 4187 | 0.010944 | 6.8307 | 6.8417 | -1.1774 | 91.3777 | 1464.1841 | -0.012885
76 |  | 0.41548 | 19.0246 | 4187 | 0.010936 | 6.8417 | 6.8526 | -1.1774 | 91.4396 | 1483.2087 | -0.012876
77 |  | 0.41548 | 19.0117 | 4187 | 0.010929 | 6.8526 | 6.8635 | -1.1774 | 91.5015 | 1502.2203 | -0.012867
78 |  | 0.41548 | 18.9988 | 4187 | 0.010921 | 6.8635 | 6.8745 | -1.1774 | 91.5635 | 1521.2191 | -0.012859
79 |  | 0.41548 | 18.9859 | 4187 | 0.010914 | 6.8745 | 6.8854 | -1.1774 | 91.6255 | 1540.2051 | -0.01285
80 |  | 0.41548 | 18.9731 | 4187 | 0.010907 | 6.8854 | 6.8963 | -1.1774 | 91.6875 | 1559.1782 | -0.012841
81 |  | 0.41548 | 18.9603 | 4187 | 0.010899 | 6.8963 | 6.9072 | -1.1774 | 91.7496 | 1578.1384 | -0.012833
82 |  | 0.41548 | 18.9474 | 4187 | 0.010892 | 6.9072 | 6.9181 | -1.1774 | 91.8118 | 1597.0859 | -0.012824
83 |  | 0.41548 | 18.9346 | 4187 | 0.010884 | 6.9181 | 6.929 | -1.1774 | 91.8739 | 1616.0205 | -0.012815
84 |  | 0.41548 | 18.9218 | 4187 | 0.010877 | 6.929 | 6.9398 | -1.1774 | 91.9362 | 1634.9423 | -0.012807
85 |  | 0.41548 | 18.909 | 4187 | 0.01087 | 6.9398 | 6.9507 | -1.1774 | 91.9984 | 1653.8512 | -0.012798
86 |  | 0.41548 | 18.8962 | 4187 | 0.010862 | 6.9507 | 6.9616 | -1.1774 | 92.0607 | 1672.7474 | -0.012789
87 |  | 0.41548 | 18.8834 | 4187 | 0.010855 | 6.9616 | 6.9724 | -1.1774 | 92.1231 | 1691.6308 | -0.012781
88 |  | 0.41548 | 18.8706 | 4187 | 0.010848 | 6.9724 | 6.9833 | -1.1774 | 92.1855 | 1710.5014 | -0.012772
89 |  | 0.41548 | 18.8578 | 4187 | 0.01084 | 6.9833 | 6.9941 | -1.1774 | 92.2479 | 1729.3593 | -0.012763
90 |  | 0.41548 | 18.8451 | 4187 | 0.010833 | 6.9941 | 7.0049 | -1.1774 | 92.3104 | 1748.2043 | -0.012755
91 |  | 0.41548 | 18.8323 | 4187 | 0.010826 | 7.0049 | 7.0158 | -1.1774 | 92.3729 | 1767.0367 | -0.012746
92 |  | 0.41548 | 18.8196 | 4187 | 0.010818 | 7.0158 | 7.0266 | -1.1774 | 92.4355 | 1785.8562 | -0.012737
93 |  | 0.41548 | 18.8068 | 4187 | 0.010811 | 7.0266 | 7.0374 | -1.1774 | 92.4981 | 1804.6631 | -0.012729
94 |  | 0.41548 | 18.7941 | 4187 | 0.010804 | 7.0374 | 7.0482 | -1.1774 | 92.5607 | 1823.4572 | -0.01272
95 |  | 0.41548 | 18.7814 | 4187 | 0.010796 | 7.0482 | 7.059 | -1.1774 | 92.6234 | 1842.2386 | -0.012712
96 |  | 0.41548 | 18.7687 | 4187 | 0.010789 | 7.059 | 7.0698 | -1.1774 | 92.6862 | 1861.0072 | -0.012703
97 |  | 0.41548 | 18.756 | 4187 | 0.010782 | 7.0698 | 7.0806 | -1.1774 | 92.7489 | 1879.7632 | -0.012694
98 |  | 0.41548 | 18.7433 | 4187 | 0.010774 | 7.0806 | 7.0913 | -1.1774 | 92.8117 | 1898.5065 | -0.012686
99 |  | 0.41548 | 18.7306 | 4187 | 0.010767 | 7.0913 | 7.1021 | -1.1774 | 92.8746 | 1917.2371 | -0.012677
100 |  | 0.41548 | 18.7179 | 4187 | 0.01076 | 7.1021 | 7.1129 | -1.1774 | 92.9375 | 1935.955 | -0.012669
101 |  | 0.41548 | 18.7052 | 4187 | 0.010753 | 7.1129 | 7.1236 | -1.1774 | 93.0004 | 1954.6603 | -0.01266
102 |  | 0.41548 | 18.6926 | 4187 | 0.010745 | 7.1236 | 7.1344 | -1.1774 | 93.0634 | 1973.3528 | -0.012651
103 |  | 0.41548 | 18.6799 | 4187 | 0.010738 | 7.1344 | 7.1451 | -1.1774 | 93.1265 | 1992.0328 | -0.012643
104 |  | 0.41548 | 18.6673 | 4187 | 0.010731 | 7.1451 | 7.1558 | -1.1774 | 93.1895 | 2010.7001 | -0.012634
105 |  | 0.41548 | 18.6547 | 4187 | 0.010724 | 7.1558 | 7.1666 | -1.1774 | 93.2526 | 2029.3547 | -0.012626
106 |  | 0.41548 | 18.642 | 4187 | 0.010716 | 7.1666 | 7.1773 | -1.1774 | 93.3158 | 2047.9968 | -0.012617
107 |  | 0.41548 | 18.6294 | 4187 | 0.010709 | 7.1773 | 7.188 | -1.1774 | 93.379 | 2066.6262 | -0.012609
108 |  | 0.41548 | 18.6168 | 4187 | 0.010702 | 7.188 | 7.1987 | -1.1774 | 93.4422 | 2085.243 | -0.0126
109 |  | 0.41548 | 18.6042 | 4187 | 0.010695 | 7.1987 | 7.2094 | -1.1774 | 93.5055 | 2103.8472 | -0.012592
110 |  | 0.41548 | 18.5916 | 4187 | 0.010687 | 7.2094 | 7.2201 | -1.1774 | 93.5689 | 2122.4388 | -0.012583
111 |  | 0.41548 | 18.579 | 4187 | 0.01068 | 7.2201 | 7.2308 | -1.1774 | 93.6322 | 2141.0179 | -0.012575
112 |  | 0.41548 | 18.5665 | 4187 | 0.010673 | 7.2308 | 7.2414 | -1.1774 | 93.6956 | 2159.5843 | -0.012566
113 |  | 0.41548 | 18.5539 | 4187 | 0.010666 | 7.2414 | 7.2521 | -1.1774 | 93.7591 | 2178.1382 | -0.012558
114 |  | 0.41548 | 18.5413 | 4187 | 0.010658 | 7.2521 | 7.2628 | -1.1774 | 93.8226 | 2196.6795 | -0.012549
115 |  | 0.41548 | 18.5288 | 4187 | 0.010651 | 7.2628 | 7.2734 | -1.1774 | 93.8862 | 2215.2083 | -0.012541
116 |  | 0.41548 | 18.5162 | 4187 | 0.010644 | 7.2734 | 7.284 | -1.1774 | 93.9497 | 2233.7246 | -0.012532
117 |  | 0.41548 | 18.5037 | 4187 | 0.010637 | 7.284 | 7.2947 | -1.1774 | 94.0134 | 2252.2283 | -0.012524
118 |  | 0.41548 | 18.4912 | 4187 | 0.01063 | 7.2947 | 7.3053 | -1.1774 | 94.077 | 2270.7195 | -0.012515
119 |  | 0.41548 | 18.4787 | 4187 | 0.010622 | 7.3053 | 7.3159 | -1.1774 | 94.1408 | 2289.1982 | -0.012507
120 |  | 0.41548 | 18.4662 | 4187 | 0.010615 | 7.3159 | 7.3266 | -1.1774 | 94.2045 | 2307.6643 | -0.012498
121 |  | 0.41548 | 18.4537 | 4187 | 0.010608 | 7.3266 | 7.3372 | -1.1774 | 94.2683 | 2326.118 | -0.01249
122 |  | 0.41548 | 18.4412 | 4187 | 0.010601 | 7.3372 | 7.3478 | -1.1774 | 94.3322 | 2344.5592 | -0.012481
123 |  | 0.41548 | 18.4287 | 4187 | 0.010594 | 7.3478 | 7.3584 | -1.1774 | 94.3961 | 2362.9879 | -0.012473
124 |  | 0.41548 | 18.4162 | 4187 | 0.010586 | 7.3584 | 7.3689 | -1.1774 | 94.46 | 2381.4041 | -0.012464
125 |  | 0.41548 | 18.4038 | 4187 | 0.010579 | 7.3689 | 7.3795 | -1.1774 | 94.524 | 2399.8079 | -0.012456
126 |  | 0.41548 | 18.3913 | 4187 | 0.010572 | 7.3795 | 7.3901 | -1.1774 | 94.588 | 2418.1992 | -0.012448
127 |  | 0.41548 | 18.3789 | 4187 | 0.010565 | 7.3901 | 7.4007 | -1.1774 | 94.652 | 2436.578 | -0.012439
128 |  | 0.41548 | 18.3664 | 4187 | 0.010558 | 7.4007 | 7.4112 | -1.1774 | 94.7161 | 2454.9444 | -0.012431
129 |  | 0.41548 | 18.354 | 4187 | 0.010551 | 7.4112 | 7.4218 | -1.1774 | 94.7803 | 2473.2984 | -0.012422
130 |  | 0.41548 | 18.3416 | 4187 | 0.010544 | 7.4218 | 7.4323 | -1.1774 | 94.8445 | 2491.64 | -0.012414
131 |  | 0.41548 | 18.3292 | 4187 | 0.010536 | 7.4323 | 7.4428 | -1.1774 | 94.9087 | 2509.9692 | -0.012405
132 |  | 0.41548 | 18.3167 | 4187 | 0.010529 | 7.4428 | 7.4534 | -1.1774 | 94.973 | 2528.2859 | -0.012397
133 |  | 0.41548 | 18.3044 | 4187 | 0.010522 | 7.4534 | 7.4639 | -1.1774 | 95.0373 | 2546.5903 | -0.012389
134 |  | 0.41548 | 18.292 | 4187 | 0.010515 | 7.4639 | 7.4744 | -1.1774 | 95.1017 | 2564.8822 | -0.01238
135 |  | 0.41548 | 18.2796 | 4187 | 0.010508 | 7.4744 | 7.4849 | -1.1774 | 95.1661 | 2583.1618 | -0.012372
136 |  | 0.41548 | 18.2672 | 4187 | 0.010501 | 7.4849 | 7.4954 | -1.1774 | 95.2306 | 2601.429 | -0.012364
137 |  | 0.41548 | 18.2548 | 4187 | 0.010494 | 7.4954 | 7.5059 | -1.1774 | 95.295 | 2619.6839 | -0.012355
138 |  | 0.41548 | 18.2425 | 4187 | 0.010487 | 7.5059 | 7.5164 | -1.1774 | 95.3596 | 2637.9263 | -0.012347
139 |  | 0.41548 | 18.2301 | 4187 | 0.01048 | 7.5164 | 7.5269 | -1.1774 | 95.4242 | 2656.1565 | -0.012338
140 |  | 0.41548 | 18.2178 | 4187 | 0.010472 | 7.5269 | 7.5374 | -1.1774 | 95.4888 | 2674.3743 | -0.01233
141 |  | 0.41548 | 18.2055 | 4187 | 0.010465 | 7.5374 | 7.5478 | -1.1774 | 95.5535 | 2692.5798 | -0.012322
142 |  | 0.41548 | 18.1932 | 4187 | 0.010458 | 7.5478 | 7.5583 | -1.1774 | 95.6182 | 2710.7729 | -0.012313
143 |  | 0.41548 | 18.1808 | 4187 | 0.010451 | 7.5583 | 7.5687 | -1.1774 | 95.6829 | 2728.9538 | -0.012305
144 |  | 0.41548 | 18.1685 | 4187 | 0.010444 | 7.5687 | 7.5792 | -1.1774 | 95.7478 | 2747.1223 | -0.012297
145 |  | 0.41548 | 18.1562 | 4187 | 0.010437 | 7.5792 | 7.5896 | -1.1774 | 95.8126 | 2765.2785 | -0.012288
146 |  | 0.41548 | 18.144 | 4187 | 0.01043 | 7.5896 | 7.6 | -1.1774 | 95.8775 | 2783.4225 | -0.01228
147 |  | 0.41548 | 18.1317 | 4187 | 0.010423 | 7.6 | 7.6105 | -1.1774 | 95.9424 | 2801.5542 | -0.012272
148 |  | 0.41548 | 18.1194 | 4187 | 0.010416 | 7.6105 | 7.6209 | -1.1774 | 96.0074 | 2819.6736 | -0.012263
149 |  | 0.41548 | 18.1071 | 4187 | 0.010409 | 7.6209 | 7.6313 | -1.1774 | 96.0724 | 2837.7807 | -0.012255
150 |  | 0.41548 | 18.0949 | 4187 | 0.010402 | 7.6313 | 7.6417 | -1.1774 | 96.1375 | 2855.8756 | -0.012247
151 |  | 0.41548 | 18.0826 | 4187 | 0.010395 | 7.6417 | 7.6521 | -1.1774 | 96.2026 | 2873.9582 | -0.012239
152 |  | 0.41548 | 18.0704 | 4187 | 0.010388 | 7.6521 | 7.6625 | -1.1774 | 96.2678 | 2892.0286 | -0.01223
153 |  | 0.41548 | 18.0582 | 4187 | 0.010381 | 7.6625 | 7.6729 | -1.1774 | 96.333 | 2910.0868 | -0.012222
154 |  | 0.41548 | 18.0459 | 4187 | 0.010374 | 7.6729 | 7.6832 | -1.1774 | 96.3982 | 2928.1327 | -0.012214
155 |  | 0.41548 | 18.0337 | 4187 | 0.010367 | 7.6832 | 7.6936 | -1.1774 | 96.4635 | 2946.1664 | -0.012205
156 |  | 0.41548 | 18.0215 | 4187 | 0.01036 | 7.6936 | 7.704 | -1.1774 | 96.5288 | 2964.188 | -0.012197
157 |  | 0.41548 | 18.0093 | 4187 | 0.010353 | 7.704 | 7.7143 | -1.1774 | 96.5942 | 2982.1973 | -0.012189
158 |  | 0.41548 | 17.9971 | 4187 | 0.010346 | 7.7143 | 7.7246 | -1.1774 | 96.6596 | 3000.1944 | -0.012181
159 |  | 0.41548 | 17.985 | 4187 | 0.010339 | 7.7246 | 7.735 | -1.1774 | 96.7251 | 3018.1794 | -0.012172
160 |  | 0.41548 | 17.9728 | 4187 | 0.010332 | 7.735 | 7.7453 | -1.1774 | 96.7906 | 3036.1522 | -0.012164
161 |  | 0.41548 | 17.9606 | 4187 | 0.010325 | 7.7453 | 7.7556 | -1.1774 | 96.8562 | 3054.1128 | -0.012156
162 |  | 0.41548 | 17.9485 | 4187 | 0.010318 | 7.7556 | 7.766 | -1.1774 | 96.9217 | 3072.0612 | -0.012148
163 |  | 0.41548 | 17.9363 | 4187 | 0.010311 | 7.766 | 7.7763 | -1.1774 | 96.9874 | 3089.9976 | -0.01214
164 |  | 0.41548 | 17.9242 | 4187 | 0.010304 | 7.7763 | 7.7866 | -1.1774 | 97.0531 | 3107.9217 | -0.012131
165 |  | 0.41548 | 17.912 | 4187 | 0.010297 | 7.7866 | 7.7969 | -1.1774 | 97.1188 | 3125.8338 | -0.012123
166 |  | 0.41548 | 17.8999 | 4187 | 0.01029 | 7.7969 | 7.8072 | -1.1774 | 97.1846 | 3143.7337 | -0.012115
167 |  | 0.41548 | 17.8878 | 4187 | 0.010283 | 7.8072 | 7.8174 | -1.1774 | 97.2504 | 3161.6215 | -0.012107
168 |  | 0.41548 | 17.8757 | 4187 | 0.010276 | 7.8174 | 7.8277 | -1.1774 | 97.3163 | 3179.4972 | -0.012099
169 |  | 0.41548 | 17.8636 | 4187 | 0.010269 | 7.8277 | 7.838 | -1.1774 | 97.3822 | 3197.3608 | -0.01209
170 |  | 0.41548 | 17.8515 | 4187 | 0.010262 | 7.838 | 7.8483 | -1.1774 | 97.4481 | 3215.2123 | -0.012082
171 |  | 0.41548 | 17.8394 | 4187 | 0.010255 | 7.8483 | 7.8585 | -1.1774 | 97.5141 | 3233.0517 | -0.012074
172 |  | 0.41548 | 17.8274 | 4187 | 0.010248 | 7.8585 | 7.8688 | -1.1774 | 97.5802 | 3250.8791 | -0.012066
173 |  | 0.41548 | 17.8153 | 4187 | 0.010241 | 7.8688 | 7.879 | -1.1774 | 97.6463 | 3268.6944 | -0.012058
174 |  | 0.41548 | 17.8032 | 4187 | 0.010234 | 7.879 | 7.8892 | -1.1774 | 97.7124 | 3286.4976 | -0.012049
175 |  | 0.41548 | 17.7912 | 4187 | 0.010227 | 7.8892 | 7.8995 | -1.1774 | 97.7786 | 3304.2888 | -0.012041
176 |  | 0.41548 | 17.7791 | 4187 | 0.01022 | 7.8995 | 7.9097 | -1.1774 | 97.8448 | 3322.0679 | -0.012033
177 |  | 0.41548 | 17.7671 | 4187 | 0.010213 | 7.9097 | 7.9199 | -1.1774 | 97.9111 | 3339.8351 | -0.012025
178 |  | 0.41548 | 17.7551 | 4187 | 0.010206 | 7.9199 | 7.9301 | -1.1774 | 97.9774 | 3357.5901 | -0.012017
179 |  | 0.41548 | 17.7431 | 4187 | 0.0102 | 7.9301 | 7.9403 | -1.1774 | 98.0437 | 3375.3332 | -0.012009
180 |  | 0.41548 | 17.7311 | 4187 | 0.010193 | 7.9403 | 7.9505 | -1.1774 | 98.1101 | 3393.0643 | -0.012001
181 |  | 0.41548 | 17.7191 | 4187 | 0.010186 | 7.9505 | 7.9607 | -1.1774 | 98.1766 | 3410.7833 | -0.011993
182 |  | 0.41548 | 17.7071 | 4187 | 0.010179 | 7.9607 | 7.9709 | -1.1774 | 98.2431 | 3428.4904 | -0.011984
183 |  | 0.41548 | 17.6951 | 4187 | 0.010172 | 7.9709 | 7.981 | -1.1774 | 98.3096 | 3446.1855 | -0.011976
184 |  | 0.41548 | 17.6831 | 4187 | 0.010165 | 7.981 | 7.9912 | -1.1774 | 98.3762 | 3463.8686 | -0.011968
185 |  | 0.41548 | 17.6711 | 4187 | 0.010158 | 7.9912 | 8.0013 | -1.1774 | 98.4428 | 3481.5397 | -0.01196
186 |  | 0.41548 | 17.6592 | 4187 | 0.010151 | 8.0013 | 8.0115 | -1.1774 | 98.5095 | 3499.1989 | -0.011952
187 |  | 0.41548 | 17.6472 | 4187 | 0.010144 | 8.0115 | 8.0216 | -1.1774 | 98.5762 | 3516.8461 | -0.011944
188 |  | 0.41548 | 17.6353 | 4187 | 0.010138 | 8.0216 | 8.0318 | -1.1774 | 98.643 | 3534.4814 | -0.011936
189 |  | 0.41548 | 17.6233 | 4187 | 0.010131 | 8.0318 | 8.0419 | -1.1774 | 98.7098 | 3552.1047 | -0.011928
190 |  | 0.41548 | 17.6114 | 4187 | 0.010124 | 8.0419 | 8.052 | -1.1774 | 98.7766 | 3569.7161 | -0.01192
191 |  | 0.41548 | 17.5995 | 4187 | 0.010117 | 8.052 | 8.0622 | -1.1774 | 98.8435 | 3587.3156 | -0.011912
192 |  | 0.41548 | 17.5876 | 4187 | 0.01011 | 8.0622 | 8.0723 | -1.1774 | 98.9105 | 3604.9032 | -0.011904
193 |  | 0.41548 | 17.5757 | 4187 | 0.010103 | 8.0723 | 8.0824 | -1.1774 | 98.9775 | 3622.4789 | -0.011895
194 |  | 0.41548 | 17.5638 | 4187 | 0.010096 | 8.0824 | 8.0925 | -1.1774 | 99.0445 | 3640.0427 | -0.011887
195 |  | 0.41548 | 17.5519 | 4187 | 0.01009 | 8.0925 | 8.1026 | -1.1774 | 99.1116 | 3657.5946 | -0.011879
196 |  | 0.41548 | 17.54 | 4187 | 0.010083 | 8.1026 | 8.1126 | -1.1774 | 99.1787 | 3675.1346 | -0.011871
197 |  | 0.41548 | 17.5281 | 4187 | 0.010076 | 8.1126 | 8.1227 | -1.1774 | 99.2459 | 3692.6627 | -0.011863
198 |  | 0.41548 | 17.5163 | 4187 | 0.010069 | 8.1227 | 8.1328 | -1.1774 | 99.3131 | 3710.179 | -0.011855
199 |  | 0.41548 | 17.5044 | 4187 | 0.010062 | 8.1328 | 8.1428 | -1.1774 | 99.3804 | 3727.6834 | -0.011847
200 |  | 0.41548 | 17.4926 | 4187 | 0.010056 | 8.1428 | 8.1529 | -1.1774 | 99.4477 | 3745.176 | -0.011839
201 |  | 0.41548 | 17.4807 | 4187 | 0.010049 | 8.1529 | 8.1629 | -1.1774 | 99.515 | 3762.6568 | -0.011831
202 |  | 0.41548 | 17.4689 | 4187 | 0.010042 | 8.1629 | 8.173 | -1.1774 | 99.5824 | 3780.1257 | -0.011823
203 |  | 0.41548 | 17.4571 | 4187 | 0.010035 | 8.173 | 8.183 | -1.1774 | 99.6499 | 3797.5828 | -0.011815
204 |  | 0.41548 | 17.4453 | 4187 | 0.010028 | 8.183 | 8.1931 | -1.1774 | 99.7174 | 3815.028 | -0.011807
205 |  | 0.41548 | 17.4335 | 4187 | 0.010022 | 8.1931 | 8.2031 | -1.1774 | 99.7849 | 3832.4615 | -0.011799
206 |  | 0.41548 | 17.4217 | 4187 | 0.010015 | 8.2031 | 8.2131 | -1.1774 | 99.8525 | 3849.8832 | -0.011791
207 |  | 0.41548 | 17.4099 | 4187 | 0.010008 | 8.2131 | 8.2231 | -1.1774 | 99.9201 | 3867.293 | -0.011783
208 |  | 0.41548 | 17.3981 | 4187 | 0.010001 | 8.2231 | 8.2331 | -1.1774 | 99.9878 | 3884.6911 | -0.011775
209 |  | 0.41548 | 17.3863 | 4187 | 0.0099945 | 8.2331 | 8.2431 | -1.1774 | 100.0555 | 3902.0774 | -0.011767
210 |  | 0.41548 | 17.3745 | 4187 | 0.0099877 | 8.2431 | 8.2531 | -1.1774 | 100.1233 | 3919.452 | -0.011759
211 |  | 0.41548 | 17.3628 | 4187 | 0.0099809 | 8.2531 | 8.2631 | -1.1774 | 100.1911 | 3936.8148 | -0.011751
212 |  | 0.41548 | 17.351 | 4187 | 0.0099742 | 8.2631 | 8.273 | -1.1774 | 100.2589 | 3954.1658 | -0.011743
213 |  | 0.41548 | 17.3393 | 4187 | 0.0099674 | 8.273 | 8.283 | -1.1774 | 100.3268 | 3971.5051 | -0.011735
214 |  | 0.41548 | 17.3276 | 4187 | 0.0099607 | 8.283 | 8.293 | -1.1774 | 100.3948 | 3988.8327 | -0.011728
215 |  | 0.41548 | 17.3158 | 4187 | 0.0099539 | 8.293 | 8.3029 | -1.1774 | 100.4628 | 4006.1485 | -0.01172
216 |  | 0.41548 | 17.3041 | 4187 | 0.0099472 | 8.3029 | 8.3129 | -1.1774 | 100.5308 | 4023.4526 | -0.011712
217 |  | 0.41548 | 17.2924 | 4187 | 0.0099405 | 8.3129 | 8.3228 | -1.1774 | 100.5989 | 4040.745 | -0.011704
218 |  | 0.41548 | 17.2807 | 4187 | 0.0099337 | 8.3228 | 8.3327 | -1.1774 | 100.667 | 4058.0257 | -0.011696
219 |  | 0.41548 | 17.269 | 4187 | 0.009927 | 8.3327 | 8.3427 | -1.1774 | 100.7352 | 4075.2947 | -0.011688
220 |  | 0.41548 | 17.2573 | 4187 | 0.0099203 | 8.3427 | 8.3526 | -1.1774 | 100.8034 | 4092.552 | -0.01168
221 |  | 0.41548 | 17.2456 | 4187 | 0.0099136 | 8.3526 | 8.3625 | -1.1774 | 100.8717 | 4109.7977 | -0.011672
222 |  | 0.41548 | 17.234 | 4187 | 0.0099069 | 8.3625 | 8.3724 | -1.1774 | 100.94 | 4127.0316 | -0.011664
223 |  | 0.41548 | 17.2223 | 4187 | 0.0099002 | 8.3724 | 8.3823 | -1.1774 | 101.0084 | 4144.2539 | -0.011656
224 |  | 0.41548 | 17.2106 | 4187 | 0.0098935 | 8.3823 | 8.3922 | -1.1774 | 101.0768 | 4161.4646 | -0.011648
225 |  | 0.41548 | 17.199 | 4187 | 0.0098868 | 8.3922 | 8.4021 | -1.1774 | 101.1453 | 4178.6636 | -0.011641
226 |  | 0.41548 | 17.1874 | 4187 | 0.0098801 | 8.4021 | 8.412 | -1.1774 | 101.2138 | 4195.8509 | -0.011633
227 |  | 0.41548 | 17.1757 | 4187 | 0.0098734 | 8.412 | 8.4218 | -1.1774 | 101.2823 | 4213.0266 | -0.011625
228 |  | 0.41548 | 17.1641 | 4187 | 0.0098667 | 8.4218 | 8.4317 | -1.1774 | 101.3509 | 4230.1907 | -0.011617
229 |  | 0.41548 | 17.1525 | 4187 | 0.00986 | 8.4317 | 8.4416 | -1.1774 | 101.4195 | 4247.3432 | -0.011609
230 |  | 0.41548 | 17.1409 | 4187 | 0.0098534 | 8.4416 | 8.4514 | -1.1774 | 101.4882 | 4264.4841 | -0.011601
231 |  | 0.41548 | 17.1293 | 4187 | 0.0098467 | 8.4514 | 8.4613 | -1.1774 | 101.557 | 4281.6133 | -0.011593
232 |  | 0.41548 | 17.1177 | 4187 | 0.00984 | 8.4613 | 8.4711 | -1.1774 | 101.6258 | 4298.731 | -0.011585
233 |  | 0.41548 | 17.1061 | 4187 | 0.0098334 | 8.4711 | 8.4809 | -1.1774 | 101.6946 | 4315.8371 | -0.011578
234 |  | 0.41548 | 17.0945 | 4187 | 0.0098267 | 8.4809 | 8.4908 | -1.1774 | 101.7635 | 4332.9316 | -0.01157
235 |  | 0.41548 | 17.0829 | 4187 | 0.0098201 | 8.4908 | 8.5006 | -1.1774 | 101.8324 | 4350.0145 | -0.011562
236 |  | 0.41548 | 17.0714 | 4187 | 0.0098134 | 8.5006 | 8.5104 | -1.1774 | 101.9013 | 4367.0859 | -0.011554

## Cu31
|  |  | buis | verlies W/M | L /°C/sec
diam | wandikte |  | inhoud l/m |  | W/M
31.8 | 1.2 | 3.1416 | 0.67887 | 25.0672 | 4187
[8 empty] | J/sec/mtr | aantal mtr. | verlies
|  | buis | verlies W/M | L /°C/sec | verlies temp | begintemp | eindtemp | verlies | bij 1°C | totaal J/sec
|  | inhoud L |  | W/M | °C per M | °C | °C | per m°C | daling | aantal mtr
1 | 31.8 | 0.67887 | 25.0672 | 4187 | 0.008819 | 6 | 6.0088 | -1.4745 | 113.3917 | 25.0672 | -0.013004
2 |  | 0.67887 | 25.0542 | 4187 | 0.0088144 | 6.0088 | 6.0176 | -1.4745 | 113.4505 | 50.1215 | -0.012997
3 |  | 0.67887 | 25.0412 | 4187 | 0.0088098 | 6.0176 | 6.0264 | -1.4745 | 113.5094 | 75.1627 | -0.01299
4 |  | 0.67887 | 25.0282 | 4187 | 0.0088053 | 6.0264 | 6.0352 | -1.4745 | 113.5683 | 100.1909 | -0.012984
5 |  | 0.67887 | 25.0153 | 4187 | 0.0088007 | 6.0352 | 6.044 | -1.4745 | 113.6273 | 125.2062 | -0.012977
6 |  | 0.67887 | 25.0023 | 4187 | 0.0087961 | 6.044 | 6.0528 | -1.4745 | 113.6863 | 150.2084 | -0.01297
7 |  | 0.67887 | 24.9893 | 4187 | 0.0087916 | 6.0528 | 6.0616 | -1.4745 | 113.7453 | 175.1978 | -0.012964
8 |  | 0.67887 | 24.9763 | 4187 | 0.008787 | 6.0616 | 6.0704 | -1.4745 | 113.8043 | 200.1741 | -0.012957
9 |  | 0.67887 | 24.9634 | 4187 | 0.0087825 | 6.0704 | 6.0792 | -1.4745 | 113.8634 | 225.1375 | -0.01295
10 |  | 0.67887 | 24.9504 | 4187 | 0.0087779 | 6.0792 | 6.088 | -1.4745 | 113.9225 | 250.0879 | -0.012943
11 |  | 0.67887 | 24.9375 | 4187 | 0.0087733 | 6.088 | 6.0968 | -1.4745 | 113.9816 | 275.0254 | -0.012937
12 |  | 0.67887 | 24.9246 | 4187 | 0.0087688 | 6.0968 | 6.1055 | -1.4745 | 114.0408 | 299.95 | -0.01293
13 |  | 0.67887 | 24.9116 | 4187 | 0.0087642 | 6.1055 | 6.1143 | -1.4745 | 114.0999 | 324.8616 | -0.012923
14 |  | 0.67887 | 24.8987 | 4187 | 0.0087597 | 6.1143 | 6.1231 | -1.4745 | 114.1592 | 349.7603 | -0.012917
15 |  | 0.67887 | 24.8858 | 4187 | 0.0087552 | 6.1231 | 6.1318 | -1.4745 | 114.2184 | 374.6461 | -0.01291
16 |  | 0.67887 | 24.8729 | 4187 | 0.0087506 | 6.1318 | 6.1406 | -1.4745 | 114.2777 | 399.519 | -0.012903
17 |  | 0.67887 | 24.86 | 4187 | 0.0087461 | 6.1406 | 6.1493 | -1.4745 | 114.337 | 424.3789 | -0.012896
18 |  | 0.67887 | 24.8471 | 4187 | 0.0087415 | 6.1493 | 6.158 | -1.4745 | 114.3964 | 449.226 | -0.01289
19 |  | 0.67887 | 24.8342 | 4187 | 0.008737 | 6.158 | 6.1668 | -1.4745 | 114.4557 | 474.0602 | -0.012883
20 |  | 0.67887 | 24.8213 | 4187 | 0.0087325 | 6.1668 | 6.1755 | -1.4745 | 114.5151 | 498.8815 | -0.012876
21 |  | 0.67887 | 24.8084 | 4187 | 0.0087279 | 6.1755 | 6.1842 | -1.4745 | 114.5746 | 523.6899 | -0.01287
22 |  | 0.67887 | 24.7956 | 4187 | 0.0087234 | 6.1842 | 6.193 | -1.4745 | 114.634 | 548.4855 | -0.012863
23 |  | 0.67887 | 24.7827 | 4187 | 0.0087189 | 6.193 | 6.2017 | -1.4745 | 114.6935 | 573.2682 | -0.012856
24 |  | 0.67887 | 24.7698 | 4187 | 0.0087144 | 6.2017 | 6.2104 | -1.4745 | 114.7531 | 598.038 | -0.01285
25 |  | 0.67887 | 24.757 | 4187 | 0.0087098 | 6.2104 | 6.2191 | -1.4745 | 114.8126 | 622.795 | -0.012843
26 |  | 0.67887 | 24.7441 | 4187 | 0.0087053 | 6.2191 | 6.2278 | -1.4745 | 114.8722 | 647.5391 | -0.012836
27 |  | 0.67887 | 24.7313 | 4187 | 0.0087008 | 6.2278 | 6.2365 | -1.4745 | 114.9319 | 672.2704 | -0.01283
28 |  | 0.67887 | 24.7185 | 4187 | 0.0086963 | 6.2365 | 6.2452 | -1.4745 | 114.9915 | 696.9889 | -0.012823
29 |  | 0.67887 | 24.7057 | 4187 | 0.0086918 | 6.2452 | 6.2539 | -1.4745 | 115.0512 | 721.6946 | -0.012816
30 |  | 0.67887 | 24.6928 | 4187 | 0.0086873 | 6.2539 | 6.2626 | -1.4745 | 115.1109 | 746.3874 | -0.01281
31 |  | 0.67887 | 24.68 | 4187 | 0.0086828 | 6.2626 | 6.2713 | -1.4745 | 115.1707 | 771.0674 | -0.012803
32 |  | 0.67887 | 24.6672 | 4187 | 0.0086783 | 6.2713 | 6.28 | -1.4745 | 115.2304 | 795.7347 | -0.012796
33 |  | 0.67887 | 24.6544 | 4187 | 0.0086738 | 6.28 | 6.2886 | -1.4745 | 115.2902 | 820.3891 | -0.01279
34 |  | 0.67887 | 24.6416 | 4187 | 0.0086693 | 6.2886 | 6.2973 | -1.4745 | 115.3501 | 845.0307 | -0.012783
35 |  | 0.67887 | 24.6289 | 4187 | 0.0086648 | 6.2973 | 6.306 | -1.4745 | 115.4099 | 869.6596 | -0.012777
36 |  | 0.67887 | 24.6161 | 4187 | 0.0086603 | 6.306 | 6.3146 | -1.4745 | 115.4698 | 894.2757 | -0.01277
37 |  | 0.67887 | 24.6033 | 4187 | 0.0086558 | 6.3146 | 6.3233 | -1.4745 | 115.5298 | 918.879 | -0.012763
38 |  | 0.67887 | 24.5905 | 4187 | 0.0086513 | 6.3233 | 6.3319 | -1.4745 | 115.5897 | 943.4695 | -0.012757
39 |  | 0.67887 | 24.5778 | 4187 | 0.0086468 | 6.3319 | 6.3406 | -1.4745 | 115.6497 | 968.0473 | -0.01275
40 |  | 0.67887 | 24.565 | 4187 | 0.0086423 | 6.3406 | 6.3492 | -1.4745 | 115.7098 | 992.6124 | -0.012743
41 |  | 0.67887 | 24.5523 | 4187 | 0.0086378 | 6.3492 | 6.3579 | -1.4745 | 115.7698 | 1017.1647 | -0.012737
42 |  | 0.67887 | 24.5396 | 4187 | 0.0086333 | 6.3579 | 6.3665 | -1.4745 | 115.8299 | 1041.7042 | -0.01273
43 |  | 0.67887 | 24.5268 | 4187 | 0.0086289 | 6.3665 | 6.3751 | -1.4745 | 115.89 | 1066.2311 | -0.012724
44 |  | 0.67887 | 24.5141 | 4187 | 0.0086244 | 6.3751 | 6.3837 | -1.4745 | 115.9502 | 1090.7452 | -0.012717
45 |  | 0.67887 | 24.5014 | 4187 | 0.0086199 | 6.3837 | 6.3924 | -1.4745 | 116.0104 | 1115.2466 | -0.01271
46 |  | 0.67887 | 24.4887 | 4187 | 0.0086154 | 6.3924 | 6.401 | -1.4745 | 116.0706 | 1139.7352 | -0.012704
47 |  | 0.67887 | 24.476 | 4187 | 0.008611 | 6.401 | 6.4096 | -1.4745 | 116.1308 | 1164.2112 | -0.012697
48 |  | 0.67887 | 24.4633 | 4187 | 0.0086065 | 6.4096 | 6.4182 | -1.4745 | 116.1911 | 1188.6745 | -0.012691
49 |  | 0.67887 | 24.4506 | 4187 | 0.008602 | 6.4182 | 6.4268 | -1.4745 | 116.2514 | 1213.1251 | -0.012684
50 |  | 0.67887 | 24.4379 | 4187 | 0.0085976 | 6.4268 | 6.4354 | -1.4745 | 116.3117 | 1237.563 | -0.012678
51 |  | 0.67887 | 24.4252 | 4187 | 0.0085931 | 6.4354 | 6.444 | -1.4745 | 116.3721 | 1261.9882 | -0.012671
52 |  | 0.67887 | 24.4126 | 4187 | 0.0085887 | 6.444 | 6.4526 | -1.4745 | 116.4325 | 1286.4008 | -0.012664
53 |  | 0.67887 | 24.3999 | 4187 | 0.0085842 | 6.4526 | 6.4612 | -1.4745 | 116.4929 | 1310.8006 | -0.012658
54 |  | 0.67887 | 24.3872 | 4187 | 0.0085798 | 6.4612 | 6.4697 | -1.4745 | 116.5534 | 1335.1879 | -0.012651
55 |  | 0.67887 | 24.3746 | 4187 | 0.0085753 | 6.4697 | 6.4783 | -1.4745 | 116.6139 | 1359.5625 | -0.012645
56 |  | 0.67887 | 24.3619 | 4187 | 0.0085709 | 6.4783 | 6.4869 | -1.4745 | 116.6744 | 1383.9244 | -0.012638
57 |  | 0.67887 | 24.3493 | 4187 | 0.0085664 | 6.4869 | 6.4954 | -1.4745 | 116.735 | 1408.2737 | -0.012632
58 |  | 0.67887 | 24.3367 | 4187 | 0.008562 | 6.4954 | 6.504 | -1.4745 | 116.7956 | 1432.6104 | -0.012625
59 |  | 0.67887 | 24.324 | 4187 | 0.0085575 | 6.504 | 6.5126 | -1.4745 | 116.8562 | 1456.9344 | -0.012618
60 |  | 0.67887 | 24.3114 | 4187 | 0.0085531 | 6.5126 | 6.5211 | -1.4745 | 116.9169 | 1481.2458 | -0.012612
61 |  | 0.67887 | 24.2988 | 4187 | 0.0085486 | 6.5211 | 6.5297 | -1.4745 | 116.9775 | 1505.5446 | -0.012605
62 |  | 0.67887 | 24.2862 | 4187 | 0.0085442 | 6.5297 | 6.5382 | -1.4745 | 117.0383 | 1529.8308 | -0.012599
63 |  | 0.67887 | 24.2736 | 4187 | 0.0085398 | 6.5382 | 6.5468 | -1.4745 | 117.099 | 1554.1045 | -0.012592
64 |  | 0.67887 | 24.261 | 4187 | 0.0085354 | 6.5468 | 6.5553 | -1.4745 | 117.1598 | 1578.3655 | -0.012586
65 |  | 0.67887 | 24.2484 | 4187 | 0.0085309 | 6.5553 | 6.5638 | -1.4745 | 117.2206 | 1602.6139 | -0.012579
66 |  | 0.67887 | 24.2359 | 4187 | 0.0085265 | 6.5638 | 6.5723 | -1.4745 | 117.2814 | 1626.8497 | -0.012573
67 |  | 0.67887 | 24.2233 | 4187 | 0.0085221 | 6.5723 | 6.5809 | -1.4745 | 117.3423 | 1651.073 | -0.012566
68 |  | 0.67887 | 24.2107 | 4187 | 0.0085177 | 6.5809 | 6.5894 | -1.4745 | 117.4032 | 1675.2837 | -0.01256
69 |  | 0.67887 | 24.1982 | 4187 | 0.0085132 | 6.5894 | 6.5979 | -1.4745 | 117.4641 | 1699.4819 | -0.012553
70 |  | 0.67887 | 24.1856 | 4187 | 0.0085088 | 6.5979 | 6.6064 | -1.4745 | 117.5251 | 1723.6675 | -0.012547
71 |  | 0.67887 | 24.1731 | 4187 | 0.0085044 | 6.6064 | 6.6149 | -1.4745 | 117.5861 | 1747.8405 | -0.01254
72 |  | 0.67887 | 24.1605 | 4187 | 0.0085 | 6.6149 | 6.6234 | -1.4745 | 117.6471 | 1772.001 | -0.012534
73 |  | 0.67887 | 24.148 | 4187 | 0.0084956 | 6.6234 | 6.6319 | -1.4745 | 117.7082 | 1796.149 | -0.012527
74 |  | 0.67887 | 24.1355 | 4187 | 0.0084912 | 6.6319 | 6.6404 | -1.4745 | 117.7693 | 1820.2845 | -0.012521
75 |  | 0.67887 | 24.1229 | 4187 | 0.0084868 | 6.6404 | 6.6489 | -1.4745 | 117.8304 | 1844.4074 | -0.012514
76 |  | 0.67887 | 24.1104 | 4187 | 0.0084824 | 6.6489 | 6.6574 | -1.4745 | 117.8916 | 1868.5178 | -0.012508
77 |  | 0.67887 | 24.0979 | 4187 | 0.008478 | 6.6574 | 6.6658 | -1.4745 | 117.9528 | 1892.6157 | -0.012501
78 |  | 0.67887 | 24.0854 | 4187 | 0.0084736 | 6.6658 | 6.6743 | -1.4745 | 118.014 | 1916.7011 | -0.012495
79 |  | 0.67887 | 24.0729 | 4187 | 0.0084692 | 6.6743 | 6.6828 | -1.4745 | 118.0752 | 1940.7741 | -0.012488
80 |  | 0.67887 | 24.0604 | 4187 | 0.0084648 | 6.6828 | 6.6913 | -1.4745 | 118.1365 | 1964.8345 | -0.012482
81 |  | 0.67887 | 24.0479 | 4187 | 0.0084604 | 6.6913 | 6.6997 | -1.4745 | 118.1978 | 1988.8824 | -0.012475
82 |  | 0.67887 | 24.0355 | 4187 | 0.008456 | 6.6997 | 6.7082 | -1.4745 | 118.2592 | 2012.9179 | -0.012469
83 |  | 0.67887 | 24.023 | 4187 | 0.0084516 | 6.7082 | 6.7166 | -1.4745 | 118.3206 | 2036.9409 | -0.012462
84 |  | 0.67887 | 24.0105 | 4187 | 0.0084472 | 6.7166 | 6.7251 | -1.4745 | 118.382 | 2060.9514 | -0.012456
85 |  | 0.67887 | 23.9981 | 4187 | 0.0084428 | 6.7251 | 6.7335 | -1.4745 | 118.4434 | 2084.9495 | -0.012449
86 |  | 0.67887 | 23.9856 | 4187 | 0.0084385 | 6.7335 | 6.742 | -1.4745 | 118.5049 | 2108.9351 | -0.012443
87 |  | 0.67887 | 23.9732 | 4187 | 0.0084341 | 6.742 | 6.7504 | -1.4745 | 118.5664 | 2132.9083 | -0.012436
88 |  | 0.67887 | 23.9608 | 4187 | 0.0084297 | 6.7504 | 6.7588 | -1.4745 | 118.628 | 2156.8691 | -0.01243
89 |  | 0.67887 | 23.9483 | 4187 | 0.0084253 | 6.7588 | 6.7672 | -1.4745 | 118.6895 | 2180.8174 | -0.012424
90 |  | 0.67887 | 23.9359 | 4187 | 0.008421 | 6.7672 | 6.7757 | -1.4745 | 118.7511 | 2204.7533 | -0.012417
91 |  | 0.67887 | 23.9235 | 4187 | 0.0084166 | 6.7757 | 6.7841 | -1.4745 | 118.8128 | 2228.6768 | -0.012411
92 |  | 0.67887 | 23.9111 | 4187 | 0.0084122 | 6.7841 | 6.7925 | -1.4745 | 118.8744 | 2252.5879 | -0.012404
93 |  | 0.67887 | 23.8987 | 4187 | 0.0084079 | 6.7925 | 6.8009 | -1.4745 | 118.9361 | 2276.4865 | -0.012398
94 |  | 0.67887 | 23.8863 | 4187 | 0.0084035 | 6.8009 | 6.8093 | -1.4745 | 118.9979 | 2300.3728 | -0.012391
95 |  | 0.67887 | 23.8739 | 4187 | 0.0083992 | 6.8093 | 6.8177 | -1.4745 | 119.0596 | 2324.2467 | -0.012385
96 |  | 0.67887 | 23.8615 | 4187 | 0.0083948 | 6.8177 | 6.8261 | -1.4745 | 119.1214 | 2348.1082 | -0.012378
97 |  | 0.67887 | 23.8491 | 4187 | 0.0083904 | 6.8261 | 6.8345 | -1.4745 | 119.1833 | 2371.9573 | -0.012372
98 |  | 0.67887 | 23.8367 | 4187 | 0.0083861 | 6.8345 | 6.8429 | -1.4745 | 119.2451 | 2395.794 | -0.012366
99 |  | 0.67887 | 23.8244 | 4187 | 0.0083817 | 6.8429 | 6.8513 | -1.4745 | 119.307 | 2419.6184 | -0.012359
100 |  | 0.67887 | 23.812 | 4187 | 0.0083774 | 6.8513 | 6.8596 | -1.4745 | 119.3689 | 2443.4304 | -0.012353
101 |  | 0.67887 | 23.7997 | 4187 | 0.008373 | 6.8596 | 6.868 | -1.4745 | 119.4309 | 2467.2301 | -0.012346
102 |  | 0.67887 | 23.7873 | 4187 | 0.0083687 | 6.868 | 6.8764 | -1.4745 | 119.4929 | 2491.0174 | -0.01234
103 |  | 0.67887 | 23.775 | 4187 | 0.0083644 | 6.8764 | 6.8847 | -1.4745 | 119.5549 | 2514.7924 | -0.012334
104 |  | 0.67887 | 23.7626 | 4187 | 0.00836 | 6.8847 | 6.8931 | -1.4745 | 119.617 | 2538.555 | -0.012327
105 |  | 0.67887 | 23.7503 | 4187 | 0.0083557 | 6.8931 | 6.9015 | -1.4745 | 119.679 | 2562.3053 | -0.012321
106 |  | 0.67887 | 23.738 | 4187 | 0.0083513 | 6.9015 | 6.9098 | -1.4745 | 119.7412 | 2586.0433 | -0.012314
107 |  | 0.67887 | 23.7257 | 4187 | 0.008347 | 6.9098 | 6.9182 | -1.4745 | 119.8033 | 2609.769 | -0.012308
108 |  | 0.67887 | 23.7134 | 4187 | 0.0083427 | 6.9182 | 6.9265 | -1.4745 | 119.8655 | 2633.4824 | -0.012302
109 |  | 0.67887 | 23.7011 | 4187 | 0.0083384 | 6.9265 | 6.9348 | -1.4745 | 119.9277 | 2657.1835 | -0.012295
110 |  | 0.67887 | 23.6888 | 4187 | 0.008334 | 6.9348 | 6.9432 | -1.4745 | 119.9899 | 2680.8722 | -0.012289
111 |  | 0.67887 | 23.6765 | 4187 | 0.0083297 | 6.9432 | 6.9515 | -1.4745 | 120.0522 | 2704.5487 | -0.012283
112 |  | 0.67887 | 23.6642 | 4187 | 0.0083254 | 6.9515 | 6.9598 | -1.4745 | 120.1145 | 2728.2129 | -0.012276
113 |  | 0.67887 | 23.6519 | 4187 | 0.0083211 | 6.9598 | 6.9681 | -1.4745 | 120.1769 | 2751.8649 | -0.01227
114 |  | 0.67887 | 23.6397 | 4187 | 0.0083168 | 6.9681 | 6.9765 | -1.4745 | 120.2393 | 2775.5045 | -0.012263
115 |  | 0.67887 | 23.6274 | 4187 | 0.0083124 | 6.9765 | 6.9848 | -1.4745 | 120.3017 | 2799.1319 | -0.012257
116 |  | 0.67887 | 23.6151 | 4187 | 0.0083081 | 6.9848 | 6.9931 | -1.4745 | 120.3641 | 2822.7471 | -0.012251
117 |  | 0.67887 | 23.6029 | 4187 | 0.0083038 | 6.9931 | 7.0014 | -1.4745 | 120.4266 | 2846.3499 | -0.012244
118 |  | 0.67887 | 23.5906 | 4187 | 0.0082995 | 7.0014 | 7.0097 | -1.4745 | 120.4891 | 2869.9406 | -0.012238
119 |  | 0.67887 | 23.5784 | 4187 | 0.0082952 | 7.0097 | 7.018 | -1.4745 | 120.5516 | 2893.519 | -0.012232
120 |  | 0.67887 | 23.5662 | 4187 | 0.0082909 | 7.018 | 7.0263 | -1.4745 | 120.6142 | 2917.0852 | -0.012225
121 |  | 0.67887 | 23.5539 | 4187 | 0.0082866 | 7.0263 | 7.0346 | -1.4745 | 120.6768 | 2940.6391 | -0.012219
122 |  | 0.67887 | 23.5417 | 4187 | 0.0082823 | 7.0346 | 7.0428 | -1.4745 | 120.7394 | 2964.1808 | -0.012213
123 |  | 0.67887 | 23.5295 | 4187 | 0.008278 | 7.0428 | 7.0511 | -1.4745 | 120.8021 | 2987.7104 | -0.012206
124 |  | 0.67887 | 23.5173 | 4187 | 0.0082737 | 7.0511 | 7.0594 | -1.4745 | 120.8648 | 3011.2277 | -0.0122
125 |  | 0.67887 | 23.5051 | 4187 | 0.0082694 | 7.0594 | 7.0677 | -1.4745 | 120.9275 | 3034.7328 | -0.012194
126 |  | 0.67887 | 23.4929 | 4187 | 0.0082651 | 7.0677 | 7.0759 | -1.4745 | 120.9903 | 3058.2257 | -0.012187
127 |  | 0.67887 | 23.4807 | 4187 | 0.0082608 | 7.0759 | 7.0842 | -1.4745 | 121.0531 | 3081.7064 | -0.012181
128 |  | 0.67887 | 23.4685 | 4187 | 0.0082566 | 7.0842 | 7.0924 | -1.4745 | 121.1159 | 3105.175 | -0.012175
129 |  | 0.67887 | 23.4564 | 4187 | 0.0082523 | 7.0924 | 7.1007 | -1.4745 | 121.1788 | 3128.6314 | -0.012168
130 |  | 0.67887 | 23.4442 | 4187 | 0.008248 | 7.1007 | 7.1089 | -1.4745 | 121.2417 | 3152.0756 | -0.012162
131 |  | 0.67887 | 23.432 | 4187 | 0.0082437 | 7.1089 | 7.1172 | -1.4745 | 121.3046 | 3175.5076 | -0.012156
132 |  | 0.67887 | 23.4199 | 4187 | 0.0082394 | 7.1172 | 7.1254 | -1.4745 | 121.3676 | 3198.9275 | -0.012149
133 |  | 0.67887 | 23.4077 | 4187 | 0.0082352 | 7.1254 | 7.1337 | -1.4745 | 121.4306 | 3222.3352 | -0.012143
134 |  | 0.67887 | 23.3956 | 4187 | 0.0082309 | 7.1337 | 7.1419 | -1.4745 | 121.4936 | 3245.7308 | -0.012137
135 |  | 0.67887 | 23.3835 | 4187 | 0.0082266 | 7.1419 | 7.1501 | -1.4745 | 121.5567 | 3269.1143 | -0.01213
136 |  | 0.67887 | 23.3713 | 4187 | 0.0082223 | 7.1501 | 7.1583 | -1.4745 | 121.6197 | 3292.4856 | -0.012124
137 |  | 0.67887 | 23.3592 | 4187 | 0.0082181 | 7.1583 | 7.1666 | -1.4745 | 121.6829 | 3315.8448 | -0.012118
138 |  | 0.67887 | 23.3471 | 4187 | 0.0082138 | 7.1666 | 7.1748 | -1.4745 | 121.746 | 3339.1919 | -0.012112
139 |  | 0.67887 | 23.335 | 4187 | 0.0082096 | 7.1748 | 7.183 | -1.4745 | 121.8092 | 3362.5269 | -0.012105
140 |  | 0.67887 | 23.3229 | 4187 | 0.0082053 | 7.183 | 7.1912 | -1.4745 | 121.8724 | 3385.8498 | -0.012099
141 |  | 0.67887 | 23.3108 | 4187 | 0.008201 | 7.1912 | 7.1994 | -1.4745 | 121.9357 | 3409.1605 | -0.012093
142 |  | 0.67887 | 23.2987 | 4187 | 0.0081968 | 7.1994 | 7.2076 | -1.4745 | 121.999 | 3432.4592 | -0.012087
143 |  | 0.67887 | 23.2866 | 4187 | 0.0081925 | 7.2076 | 7.2158 | -1.4745 | 122.0623 | 3455.7458 | -0.01208
144 |  | 0.67887 | 23.2745 | 4187 | 0.0081883 | 7.2158 | 7.224 | -1.4745 | 122.1257 | 3479.0203 | -0.012074
145 |  | 0.67887 | 23.2624 | 4187 | 0.008184 | 7.224 | 7.2322 | -1.4745 | 122.189 | 3502.2828 | -0.012068
146 |  | 0.67887 | 23.2504 | 4187 | 0.0081798 | 7.2322 | 7.2403 | -1.4745 | 122.2525 | 3525.5331 | -0.012061
147 |  | 0.67887 | 23.2383 | 4187 | 0.0081756 | 7.2403 | 7.2485 | -1.4745 | 122.3159 | 3548.7714 | -0.012055
148 |  | 0.67887 | 23.2263 | 4187 | 0.0081713 | 7.2485 | 7.2567 | -1.4745 | 122.3794 | 3571.9977 | -0.012049
149 |  | 0.67887 | 23.2142 | 4187 | 0.0081671 | 7.2567 | 7.2648 | -1.4745 | 122.4429 | 3595.2119 | -0.012043
150 |  | 0.67887 | 23.2022 | 4187 | 0.0081628 | 7.2648 | 7.273 | -1.4745 | 122.5065 | 3618.4141 | -0.012036
151 |  | 0.67887 | 23.1901 | 4187 | 0.0081586 | 7.273 | 7.2812 | -1.4745 | 122.5701 | 3641.6042 | -0.01203
152 |  | 0.67887 | 23.1781 | 4187 | 0.0081544 | 7.2812 | 7.2893 | -1.4745 | 122.6337 | 3664.7823 | -0.012024
153 |  | 0.67887 | 23.1661 | 4187 | 0.0081501 | 7.2893 | 7.2975 | -1.4745 | 122.6973 | 3687.9484 | -0.012018
154 |  | 0.67887 | 23.1541 | 4187 | 0.0081459 | 7.2975 | 7.3056 | -1.4745 | 122.761 | 3711.1024 | -0.012011
155 |  | 0.67887 | 23.142 | 4187 | 0.0081417 | 7.3056 | 7.3138 | -1.4745 | 122.8247 | 3734.2444 | -0.012005
156 |  | 0.67887 | 23.13 | 4187 | 0.0081375 | 7.3138 | 7.3219 | -1.4745 | 122.8885 | 3757.3745 | -0.011999
157 |  | 0.67887 | 23.118 | 4187 | 0.0081332 | 7.3219 | 7.33 | -1.4745 | 122.9523 | 3780.4925 | -0.011993
158 |  | 0.67887 | 23.106 | 4187 | 0.008129 | 7.33 | 7.3382 | -1.4745 | 123.0161 | 3803.5986 | -0.011987
159 |  | 0.67887 | 23.0941 | 4187 | 0.0081248 | 7.3382 | 7.3463 | -1.4745 | 123.0799 | 3826.6926 | -0.01198
160 |  | 0.67887 | 23.0821 | 4187 | 0.0081206 | 7.3463 | 7.3544 | -1.4745 | 123.1438 | 3849.7747 | -0.011974
161 |  | 0.67887 | 23.0701 | 4187 | 0.0081164 | 7.3544 | 7.3625 | -1.4745 | 123.2077 | 3872.8448 | -0.011968
162 |  | 0.67887 | 23.0581 | 4187 | 0.0081122 | 7.3625 | 7.3706 | -1.4745 | 123.2717 | 3895.9029 | -0.011962
163 |  | 0.67887 | 23.0462 | 4187 | 0.008108 | 7.3706 | 7.3787 | -1.4745 | 123.3357 | 3918.9491 | -0.011956
164 |  | 0.67887 | 23.0342 | 4187 | 0.0081037 | 7.3787 | 7.3868 | -1.4745 | 123.3997 | 3941.9833 | -0.011949
165 |  | 0.67887 | 23.0223 | 4187 | 0.0080995 | 7.3868 | 7.3949 | -1.4745 | 123.4637 | 3965.0056 | -0.011943
166 |  | 0.67887 | 23.0103 | 4187 | 0.0080953 | 7.3949 | 7.403 | -1.4745 | 123.5278 | 3988.0159 | -0.011937
167 |  | 0.67887 | 22.9984 | 4187 | 0.0080911 | 7.403 | 7.4111 | -1.4745 | 123.5919 | 4011.0143 | -0.011931
168 |  | 0.67887 | 22.9865 | 4187 | 0.0080869 | 7.4111 | 7.4192 | -1.4745 | 123.6561 | 4034.0008 | -0.011925
169 |  | 0.67887 | 22.9745 | 4187 | 0.0080828 | 7.4192 | 7.4273 | -1.4745 | 123.7203 | 4056.9753 | -0.011918
170 |  | 0.67887 | 22.9626 | 4187 | 0.0080786 | 7.4273 | 7.4354 | -1.4745 | 123.7845 | 4079.9379 | -0.011912
171 |  | 0.67887 | 22.9507 | 4187 | 0.0080744 | 7.4354 | 7.4435 | -1.4745 | 123.8487 | 4102.8886 | -0.011906
172 |  | 0.67887 | 22.9388 | 4187 | 0.0080702 | 7.4435 | 7.4515 | -1.4745 | 123.913 | 4125.8274 | -0.0119
173 |  | 0.67887 | 22.9269 | 4187 | 0.008066 | 7.4515 | 7.4596 | -1.4745 | 123.9773 | 4148.7543 | -0.011894
174 |  | 0.67887 | 22.915 | 4187 | 0.0080618 | 7.4596 | 7.4676 | -1.4745 | 124.0417 | 4171.6693 | -0.011887
175 |  | 0.67887 | 22.9031 | 4187 | 0.0080576 | 7.4676 | 7.4757 | -1.4745 | 124.106 | 4194.5724 | -0.011881
176 |  | 0.67887 | 22.8912 | 4187 | 0.0080534 | 7.4757 | 7.4838 | -1.4745 | 124.1705 | 4217.4637 | -0.011875
177 |  | 0.67887 | 22.8794 | 4187 | 0.0080493 | 7.4838 | 7.4918 | -1.4745 | 124.2349 | 4240.343 | -0.011869
178 |  | 0.67887 | 22.8675 | 4187 | 0.0080451 | 7.4918 | 7.4999 | -1.4745 | 124.2994 | 4263.2105 | -0.011863
179 |  | 0.67887 | 22.8556 | 4187 | 0.0080409 | 7.4999 | 7.5079 | -1.4745 | 124.3639 | 4286.0662 | -0.011857
180 |  | 0.67887 | 22.8438 | 4187 | 0.0080367 | 7.5079 | 7.5159 | -1.4745 | 124.4285 | 4308.9099 | -0.011851
181 |  | 0.67887 | 22.8319 | 4187 | 0.0080326 | 7.5159 | 7.524 | -1.4745 | 124.493 | 4331.7419 | -0.011844
182 |  | 0.67887 | 22.8201 | 4187 | 0.0080284 | 7.524 | 7.532 | -1.4745 | 124.5577 | 4354.5619 | -0.011838
183 |  | 0.67887 | 22.8082 | 4187 | 0.0080242 | 7.532 | 7.54 | -1.4745 | 124.6223 | 4377.3702 | -0.011832
184 |  | 0.67887 | 22.7964 | 4187 | 0.0080201 | 7.54 | 7.548 | -1.4745 | 124.687 | 4400.1666 | -0.011826
185 |  | 0.67887 | 22.7846 | 4187 | 0.0080159 | 7.548 | 7.5561 | -1.4745 | 124.7517 | 4422.9512 | -0.01182
186 |  | 0.67887 | 22.7728 | 4187 | 0.0080118 | 7.5561 | 7.5641 | -1.4745 | 124.8164 | 4445.7239 | -0.011814
187 |  | 0.67887 | 22.7609 | 4187 | 0.0080076 | 7.5641 | 7.5721 | -1.4745 | 124.8812 | 4468.4849 | -0.011808
188 |  | 0.67887 | 22.7491 | 4187 | 0.0080035 | 7.5721 | 7.5801 | -1.4745 | 124.9461 | 4491.234 | -0.011801
189 |  | 0.67887 | 22.7373 | 4187 | 0.0079993 | 7.5801 | 7.5881 | -1.4745 | 125.0109 | 4513.9713 | -0.011795
190 |  | 0.67887 | 22.7255 | 4187 | 0.0079952 | 7.5881 | 7.5961 | -1.4745 | 125.0758 | 4536.6969 | -0.011789
191 |  | 0.67887 | 22.7138 | 4187 | 0.007991 | 7.5961 | 7.6041 | -1.4745 | 125.1407 | 4559.4106 | -0.011783
192 |  | 0.67887 | 22.702 | 4187 | 0.0079869 | 7.6041 | 7.612 | -1.4745 | 125.2057 | 4582.1126 | -0.011777
193 |  | 0.67887 | 22.6902 | 4187 | 0.0079827 | 7.612 | 7.62 | -1.4745 | 125.2706 | 4604.8028 | -0.011771
194 |  | 0.67887 | 22.6784 | 4187 | 0.0079786 | 7.62 | 7.628 | -1.4745 | 125.3357 | 4627.4812 | -0.011765
195 |  | 0.67887 | 22.6667 | 4187 | 0.0079744 | 7.628 | 7.636 | -1.4745 | 125.4007 | 4650.1479 | -0.011759
196 |  | 0.67887 | 22.6549 | 4187 | 0.0079703 | 7.636 | 7.644 | -1.4745 | 125.4658 | 4672.8028 | -0.011753
197 |  | 0.67887 | 22.6431 | 4187 | 0.0079662 | 7.644 | 7.6519 | -1.4745 | 125.5309 | 4695.4459 | -0.011746
198 |  | 0.67887 | 22.6314 | 4187 | 0.007962 | 7.6519 | 7.6599 | -1.4745 | 125.5961 | 4718.0773 | -0.01174
199 |  | 0.67887 | 22.6197 | 4187 | 0.0079579 | 7.6599 | 7.6678 | -1.4745 | 125.6613 | 4740.697 | -0.011734
200 |  | 0.67887 | 22.6079 | 4187 | 0.0079538 | 7.6678 | 7.6758 | -1.4745 | 125.7265 | 4763.3049 | -0.011728
201 |  | 0.67887 | 22.5962 | 4187 | 0.0079496 | 7.6758 | 7.6837 | -1.4745 | 125.7917 | 4785.9011 | -0.011722
202 |  | 0.67887 | 22.5845 | 4187 | 0.0079455 | 7.6837 | 7.6917 | -1.4745 | 125.857 | 4808.4856 | -0.011716
203 |  | 0.67887 | 22.5728 | 4187 | 0.0079414 | 7.6917 | 7.6996 | -1.4745 | 125.9224 | 4831.0583 | -0.01171
204 |  | 0.67887 | 22.561 | 4187 | 0.0079373 | 7.6996 | 7.7076 | -1.4745 | 125.9877 | 4853.6194 | -0.011704
205 |  | 0.67887 | 22.5493 | 4187 | 0.0079332 | 7.7076 | 7.7155 | -1.4745 | 126.0531 | 4876.1687 | -0.011698
206 |  | 0.67887 | 22.5376 | 4187 | 0.007929 | 7.7155 | 7.7234 | -1.4745 | 126.1185 | 4898.7064 | -0.011692
207 |  | 0.67887 | 22.526 | 4187 | 0.0079249 | 7.7234 | 7.7314 | -1.4745 | 126.184 | 4921.2323 | -0.011686
208 |  | 0.67887 | 22.5143 | 4187 | 0.0079208 | 7.7314 | 7.7393 | -1.4745 | 126.2495 | 4943.7466 | -0.01168
209 |  | 0.67887 | 22.5026 | 4187 | 0.0079167 | 7.7393 | 7.7472 | -1.4745 | 126.315 | 4966.2492 | -0.011674
210 |  | 0.67887 | 22.4909 | 4187 | 0.0079126 | 7.7472 | 7.7551 | -1.4745 | 126.3806 | 4988.7401 | -0.011667
211 |  | 0.67887 | 22.4792 | 4187 | 0.0079085 | 7.7551 | 7.763 | -1.4745 | 126.4462 | 5011.2194 | -0.011661
212 |  | 0.67887 | 22.4676 | 4187 | 0.0079044 | 7.763 | 7.7709 | -1.4745 | 126.5118 | 5033.687 | -0.011655
213 |  | 0.67887 | 22.4559 | 4187 | 0.0079003 | 7.7709 | 7.7788 | -1.4745 | 126.5775 | 5056.1429 | -0.011649
214 |  | 0.67887 | 22.4443 | 4187 | 0.0078962 | 7.7788 | 7.7867 | -1.4745 | 126.6432 | 5078.5872 | -0.011643
215 |  | 0.67887 | 22.4326 | 4187 | 0.0078921 | 7.7867 | 7.7946 | -1.4745 | 126.7089 | 5101.0198 | -0.011637
216 |  | 0.67887 | 22.421 | 4187 | 0.007888 | 7.7946 | 7.8025 | -1.4745 | 126.7747 | 5123.4408 | -0.011631
217 |  | 0.67887 | 22.4094 | 4187 | 0.0078839 | 7.8025 | 7.8104 | -1.4745 | 126.8405 | 5145.8502 | -0.011625
218 |  | 0.67887 | 22.3977 | 4187 | 0.0078798 | 7.8104 | 7.8183 | -1.4745 | 126.9063 | 5168.2479 | -0.011619
219 |  | 0.67887 | 22.3861 | 4187 | 0.0078757 | 7.8183 | 7.8261 | -1.4745 | 126.9722 | 5190.6341 | -0.011613
220 |  | 0.67887 | 22.3745 | 4187 | 0.0078717 | 7.8261 | 7.834 | -1.4745 | 127.0381 | 5213.0086 | -0.011607
221 |  | 0.67887 | 22.3629 | 4187 | 0.0078676 | 7.834 | 7.8419 | -1.4745 | 127.104 | 5235.3715 | -0.011601
222 |  | 0.67887 | 22.3513 | 4187 | 0.0078635 | 7.8419 | 7.8497 | -1.4745 | 127.17 | 5257.7228 | -0.011595
223 |  | 0.67887 | 22.3397 | 4187 | 0.0078594 | 7.8497 | 7.8576 | -1.4745 | 127.236 | 5280.0625 | -0.011589
224 |  | 0.67887 | 22.3281 | 4187 | 0.0078553 | 7.8576 | 7.8655 | -1.4745 | 127.302 | 5302.3906 | -0.011583
225 |  | 0.67887 | 22.3165 | 4187 | 0.0078513 | 7.8655 | 7.8733 | -1.4745 | 127.3681 | 5324.7072 | -0.011577
226 |  | 0.67887 | 22.305 | 4187 | 0.0078472 | 7.8733 | 7.8812 | -1.4745 | 127.4342 | 5347.0121 | -0.011571
227 |  | 0.67887 | 22.2934 | 4187 | 0.0078431 | 7.8812 | 7.889 | -1.4745 | 127.5003 | 5369.3055 | -0.011565
228 |  | 0.67887 | 22.2818 | 4187 | 0.007839 | 7.889 | 7.8968 | -1.4745 | 127.5665 | 5391.5873 | -0.011559
229 |  | 0.67887 | 22.2703 | 4187 | 0.007835 | 7.8968 | 7.9047 | -1.4745 | 127.6327 | 5413.8576 | -0.011553
230 |  | 0.67887 | 22.2587 | 4187 | 0.0078309 | 7.9047 | 7.9125 | -1.4745 | 127.699 | 5436.1163 | -0.011547
231 |  | 0.67887 | 22.2472 | 4187 | 0.0078269 | 7.9125 | 7.9203 | -1.4745 | 127.7653 | 5458.3635 | -0.011541
232 |  | 0.67887 | 22.2356 | 4187 | 0.0078228 | 7.9203 | 7.9281 | -1.4745 | 127.8316 | 5480.5991 | -0.011535
233 |  | 0.67887 | 22.2241 | 4187 | 0.0078187 | 7.9281 | 7.936 | -1.4745 | 127.8979 | 5502.8232 | -0.011529
234 |  | 0.67887 | 22.2126 | 4187 | 0.0078147 | 7.936 | 7.9438 | -1.4745 | 127.9643 | 5525.0358 | -0.011523
235 |  | 0.67887 | 22.201 | 4187 | 0.0078106 | 7.9438 | 7.9516 | -1.4745 | 128.0307 | 5547.2368 | -0.011517
236 |  | 0.67887 | 22.1895 | 4187 | 0.0078066 | 7.9516 | 7.9594 | -1.4745 | 128.0972 | 5569.4263 | -0.011511

## Cu38
|  |  | buis | verlies W/M | L /°C/sec
diam | wandikte |  | inhoud l/m |  | W/M
38.1 | 1.2 | 3.1416 | 1.001 | 30.0398 | 4187
[8 empty] | J/sec/mtr | aantal mtr. | verlies
|  | buis | verlies W/M | L /°C/sec | verlies temp | begintemp | eindtemp | verlies | bij 1°C | totaal J/sec
|  | inhoud L |  | W/M | °C per M | °C | °C | per m°C | daling | aantal mtr
1 | 38.1 | 1.001 | 30.0398 | 4187 | 0.0071675 | 6 | 6.0072 | -1.767 | 139.5188 | 30.0398 | -0.012665
2 |  | 1.001 | 30.0271 | 4187 | 0.0071645 | 6.0072 | 6.0143 | -1.767 | 139.5776 | 60.0669 | -0.01266
3 |  | 1.001 | 30.0144 | 4187 | 0.0071615 | 6.0143 | 6.0215 | -1.767 | 139.6365 | 90.0813 | -0.012655
4 |  | 1.001 | 30.0018 | 4187 | 0.0071584 | 6.0215 | 6.0287 | -1.767 | 139.6954 | 120.0831 | -0.012649
5 |  | 1.001 | 29.9891 | 4187 | 0.0071554 | 6.0287 | 6.0358 | -1.767 | 139.7543 | 150.0723 | -0.012644
6 |  | 1.001 | 29.9765 | 4187 | 0.0071524 | 6.0358 | 6.043 | -1.767 | 139.8133 | 180.0488 | -0.012639
7 |  | 1.001 | 29.9639 | 4187 | 0.0071494 | 6.043 | 6.0501 | -1.767 | 139.8722 | 210.0126 | -0.012633
8 |  | 1.001 | 29.9512 | 4187 | 0.0071464 | 6.0501 | 6.0573 | -1.767 | 139.9312 | 239.9639 | -0.012628
9 |  | 1.001 | 29.9386 | 4187 | 0.0071434 | 6.0573 | 6.0644 | -1.767 | 139.9902 | 269.9025 | -0.012623
10 |  | 1.001 | 29.926 | 4187 | 0.0071403 | 6.0644 | 6.0715 | -1.767 | 140.0493 | 299.8284 | -0.012617
11 |  | 1.001 | 29.9134 | 4187 | 0.0071373 | 6.0715 | 6.0787 | -1.767 | 140.1084 | 329.7418 | -0.012612
12 |  | 1.001 | 29.9007 | 4187 | 0.0071343 | 6.0787 | 6.0858 | -1.767 | 140.1675 | 359.6426 | -0.012607
13 |  | 1.001 | 29.8881 | 4187 | 0.0071313 | 6.0858 | 6.0929 | -1.767 | 140.2266 | 389.5307 | -0.012601
14 |  | 1.001 | 29.8755 | 4187 | 0.0071283 | 6.0929 | 6.1001 | -1.767 | 140.2857 | 419.4062 | -0.012596
15 |  | 1.001 | 29.8629 | 4187 | 0.0071253 | 6.1001 | 6.1072 | -1.767 | 140.3449 | 449.2692 | -0.012591
16 |  | 1.001 | 29.8504 | 4187 | 0.0071223 | 6.1072 | 6.1143 | -1.767 | 140.4041 | 479.1195 | -0.012585
17 |  | 1.001 | 29.8378 | 4187 | 0.0071193 | 6.1143 | 6.1214 | -1.767 | 140.4633 | 508.9573 | -0.01258
18 |  | 1.001 | 29.8252 | 4187 | 0.0071163 | 6.1214 | 6.1286 | -1.767 | 140.5226 | 538.7825 | -0.012575
19 |  | 1.001 | 29.8126 | 4187 | 0.0071133 | 6.1286 | 6.1357 | -1.767 | 140.5818 | 568.5951 | -0.01257
20 |  | 1.001 | 29.8 | 4187 | 0.0071103 | 6.1357 | 6.1428 | -1.767 | 140.6411 | 598.3952 | -0.012564
21 |  | 1.001 | 29.7875 | 4187 | 0.0071073 | 6.1428 | 6.1499 | -1.767 | 140.7005 | 628.1826 | -0.012559
22 |  | 1.001 | 29.7749 | 4187 | 0.0071043 | 6.1499 | 6.157 | -1.767 | 140.7598 | 657.9576 | -0.012554
23 |  | 1.001 | 29.7624 | 4187 | 0.0071013 | 6.157 | 6.1641 | -1.767 | 140.8192 | 687.7199 | -0.012548
24 |  | 1.001 | 29.7498 | 4187 | 0.0070983 | 6.1641 | 6.1712 | -1.767 | 140.8786 | 717.4697 | -0.012543
25 |  | 1.001 | 29.7373 | 4187 | 0.0070953 | 6.1712 | 6.1783 | -1.767 | 140.938 | 747.207 | -0.012538
26 |  | 1.001 | 29.7247 | 4187 | 0.0070923 | 6.1783 | 6.1854 | -1.767 | 140.9974 | 776.9318 | -0.012532
27 |  | 1.001 | 29.7122 | 4187 | 0.0070893 | 6.1854 | 6.1925 | -1.767 | 141.0569 | 806.644 | -0.012527
28 |  | 1.001 | 29.6997 | 4187 | 0.0070863 | 6.1925 | 6.1996 | -1.767 | 141.1164 | 836.3437 | -0.012522
29 |  | 1.001 | 29.6872 | 4187 | 0.0070834 | 6.1996 | 6.2066 | -1.767 | 141.1759 | 866.0308 | -0.012517
30 |  | 1.001 | 29.6746 | 4187 | 0.0070804 | 6.2066 | 6.2137 | -1.767 | 141.2355 | 895.7054 | -0.012511
31 |  | 1.001 | 29.6621 | 4187 | 0.0070774 | 6.2137 | 6.2208 | -1.767 | 141.2951 | 925.3676 | -0.012506
32 |  | 1.001 | 29.6496 | 4187 | 0.0070744 | 6.2208 | 6.2279 | -1.767 | 141.3546 | 955.0172 | -0.012501
33 |  | 1.001 | 29.6371 | 4187 | 0.0070714 | 6.2279 | 6.2349 | -1.767 | 141.4143 | 984.6543 | -0.012496
34 |  | 1.001 | 29.6246 | 4187 | 0.0070684 | 6.2349 | 6.242 | -1.767 | 141.4739 | 1014.279 | -0.01249
35 |  | 1.001 | 29.6121 | 4187 | 0.0070655 | 6.242 | 6.2491 | -1.767 | 141.5336 | 1043.8911 | -0.012485
36 |  | 1.001 | 29.5997 | 4187 | 0.0070625 | 6.2491 | 6.2561 | -1.767 | 141.5933 | 1073.4907 | -0.01248
37 |  | 1.001 | 29.5872 | 4187 | 0.0070595 | 6.2561 | 6.2632 | -1.767 | 141.653 | 1103.0779 | -0.012474
38 |  | 1.001 | 29.5747 | 4187 | 0.0070565 | 6.2632 | 6.2703 | -1.767 | 141.7128 | 1132.6526 | -0.012469
39 |  | 1.001 | 29.5622 | 4187 | 0.0070536 | 6.2703 | 6.2773 | -1.767 | 141.7725 | 1162.2148 | -0.012464
40 |  | 1.001 | 29.5498 | 4187 | 0.0070506 | 6.2773 | 6.2844 | -1.767 | 141.8323 | 1191.7646 | -0.012459
41 |  | 1.001 | 29.5373 | 4187 | 0.0070476 | 6.2844 | 6.2914 | -1.767 | 141.8922 | 1221.3019 | -0.012453
42 |  | 1.001 | 29.5249 | 4187 | 0.0070446 | 6.2914 | 6.2984 | -1.767 | 141.952 | 1250.8268 | -0.012448
43 |  | 1.001 | 29.5124 | 4187 | 0.0070417 | 6.2984 | 6.3055 | -1.767 | 142.0119 | 1280.3392 | -0.012443
44 |  | 1.001 | 29.5 | 4187 | 0.0070387 | 6.3055 | 6.3125 | -1.767 | 142.0718 | 1309.8391 | -0.012438
45 |  | 1.001 | 29.4875 | 4187 | 0.0070357 | 6.3125 | 6.3196 | -1.767 | 142.1317 | 1339.3266 | -0.012432
46 |  | 1.001 | 29.4751 | 4187 | 0.0070328 | 6.3196 | 6.3266 | -1.767 | 142.1917 | 1368.8017 | -0.012427
47 |  | 1.001 | 29.4627 | 4187 | 0.0070298 | 6.3266 | 6.3336 | -1.767 | 142.2516 | 1398.2644 | -0.012422
48 |  | 1.001 | 29.4502 | 4187 | 0.0070268 | 6.3336 | 6.3407 | -1.767 | 142.3116 | 1427.7146 | -0.012417
49 |  | 1.001 | 29.4378 | 4187 | 0.0070239 | 6.3407 | 6.3477 | -1.767 | 142.3717 | 1457.1525 | -0.012411
50 |  | 1.001 | 29.4254 | 4187 | 0.0070209 | 6.3477 | 6.3547 | -1.767 | 142.4317 | 1486.5779 | -0.012406
51 |  | 1.001 | 29.413 | 4187 | 0.0070179 | 6.3547 | 6.3617 | -1.767 | 142.4918 | 1515.9909 | -0.012401
52 |  | 1.001 | 29.4006 | 4187 | 0.007015 | 6.3617 | 6.3687 | -1.767 | 142.5519 | 1545.3915 | -0.012396
53 |  | 1.001 | 29.3882 | 4187 | 0.007012 | 6.3687 | 6.3757 | -1.767 | 142.612 | 1574.7797 | -0.012391
54 |  | 1.001 | 29.3758 | 4187 | 0.0070091 | 6.3757 | 6.3828 | -1.767 | 142.6722 | 1604.1555 | -0.012385
55 |  | 1.001 | 29.3634 | 4187 | 0.0070061 | 6.3828 | 6.3898 | -1.767 | 142.7324 | 1633.519 | -0.01238
56 |  | 1.001 | 29.3511 | 4187 | 0.0070032 | 6.3898 | 6.3968 | -1.767 | 142.7926 | 1662.87 | -0.012375
57 |  | 1.001 | 29.3387 | 4187 | 0.0070002 | 6.3968 | 6.4038 | -1.767 | 142.8528 | 1692.2087 | -0.01237
58 |  | 1.001 | 29.3263 | 4187 | 0.0069973 | 6.4038 | 6.4108 | -1.767 | 142.913 | 1721.535 | -0.012364
59 |  | 1.001 | 29.3139 | 4187 | 0.0069943 | 6.4108 | 6.4178 | -1.767 | 142.9733 | 1750.849 | -0.012359
60 |  | 1.001 | 29.3016 | 4187 | 0.0069914 | 6.4178 | 6.4247 | -1.767 | 143.0336 | 1780.1505 | -0.012354
61 |  | 1.001 | 29.2892 | 4187 | 0.0069884 | 6.4247 | 6.4317 | -1.767 | 143.094 | 1809.4398 | -0.012349
62 |  | 1.001 | 29.2769 | 4187 | 0.0069855 | 6.4317 | 6.4387 | -1.767 | 143.1543 | 1838.7167 | -0.012344
63 |  | 1.001 | 29.2645 | 4187 | 0.0069825 | 6.4387 | 6.4457 | -1.767 | 143.2147 | 1867.9812 | -0.012338
64 |  | 1.001 | 29.2522 | 4187 | 0.0069796 | 6.4457 | 6.4527 | -1.767 | 143.2751 | 1897.2334 | -0.012333
65 |  | 1.001 | 29.2399 | 4187 | 0.0069766 | 6.4527 | 6.4597 | -1.767 | 143.3355 | 1926.4733 | -0.012328
66 |  | 1.001 | 29.2275 | 4187 | 0.0069737 | 6.4597 | 6.4666 | -1.767 | 143.396 | 1955.7008 | -0.012323
67 |  | 1.001 | 29.2152 | 4187 | 0.0069708 | 6.4666 | 6.4736 | -1.767 | 143.4565 | 1984.916 | -0.012318
68 |  | 1.001 | 29.2029 | 4187 | 0.0069678 | 6.4736 | 6.4806 | -1.767 | 143.517 | 2014.1189 | -0.012312
69 |  | 1.001 | 29.1906 | 4187 | 0.0069649 | 6.4806 | 6.4875 | -1.767 | 143.5775 | 2043.3095 | -0.012307
70 |  | 1.001 | 29.1783 | 4187 | 0.0069619 | 6.4875 | 6.4945 | -1.767 | 143.6381 | 2072.4878 | -0.012302
71 |  | 1.001 | 29.166 | 4187 | 0.006959 | 6.4945 | 6.5015 | -1.767 | 143.6987 | 2101.6538 | -0.012297
72 |  | 1.001 | 29.1537 | 4187 | 0.0069561 | 6.5015 | 6.5084 | -1.767 | 143.7593 | 2130.8074 | -0.012292
73 |  | 1.001 | 29.1414 | 4187 | 0.0069531 | 6.5084 | 6.5154 | -1.767 | 143.8199 | 2159.9488 | -0.012287
74 |  | 1.001 | 29.1291 | 4187 | 0.0069502 | 6.5154 | 6.5223 | -1.767 | 143.8806 | 2189.0779 | -0.012281
75 |  | 1.001 | 29.1168 | 4187 | 0.0069473 | 6.5223 | 6.5293 | -1.767 | 143.9413 | 2218.1948 | -0.012276
76 |  | 1.001 | 29.1045 | 4187 | 0.0069443 | 6.5293 | 6.5362 | -1.767 | 144.002 | 2247.2993 | -0.012271
77 |  | 1.001 | 29.0923 | 4187 | 0.0069414 | 6.5362 | 6.5431 | -1.767 | 144.0627 | 2276.3916 | -0.012266
78 |  | 1.001 | 29.08 | 4187 | 0.0069385 | 6.5431 | 6.5501 | -1.767 | 144.1235 | 2305.4716 | -0.012261
79 |  | 1.001 | 29.0677 | 4187 | 0.0069356 | 6.5501 | 6.557 | -1.767 | 144.1843 | 2334.5393 | -0.012255
80 |  | 1.001 | 29.0555 | 4187 | 0.0069326 | 6.557 | 6.564 | -1.767 | 144.2451 | 2363.5948 | -0.01225
81 |  | 1.001 | 29.0432 | 4187 | 0.0069297 | 6.564 | 6.5709 | -1.767 | 144.3059 | 2392.6381 | -0.012245
82 |  | 1.001 | 29.031 | 4187 | 0.0069268 | 6.5709 | 6.5778 | -1.767 | 144.3668 | 2421.6691 | -0.01224
83 |  | 1.001 | 29.0188 | 4187 | 0.0069239 | 6.5778 | 6.5847 | -1.767 | 144.4277 | 2450.6878 | -0.012235
84 |  | 1.001 | 29.0065 | 4187 | 0.006921 | 6.5847 | 6.5917 | -1.767 | 144.4886 | 2479.6943 | -0.01223
85 |  | 1.001 | 28.9943 | 4187 | 0.006918 | 6.5917 | 6.5986 | -1.767 | 144.5496 | 2508.6886 | -0.012224
86 |  | 1.001 | 28.9821 | 4187 | 0.0069151 | 6.5986 | 6.6055 | -1.767 | 144.6105 | 2537.6707 | -0.012219
87 |  | 1.001 | 28.9698 | 4187 | 0.0069122 | 6.6055 | 6.6124 | -1.767 | 144.6715 | 2566.6405 | -0.012214
88 |  | 1.001 | 28.9576 | 4187 | 0.0069093 | 6.6124 | 6.6193 | -1.767 | 144.7325 | 2595.5982 | -0.012209
89 |  | 1.001 | 28.9454 | 4187 | 0.0069064 | 6.6193 | 6.6262 | -1.767 | 144.7936 | 2624.5436 | -0.012204
90 |  | 1.001 | 28.9332 | 4187 | 0.0069035 | 6.6262 | 6.6331 | -1.767 | 144.8547 | 2653.4768 | -0.012199
91 |  | 1.001 | 28.921 | 4187 | 0.0069006 | 6.6331 | 6.64 | -1.767 | 144.9158 | 2682.3979 | -0.012194
92 |  | 1.001 | 28.9088 | 4187 | 0.0068977 | 6.64 | 6.6469 | -1.767 | 144.9769 | 2711.3067 | -0.012188
93 |  | 1.001 | 28.8966 | 4187 | 0.0068947 | 6.6469 | 6.6538 | -1.767 | 145.038 | 2740.2033 | -0.012183
94 |  | 1.001 | 28.8845 | 4187 | 0.0068918 | 6.6538 | 6.6607 | -1.767 | 145.0992 | 2769.0878 | -0.012178
95 |  | 1.001 | 28.8723 | 4187 | 0.0068889 | 6.6607 | 6.6676 | -1.767 | 145.1604 | 2797.9601 | -0.012173
96 |  | 1.001 | 28.8601 | 4187 | 0.006886 | 6.6676 | 6.6745 | -1.767 | 145.2216 | 2826.8202 | -0.012168
97 |  | 1.001 | 28.8479 | 4187 | 0.0068831 | 6.6745 | 6.6814 | -1.767 | 145.2829 | 2855.6681 | -0.012163
98 |  | 1.001 | 28.8358 | 4187 | 0.0068802 | 6.6814 | 6.6882 | -1.767 | 145.3442 | 2884.5039 | -0.012158
99 |  | 1.001 | 28.8236 | 4187 | 0.0068773 | 6.6882 | 6.6951 | -1.767 | 145.4055 | 2913.3275 | -0.012153
100 |  | 1.001 | 28.8115 | 4187 | 0.0068744 | 6.6951 | 6.702 | -1.767 | 145.4668 | 2942.139 | -0.012147
101 |  | 1.001 | 28.7993 | 4187 | 0.0068715 | 6.702 | 6.7089 | -1.767 | 145.5282 | 2970.9383 | -0.012142
102 |  | 1.001 | 28.7872 | 4187 | 0.0068686 | 6.7089 | 6.7157 | -1.767 | 145.5896 | 2999.7255 | -0.012137
103 |  | 1.001 | 28.775 | 4187 | 0.0068657 | 6.7157 | 6.7226 | -1.767 | 145.651 | 3028.5005 | -0.012132
104 |  | 1.001 | 28.7629 | 4187 | 0.0068628 | 6.7226 | 6.7295 | -1.767 | 145.7124 | 3057.2634 | -0.012127
105 |  | 1.001 | 28.7508 | 4187 | 0.0068599 | 6.7295 | 6.7363 | -1.767 | 145.7739 | 3086.0142 | -0.012122
106 |  | 1.001 | 28.7387 | 4187 | 0.006857 | 6.7363 | 6.7432 | -1.767 | 145.8353 | 3114.7528 | -0.012117
107 |  | 1.001 | 28.7265 | 4187 | 0.0068542 | 6.7432 | 6.75 | -1.767 | 145.8969 | 3143.4794 | -0.012112
108 |  | 1.001 | 28.7144 | 4187 | 0.0068513 | 6.75 | 6.7569 | -1.767 | 145.9584 | 3172.1938 | -0.012107
109 |  | 1.001 | 28.7023 | 4187 | 0.0068484 | 6.7569 | 6.7637 | -1.767 | 146.02 | 3200.8961 | -0.012101
110 |  | 1.001 | 28.6902 | 4187 | 0.0068455 | 6.7637 | 6.7706 | -1.767 | 146.0816 | 3229.5863 | -0.012096
111 |  | 1.001 | 28.6781 | 4187 | 0.0068426 | 6.7706 | 6.7774 | -1.767 | 146.1432 | 3258.2645 | -0.012091
112 |  | 1.001 | 28.666 | 4187 | 0.0068397 | 6.7774 | 6.7843 | -1.767 | 146.2048 | 3286.9305 | -0.012086
113 |  | 1.001 | 28.6539 | 4187 | 0.0068368 | 6.7843 | 6.7911 | -1.767 | 146.2665 | 3315.5845 | -0.012081
114 |  | 1.001 | 28.6419 | 4187 | 0.006834 | 6.7911 | 6.7979 | -1.767 | 146.3282 | 3344.2263 | -0.012076
115 |  | 1.001 | 28.6298 | 4187 | 0.0068311 | 6.7979 | 6.8048 | -1.767 | 146.3899 | 3372.8561 | -0.012071
116 |  | 1.001 | 28.6177 | 4187 | 0.0068282 | 6.8048 | 6.8116 | -1.767 | 146.4516 | 3401.4738 | -0.012066
117 |  | 1.001 | 28.6057 | 4187 | 0.0068253 | 6.8116 | 6.8184 | -1.767 | 146.5134 | 3430.0795 | -0.012061
118 |  | 1.001 | 28.5936 | 4187 | 0.0068224 | 6.8184 | 6.8252 | -1.767 | 146.5752 | 3458.6731 | -0.012056
119 |  | 1.001 | 28.5815 | 4187 | 0.0068196 | 6.8252 | 6.8321 | -1.767 | 146.637 | 3487.2546 | -0.01205
120 |  | 1.001 | 28.5695 | 4187 | 0.0068167 | 6.8321 | 6.8389 | -1.767 | 146.6989 | 3515.8241 | -0.012045
121 |  | 1.001 | 28.5574 | 4187 | 0.0068138 | 6.8389 | 6.8457 | -1.767 | 146.7608 | 3544.3815 | -0.01204
122 |  | 1.001 | 28.5454 | 4187 | 0.0068109 | 6.8457 | 6.8525 | -1.767 | 146.8227 | 3572.9269 | -0.012035
123 |  | 1.001 | 28.5334 | 4187 | 0.0068081 | 6.8525 | 6.8593 | -1.767 | 146.8846 | 3601.4603 | -0.01203
124 |  | 1.001 | 28.5213 | 4187 | 0.0068052 | 6.8593 | 6.8661 | -1.767 | 146.9466 | 3629.9816 | -0.012025
125 |  | 1.001 | 28.5093 | 4187 | 0.0068023 | 6.8661 | 6.8729 | -1.767 | 147.0085 | 3658.491 | -0.01202
126 |  | 1.001 | 28.4973 | 4187 | 0.0067995 | 6.8729 | 6.8797 | -1.767 | 147.0705 | 3686.9883 | -0.012015
127 |  | 1.001 | 28.4853 | 4187 | 0.0067966 | 6.8797 | 6.8865 | -1.767 | 147.1326 | 3715.4735 | -0.01201
128 |  | 1.001 | 28.4733 | 4187 | 0.0067937 | 6.8865 | 6.8933 | -1.767 | 147.1946 | 3743.9468 | -0.012005
129 |  | 1.001 | 28.4613 | 4187 | 0.0067909 | 6.8933 | 6.9001 | -1.767 | 147.2567 | 3772.4081 | -0.012
130 |  | 1.001 | 28.4493 | 4187 | 0.006788 | 6.9001 | 6.9069 | -1.767 | 147.3188 | 3800.8573 | -0.011995
131 |  | 1.001 | 28.4373 | 4187 | 0.0067851 | 6.9069 | 6.9137 | -1.767 | 147.381 | 3829.2946 | -0.01199
132 |  | 1.001 | 28.4253 | 4187 | 0.0067823 | 6.9137 | 6.9205 | -1.767 | 147.4431 | 3857.7199 | -0.011985
133 |  | 1.001 | 28.4133 | 4187 | 0.0067794 | 6.9205 | 6.9272 | -1.767 | 147.5053 | 3886.1332 | -0.01198
134 |  | 1.001 | 28.4013 | 4187 | 0.0067766 | 6.9272 | 6.934 | -1.767 | 147.5675 | 3914.5345 | -0.011974
135 |  | 1.001 | 28.3893 | 4187 | 0.0067737 | 6.934 | 6.9408 | -1.767 | 147.6298 | 3942.9238 | -0.011969
136 |  | 1.001 | 28.3774 | 4187 | 0.0067708 | 6.9408 | 6.9476 | -1.767 | 147.6921 | 3971.3012 | -0.011964
137 |  | 1.001 | 28.3654 | 4187 | 0.006768 | 6.9476 | 6.9543 | -1.767 | 147.7544 | 3999.6666 | -0.011959
138 |  | 1.001 | 28.3534 | 4187 | 0.0067651 | 6.9543 | 6.9611 | -1.767 | 147.8167 | 4028.02 | -0.011954
139 |  | 1.001 | 28.3415 | 4187 | 0.0067623 | 6.9611 | 6.9678 | -1.767 | 147.879 | 4056.3615 | -0.011949
140 |  | 1.001 | 28.3295 | 4187 | 0.0067594 | 6.9678 | 6.9746 | -1.767 | 147.9414 | 4084.6911 | -0.011944
141 |  | 1.001 | 28.3176 | 4187 | 0.0067566 | 6.9746 | 6.9814 | -1.767 | 148.0038 | 4113.0087 | -0.011939
142 |  | 1.001 | 28.3057 | 4187 | 0.0067537 | 6.9814 | 6.9881 | -1.767 | 148.0662 | 4141.3143 | -0.011934
143 |  | 1.001 | 28.2937 | 4187 | 0.0067509 | 6.9881 | 6.9949 | -1.767 | 148.1287 | 4169.608 | -0.011929
144 |  | 1.001 | 28.2818 | 4187 | 0.006748 | 6.9949 | 7.0016 | -1.767 | 148.1912 | 4197.8898 | -0.011924
145 |  | 1.001 | 28.2699 | 4187 | 0.0067452 | 7.0016 | 7.0084 | -1.767 | 148.2537 | 4226.1597 | -0.011919
146 |  | 1.001 | 28.258 | 4187 | 0.0067424 | 7.0084 | 7.0151 | -1.767 | 148.3162 | 4254.4177 | -0.011914
147 |  | 1.001 | 28.246 | 4187 | 0.0067395 | 7.0151 | 7.0218 | -1.767 | 148.3788 | 4282.6637 | -0.011909
148 |  | 1.001 | 28.2341 | 4187 | 0.0067367 | 7.0218 | 7.0286 | -1.767 | 148.4413 | 4310.8978 | -0.011904
149 |  | 1.001 | 28.2222 | 4187 | 0.0067338 | 7.0286 | 7.0353 | -1.767 | 148.504 | 4339.1201 | -0.011899
150 |  | 1.001 | 28.2103 | 4187 | 0.006731 | 7.0353 | 7.042 | -1.767 | 148.5666 | 4367.3304 | -0.011894
151 |  | 1.001 | 28.1984 | 4187 | 0.0067282 | 7.042 | 7.0488 | -1.767 | 148.6293 | 4395.5288 | -0.011889
152 |  | 1.001 | 28.1865 | 4187 | 0.0067253 | 7.0488 | 7.0555 | -1.767 | 148.692 | 4423.7154 | -0.011884
153 |  | 1.001 | 28.1747 | 4187 | 0.0067225 | 7.0555 | 7.0622 | -1.767 | 148.7547 | 4451.89 | -0.011879
154 |  | 1.001 | 28.1628 | 4187 | 0.0067196 | 7.0622 | 7.0689 | -1.767 | 148.8174 | 4480.0528 | -0.011874
155 |  | 1.001 | 28.1509 | 4187 | 0.0067168 | 7.0689 | 7.0757 | -1.767 | 148.8802 | 4508.2037 | -0.011869
156 |  | 1.001 | 28.139 | 4187 | 0.006714 | 7.0757 | 7.0824 | -1.767 | 148.943 | 4536.3427 | -0.011864
157 |  | 1.001 | 28.1272 | 4187 | 0.0067111 | 7.0824 | 7.0891 | -1.767 | 149.0058 | 4564.4699 | -0.011859
158 |  | 1.001 | 28.1153 | 4187 | 0.0067083 | 7.0891 | 7.0958 | -1.767 | 149.0687 | 4592.5852 | -0.011854
159 |  | 1.001 | 28.1035 | 4187 | 0.0067055 | 7.0958 | 7.1025 | -1.767 | 149.1315 | 4620.6887 | -0.011849
160 |  | 1.001 | 28.0916 | 4187 | 0.0067027 | 7.1025 | 7.1092 | -1.767 | 149.1944 | 4648.7803 | -0.011844
161 |  | 1.001 | 28.0798 | 4187 | 0.0066998 | 7.1092 | 7.1159 | -1.767 | 149.2574 | 4676.8601 | -0.011839
162 |  | 1.001 | 28.0679 | 4187 | 0.006697 | 7.1159 | 7.1226 | -1.767 | 149.3203 | 4704.928 | -0.011834
163 |  | 1.001 | 28.0561 | 4187 | 0.0066942 | 7.1226 | 7.1293 | -1.767 | 149.3833 | 4732.9841 | -0.011829
164 |  | 1.001 | 28.0443 | 4187 | 0.0066914 | 7.1293 | 7.136 | -1.767 | 149.4463 | 4761.0284 | -0.011824
165 |  | 1.001 | 28.0324 | 4187 | 0.0066885 | 7.136 | 7.1427 | -1.767 | 149.5093 | 4789.0608 | -0.011819
166 |  | 1.001 | 28.0206 | 4187 | 0.0066857 | 7.1427 | 7.1494 | -1.767 | 149.5724 | 4817.0814 | -0.011814
167 |  | 1.001 | 28.0088 | 4187 | 0.0066829 | 7.1494 | 7.156 | -1.767 | 149.6355 | 4845.0902 | -0.011809
168 |  | 1.001 | 27.997 | 4187 | 0.0066801 | 7.156 | 7.1627 | -1.767 | 149.6986 | 4873.0872 | -0.011804
169 |  | 1.001 | 27.9852 | 4187 | 0.0066773 | 7.1627 | 7.1694 | -1.767 | 149.7618 | 4901.0724 | -0.011799
170 |  | 1.001 | 27.9734 | 4187 | 0.0066745 | 7.1694 | 7.1761 | -1.767 | 149.8249 | 4929.0458 | -0.011794
171 |  | 1.001 | 27.9616 | 4187 | 0.0066716 | 7.1761 | 7.1827 | -1.767 | 149.8881 | 4957.0074 | -0.011789
172 |  | 1.001 | 27.9498 | 4187 | 0.0066688 | 7.1827 | 7.1894 | -1.767 | 149.9513 | 4984.9572 | -0.011784
173 |  | 1.001 | 27.938 | 4187 | 0.006666 | 7.1894 | 7.1961 | -1.767 | 150.0146 | 5012.8953 | -0.011779
174 |  | 1.001 | 27.9263 | 4187 | 0.0066632 | 7.1961 | 7.2027 | -1.767 | 150.0779 | 5040.8215 | -0.011774
175 |  | 1.001 | 27.9145 | 4187 | 0.0066604 | 7.2027 | 7.2094 | -1.767 | 150.1412 | 5068.736 | -0.011769
176 |  | 1.001 | 27.9027 | 4187 | 0.0066576 | 7.2094 | 7.2161 | -1.767 | 150.2045 | 5096.6387 | -0.011764
177 |  | 1.001 | 27.8909 | 4187 | 0.0066548 | 7.2161 | 7.2227 | -1.767 | 150.2679 | 5124.5296 | -0.011759
178 |  | 1.001 | 27.8792 | 4187 | 0.006652 | 7.2227 | 7.2294 | -1.767 | 150.3312 | 5152.4088 | -0.011754
179 |  | 1.001 | 27.8674 | 4187 | 0.0066492 | 7.2294 | 7.236 | -1.767 | 150.3946 | 5180.2763 | -0.011749
180 |  | 1.001 | 27.8557 | 4187 | 0.0066464 | 7.236 | 7.2427 | -1.767 | 150.4581 | 5208.1319 | -0.011744
181 |  | 1.001 | 27.8439 | 4187 | 0.0066436 | 7.2427 | 7.2493 | -1.767 | 150.5215 | 5235.9759 | -0.011739
182 |  | 1.001 | 27.8322 | 4187 | 0.0066408 | 7.2493 | 7.2559 | -1.767 | 150.585 | 5263.8081 | -0.011735
183 |  | 1.001 | 27.8205 | 4187 | 0.006638 | 7.2559 | 7.2626 | -1.767 | 150.6485 | 5291.6285 | -0.01173
184 |  | 1.001 | 27.8087 | 4187 | 0.0066352 | 7.2626 | 7.2692 | -1.767 | 150.7121 | 5319.4373 | -0.011725
185 |  | 1.001 | 27.797 | 4187 | 0.0066324 | 7.2692 | 7.2759 | -1.767 | 150.7757 | 5347.2343 | -0.01172
186 |  | 1.001 | 27.7853 | 4187 | 0.0066296 | 7.2759 | 7.2825 | -1.767 | 150.8393 | 5375.0196 | -0.011715
187 |  | 1.001 | 27.7736 | 4187 | 0.0066268 | 7.2825 | 7.2891 | -1.767 | 150.9029 | 5402.7931 | -0.01171
188 |  | 1.001 | 27.7619 | 4187 | 0.006624 | 7.2891 | 7.2957 | -1.767 | 150.9665 | 5430.555 | -0.011705
189 |  | 1.001 | 27.7502 | 4187 | 0.0066212 | 7.2957 | 7.3024 | -1.767 | 151.0302 | 5458.3052 | -0.0117
190 |  | 1.001 | 27.7385 | 4187 | 0.0066184 | 7.3024 | 7.309 | -1.767 | 151.0939 | 5486.0436 | -0.011695
191 |  | 1.001 | 27.7268 | 4187 | 0.0066156 | 7.309 | 7.3156 | -1.767 | 151.1576 | 5513.7704 | -0.01169
192 |  | 1.001 | 27.7151 | 4187 | 0.0066128 | 7.3156 | 7.3222 | -1.767 | 151.2214 | 5541.4855 | -0.011685
193 |  | 1.001 | 27.7034 | 4187 | 0.00661 | 7.3222 | 7.3288 | -1.767 | 151.2852 | 5569.1888 | -0.01168
194 |  | 1.001 | 27.6917 | 4187 | 0.0066072 | 7.3288 | 7.3354 | -1.767 | 151.349 | 5596.8805 | -0.011675
195 |  | 1.001 | 27.68 | 4187 | 0.0066045 | 7.3354 | 7.342 | -1.767 | 151.4128 | 5624.5606 | -0.01167
196 |  | 1.001 | 27.6684 | 4187 | 0.0066017 | 7.342 | 7.3486 | -1.767 | 151.4767 | 5652.2289 | -0.011665
197 |  | 1.001 | 27.6567 | 4187 | 0.0065989 | 7.3486 | 7.3552 | -1.767 | 151.5406 | 5679.8856 | -0.011661
198 |  | 1.001 | 27.645 | 4187 | 0.0065961 | 7.3552 | 7.3618 | -1.767 | 151.6045 | 5707.5307 | -0.011656
199 |  | 1.001 | 27.6334 | 4187 | 0.0065933 | 7.3618 | 7.3684 | -1.767 | 151.6685 | 5735.1641 | -0.011651
200 |  | 1.001 | 27.6217 | 4187 | 0.0065905 | 7.3684 | 7.375 | -1.767 | 151.7324 | 5762.7858 | -0.011646
201 |  | 1.001 | 27.6101 | 4187 | 0.0065878 | 7.375 | 7.3816 | -1.767 | 151.7964 | 5790.3959 | -0.011641
202 |  | 1.001 | 27.5984 | 4187 | 0.006585 | 7.3816 | 7.3882 | -1.767 | 151.8605 | 5817.9943 | -0.011636
203 |  | 1.001 | 27.5868 | 4187 | 0.0065822 | 7.3882 | 7.3948 | -1.767 | 151.9245 | 5845.5811 | -0.011631
204 |  | 1.001 | 27.5752 | 4187 | 0.0065794 | 7.3948 | 7.4013 | -1.767 | 151.9886 | 5873.1563 | -0.011626
205 |  | 1.001 | 27.5635 | 4187 | 0.0065767 | 7.4013 | 7.4079 | -1.767 | 152.0527 | 5900.7198 | -0.011621
206 |  | 1.001 | 27.5519 | 4187 | 0.0065739 | 7.4079 | 7.4145 | -1.767 | 152.1168 | 5928.2718 | -0.011616
207 |  | 1.001 | 27.5403 | 4187 | 0.0065711 | 7.4145 | 7.4211 | -1.767 | 152.181 | 5955.8121 | -0.011611
208 |  | 1.001 | 27.5287 | 4187 | 0.0065684 | 7.4211 | 7.4276 | -1.767 | 152.2452 | 5983.3408 | -0.011607
209 |  | 1.001 | 27.5171 | 4187 | 0.0065656 | 7.4276 | 7.4342 | -1.767 | 152.3094 | 6010.8579 | -0.011602
210 |  | 1.001 | 27.5055 | 4187 | 0.0065628 | 7.4342 | 7.4408 | -1.767 | 152.3736 | 6038.3634 | -0.011597
211 |  | 1.001 | 27.4939 | 4187 | 0.00656 | 7.4408 | 7.4473 | -1.767 | 152.4379 | 6065.8573 | -0.011592
212 |  | 1.001 | 27.4823 | 4187 | 0.0065573 | 7.4473 | 7.4539 | -1.767 | 152.5022 | 6093.3396 | -0.011587
213 |  | 1.001 | 27.4707 | 4187 | 0.0065545 | 7.4539 | 7.4604 | -1.767 | 152.5665 | 6120.8103 | -0.011582
214 |  | 1.001 | 27.4591 | 4187 | 0.0065518 | 7.4604 | 7.467 | -1.767 | 152.6309 | 6148.2694 | -0.011577
215 |  | 1.001 | 27.4476 | 4187 | 0.006549 | 7.467 | 7.4735 | -1.767 | 152.6953 | 6175.717 | -0.011572
216 |  | 1.001 | 27.436 | 4187 | 0.0065462 | 7.4735 | 7.4801 | -1.767 | 152.7597 | 6203.153 | -0.011567
217 |  | 1.001 | 27.4244 | 4187 | 0.0065435 | 7.4801 | 7.4866 | -1.767 | 152.8241 | 6230.5774 | -0.011563
218 |  | 1.001 | 27.4129 | 4187 | 0.0065407 | 7.4866 | 7.4932 | -1.767 | 152.8886 | 6257.9902 | -0.011558
219 |  | 1.001 | 27.4013 | 4187 | 0.006538 | 7.4932 | 7.4997 | -1.767 | 152.9531 | 6285.3915 | -0.011553
220 |  | 1.001 | 27.3897 | 4187 | 0.0065352 | 7.4997 | 7.5062 | -1.767 | 153.0176 | 6312.7813 | -0.011548
221 |  | 1.001 | 27.3782 | 4187 | 0.0065324 | 7.5062 | 7.5128 | -1.767 | 153.0821 | 6340.1595 | -0.011543
222 |  | 1.001 | 27.3667 | 4187 | 0.0065297 | 7.5128 | 7.5193 | -1.767 | 153.1467 | 6367.5261 | -0.011538
223 |  | 1.001 | 27.3551 | 4187 | 0.0065269 | 7.5193 | 7.5258 | -1.767 | 153.2113 | 6394.8812 | -0.011533
224 |  | 1.001 | 27.3436 | 4187 | 0.0065242 | 7.5258 | 7.5323 | -1.767 | 153.2759 | 6422.2248 | -0.011529
225 |  | 1.001 | 27.3321 | 4187 | 0.0065214 | 7.5323 | 7.5389 | -1.767 | 153.3406 | 6449.5569 | -0.011524
226 |  | 1.001 | 27.3205 | 4187 | 0.0065187 | 7.5389 | 7.5454 | -1.767 | 153.4052 | 6476.8774 | -0.011519
227 |  | 1.001 | 27.309 | 4187 | 0.0065159 | 7.5454 | 7.5519 | -1.767 | 153.4699 | 6504.1864 | -0.011514
228 |  | 1.001 | 27.2975 | 4187 | 0.0065132 | 7.5519 | 7.5584 | -1.767 | 153.5347 | 6531.4839 | -0.011509
229 |  | 1.001 | 27.286 | 4187 | 0.0065104 | 7.5584 | 7.5649 | -1.767 | 153.5994 | 6558.7699 | -0.011504
230 |  | 1.001 | 27.2745 | 4187 | 0.0065077 | 7.5649 | 7.5714 | -1.767 | 153.6642 | 6586.0444 | -0.011499
231 |  | 1.001 | 27.263 | 4187 | 0.006505 | 7.5714 | 7.5779 | -1.767 | 153.729 | 6613.3074 | -0.011495
232 |  | 1.001 | 27.2515 | 4187 | 0.0065022 | 7.5779 | 7.5844 | -1.767 | 153.7939 | 6640.5589 | -0.01149
233 |  | 1.001 | 27.24 | 4187 | 0.0064995 | 7.5844 | 7.5909 | -1.767 | 153.8587 | 6667.7989 | -0.011485
234 |  | 1.001 | 27.2285 | 4187 | 0.0064967 | 7.5909 | 7.5974 | -1.767 | 153.9236 | 6695.0274 | -0.01148
235 |  | 1.001 | 27.217 | 4187 | 0.006494 | 7.5974 | 7.6039 | -1.767 | 153.9886 | 6722.2444 | -0.011475
236 |  | 1.001 | 27.2056 | 4187 | 0.0064913 | 7.6039 | 7.6104 | -1.767 | 154.0535 | 6749.45 | -0.01147

## Cu50
|  |  | buis | verlies W/M | L /°C/sec
diam | wandikte |  | inhoud l/m |  | W/M
50.8 | 1.2 | 3.1416 | 1.8398 | 40.0635 | 4187
|  |  |  | 6 |  |  |  | J/sec/mtr | aantal mtr. | verlies
|  | buis | verlies W/M | L /°C/sec | verlies temp | begintemp | eindtemp | verlies | bij 1°C | totaal J/sec
|  | inhoud L |  | W/M | °C per M | °C | °C | per m°C | daling | aantal mtr
1 | 50.8 | 1.8398 | 40.0635 | 4187 | 0.0052007 | 6 | 6.0052 | -2.3567 | 192.2803 | 40.0635 | -0.012256
2 |  | 1.8398 | 40.0512 | 4187 | 0.0051991 | 6.0052 | 6.0104 | -2.3567 | 192.3392 | 80.1147 | -0.012253
3 |  | 1.8398 | 40.039 | 4187 | 0.0051976 | 6.0104 | 6.0156 | -2.3567 | 192.398 | 120.1537 | -0.012249
4 |  | 1.8398 | 40.0267 | 4187 | 0.005196 | 6.0156 | 6.0208 | -2.3567 | 192.4569 | 160.1804 | -0.012245
5 |  | 1.8398 | 40.0145 | 4187 | 0.0051944 | 6.0208 | 6.026 | -2.3567 | 192.5158 | 200.1949 | -0.012241
6 |  | 1.8398 | 40.0022 | 4187 | 0.0051928 | 6.026 | 6.0312 | -2.3567 | 192.5747 | 240.1971 | -0.012238
7 |  | 1.8398 | 39.99 | 4187 | 0.0051912 | 6.0312 | 6.0364 | -2.3567 | 192.6337 | 280.1871 | -0.012234
8 |  | 1.8398 | 39.9778 | 4187 | 0.0051896 | 6.0364 | 6.0416 | -2.3567 | 192.6926 | 320.1649 | -0.01223
9 |  | 1.8398 | 39.9655 | 4187 | 0.005188 | 6.0416 | 6.0467 | -2.3567 | 192.7516 | 360.1304 | -0.012226
10 |  | 1.8398 | 39.9533 | 4187 | 0.0051864 | 6.0467 | 6.0519 | -2.3567 | 192.8106 | 400.0837 | -0.012223
11 |  | 1.8398 | 39.9411 | 4187 | 0.0051849 | 6.0519 | 6.0571 | -2.3567 | 192.8696 | 440.0248 | -0.012219
12 |  | 1.8398 | 39.9289 | 4187 | 0.0051833 | 6.0571 | 6.0623 | -2.3567 | 192.9286 | 479.9537 | -0.012215
13 |  | 1.8398 | 39.9167 | 4187 | 0.0051817 | 6.0623 | 6.0675 | -2.3567 | 192.9876 | 519.8703 | -0.012212
14 |  | 1.8398 | 39.9044 | 4187 | 0.0051801 | 6.0675 | 6.0727 | -2.3567 | 193.0467 | 559.7748 | -0.012208
15 |  | 1.8398 | 39.8922 | 4187 | 0.0051785 | 6.0727 | 6.0778 | -2.3567 | 193.1058 | 599.667 | -0.012204
16 |  | 1.8398 | 39.88 | 4187 | 0.0051769 | 6.0778 | 6.083 | -2.3567 | 193.1649 | 639.547 | -0.0122
17 |  | 1.8398 | 39.8678 | 4187 | 0.0051753 | 6.083 | 6.0882 | -2.3567 | 193.224 | 679.4149 | -0.012197
18 |  | 1.8398 | 39.8556 | 4187 | 0.0051738 | 6.0882 | 6.0934 | -2.3567 | 193.2831 | 719.2705 | -0.012193
19 |  | 1.8398 | 39.8434 | 4187 | 0.0051722 | 6.0934 | 6.0985 | -2.3567 | 193.3422 | 759.1139 | -0.012189
20 |  | 1.8398 | 39.8312 | 4187 | 0.0051706 | 6.0985 | 6.1037 | -2.3567 | 193.4014 | 798.9452 | -0.012185
21 |  | 1.8398 | 39.8191 | 4187 | 0.005169 | 6.1037 | 6.1089 | -2.3567 | 193.4606 | 838.7642 | -0.012182
22 |  | 1.8398 | 39.8069 | 4187 | 0.0051674 | 6.1089 | 6.114 | -2.3567 | 193.5198 | 878.5711 | -0.012178
23 |  | 1.8398 | 39.7947 | 4187 | 0.0051658 | 6.114 | 6.1192 | -2.3567 | 193.579 | 918.3658 | -0.012174
24 |  | 1.8398 | 39.7825 | 4187 | 0.0051643 | 6.1192 | 6.1244 | -2.3567 | 193.6383 | 958.1484 | -0.012171
25 |  | 1.8398 | 39.7704 | 4187 | 0.0051627 | 6.1244 | 6.1295 | -2.3567 | 193.6975 | 997.9187 | -0.012167
26 |  | 1.8398 | 39.7582 | 4187 | 0.0051611 | 6.1295 | 6.1347 | -2.3567 | 193.7568 | 1037.6769 | -0.012163
27 |  | 1.8398 | 39.746 | 4187 | 0.0051595 | 6.1347 | 6.1399 | -2.3567 | 193.8161 | 1077.4229 | -0.012159
28 |  | 1.8398 | 39.7339 | 4187 | 0.005158 | 6.1399 | 6.145 | -2.3567 | 193.8754 | 1117.1568 | -0.012156
29 |  | 1.8398 | 39.7217 | 4187 | 0.0051564 | 6.145 | 6.1502 | -2.3567 | 193.9347 | 1156.8785 | -0.012152
30 |  | 1.8398 | 39.7096 | 4187 | 0.0051548 | 6.1502 | 6.1553 | -2.3567 | 193.9941 | 1196.5881 | -0.012148
31 |  | 1.8398 | 39.6974 | 4187 | 0.0051532 | 6.1553 | 6.1605 | -2.3567 | 194.0534 | 1236.2855 | -0.012144
32 |  | 1.8398 | 39.6853 | 4187 | 0.0051516 | 6.1605 | 6.1656 | -2.3567 | 194.1128 | 1275.9708 | -0.012141
33 |  | 1.8398 | 39.6731 | 4187 | 0.0051501 | 6.1656 | 6.1708 | -2.3567 | 194.1722 | 1315.6439 | -0.012137
34 |  | 1.8398 | 39.661 | 4187 | 0.0051485 | 6.1708 | 6.1759 | -2.3567 | 194.2316 | 1355.3049 | -0.012133
35 |  | 1.8398 | 39.6489 | 4187 | 0.0051469 | 6.1759 | 6.1811 | -2.3567 | 194.2911 | 1394.9537 | -0.01213
36 |  | 1.8398 | 39.6367 | 4187 | 0.0051453 | 6.1811 | 6.1862 | -2.3567 | 194.3505 | 1434.5905 | -0.012126
37 |  | 1.8398 | 39.6246 | 4187 | 0.0051438 | 6.1862 | 6.1914 | -2.3567 | 194.41 | 1474.2151 | -0.012122
38 |  | 1.8398 | 39.6125 | 4187 | 0.0051422 | 6.1914 | 6.1965 | -2.3567 | 194.4695 | 1513.8276 | -0.012118
39 |  | 1.8398 | 39.6004 | 4187 | 0.0051406 | 6.1965 | 6.2017 | -2.3567 | 194.529 | 1553.4279 | -0.012115
40 |  | 1.8398 | 39.5882 | 4187 | 0.005139 | 6.2017 | 6.2068 | -2.3567 | 194.5886 | 1593.0162 | -0.012111
41 |  | 1.8398 | 39.5761 | 4187 | 0.0051375 | 6.2068 | 6.2119 | -2.3567 | 194.6481 | 1632.5923 | -0.012107
42 |  | 1.8398 | 39.564 | 4187 | 0.0051359 | 6.2119 | 6.2171 | -2.3567 | 194.7077 | 1672.1563 | -0.012104
43 |  | 1.8398 | 39.5519 | 4187 | 0.0051343 | 6.2171 | 6.2222 | -2.3567 | 194.7673 | 1711.7083 | -0.0121
44 |  | 1.8398 | 39.5398 | 4187 | 0.0051328 | 6.2222 | 6.2273 | -2.3567 | 194.8269 | 1751.2481 | -0.012096
45 |  | 1.8398 | 39.5277 | 4187 | 0.0051312 | 6.2273 | 6.2325 | -2.3567 | 194.8865 | 1790.7758 | -0.012093
46 |  | 1.8398 | 39.5156 | 4187 | 0.0051296 | 6.2325 | 6.2376 | -2.3567 | 194.9461 | 1830.2915 | -0.012089
47 |  | 1.8398 | 39.5035 | 4187 | 0.0051281 | 6.2376 | 6.2427 | -2.3567 | 195.0058 | 1869.795 | -0.012085
48 |  | 1.8398 | 39.4915 | 4187 | 0.0051265 | 6.2427 | 6.2478 | -2.3567 | 195.0654 | 1909.2865 | -0.012081
49 |  | 1.8398 | 39.4794 | 4187 | 0.0051249 | 6.2478 | 6.253 | -2.3567 | 195.1251 | 1948.7658 | -0.012078
50 |  | 1.8398 | 39.4673 | 4187 | 0.0051233 | 6.253 | 6.2581 | -2.3567 | 195.1849 | 1988.2331 | -0.012074
51 |  | 1.8398 | 39.4552 | 4187 | 0.0051218 | 6.2581 | 6.2632 | -2.3567 | 195.2446 | 2027.6884 | -0.01207
52 |  | 1.8398 | 39.4432 | 4187 | 0.0051202 | 6.2632 | 6.2683 | -2.3567 | 195.3043 | 2067.1315 | -0.012067
53 |  | 1.8398 | 39.4311 | 4187 | 0.0051186 | 6.2683 | 6.2735 | -2.3567 | 195.3641 | 2106.5626 | -0.012063
54 |  | 1.8398 | 39.419 | 4187 | 0.0051171 | 6.2735 | 6.2786 | -2.3567 | 195.4239 | 2145.9817 | -0.012059
55 |  | 1.8398 | 39.407 | 4187 | 0.0051155 | 6.2786 | 6.2837 | -2.3567 | 195.4837 | 2185.3886 | -0.012056
56 |  | 1.8398 | 39.3949 | 4187 | 0.005114 | 6.2837 | 6.2888 | -2.3567 | 195.5435 | 2224.7835 | -0.012052
57 |  | 1.8398 | 39.3829 | 4187 | 0.0051124 | 6.2888 | 6.2939 | -2.3567 | 195.6033 | 2264.1664 | -0.012048
58 |  | 1.8398 | 39.3708 | 4187 | 0.0051108 | 6.2939 | 6.299 | -2.3567 | 195.6632 | 2303.5372 | -0.012045
59 |  | 1.8398 | 39.3588 | 4187 | 0.0051093 | 6.299 | 6.3041 | -2.3567 | 195.7231 | 2342.896 | -0.012041
60 |  | 1.8398 | 39.3467 | 4187 | 0.0051077 | 6.3041 | 6.3092 | -2.3567 | 195.783 | 2382.2427 | -0.012037
61 |  | 1.8398 | 39.3347 | 4187 | 0.0051061 | 6.3092 | 6.3144 | -2.3567 | 195.8429 | 2421.5774 | -0.012033
62 |  | 1.8398 | 39.3227 | 4187 | 0.0051046 | 6.3144 | 6.3195 | -2.3567 | 195.9028 | 2460.9001 | -0.01203
63 |  | 1.8398 | 39.3106 | 4187 | 0.005103 | 6.3195 | 6.3246 | -2.3567 | 195.9628 | 2500.2107 | -0.012026
64 |  | 1.8398 | 39.2986 | 4187 | 0.0051014 | 6.3246 | 6.3297 | -2.3567 | 196.0227 | 2539.5093 | -0.012022
65 |  | 1.8398 | 39.2866 | 4187 | 0.0050999 | 6.3297 | 6.3348 | -2.3567 | 196.0827 | 2578.7959 | -0.012019
66 |  | 1.8398 | 39.2746 | 4187 | 0.0050983 | 6.3348 | 6.3399 | -2.3567 | 196.1427 | 2618.0704 | -0.012015
67 |  | 1.8398 | 39.2625 | 4187 | 0.0050968 | 6.3399 | 6.345 | -2.3567 | 196.2028 | 2657.333 | -0.012011
68 |  | 1.8398 | 39.2505 | 4187 | 0.0050952 | 6.345 | 6.3501 | -2.3567 | 196.2628 | 2696.5835 | -0.012008
69 |  | 1.8398 | 39.2385 | 4187 | 0.0050937 | 6.3501 | 6.3551 | -2.3567 | 196.3229 | 2735.8221 | -0.012004
70 |  | 1.8398 | 39.2265 | 4187 | 0.0050921 | 6.3551 | 6.3602 | -2.3567 | 196.3829 | 2775.0486 | -0.012
71 |  | 1.8398 | 39.2145 | 4187 | 0.0050905 | 6.3602 | 6.3653 | -2.3567 | 196.443 | 2814.2631 | -0.011997
72 |  | 1.8398 | 39.2025 | 4187 | 0.005089 | 6.3653 | 6.3704 | -2.3567 | 196.5032 | 2853.4656 | -0.011993
73 |  | 1.8398 | 39.1905 | 4187 | 0.0050874 | 6.3704 | 6.3755 | -2.3567 | 196.5633 | 2892.6562 | -0.011989
74 |  | 1.8398 | 39.1785 | 4187 | 0.0050859 | 6.3755 | 6.3806 | -2.3567 | 196.6234 | 2931.8347 | -0.011986
75 |  | 1.8398 | 39.1666 | 4187 | 0.0050843 | 6.3806 | 6.3857 | -2.3567 | 196.6836 | 2971.0013 | -0.011982
76 |  | 1.8398 | 39.1546 | 4187 | 0.0050828 | 6.3857 | 6.3908 | -2.3567 | 196.7438 | 3010.1558 | -0.011978
77 |  | 1.8398 | 39.1426 | 4187 | 0.0050812 | 6.3908 | 6.3958 | -2.3567 | 196.804 | 3049.2984 | -0.011975
78 |  | 1.8398 | 39.1306 | 4187 | 0.0050796 | 6.3958 | 6.4009 | -2.3567 | 196.8642 | 3088.429 | -0.011971
79 |  | 1.8398 | 39.1187 | 4187 | 0.0050781 | 6.4009 | 6.406 | -2.3567 | 196.9245 | 3127.5477 | -0.011967
80 |  | 1.8398 | 39.1067 | 4187 | 0.0050765 | 6.406 | 6.4111 | -2.3567 | 196.9847 | 3166.6544 | -0.011964
81 |  | 1.8398 | 39.0947 | 4187 | 0.005075 | 6.4111 | 6.4161 | -2.3567 | 197.045 | 3205.7491 | -0.01196
82 |  | 1.8398 | 39.0828 | 4187 | 0.0050734 | 6.4161 | 6.4212 | -2.3567 | 197.1053 | 3244.8319 | -0.011956
83 |  | 1.8398 | 39.0708 | 4187 | 0.0050719 | 6.4212 | 6.4263 | -2.3567 | 197.1656 | 3283.9027 | -0.011953
84 |  | 1.8398 | 39.0589 | 4187 | 0.0050703 | 6.4263 | 6.4314 | -2.3567 | 197.226 | 3322.9615 | -0.011949
85 |  | 1.8398 | 39.0469 | 4187 | 0.0050688 | 6.4314 | 6.4364 | -2.3567 | 197.2863 | 3362.0084 | -0.011945
86 |  | 1.8398 | 39.035 | 4187 | 0.0050672 | 6.4364 | 6.4415 | -2.3567 | 197.3467 | 3401.0434 | -0.011942
87 |  | 1.8398 | 39.023 | 4187 | 0.0050657 | 6.4415 | 6.4466 | -2.3567 | 197.4071 | 3440.0664 | -0.011938
88 |  | 1.8398 | 39.0111 | 4187 | 0.0050641 | 6.4466 | 6.4516 | -2.3567 | 197.4675 | 3479.0775 | -0.011934
89 |  | 1.8398 | 38.9991 | 4187 | 0.0050626 | 6.4516 | 6.4567 | -2.3567 | 197.5279 | 3518.0766 | -0.011931
90 |  | 1.8398 | 38.9872 | 4187 | 0.005061 | 6.4567 | 6.4618 | -2.3567 | 197.5884 | 3557.0638 | -0.011927
91 |  | 1.8398 | 38.9753 | 4187 | 0.0050595 | 6.4618 | 6.4668 | -2.3567 | 197.6488 | 3596.0391 | -0.011924
92 |  | 1.8398 | 38.9634 | 4187 | 0.0050579 | 6.4668 | 6.4719 | -2.3567 | 197.7093 | 3635.0025 | -0.01192
93 |  | 1.8398 | 38.9514 | 4187 | 0.0050564 | 6.4719 | 6.4769 | -2.3567 | 197.7698 | 3673.9539 | -0.011916
94 |  | 1.8398 | 38.9395 | 4187 | 0.0050548 | 6.4769 | 6.482 | -2.3567 | 197.8304 | 3712.8934 | -0.011913
95 |  | 1.8398 | 38.9276 | 4187 | 0.0050533 | 6.482 | 6.487 | -2.3567 | 197.8909 | 3751.821 | -0.011909
96 |  | 1.8398 | 38.9157 | 4187 | 0.0050517 | 6.487 | 6.4921 | -2.3567 | 197.9515 | 3790.7367 | -0.011905
97 |  | 1.8398 | 38.9038 | 4187 | 0.0050502 | 6.4921 | 6.4971 | -2.3567 | 198.012 | 3829.6405 | -0.011902
98 |  | 1.8398 | 38.8919 | 4187 | 0.0050487 | 6.4971 | 6.5022 | -2.3567 | 198.0726 | 3868.5324 | -0.011898
99 |  | 1.8398 | 38.88 | 4187 | 0.0050471 | 6.5022 | 6.5072 | -2.3567 | 198.1332 | 3907.4124 | -0.011894
100 |  | 1.8398 | 38.8681 | 4187 | 0.0050456 | 6.5072 | 6.5123 | -2.3567 | 198.1939 | 3946.2805 | -0.011891
101 |  | 1.8398 | 38.8562 | 4187 | 0.005044 | 6.5123 | 6.5173 | -2.3567 | 198.2545 | 3985.1367 | -0.011887
102 |  | 1.8398 | 38.8443 | 4187 | 0.0050425 | 6.5173 | 6.5224 | -2.3567 | 198.3152 | 4023.9811 | -0.011883
103 |  | 1.8398 | 38.8324 | 4187 | 0.0050409 | 6.5224 | 6.5274 | -2.3567 | 198.3759 | 4062.8135 | -0.01188
104 |  | 1.8398 | 38.8206 | 4187 | 0.0050394 | 6.5274 | 6.5324 | -2.3567 | 198.4366 | 4101.6341 | -0.011876
105 |  | 1.8398 | 38.8087 | 4187 | 0.0050379 | 6.5324 | 6.5375 | -2.3567 | 198.4973 | 4140.4428 | -0.011873
106 |  | 1.8398 | 38.7968 | 4187 | 0.0050363 | 6.5375 | 6.5425 | -2.3567 | 198.5581 | 4179.2396 | -0.011869
107 |  | 1.8398 | 38.7849 | 4187 | 0.0050348 | 6.5425 | 6.5476 | -2.3567 | 198.6188 | 4218.0245 | -0.011865
108 |  | 1.8398 | 38.7731 | 4187 | 0.0050332 | 6.5476 | 6.5526 | -2.3567 | 198.6796 | 4256.7976 | -0.011862
109 |  | 1.8398 | 38.7612 | 4187 | 0.0050317 | 6.5526 | 6.5576 | -2.3567 | 198.7404 | 4295.5588 | -0.011858
110 |  | 1.8398 | 38.7494 | 4187 | 0.0050302 | 6.5576 | 6.5626 | -2.3567 | 198.8012 | 4334.3082 | -0.011854
111 |  | 1.8398 | 38.7375 | 4187 | 0.0050286 | 6.5626 | 6.5677 | -2.3567 | 198.8621 | 4373.0457 | -0.011851
112 |  | 1.8398 | 38.7257 | 4187 | 0.0050271 | 6.5677 | 6.5727 | -2.3567 | 198.9229 | 4411.7713 | -0.011847
113 |  | 1.8398 | 38.7138 | 4187 | 0.0050255 | 6.5727 | 6.5777 | -2.3567 | 198.9838 | 4450.4851 | -0.011844
114 |  | 1.8398 | 38.702 | 4187 | 0.005024 | 6.5777 | 6.5828 | -2.3567 | 199.0447 | 4489.1871 | -0.01184
115 |  | 1.8398 | 38.6901 | 4187 | 0.0050225 | 6.5828 | 6.5878 | -2.3567 | 199.1056 | 4527.8772 | -0.011836
116 |  | 1.8398 | 38.6783 | 4187 | 0.0050209 | 6.5878 | 6.5928 | -2.3567 | 199.1665 | 4566.5555 | -0.011833
117 |  | 1.8398 | 38.6665 | 4187 | 0.0050194 | 6.5928 | 6.5978 | -2.3567 | 199.2275 | 4605.222 | -0.011829
118 |  | 1.8398 | 38.6546 | 4187 | 0.0050179 | 6.5978 | 6.6028 | -2.3567 | 199.2884 | 4643.8766 | -0.011825
119 |  | 1.8398 | 38.6428 | 4187 | 0.0050163 | 6.6028 | 6.6078 | -2.3567 | 199.3494 | 4682.5194 | -0.011822
120 |  | 1.8398 | 38.631 | 4187 | 0.0050148 | 6.6078 | 6.6129 | -2.3567 | 199.4104 | 4721.1504 | -0.011818
121 |  | 1.8398 | 38.6192 | 4187 | 0.0050132 | 6.6129 | 6.6179 | -2.3567 | 199.4715 | 4759.7695 | -0.011815
122 |  | 1.8398 | 38.6073 | 4187 | 0.0050117 | 6.6179 | 6.6229 | -2.3567 | 199.5325 | 4798.3769 | -0.011811
123 |  | 1.8398 | 38.5955 | 4187 | 0.0050102 | 6.6229 | 6.6279 | -2.3567 | 199.5936 | 4836.9724 | -0.011807
124 |  | 1.8398 | 38.5837 | 4187 | 0.0050086 | 6.6279 | 6.6329 | -2.3567 | 199.6546 | 4875.5561 | -0.011804
125 |  | 1.8398 | 38.5719 | 4187 | 0.0050071 | 6.6329 | 6.6379 | -2.3567 | 199.7157 | 4914.1281 | -0.0118
126 |  | 1.8398 | 38.5601 | 4187 | 0.0050056 | 6.6379 | 6.6429 | -2.3567 | 199.7768 | 4952.6882 | -0.011797
127 |  | 1.8398 | 38.5483 | 4187 | 0.0050041 | 6.6429 | 6.6479 | -2.3567 | 199.838 | 4991.2365 | -0.011793
128 |  | 1.8398 | 38.5365 | 4187 | 0.0050025 | 6.6479 | 6.6529 | -2.3567 | 199.8991 | 5029.773 | -0.011789
129 |  | 1.8398 | 38.5247 | 4187 | 0.005001 | 6.6529 | 6.6579 | -2.3567 | 199.9603 | 5068.2978 | -0.011786
130 |  | 1.8398 | 38.513 | 4187 | 0.0049995 | 6.6579 | 6.6629 | -2.3567 | 200.0215 | 5106.8107 | -0.011782
131 |  | 1.8398 | 38.5012 | 4187 | 0.0049979 | 6.6629 | 6.6679 | -2.3567 | 200.0827 | 5145.3119 | -0.011779
132 |  | 1.8398 | 38.4894 | 4187 | 0.0049964 | 6.6679 | 6.6729 | -2.3567 | 200.1439 | 5183.8013 | -0.011775
133 |  | 1.8398 | 38.4776 | 4187 | 0.0049949 | 6.6729 | 6.6779 | -2.3567 | 200.2052 | 5222.2789 | -0.011771
134 |  | 1.8398 | 38.4659 | 4187 | 0.0049933 | 6.6779 | 6.6829 | -2.3567 | 200.2665 | 5260.7448 | -0.011768
135 |  | 1.8398 | 38.4541 | 4187 | 0.0049918 | 6.6829 | 6.6879 | -2.3567 | 200.3277 | 5299.1989 | -0.011764
136 |  | 1.8398 | 38.4423 | 4187 | 0.0049903 | 6.6879 | 6.6929 | -2.3567 | 200.389 | 5337.6412 | -0.01176
137 |  | 1.8398 | 38.4306 | 4187 | 0.0049888 | 6.6929 | 6.6979 | -2.3567 | 200.4504 | 5376.0718 | -0.011757
138 |  | 1.8398 | 38.4188 | 4187 | 0.0049872 | 6.6979 | 6.7029 | -2.3567 | 200.5117 | 5414.4906 | -0.011753
139 |  | 1.8398 | 38.407 | 4187 | 0.0049857 | 6.7029 | 6.7079 | -2.3567 | 200.5731 | 5452.8976 | -0.01175
140 |  | 1.8398 | 38.3953 | 4187 | 0.0049842 | 6.7079 | 6.7128 | -2.3567 | 200.6345 | 5491.2929 | -0.011746
141 |  | 1.8398 | 38.3836 | 4187 | 0.0049827 | 6.7128 | 6.7178 | -2.3567 | 200.6959 | 5529.6765 | -0.011743
142 |  | 1.8398 | 38.3718 | 4187 | 0.0049811 | 6.7178 | 6.7228 | -2.3567 | 200.7573 | 5568.0483 | -0.011739
143 |  | 1.8398 | 38.3601 | 4187 | 0.0049796 | 6.7228 | 6.7278 | -2.3567 | 200.8187 | 5606.4083 | -0.011735
144 |  | 1.8398 | 38.3483 | 4187 | 0.0049781 | 6.7278 | 6.7328 | -2.3567 | 200.8802 | 5644.7567 | -0.011732
145 |  | 1.8398 | 38.3366 | 4187 | 0.0049766 | 6.7328 | 6.7377 | -2.3567 | 200.9416 | 5683.0933 | -0.011728
146 |  | 1.8398 | 38.3249 | 4187 | 0.004975 | 6.7377 | 6.7427 | -2.3567 | 201.0031 | 5721.4182 | -0.011725
147 |  | 1.8398 | 38.3132 | 4187 | 0.0049735 | 6.7427 | 6.7477 | -2.3567 | 201.0646 | 5759.7313 | -0.011721
148 |  | 1.8398 | 38.3014 | 4187 | 0.004972 | 6.7477 | 6.7527 | -2.3567 | 201.1262 | 5798.0327 | -0.011717
149 |  | 1.8398 | 38.2897 | 4187 | 0.0049705 | 6.7527 | 6.7576 | -2.3567 | 201.1877 | 5836.3224 | -0.011714
150 |  | 1.8398 | 38.278 | 4187 | 0.004969 | 6.7576 | 6.7626 | -2.3567 | 201.2493 | 5874.6004 | -0.01171
151 |  | 1.8398 | 38.2663 | 4187 | 0.0049674 | 6.7626 | 6.7676 | -2.3567 | 201.3109 | 5912.8667 | -0.011707
152 |  | 1.8398 | 38.2546 | 4187 | 0.0049659 | 6.7676 | 6.7725 | -2.3567 | 201.3725 | 5951.1213 | -0.011703
153 |  | 1.8398 | 38.2429 | 4187 | 0.0049644 | 6.7725 | 6.7775 | -2.3567 | 201.4341 | 5989.3642 | -0.011699
154 |  | 1.8398 | 38.2312 | 4187 | 0.0049629 | 6.7775 | 6.7825 | -2.3567 | 201.4957 | 6027.5954 | -0.011696
155 |  | 1.8398 | 38.2195 | 4187 | 0.0049614 | 6.7825 | 6.7874 | -2.3567 | 201.5574 | 6065.8149 | -0.011692
156 |  | 1.8398 | 38.2078 | 4187 | 0.0049598 | 6.7874 | 6.7924 | -2.3567 | 201.6191 | 6104.0227 | -0.011689
157 |  | 1.8398 | 38.1961 | 4187 | 0.0049583 | 6.7924 | 6.7973 | -2.3567 | 201.6808 | 6142.2188 | -0.011685
158 |  | 1.8398 | 38.1844 | 4187 | 0.0049568 | 6.7973 | 6.8023 | -2.3567 | 201.7425 | 6180.4032 | -0.011682
159 |  | 1.8398 | 38.1727 | 4187 | 0.0049553 | 6.8023 | 6.8072 | -2.3567 | 201.8042 | 6218.5759 | -0.011678
160 |  | 1.8398 | 38.1611 | 4187 | 0.0049538 | 6.8072 | 6.8122 | -2.3567 | 201.866 | 6256.737 | -0.011674
161 |  | 1.8398 | 38.1494 | 4187 | 0.0049523 | 6.8122 | 6.8172 | -2.3567 | 201.9278 | 6294.8864 | -0.011671
162 |  | 1.8398 | 38.1377 | 4187 | 0.0049508 | 6.8172 | 6.8221 | -2.3567 | 201.9896 | 6333.0241 | -0.011667
163 |  | 1.8398 | 38.126 | 4187 | 0.0049492 | 6.8221 | 6.8271 | -2.3567 | 202.0514 | 6371.1501 | -0.011664
164 |  | 1.8398 | 38.1144 | 4187 | 0.0049477 | 6.8271 | 6.832 | -2.3567 | 202.1132 | 6409.2645 | -0.01166
165 |  | 1.8398 | 38.1027 | 4187 | 0.0049462 | 6.832 | 6.8369 | -2.3567 | 202.1751 | 6447.3672 | -0.011657
166 |  | 1.8398 | 38.0911 | 4187 | 0.0049447 | 6.8369 | 6.8419 | -2.3567 | 202.2369 | 6485.4583 | -0.011653
167 |  | 1.8398 | 38.0794 | 4187 | 0.0049432 | 6.8419 | 6.8468 | -2.3567 | 202.2988 | 6523.5377 | -0.011649
168 |  | 1.8398 | 38.0678 | 4187 | 0.0049417 | 6.8468 | 6.8518 | -2.3567 | 202.3607 | 6561.6055 | -0.011646
169 |  | 1.8398 | 38.0561 | 4187 | 0.0049402 | 6.8518 | 6.8567 | -2.3567 | 202.4226 | 6599.6616 | -0.011642
170 |  | 1.8398 | 38.0445 | 4187 | 0.0049386 | 6.8567 | 6.8617 | -2.3567 | 202.4846 | 6637.706 | -0.011639
171 |  | 1.8398 | 38.0328 | 4187 | 0.0049371 | 6.8617 | 6.8666 | -2.3567 | 202.5466 | 6675.7389 | -0.011635
172 |  | 1.8398 | 38.0212 | 4187 | 0.0049356 | 6.8666 | 6.8715 | -2.3567 | 202.6085 | 6713.7601 | -0.011632
173 |  | 1.8398 | 38.0096 | 4187 | 0.0049341 | 6.8715 | 6.8765 | -2.3567 | 202.6705 | 6751.7697 | -0.011628
174 |  | 1.8398 | 37.9979 | 4187 | 0.0049326 | 6.8765 | 6.8814 | -2.3567 | 202.7326 | 6789.7676 | -0.011625
175 |  | 1.8398 | 37.9863 | 4187 | 0.0049311 | 6.8814 | 6.8863 | -2.3567 | 202.7946 | 6827.7539 | -0.011621
176 |  | 1.8398 | 37.9747 | 4187 | 0.0049296 | 6.8863 | 6.8913 | -2.3567 | 202.8567 | 6865.7286 | -0.011617
177 |  | 1.8398 | 37.9631 | 4187 | 0.0049281 | 6.8913 | 6.8962 | -2.3567 | 202.9187 | 6903.6917 | -0.011614
178 |  | 1.8398 | 37.9515 | 4187 | 0.0049266 | 6.8962 | 6.9011 | -2.3567 | 202.9808 | 6941.6431 | -0.01161
179 |  | 1.8398 | 37.9399 | 4187 | 0.0049251 | 6.9011 | 6.906 | -2.3567 | 203.043 | 6979.583 | -0.011607
180 |  | 1.8398 | 37.9282 | 4187 | 0.0049236 | 6.906 | 6.911 | -2.3567 | 203.1051 | 7017.5112 | -0.011603
181 |  | 1.8398 | 37.9166 | 4187 | 0.0049221 | 6.911 | 6.9159 | -2.3567 | 203.1672 | 7055.4279 | -0.0116
182 |  | 1.8398 | 37.905 | 4187 | 0.0049205 | 6.9159 | 6.9208 | -2.3567 | 203.2294 | 7093.3329 | -0.011596
183 |  | 1.8398 | 37.8934 | 4187 | 0.004919 | 6.9208 | 6.9257 | -2.3567 | 203.2916 | 7131.2264 | -0.011593
184 |  | 1.8398 | 37.8819 | 4187 | 0.0049175 | 6.9257 | 6.9306 | -2.3567 | 203.3538 | 7169.1082 | -0.011589
185 |  | 1.8398 | 37.8703 | 4187 | 0.004916 | 6.9306 | 6.9356 | -2.3567 | 203.416 | 7206.9785 | -0.011585
186 |  | 1.8398 | 37.8587 | 4187 | 0.0049145 | 6.9356 | 6.9405 | -2.3567 | 203.4783 | 7244.8372 | -0.011582
187 |  | 1.8398 | 37.8471 | 4187 | 0.004913 | 6.9405 | 6.9454 | -2.3567 | 203.5406 | 7282.6843 | -0.011578
188 |  | 1.8398 | 37.8355 | 4187 | 0.0049115 | 6.9454 | 6.9503 | -2.3567 | 203.6029 | 7320.5198 | -0.011575
189 |  | 1.8398 | 37.8239 | 4187 | 0.00491 | 6.9503 | 6.9552 | -2.3567 | 203.6652 | 7358.3437 | -0.011571
190 |  | 1.8398 | 37.8124 | 4187 | 0.0049085 | 6.9552 | 6.9601 | -2.3567 | 203.7275 | 7396.1561 | -0.011568
191 |  | 1.8398 | 37.8008 | 4187 | 0.004907 | 6.9601 | 6.965 | -2.3567 | 203.7898 | 7433.9569 | -0.011564
192 |  | 1.8398 | 37.7892 | 4187 | 0.0049055 | 6.965 | 6.9699 | -2.3567 | 203.8522 | 7471.7462 | -0.011561
193 |  | 1.8398 | 37.7777 | 4187 | 0.004904 | 6.9699 | 6.9748 | -2.3567 | 203.9146 | 7509.5238 | -0.011557
194 |  | 1.8398 | 37.7661 | 4187 | 0.0049025 | 6.9748 | 6.9797 | -2.3567 | 203.977 | 7547.29 | -0.011554
195 |  | 1.8398 | 37.7546 | 4187 | 0.004901 | 6.9797 | 6.9846 | -2.3567 | 204.0394 | 7585.0445 | -0.01155
196 |  | 1.8398 | 37.743 | 4187 | 0.0048995 | 6.9846 | 6.9895 | -2.3567 | 204.1018 | 7622.7876 | -0.011547
197 |  | 1.8398 | 37.7315 | 4187 | 0.004898 | 6.9895 | 6.9944 | -2.3567 | 204.1643 | 7660.519 | -0.011543
198 |  | 1.8398 | 37.7199 | 4187 | 0.0048965 | 6.9944 | 6.9993 | -2.3567 | 204.2268 | 7698.239 | -0.01154
199 |  | 1.8398 | 37.7084 | 4187 | 0.004895 | 6.9993 | 7.0042 | -2.3567 | 204.2893 | 7735.9474 | -0.011536
200 |  | 1.8398 | 37.6969 | 4187 | 0.0048935 | 7.0042 | 7.0091 | -2.3567 | 204.3518 | 7773.6442 | -0.011532
201 |  | 1.8398 | 37.6853 | 4187 | 0.004892 | 7.0091 | 7.014 | -2.3567 | 204.4143 | 7811.3295 | -0.011529
202 |  | 1.8398 | 37.6738 | 4187 | 0.0048905 | 7.014 | 7.0189 | -2.3567 | 204.4769 | 7849.0033 | -0.011525
203 |  | 1.8398 | 37.6623 | 4187 | 0.004889 | 7.0189 | 7.0238 | -2.3567 | 204.5395 | 7886.6656 | -0.011522
204 |  | 1.8398 | 37.6507 | 4187 | 0.0048875 | 7.0238 | 7.0287 | -2.3567 | 204.602 | 7924.3163 | -0.011518
205 |  | 1.8398 | 37.6392 | 4187 | 0.004886 | 7.0287 | 7.0336 | -2.3567 | 204.6647 | 7961.9556 | -0.011515
206 |  | 1.8398 | 37.6277 | 4187 | 0.0048845 | 7.0336 | 7.0384 | -2.3567 | 204.7273 | 7999.5833 | -0.011511
207 |  | 1.8398 | 37.6162 | 4187 | 0.0048831 | 7.0384 | 7.0433 | -2.3567 | 204.7899 | 8037.1995 | -0.011508
208 |  | 1.8398 | 37.6047 | 4187 | 0.0048816 | 7.0433 | 7.0482 | -2.3567 | 204.8526 | 8074.8042 | -0.011504
209 |  | 1.8398 | 37.5932 | 4187 | 0.0048801 | 7.0482 | 7.0531 | -2.3567 | 204.9153 | 8112.3974 | -0.011501
210 |  | 1.8398 | 37.5817 | 4187 | 0.0048786 | 7.0531 | 7.058 | -2.3567 | 204.978 | 8149.9791 | -0.011497
211 |  | 1.8398 | 37.5702 | 4187 | 0.0048771 | 7.058 | 7.0628 | -2.3567 | 205.0407 | 8187.5493 | -0.011494
212 |  | 1.8398 | 37.5587 | 4187 | 0.0048756 | 7.0628 | 7.0677 | -2.3567 | 205.1035 | 8225.108 | -0.01149
213 |  | 1.8398 | 37.5472 | 4187 | 0.0048741 | 7.0677 | 7.0726 | -2.3567 | 205.1662 | 8262.6552 | -0.011487
214 |  | 1.8398 | 37.5357 | 4187 | 0.0048726 | 7.0726 | 7.0775 | -2.3567 | 205.229 | 8300.1909 | -0.011483
215 |  | 1.8398 | 37.5242 | 4187 | 0.0048711 | 7.0775 | 7.0823 | -2.3567 | 205.2918 | 8337.7151 | -0.01148
216 |  | 1.8398 | 37.5128 | 4187 | 0.0048696 | 7.0823 | 7.0872 | -2.3567 | 205.3547 | 8375.2279 | -0.011476
217 |  | 1.8398 | 37.5013 | 4187 | 0.0048681 | 7.0872 | 7.0921 | -2.3567 | 205.4175 | 8412.7292 | -0.011473
218 |  | 1.8398 | 37.4898 | 4187 | 0.0048666 | 7.0921 | 7.0969 | -2.3567 | 205.4804 | 8450.219 | -0.011469
219 |  | 1.8398 | 37.4783 | 4187 | 0.0048652 | 7.0969 | 7.1018 | -2.3567 | 205.5432 | 8487.6973 | -0.011466
220 |  | 1.8398 | 37.4669 | 4187 | 0.0048637 | 7.1018 | 7.1067 | -2.3567 | 205.6061 | 8525.1642 | -0.011462
221 |  | 1.8398 | 37.4554 | 4187 | 0.0048622 | 7.1067 | 7.1115 | -2.3567 | 205.6691 | 8562.6196 | -0.011459
222 |  | 1.8398 | 37.444 | 4187 | 0.0048607 | 7.1115 | 7.1164 | -2.3567 | 205.732 | 8600.0636 | -0.011455
223 |  | 1.8398 | 37.4325 | 4187 | 0.0048592 | 7.1164 | 7.1213 | -2.3567 | 205.795 | 8637.4961 | -0.011452
224 |  | 1.8398 | 37.421 | 4187 | 0.0048577 | 7.1213 | 7.1261 | -2.3567 | 205.8579 | 8674.9171 | -0.011448
225 |  | 1.8398 | 37.4096 | 4187 | 0.0048562 | 7.1261 | 7.131 | -2.3567 | 205.9209 | 8712.3267 | -0.011445
226 |  | 1.8398 | 37.3982 | 4187 | 0.0048547 | 7.131 | 7.1358 | -2.3567 | 205.984 | 8749.7249 | -0.011441
227 |  | 1.8398 | 37.3867 | 4187 | 0.0048533 | 7.1358 | 7.1407 | -2.3567 | 206.047 | 8787.1116 | -0.011438
228 |  | 1.8398 | 37.3753 | 4187 | 0.0048518 | 7.1407 | 7.1455 | -2.3567 | 206.11 | 8824.4869 | -0.011434
229 |  | 1.8398 | 37.3638 | 4187 | 0.0048503 | 7.1455 | 7.1504 | -2.3567 | 206.1731 | 8861.8507 | -0.011431
230 |  | 1.8398 | 37.3524 | 4187 | 0.0048488 | 7.1504 | 7.1552 | -2.3567 | 206.2362 | 8899.2031 | -0.011427
231 |  | 1.8398 | 37.341 | 4187 | 0.0048473 | 7.1552 | 7.1601 | -2.3567 | 206.2993 | 8936.5441 | -0.011424
232 |  | 1.8398 | 37.3296 | 4187 | 0.0048458 | 7.1601 | 7.1649 | -2.3567 | 206.3625 | 8973.8737 | -0.01142
233 |  | 1.8398 | 37.3181 | 4187 | 0.0048444 | 7.1649 | 7.1698 | -2.3567 | 206.4256 | 9011.1918 | -0.011417
234 |  | 1.8398 | 37.3067 | 4187 | 0.0048429 | 7.1698 | 7.1746 | -2.3567 | 206.4888 | 9048.4985 | -0.011413
235 |  | 1.8398 | 37.2953 | 4187 | 0.0048414 | 7.1746 | 7.1794 | -2.3567 | 206.552 | 9085.7938 | -0.01141
236 |  | 1.8398 | 37.2839 | 4187 | 0.0048399 | 7.1794 | 7.1843 | -2.3567 | 206.6152 | 9123.0777 | -0.011406

## Cu63
|  |  | buis | verlies W/M | L /°C/sec
diam | wandikte |  | inhoud l/m |  | W/M
63.5 | 1.2 | 3.1416 | 2.9321 | 50.087 | 4187
[8 empty] | J/sec/mtr | aantal mtr. | verlies
|  | buis | verlies W/M | L /°C/sec | verlies temp | begintemp | eindtemp | verlies | bij 1°C | totaal J/sec
|  | inhoud L |  | W/M | °C per M | °C | °C | per m°C | daling | aantal mtr
1 | 63.5 | 2.9321 | 50.087 | 4187 | 0.0040799 | 6 | 6.0041 | -2.9463 | 245.104 | 50.087 | -0.012021
2 |  | 2.9321 | 50.075 | 4187 | 0.0040789 | 6.0041 | 6.0082 | -2.9463 | 245.1628 | 100.162 | -0.012018
3 |  | 2.9321 | 50.0629 | 4187 | 0.0040779 | 6.0082 | 6.0122 | -2.9463 | 245.2217 | 150.2249 | -0.012015
4 |  | 2.9321 | 50.0509 | 4187 | 0.004077 | 6.0122 | 6.0163 | -2.9463 | 245.2805 | 200.2758 | -0.012012
5 |  | 2.9321 | 50.0389 | 4187 | 0.004076 | 6.0163 | 6.0204 | -2.9463 | 245.3394 | 250.3148 | -0.012009
6 |  | 2.9321 | 50.0269 | 4187 | 0.004075 | 6.0204 | 6.0245 | -2.9463 | 245.3983 | 300.3417 | -0.012006
7 |  | 2.9321 | 50.0149 | 4187 | 0.004074 | 6.0245 | 6.0285 | -2.9463 | 245.4572 | 350.3566 | -0.012003
8 |  | 2.9321 | 50.0029 | 4187 | 0.0040731 | 6.0285 | 6.0326 | -2.9463 | 245.5161 | 400.3595 | -0.012
9 |  | 2.9321 | 49.9909 | 4187 | 0.0040721 | 6.0326 | 6.0367 | -2.9463 | 245.5751 | 450.3504 | -0.011998
10 |  | 2.9321 | 49.9789 | 4187 | 0.0040711 | 6.0367 | 6.0408 | -2.9463 | 245.634 | 500.3293 | -0.011995
11 |  | 2.9321 | 49.9669 | 4187 | 0.0040701 | 6.0408 | 6.0448 | -2.9463 | 245.693 | 550.2962 | -0.011992
12 |  | 2.9321 | 49.9549 | 4187 | 0.0040691 | 6.0448 | 6.0489 | -2.9463 | 245.752 | 600.2511 | -0.011989
13 |  | 2.9321 | 49.9429 | 4187 | 0.0040682 | 6.0489 | 6.053 | -2.9463 | 245.811 | 650.194 | -0.011986
14 |  | 2.9321 | 49.9309 | 4187 | 0.0040672 | 6.053 | 6.057 | -2.9463 | 245.87 | 700.125 | -0.011983
15 |  | 2.9321 | 49.919 | 4187 | 0.0040662 | 6.057 | 6.0611 | -2.9463 | 245.929 | 750.044 | -0.01198
16 |  | 2.9321 | 49.907 | 4187 | 0.0040652 | 6.0611 | 6.0652 | -2.9463 | 245.988 | 799.9509 | -0.011977
17 |  | 2.9321 | 49.895 | 4187 | 0.0040643 | 6.0652 | 6.0692 | -2.9463 | 246.0471 | 849.8459 | -0.011975
18 |  | 2.9321 | 49.883 | 4187 | 0.0040633 | 6.0692 | 6.0733 | -2.9463 | 246.1061 | 899.729 | -0.011972
19 |  | 2.9321 | 49.8711 | 4187 | 0.0040623 | 6.0733 | 6.0774 | -2.9463 | 246.1652 | 949.6 | -0.011969
20 |  | 2.9321 | 49.8591 | 4187 | 0.0040613 | 6.0774 | 6.0814 | -2.9463 | 246.2243 | 999.4591 | -0.011966
21 |  | 2.9321 | 49.8471 | 4187 | 0.0040604 | 6.0814 | 6.0855 | -2.9463 | 246.2834 | 1049.3062 | -0.011963
22 |  | 2.9321 | 49.8352 | 4187 | 0.0040594 | 6.0855 | 6.0895 | -2.9463 | 246.3425 | 1099.1414 | -0.01196
23 |  | 2.9321 | 49.8232 | 4187 | 0.0040584 | 6.0895 | 6.0936 | -2.9463 | 246.4017 | 1148.9646 | -0.011957
24 |  | 2.9321 | 49.8112 | 4187 | 0.0040574 | 6.0936 | 6.0976 | -2.9463 | 246.4608 | 1198.7758 | -0.011954
25 |  | 2.9321 | 49.7993 | 4187 | 0.0040565 | 6.0976 | 6.1017 | -2.9463 | 246.52 | 1248.5751 | -0.011952
26 |  | 2.9321 | 49.7873 | 4187 | 0.0040555 | 6.1017 | 6.1058 | -2.9463 | 246.5792 | 1298.3625 | -0.011949
27 |  | 2.9321 | 49.7754 | 4187 | 0.0040545 | 6.1058 | 6.1098 | -2.9463 | 246.6384 | 1348.1378 | -0.011946
28 |  | 2.9321 | 49.7634 | 4187 | 0.0040535 | 6.1098 | 6.1139 | -2.9463 | 246.6976 | 1397.9013 | -0.011943
29 |  | 2.9321 | 49.7515 | 4187 | 0.0040526 | 6.1139 | 6.1179 | -2.9463 | 246.7568 | 1447.6528 | -0.01194
30 |  | 2.9321 | 49.7396 | 4187 | 0.0040516 | 6.1179 | 6.122 | -2.9463 | 246.816 | 1497.3923 | -0.011937
31 |  | 2.9321 | 49.7276 | 4187 | 0.0040506 | 6.122 | 6.126 | -2.9463 | 246.8753 | 1547.12 | -0.011934
32 |  | 2.9321 | 49.7157 | 4187 | 0.0040497 | 6.126 | 6.1301 | -2.9463 | 246.9345 | 1596.8357 | -0.011931
33 |  | 2.9321 | 49.7038 | 4187 | 0.0040487 | 6.1301 | 6.1341 | -2.9463 | 246.9938 | 1646.5394 | -0.011929
34 |  | 2.9321 | 49.6918 | 4187 | 0.0040477 | 6.1341 | 6.1382 | -2.9463 | 247.0531 | 1696.2312 | -0.011926
35 |  | 2.9321 | 49.6799 | 4187 | 0.0040467 | 6.1382 | 6.1422 | -2.9463 | 247.1124 | 1745.9111 | -0.011923
36 |  | 2.9321 | 49.668 | 4187 | 0.0040458 | 6.1422 | 6.1463 | -2.9463 | 247.1717 | 1795.5791 | -0.01192
37 |  | 2.9321 | 49.6561 | 4187 | 0.0040448 | 6.1463 | 6.1503 | -2.9463 | 247.2311 | 1845.2352 | -0.011917
38 |  | 2.9321 | 49.6441 | 4187 | 0.0040438 | 6.1503 | 6.1543 | -2.9463 | 247.2904 | 1894.8793 | -0.011914
39 |  | 2.9321 | 49.6322 | 4187 | 0.0040429 | 6.1543 | 6.1584 | -2.9463 | 247.3498 | 1944.5115 | -0.011911
40 |  | 2.9321 | 49.6203 | 4187 | 0.0040419 | 6.1584 | 6.1624 | -2.9463 | 247.4091 | 1994.1319 | -0.011909
41 |  | 2.9321 | 49.6084 | 4187 | 0.0040409 | 6.1624 | 6.1665 | -2.9463 | 247.4685 | 2043.7403 | -0.011906
42 |  | 2.9321 | 49.5965 | 4187 | 0.0040399 | 6.1665 | 6.1705 | -2.9463 | 247.5279 | 2093.3368 | -0.011903
43 |  | 2.9321 | 49.5846 | 4187 | 0.004039 | 6.1705 | 6.1746 | -2.9463 | 247.5874 | 2142.9214 | -0.0119
44 |  | 2.9321 | 49.5727 | 4187 | 0.004038 | 6.1746 | 6.1786 | -2.9463 | 247.6468 | 2192.4941 | -0.011897
45 |  | 2.9321 | 49.5608 | 4187 | 0.004037 | 6.1786 | 6.1826 | -2.9463 | 247.7062 | 2242.0549 | -0.011894
46 |  | 2.9321 | 49.5489 | 4187 | 0.0040361 | 6.1826 | 6.1867 | -2.9463 | 247.7657 | 2291.6038 | -0.011891
47 |  | 2.9321 | 49.537 | 4187 | 0.0040351 | 6.1867 | 6.1907 | -2.9463 | 247.8252 | 2341.1408 | -0.011889
48 |  | 2.9321 | 49.5251 | 4187 | 0.0040341 | 6.1907 | 6.1947 | -2.9463 | 247.8847 | 2390.6659 | -0.011886
49 |  | 2.9321 | 49.5132 | 4187 | 0.0040332 | 6.1947 | 6.1988 | -2.9463 | 247.9442 | 2440.1791 | -0.011883
50 |  | 2.9321 | 49.5014 | 4187 | 0.0040322 | 6.1988 | 6.2028 | -2.9463 | 248.0037 | 2489.6805 | -0.01188
51 |  | 2.9321 | 49.4895 | 4187 | 0.0040312 | 6.2028 | 6.2068 | -2.9463 | 248.0632 | 2539.17 | -0.011877
52 |  | 2.9321 | 49.4776 | 4187 | 0.0040303 | 6.2068 | 6.2109 | -2.9463 | 248.1228 | 2588.6476 | -0.011874
53 |  | 2.9321 | 49.4657 | 4187 | 0.0040293 | 6.2109 | 6.2149 | -2.9463 | 248.1823 | 2638.1133 | -0.011871
54 |  | 2.9321 | 49.4539 | 4187 | 0.0040283 | 6.2149 | 6.2189 | -2.9463 | 248.2419 | 2687.5672 | -0.011869
55 |  | 2.9321 | 49.442 | 4187 | 0.0040274 | 6.2189 | 6.2229 | -2.9463 | 248.3015 | 2737.0092 | -0.011866
56 |  | 2.9321 | 49.4301 | 4187 | 0.0040264 | 6.2229 | 6.227 | -2.9463 | 248.3611 | 2786.4393 | -0.011863
57 |  | 2.9321 | 49.4183 | 4187 | 0.0040254 | 6.227 | 6.231 | -2.9463 | 248.4207 | 2835.8575 | -0.01186
58 |  | 2.9321 | 49.4064 | 4187 | 0.0040245 | 6.231 | 6.235 | -2.9463 | 248.4804 | 2885.2639 | -0.011857
59 |  | 2.9321 | 49.3945 | 4187 | 0.0040235 | 6.235 | 6.239 | -2.9463 | 248.54 | 2934.6585 | -0.011854
60 |  | 2.9321 | 49.3827 | 4187 | 0.0040225 | 6.239 | 6.2431 | -2.9463 | 248.5997 | 2984.0412 | -0.011852
61 |  | 2.9321 | 49.3708 | 4187 | 0.0040216 | 6.2431 | 6.2471 | -2.9463 | 248.6594 | 3033.412 | -0.011849
62 |  | 2.9321 | 49.359 | 4187 | 0.0040206 | 6.2471 | 6.2511 | -2.9463 | 248.719 | 3082.771 | -0.011846
63 |  | 2.9321 | 49.3471 | 4187 | 0.0040196 | 6.2511 | 6.2551 | -2.9463 | 248.7787 | 3132.1181 | -0.011843
64 |  | 2.9321 | 49.3353 | 4187 | 0.0040187 | 6.2551 | 6.2591 | -2.9463 | 248.8385 | 3181.4534 | -0.01184
65 |  | 2.9321 | 49.3235 | 4187 | 0.0040177 | 6.2591 | 6.2632 | -2.9463 | 248.8982 | 3230.7769 | -0.011837
66 |  | 2.9321 | 49.3116 | 4187 | 0.0040167 | 6.2632 | 6.2672 | -2.9463 | 248.958 | 3280.0885 | -0.011835
67 |  | 2.9321 | 49.2998 | 4187 | 0.0040158 | 6.2672 | 6.2712 | -2.9463 | 249.0177 | 3329.3883 | -0.011832
68 |  | 2.9321 | 49.288 | 4187 | 0.0040148 | 6.2712 | 6.2752 | -2.9463 | 249.0775 | 3378.6762 | -0.011829
69 |  | 2.9321 | 49.2761 | 4187 | 0.0040139 | 6.2752 | 6.2792 | -2.9463 | 249.1373 | 3427.9523 | -0.011826
70 |  | 2.9321 | 49.2643 | 4187 | 0.0040129 | 6.2792 | 6.2832 | -2.9463 | 249.1971 | 3477.2166 | -0.011823
71 |  | 2.9321 | 49.2525 | 4187 | 0.0040119 | 6.2832 | 6.2873 | -2.9463 | 249.2569 | 3526.4691 | -0.01182
72 |  | 2.9321 | 49.2407 | 4187 | 0.004011 | 6.2873 | 6.2913 | -2.9463 | 249.3167 | 3575.7098 | -0.011817
73 |  | 2.9321 | 49.2288 | 4187 | 0.00401 | 6.2913 | 6.2953 | -2.9463 | 249.3766 | 3624.9386 | -0.011815
74 |  | 2.9321 | 49.217 | 4187 | 0.004009 | 6.2953 | 6.2993 | -2.9463 | 249.4365 | 3674.1556 | -0.011812
75 |  | 2.9321 | 49.2052 | 4187 | 0.0040081 | 6.2993 | 6.3033 | -2.9463 | 249.4963 | 3723.3608 | -0.011809
76 |  | 2.9321 | 49.1934 | 4187 | 0.0040071 | 6.3033 | 6.3073 | -2.9463 | 249.5562 | 3772.5542 | -0.011806
77 |  | 2.9321 | 49.1816 | 4187 | 0.0040062 | 6.3073 | 6.3113 | -2.9463 | 249.6161 | 3821.7358 | -0.011803
78 |  | 2.9321 | 49.1698 | 4187 | 0.0040052 | 6.3113 | 6.3153 | -2.9463 | 249.6761 | 3870.9056 | -0.0118
79 |  | 2.9321 | 49.158 | 4187 | 0.0040042 | 6.3153 | 6.3193 | -2.9463 | 249.736 | 3920.0636 | -0.011798
80 |  | 2.9321 | 49.1462 | 4187 | 0.0040033 | 6.3193 | 6.3233 | -2.9463 | 249.7959 | 3969.2098 | -0.011795
81 |  | 2.9321 | 49.1344 | 4187 | 0.0040023 | 6.3233 | 6.3273 | -2.9463 | 249.8559 | 4018.3442 | -0.011792
82 |  | 2.9321 | 49.1226 | 4187 | 0.0040013 | 6.3273 | 6.3313 | -2.9463 | 249.9159 | 4067.4668 | -0.011789
83 |  | 2.9321 | 49.1108 | 4187 | 0.0040004 | 6.3313 | 6.3353 | -2.9463 | 249.9759 | 4116.5776 | -0.011786
84 |  | 2.9321 | 49.099 | 4187 | 0.0039994 | 6.3353 | 6.3393 | -2.9463 | 250.0359 | 4165.6767 | -0.011783
85 |  | 2.9321 | 49.0872 | 4187 | 0.0039985 | 6.3393 | 6.3433 | -2.9463 | 250.0959 | 4214.7639 | -0.011781
86 |  | 2.9321 | 49.0755 | 4187 | 0.0039975 | 6.3433 | 6.3473 | -2.9463 | 250.1559 | 4263.8394 | -0.011778
87 |  | 2.9321 | 49.0637 | 4187 | 0.0039965 | 6.3473 | 6.3513 | -2.9463 | 250.216 | 4312.9031 | -0.011775
88 |  | 2.9321 | 49.0519 | 4187 | 0.0039956 | 6.3513 | 6.3553 | -2.9463 | 250.2761 | 4361.955 | -0.011772
89 |  | 2.9321 | 49.0401 | 4187 | 0.0039946 | 6.3553 | 6.3593 | -2.9463 | 250.3361 | 4410.9951 | -0.011769
90 |  | 2.9321 | 49.0284 | 4187 | 0.0039937 | 6.3593 | 6.3633 | -2.9463 | 250.3962 | 4460.0235 | -0.011767
91 |  | 2.9321 | 49.0166 | 4187 | 0.0039927 | 6.3633 | 6.3673 | -2.9463 | 250.4563 | 4509.0401 | -0.011764
92 |  | 2.9321 | 49.0048 | 4187 | 0.0039918 | 6.3673 | 6.3713 | -2.9463 | 250.5165 | 4558.045 | -0.011761
93 |  | 2.9321 | 48.9931 | 4187 | 0.0039908 | 6.3713 | 6.3753 | -2.9463 | 250.5766 | 4607.038 | -0.011758
94 |  | 2.9321 | 48.9813 | 4187 | 0.0039898 | 6.3753 | 6.3793 | -2.9463 | 250.6367 | 4656.0194 | -0.011755
95 |  | 2.9321 | 48.9696 | 4187 | 0.0039889 | 6.3793 | 6.3833 | -2.9463 | 250.6969 | 4704.9889 | -0.011752
96 |  | 2.9321 | 48.9578 | 4187 | 0.0039879 | 6.3833 | 6.3872 | -2.9463 | 250.7571 | 4753.9468 | -0.01175
97 |  | 2.9321 | 48.9461 | 4187 | 0.003987 | 6.3872 | 6.3912 | -2.9463 | 250.8173 | 4802.8928 | -0.011747
98 |  | 2.9321 | 48.9343 | 4187 | 0.003986 | 6.3912 | 6.3952 | -2.9463 | 250.8775 | 4851.8271 | -0.011744
99 |  | 2.9321 | 48.9226 | 4187 | 0.0039851 | 6.3952 | 6.3992 | -2.9463 | 250.9377 | 4900.7497 | -0.011741
100 |  | 2.9321 | 48.9108 | 4187 | 0.0039841 | 6.3992 | 6.4032 | -2.9463 | 250.998 | 4949.6606 | -0.011738
101 |  | 2.9321 | 48.8991 | 4187 | 0.0039831 | 6.4032 | 6.4072 | -2.9463 | 251.0582 | 4998.5597 | -0.011735
102 |  | 2.9321 | 48.8874 | 4187 | 0.0039822 | 6.4072 | 6.4111 | -2.9463 | 251.1185 | 5047.447 | -0.011733
103 |  | 2.9321 | 48.8756 | 4187 | 0.0039812 | 6.4111 | 6.4151 | -2.9463 | 251.1788 | 5096.3226 | -0.01173
104 |  | 2.9321 | 48.8639 | 4187 | 0.0039803 | 6.4151 | 6.4191 | -2.9463 | 251.2391 | 5145.1865 | -0.011727
105 |  | 2.9321 | 48.8522 | 4187 | 0.0039793 | 6.4191 | 6.4231 | -2.9463 | 251.2994 | 5194.0387 | -0.011724
106 |  | 2.9321 | 48.8404 | 4187 | 0.0039784 | 6.4231 | 6.4271 | -2.9463 | 251.3597 | 5242.8792 | -0.011721
107 |  | 2.9321 | 48.8287 | 4187 | 0.0039774 | 6.4271 | 6.431 | -2.9463 | 251.42 | 5291.7079 | -0.011719
108 |  | 2.9321 | 48.817 | 4187 | 0.0039765 | 6.431 | 6.435 | -2.9463 | 251.4804 | 5340.5249 | -0.011716
109 |  | 2.9321 | 48.8053 | 4187 | 0.0039755 | 6.435 | 6.439 | -2.9463 | 251.5407 | 5389.3302 | -0.011713
110 |  | 2.9321 | 48.7936 | 4187 | 0.0039745 | 6.439 | 6.443 | -2.9463 | 251.6011 | 5438.1238 | -0.01171
111 |  | 2.9321 | 48.7819 | 4187 | 0.0039736 | 6.443 | 6.4469 | -2.9463 | 251.6615 | 5486.9056 | -0.011707
112 |  | 2.9321 | 48.7702 | 4187 | 0.0039726 | 6.4469 | 6.4509 | -2.9463 | 251.7219 | 5535.6758 | -0.011705
113 |  | 2.9321 | 48.7585 | 4187 | 0.0039717 | 6.4509 | 6.4549 | -2.9463 | 251.7824 | 5584.4343 | -0.011702
114 |  | 2.9321 | 48.7468 | 4187 | 0.0039707 | 6.4549 | 6.4589 | -2.9463 | 251.8428 | 5633.181 | -0.011699
115 |  | 2.9321 | 48.7351 | 4187 | 0.0039698 | 6.4589 | 6.4628 | -2.9463 | 251.9033 | 5681.9161 | -0.011696
116 |  | 2.9321 | 48.7234 | 4187 | 0.0039688 | 6.4628 | 6.4668 | -2.9463 | 251.9637 | 5730.6394 | -0.011693
117 |  | 2.9321 | 48.7117 | 4187 | 0.0039679 | 6.4668 | 6.4708 | -2.9463 | 252.0242 | 5779.3511 | -0.011691
118 |  | 2.9321 | 48.7 | 4187 | 0.0039669 | 6.4708 | 6.4747 | -2.9463 | 252.0847 | 5828.0511 | -0.011688
119 |  | 2.9321 | 48.6883 | 4187 | 0.003966 | 6.4747 | 6.4787 | -2.9463 | 252.1452 | 5876.7394 | -0.011685
120 |  | 2.9321 | 48.6766 | 4187 | 0.003965 | 6.4787 | 6.4827 | -2.9463 | 252.2058 | 5925.416 | -0.011682
121 |  | 2.9321 | 48.6649 | 4187 | 0.0039641 | 6.4827 | 6.4866 | -2.9463 | 252.2663 | 5974.0809 | -0.011679
122 |  | 2.9321 | 48.6532 | 4187 | 0.0039631 | 6.4866 | 6.4906 | -2.9463 | 252.3269 | 6022.7341 | -0.011676
123 |  | 2.9321 | 48.6416 | 4187 | 0.0039622 | 6.4906 | 6.4946 | -2.9463 | 252.3874 | 6071.3757 | -0.011674
124 |  | 2.9321 | 48.6299 | 4187 | 0.0039612 | 6.4946 | 6.4985 | -2.9463 | 252.448 | 6120.0056 | -0.011671
125 |  | 2.9321 | 48.6182 | 4187 | 0.0039603 | 6.4985 | 6.5025 | -2.9463 | 252.5086 | 6168.6238 | -0.011668
126 |  | 2.9321 | 48.6066 | 4187 | 0.0039593 | 6.5025 | 6.5064 | -2.9463 | 252.5692 | 6217.2304 | -0.011665
127 |  | 2.9321 | 48.5949 | 4187 | 0.0039584 | 6.5064 | 6.5104 | -2.9463 | 252.6299 | 6265.8252 | -0.011662
128 |  | 2.9321 | 48.5832 | 4187 | 0.0039574 | 6.5104 | 6.5143 | -2.9463 | 252.6905 | 6314.4085 | -0.01166
129 |  | 2.9321 | 48.5716 | 4187 | 0.0039565 | 6.5143 | 6.5183 | -2.9463 | 252.7512 | 6362.98 | -0.011657
130 |  | 2.9321 | 48.5599 | 4187 | 0.0039555 | 6.5183 | 6.5223 | -2.9463 | 252.8118 | 6411.5399 | -0.011654
131 |  | 2.9321 | 48.5483 | 4187 | 0.0039546 | 6.5223 | 6.5262 | -2.9463 | 252.8725 | 6460.0882 | -0.011651
132 |  | 2.9321 | 48.5366 | 4187 | 0.0039536 | 6.5262 | 6.5302 | -2.9463 | 252.9332 | 6508.6248 | -0.011649
133 |  | 2.9321 | 48.525 | 4187 | 0.0039527 | 6.5302 | 6.5341 | -2.9463 | 252.9939 | 6557.1498 | -0.011646
134 |  | 2.9321 | 48.5133 | 4187 | 0.0039517 | 6.5341 | 6.5381 | -2.9463 | 253.0547 | 6605.6631 | -0.011643
135 |  | 2.9321 | 48.5017 | 4187 | 0.0039508 | 6.5381 | 6.542 | -2.9463 | 253.1154 | 6654.1647 | -0.01164
136 |  | 2.9321 | 48.49 | 4187 | 0.0039498 | 6.542 | 6.546 | -2.9463 | 253.1762 | 6702.6548 | -0.011637
137 |  | 2.9321 | 48.4784 | 4187 | 0.0039489 | 6.546 | 6.5499 | -2.9463 | 253.237 | 6751.1331 | -0.011635
138 |  | 2.9321 | 48.4668 | 4187 | 0.0039479 | 6.5499 | 6.5539 | -2.9463 | 253.2977 | 6799.5999 | -0.011632
139 |  | 2.9321 | 48.4551 | 4187 | 0.003947 | 6.5539 | 6.5578 | -2.9463 | 253.3586 | 6848.055 | -0.011629
140 |  | 2.9321 | 48.4435 | 4187 | 0.003946 | 6.5578 | 6.5618 | -2.9463 | 253.4194 | 6896.4985 | -0.011626
141 |  | 2.9321 | 48.4319 | 4187 | 0.0039451 | 6.5618 | 6.5657 | -2.9463 | 253.4802 | 6944.9304 | -0.011623
142 |  | 2.9321 | 48.4202 | 4187 | 0.0039441 | 6.5657 | 6.5697 | -2.9463 | 253.5411 | 6993.3506 | -0.011621
143 |  | 2.9321 | 48.4086 | 4187 | 0.0039432 | 6.5697 | 6.5736 | -2.9463 | 253.6019 | 7041.7593 | -0.011618
144 |  | 2.9321 | 48.397 | 4187 | 0.0039422 | 6.5736 | 6.5775 | -2.9463 | 253.6628 | 7090.1563 | -0.011615
145 |  | 2.9321 | 48.3854 | 4187 | 0.0039413 | 6.5775 | 6.5815 | -2.9463 | 253.7237 | 7138.5416 | -0.011612
146 |  | 2.9321 | 48.3738 | 4187 | 0.0039403 | 6.5815 | 6.5854 | -2.9463 | 253.7846 | 7186.9154 | -0.011609
147 |  | 2.9321 | 48.3622 | 4187 | 0.0039394 | 6.5854 | 6.5894 | -2.9463 | 253.8455 | 7235.2776 | -0.011607
148 |  | 2.9321 | 48.3506 | 4187 | 0.0039385 | 6.5894 | 6.5933 | -2.9463 | 253.9065 | 7283.6282 | -0.011604
149 |  | 2.9321 | 48.339 | 4187 | 0.0039375 | 6.5933 | 6.5972 | -2.9463 | 253.9674 | 7331.9671 | -0.011601
150 |  | 2.9321 | 48.3274 | 4187 | 0.0039366 | 6.5972 | 6.6012 | -2.9463 | 254.0284 | 7380.2945 | -0.011598
151 |  | 2.9321 | 48.3158 | 4187 | 0.0039356 | 6.6012 | 6.6051 | -2.9463 | 254.0893 | 7428.6102 | -0.011596
152 |  | 2.9321 | 48.3042 | 4187 | 0.0039347 | 6.6051 | 6.609 | -2.9463 | 254.1503 | 7476.9144 | -0.011593
153 |  | 2.9321 | 48.2926 | 4187 | 0.0039337 | 6.609 | 6.613 | -2.9463 | 254.2114 | 7525.207 | -0.01159
154 |  | 2.9321 | 48.281 | 4187 | 0.0039328 | 6.613 | 6.6169 | -2.9463 | 254.2724 | 7573.4879 | -0.011587
155 |  | 2.9321 | 48.2694 | 4187 | 0.0039318 | 6.6169 | 6.6208 | -2.9463 | 254.3334 | 7621.7573 | -0.011584
156 |  | 2.9321 | 48.2578 | 4187 | 0.0039309 | 6.6208 | 6.6248 | -2.9463 | 254.3945 | 7670.0151 | -0.011582
157 |  | 2.9321 | 48.2462 | 4187 | 0.00393 | 6.6248 | 6.6287 | -2.9463 | 254.4555 | 7718.2614 | -0.011579
158 |  | 2.9321 | 48.2346 | 4187 | 0.003929 | 6.6287 | 6.6326 | -2.9463 | 254.5166 | 7766.496 | -0.011576
159 |  | 2.9321 | 48.2231 | 4187 | 0.0039281 | 6.6326 | 6.6366 | -2.9463 | 254.5777 | 7814.7191 | -0.011573
160 |  | 2.9321 | 48.2115 | 4187 | 0.0039271 | 6.6366 | 6.6405 | -2.9463 | 254.6388 | 7862.9306 | -0.01157
161 |  | 2.9321 | 48.1999 | 4187 | 0.0039262 | 6.6405 | 6.6444 | -2.9463 | 254.7 | 7911.1305 | -0.011568
162 |  | 2.9321 | 48.1884 | 4187 | 0.0039252 | 6.6444 | 6.6483 | -2.9463 | 254.7611 | 7959.3189 | -0.011565
163 |  | 2.9321 | 48.1768 | 4187 | 0.0039243 | 6.6483 | 6.6523 | -2.9463 | 254.8222 | 8007.4957 | -0.011562
164 |  | 2.9321 | 48.1652 | 4187 | 0.0039234 | 6.6523 | 6.6562 | -2.9463 | 254.8834 | 8055.6609 | -0.011559
165 |  | 2.9321 | 48.1537 | 4187 | 0.0039224 | 6.6562 | 6.6601 | -2.9463 | 254.9446 | 8103.8146 | -0.011557
166 |  | 2.9321 | 48.1421 | 4187 | 0.0039215 | 6.6601 | 6.664 | -2.9463 | 255.0058 | 8151.9567 | -0.011554
167 |  | 2.9321 | 48.1306 | 4187 | 0.0039205 | 6.664 | 6.6679 | -2.9463 | 255.067 | 8200.0873 | -0.011551
168 |  | 2.9321 | 48.119 | 4187 | 0.0039196 | 6.6679 | 6.6719 | -2.9463 | 255.1282 | 8248.2063 | -0.011548
169 |  | 2.9321 | 48.1075 | 4187 | 0.0039187 | 6.6719 | 6.6758 | -2.9463 | 255.1895 | 8296.3138 | -0.011546
170 |  | 2.9321 | 48.0959 | 4187 | 0.0039177 | 6.6758 | 6.6797 | -2.9463 | 255.2508 | 8344.4097 | -0.011543
171 |  | 2.9321 | 48.0844 | 4187 | 0.0039168 | 6.6797 | 6.6836 | -2.9463 | 255.312 | 8392.4941 | -0.01154
172 |  | 2.9321 | 48.0728 | 4187 | 0.0039158 | 6.6836 | 6.6875 | -2.9463 | 255.3733 | 8440.5669 | -0.011537
173 |  | 2.9321 | 48.0613 | 4187 | 0.0039149 | 6.6875 | 6.6915 | -2.9463 | 255.4346 | 8488.6282 | -0.011534
174 |  | 2.9321 | 48.0498 | 4187 | 0.003914 | 6.6915 | 6.6954 | -2.9463 | 255.4959 | 8536.678 | -0.011532
175 |  | 2.9321 | 48.0382 | 4187 | 0.003913 | 6.6954 | 6.6993 | -2.9463 | 255.5573 | 8584.7162 | -0.011529
176 |  | 2.9321 | 48.0267 | 4187 | 0.0039121 | 6.6993 | 6.7032 | -2.9463 | 255.6186 | 8632.7429 | -0.011526
177 |  | 2.9321 | 48.0152 | 4187 | 0.0039111 | 6.7032 | 6.7071 | -2.9463 | 255.68 | 8680.7581 | -0.011523
178 |  | 2.9321 | 48.0037 | 4187 | 0.0039102 | 6.7071 | 6.711 | -2.9463 | 255.7414 | 8728.7617 | -0.011521
179 |  | 2.9321 | 47.9921 | 4187 | 0.0039093 | 6.711 | 6.7149 | -2.9463 | 255.8027 | 8776.7539 | -0.011518
180 |  | 2.9321 | 47.9806 | 4187 | 0.0039083 | 6.7149 | 6.7188 | -2.9463 | 255.8641 | 8824.7345 | -0.011515
181 |  | 2.9321 | 47.9691 | 4187 | 0.0039074 | 6.7188 | 6.7227 | -2.9463 | 255.9256 | 8872.7036 | -0.011512
182 |  | 2.9321 | 47.9576 | 4187 | 0.0039064 | 6.7227 | 6.7266 | -2.9463 | 255.987 | 8920.6612 | -0.01151
183 |  | 2.9321 | 47.9461 | 4187 | 0.0039055 | 6.7266 | 6.7305 | -2.9463 | 256.0485 | 8968.6072 | -0.011507
184 |  | 2.9321 | 47.9346 | 4187 | 0.0039046 | 6.7305 | 6.7345 | -2.9463 | 256.1099 | 9016.5418 | -0.011504
185 |  | 2.9321 | 47.9231 | 4187 | 0.0039036 | 6.7345 | 6.7384 | -2.9463 | 256.1714 | 9064.4649 | -0.011501
186 |  | 2.9321 | 47.9116 | 4187 | 0.0039027 | 6.7384 | 6.7423 | -2.9463 | 256.2329 | 9112.3765 | -0.011498
187 |  | 2.9321 | 47.9001 | 4187 | 0.0039018 | 6.7423 | 6.7462 | -2.9463 | 256.2944 | 9160.2765 | -0.011496
188 |  | 2.9321 | 47.8886 | 4187 | 0.0039008 | 6.7462 | 6.7501 | -2.9463 | 256.3559 | 9208.1651 | -0.011493
189 |  | 2.9321 | 47.8771 | 4187 | 0.0038999 | 6.7501 | 6.754 | -2.9463 | 256.4175 | 9256.0422 | -0.01149
190 |  | 2.9321 | 47.8656 | 4187 | 0.003899 | 6.754 | 6.7579 | -2.9463 | 256.479 | 9303.9078 | -0.011487
191 |  | 2.9321 | 47.8541 | 4187 | 0.003898 | 6.7579 | 6.7618 | -2.9463 | 256.5406 | 9351.7619 | -0.011485
192 |  | 2.9321 | 47.8426 | 4187 | 0.0038971 | 6.7618 | 6.7657 | -2.9463 | 256.6022 | 9399.6045 | -0.011482
193 |  | 2.9321 | 47.8311 | 4187 | 0.0038961 | 6.7657 | 6.7696 | -2.9463 | 256.6638 | 9447.4356 | -0.011479
194 |  | 2.9321 | 47.8197 | 4187 | 0.0038952 | 6.7696 | 6.7734 | -2.9463 | 256.7254 | 9495.2553 | -0.011476
195 |  | 2.9321 | 47.8082 | 4187 | 0.0038943 | 6.7734 | 6.7773 | -2.9463 | 256.787 | 9543.0635 | -0.011474
196 |  | 2.9321 | 47.7967 | 4187 | 0.0038933 | 6.7773 | 6.7812 | -2.9463 | 256.8486 | 9590.8602 | -0.011471
197 |  | 2.9321 | 47.7852 | 4187 | 0.0038924 | 6.7812 | 6.7851 | -2.9463 | 256.9103 | 9638.6454 | -0.011468
198 |  | 2.9321 | 47.7738 | 4187 | 0.0038915 | 6.7851 | 6.789 | -2.9463 | 256.972 | 9686.4192 | -0.011465
199 |  | 2.9321 | 47.7623 | 4187 | 0.0038905 | 6.789 | 6.7929 | -2.9463 | 257.0337 | 9734.1815 | -0.011463
200 |  | 2.9321 | 47.7508 | 4187 | 0.0038896 | 6.7929 | 6.7968 | -2.9463 | 257.0954 | 9781.9323 | -0.01146
201 |  | 2.9321 | 47.7394 | 4187 | 0.0038887 | 6.7968 | 6.8007 | -2.9463 | 257.1571 | 9829.6717 | -0.011457
202 |  | 2.9321 | 47.7279 | 4187 | 0.0038877 | 6.8007 | 6.8046 | -2.9463 | 257.2188 | 9877.3996 | -0.011454
203 |  | 2.9321 | 47.7165 | 4187 | 0.0038868 | 6.8046 | 6.8085 | -2.9463 | 257.2806 | 9925.1161 | -0.011452
204 |  | 2.9321 | 47.705 | 4187 | 0.0038859 | 6.8085 | 6.8123 | -2.9463 | 257.3423 | 9972.8211 | -0.011449
205 |  | 2.9321 | 47.6936 | 4187 | 0.0038849 | 6.8123 | 6.8162 | -2.9463 | 257.4041 | 10020.5147 | -0.011446
206 |  | 2.9321 | 47.6821 | 4187 | 0.003884 | 6.8162 | 6.8201 | -2.9463 | 257.4659 | 10068.1968 | -0.011443
207 |  | 2.9321 | 47.6707 | 4187 | 0.0038831 | 6.8201 | 6.824 | -2.9463 | 257.5277 | 10115.8675 | -0.011441
208 |  | 2.9321 | 47.6592 | 4187 | 0.0038821 | 6.824 | 6.8279 | -2.9463 | 257.5895 | 10163.5267 | -0.011438
209 |  | 2.9321 | 47.6478 | 4187 | 0.0038812 | 6.8279 | 6.8318 | -2.9463 | 257.6513 | 10211.1745 | -0.011435
210 |  | 2.9321 | 47.6364 | 4187 | 0.0038803 | 6.8318 | 6.8356 | -2.9463 | 257.7132 | 10258.8109 | -0.011432
211 |  | 2.9321 | 47.6249 | 4187 | 0.0038794 | 6.8356 | 6.8395 | -2.9463 | 257.7751 | 10306.4358 | -0.01143
212 |  | 2.9321 | 47.6135 | 4187 | 0.0038784 | 6.8395 | 6.8434 | -2.9463 | 257.8369 | 10354.0493 | -0.011427
213 |  | 2.9321 | 47.6021 | 4187 | 0.0038775 | 6.8434 | 6.8473 | -2.9463 | 257.8988 | 10401.6514 | -0.011424
214 |  | 2.9321 | 47.5907 | 4187 | 0.0038766 | 6.8473 | 6.8512 | -2.9463 | 257.9607 | 10449.242 | -0.011421
215 |  | 2.9321 | 47.5792 | 4187 | 0.0038756 | 6.8512 | 6.855 | -2.9463 | 258.0227 | 10496.8213 | -0.011419
216 |  | 2.9321 | 47.5678 | 4187 | 0.0038747 | 6.855 | 6.8589 | -2.9463 | 258.0846 | 10544.3891 | -0.011416
217 |  | 2.9321 | 47.5564 | 4187 | 0.0038738 | 6.8589 | 6.8628 | -2.9463 | 258.1466 | 10591.9455 | -0.011413
218 |  | 2.9321 | 47.545 | 4187 | 0.0038728 | 6.8628 | 6.8667 | -2.9463 | 258.2085 | 10639.4905 | -0.011411
219 |  | 2.9321 | 47.5336 | 4187 | 0.0038719 | 6.8667 | 6.8705 | -2.9463 | 258.2705 | 10687.024 | -0.011408
220 |  | 2.9321 | 47.5222 | 4187 | 0.003871 | 6.8705 | 6.8744 | -2.9463 | 258.3325 | 10734.5462 | -0.011405
221 |  | 2.9321 | 47.5108 | 4187 | 0.0038701 | 6.8744 | 6.8783 | -2.9463 | 258.3945 | 10782.0569 | -0.011402
222 |  | 2.9321 | 47.4994 | 4187 | 0.0038691 | 6.8783 | 6.8821 | -2.9463 | 258.4566 | 10829.5563 | -0.0114
223 |  | 2.9321 | 47.488 | 4187 | 0.0038682 | 6.8821 | 6.886 | -2.9463 | 258.5186 | 10877.0443 | -0.011397
224 |  | 2.9321 | 47.4766 | 4187 | 0.0038673 | 6.886 | 6.8899 | -2.9463 | 258.5807 | 10924.5208 | -0.011394
225 |  | 2.9321 | 47.4652 | 4187 | 0.0038663 | 6.8899 | 6.8937 | -2.9463 | 258.6427 | 10971.986 | -0.011391
226 |  | 2.9321 | 47.4538 | 4187 | 0.0038654 | 6.8937 | 6.8976 | -2.9463 | 258.7048 | 11019.4398 | -0.011389
227 |  | 2.9321 | 47.4424 | 4187 | 0.0038645 | 6.8976 | 6.9015 | -2.9463 | 258.7669 | 11066.8821 | -0.011386
228 |  | 2.9321 | 47.431 | 4187 | 0.0038636 | 6.9015 | 6.9053 | -2.9463 | 258.829 | 11114.3131 | -0.011383
229 |  | 2.9321 | 47.4196 | 4187 | 0.0038626 | 6.9053 | 6.9092 | -2.9463 | 258.8912 | 11161.7328 | -0.01138
230 |  | 2.9321 | 47.4082 | 4187 | 0.0038617 | 6.9092 | 6.9131 | -2.9463 | 258.9533 | 11209.141 | -0.011378
231 |  | 2.9321 | 47.3969 | 4187 | 0.0038608 | 6.9131 | 6.9169 | -2.9463 | 259.0155 | 11256.5379 | -0.011375
232 |  | 2.9321 | 47.3855 | 4187 | 0.0038598 | 6.9169 | 6.9208 | -2.9463 | 259.0777 | 11303.9233 | -0.011372
233 |  | 2.9321 | 47.3741 | 4187 | 0.0038589 | 6.9208 | 6.9246 | -2.9463 | 259.1398 | 11351.2974 | -0.01137
234 |  | 2.9321 | 47.3627 | 4187 | 0.003858 | 6.9246 | 6.9285 | -2.9463 | 259.202 | 11398.6602 | -0.011367
235 |  | 2.9321 | 47.3514 | 4187 | 0.0038571 | 6.9285 | 6.9323 | -2.9463 | 259.2643 | 11446.0116 | -0.011364
236 |  | 2.9321 | 47.34 | 4187 | 0.0038561 | 6.9323 | 6.9362 | -2.9463 | 259.3265 | 11493.3516 | -0.011361

## Cu76
|  |  | buis | verlies W/M | L /°C/sec
diam | wandikte |  | inhoud l/m |  | W/M
76.2 | 1.6 | 3.1416 | 4.1854 | 60.0994 | 4187
[8 empty] | J/sec/mtr | aantal mtr. | verlies
|  | buis | verlies W/M | L /°C/sec | verlies temp | begintemp | eindtemp | verlies | bij 1°C | totaal J/sec
|  | inhoud L |  | W/M | °C per M | °C | °C | per m°C | daling | aantal mtr
1 | 76.2 | 4.1854 | 60.0994 | 4187 | 0.0034295 | 6 | 6.0034 | -3.5353 | 291.5872 | 60.0994 | -0.012124
2 |  | 4.1854 | 60.0873 | 4187 | 0.0034288 | 6.0034 | 6.0069 | -3.5353 | 291.6461 | 120.1867 | -0.012122
3 |  | 4.1854 | 60.0751 | 4187 | 0.0034281 | 6.0069 | 6.0103 | -3.5353 | 291.7049 | 180.2618 | -0.012119
4 |  | 4.1854 | 60.063 | 4187 | 0.0034274 | 6.0103 | 6.0137 | -3.5353 | 291.7638 | 240.3248 | -0.012117
5 |  | 4.1854 | 60.0509 | 4187 | 0.0034267 | 6.0137 | 6.0171 | -3.5353 | 291.8226 | 300.3757 | -0.012114
6 |  | 4.1854 | 60.0388 | 4187 | 0.003426 | 6.0171 | 6.0206 | -3.5353 | 291.8815 | 360.4145 | -0.012112
7 |  | 4.1854 | 60.0267 | 4187 | 0.0034254 | 6.0206 | 6.024 | -3.5353 | 291.9404 | 420.4412 | -0.01211
8 |  | 4.1854 | 60.0146 | 4187 | 0.0034247 | 6.024 | 6.0274 | -3.5353 | 291.9993 | 480.4558 | -0.012107
9 |  | 4.1854 | 60.0025 | 4187 | 0.003424 | 6.0274 | 6.0308 | -3.5353 | 292.0582 | 540.4582 | -0.012105
10 |  | 4.1854 | 59.9904 | 4187 | 0.0034233 | 6.0308 | 6.0343 | -3.5353 | 292.1172 | 600.4486 | -0.012102
11 |  | 4.1854 | 59.9783 | 4187 | 0.0034226 | 6.0343 | 6.0377 | -3.5353 | 292.1761 | 660.4269 | -0.0121
12 |  | 4.1854 | 59.9662 | 4187 | 0.0034219 | 6.0377 | 6.0411 | -3.5353 | 292.2351 | 720.393 | -0.012097
13 |  | 4.1854 | 59.9541 | 4187 | 0.0034212 | 6.0411 | 6.0445 | -3.5353 | 292.294 | 780.3471 | -0.012095
14 |  | 4.1854 | 59.942 | 4187 | 0.0034205 | 6.0445 | 6.048 | -3.5353 | 292.353 | 840.289 | -0.012092
15 |  | 4.1854 | 59.9299 | 4187 | 0.0034198 | 6.048 | 6.0514 | -3.5353 | 292.412 | 900.2189 | -0.01209
16 |  | 4.1854 | 59.9178 | 4187 | 0.0034191 | 6.0514 | 6.0548 | -3.5353 | 292.471 | 960.1367 | -0.012088
17 |  | 4.1854 | 59.9057 | 4187 | 0.0034185 | 6.0548 | 6.0582 | -3.5353 | 292.53 | 1020.0424 | -0.012085
18 |  | 4.1854 | 59.8936 | 4187 | 0.0034178 | 6.0582 | 6.0616 | -3.5353 | 292.589 | 1079.936 | -0.012083
19 |  | 4.1854 | 59.8815 | 4187 | 0.0034171 | 6.0616 | 6.065 | -3.5353 | 292.6481 | 1139.8175 | -0.01208
20 |  | 4.1854 | 59.8694 | 4187 | 0.0034164 | 6.065 | 6.0685 | -3.5353 | 292.7071 | 1199.687 | -0.012078
21 |  | 4.1854 | 59.8574 | 4187 | 0.0034157 | 6.0685 | 6.0719 | -3.5353 | 292.7662 | 1259.5444 | -0.012075
22 |  | 4.1854 | 59.8453 | 4187 | 0.003415 | 6.0719 | 6.0753 | -3.5353 | 292.8253 | 1319.3896 | -0.012073
23 |  | 4.1854 | 59.8332 | 4187 | 0.0034143 | 6.0753 | 6.0787 | -3.5353 | 292.8844 | 1379.2229 | -0.01207
24 |  | 4.1854 | 59.8212 | 4187 | 0.0034136 | 6.0787 | 6.0821 | -3.5353 | 292.9435 | 1439.044 | -0.012068
25 |  | 4.1854 | 59.8091 | 4187 | 0.0034129 | 6.0821 | 6.0855 | -3.5353 | 293.0026 | 1498.8531 | -0.012066
26 |  | 4.1854 | 59.797 | 4187 | 0.0034123 | 6.0855 | 6.0889 | -3.5353 | 293.0617 | 1558.6501 | -0.012063
27 |  | 4.1854 | 59.785 | 4187 | 0.0034116 | 6.0889 | 6.0924 | -3.5353 | 293.1208 | 1618.4351 | -0.012061
28 |  | 4.1854 | 59.7729 | 4187 | 0.0034109 | 6.0924 | 6.0958 | -3.5353 | 293.18 | 1678.208 | -0.012058
29 |  | 4.1854 | 59.7608 | 4187 | 0.0034102 | 6.0958 | 6.0992 | -3.5353 | 293.2391 | 1737.9688 | -0.012056
30 |  | 4.1854 | 59.7488 | 4187 | 0.0034095 | 6.0992 | 6.1026 | -3.5353 | 293.2983 | 1797.7176 | -0.012053
31 |  | 4.1854 | 59.7367 | 4187 | 0.0034088 | 6.1026 | 6.106 | -3.5353 | 293.3575 | 1857.4543 | -0.012051
32 |  | 4.1854 | 59.7247 | 4187 | 0.0034081 | 6.106 | 6.1094 | -3.5353 | 293.4167 | 1917.179 | -0.012049
33 |  | 4.1854 | 59.7126 | 4187 | 0.0034074 | 6.1094 | 6.1128 | -3.5353 | 293.4759 | 1976.8916 | -0.012046
34 |  | 4.1854 | 59.7006 | 4187 | 0.0034067 | 6.1128 | 6.1162 | -3.5353 | 293.5351 | 2036.5922 | -0.012044
35 |  | 4.1854 | 59.6885 | 4187 | 0.0034061 | 6.1162 | 6.1196 | -3.5353 | 293.5943 | 2096.2807 | -0.012041
36 |  | 4.1854 | 59.6765 | 4187 | 0.0034054 | 6.1196 | 6.123 | -3.5353 | 293.6535 | 2155.9572 | -0.012039
37 |  | 4.1854 | 59.6645 | 4187 | 0.0034047 | 6.123 | 6.1264 | -3.5353 | 293.7128 | 2215.6217 | -0.012036
38 |  | 4.1854 | 59.6524 | 4187 | 0.003404 | 6.1264 | 6.1298 | -3.5353 | 293.7721 | 2275.2741 | -0.012034
39 |  | 4.1854 | 59.6404 | 4187 | 0.0034033 | 6.1298 | 6.1332 | -3.5353 | 293.8313 | 2334.9145 | -0.012032
40 |  | 4.1854 | 59.6284 | 4187 | 0.0034026 | 6.1332 | 6.1366 | -3.5353 | 293.8906 | 2394.5428 | -0.012029
41 |  | 4.1854 | 59.6163 | 4187 | 0.0034019 | 6.1366 | 6.14 | -3.5353 | 293.9499 | 2454.1592 | -0.012027
42 |  | 4.1854 | 59.6043 | 4187 | 0.0034013 | 6.14 | 6.1434 | -3.5353 | 294.0092 | 2513.7635 | -0.012024
43 |  | 4.1854 | 59.5923 | 4187 | 0.0034006 | 6.1434 | 6.1468 | -3.5353 | 294.0686 | 2573.3557 | -0.012022
44 |  | 4.1854 | 59.5803 | 4187 | 0.0033999 | 6.1468 | 6.1502 | -3.5353 | 294.1279 | 2632.936 | -0.012019
45 |  | 4.1854 | 59.5682 | 4187 | 0.0033992 | 6.1502 | 6.1536 | -3.5353 | 294.1873 | 2692.5042 | -0.012017
46 |  | 4.1854 | 59.5562 | 4187 | 0.0033985 | 6.1536 | 6.157 | -3.5353 | 294.2466 | 2752.0604 | -0.012015
47 |  | 4.1854 | 59.5442 | 4187 | 0.0033978 | 6.157 | 6.1604 | -3.5353 | 294.306 | 2811.6046 | -0.012012
48 |  | 4.1854 | 59.5322 | 4187 | 0.0033971 | 6.1604 | 6.1638 | -3.5353 | 294.3654 | 2871.1368 | -0.01201
49 |  | 4.1854 | 59.5202 | 4187 | 0.0033965 | 6.1638 | 6.1672 | -3.5353 | 294.4248 | 2930.657 | -0.012007
50 |  | 4.1854 | 59.5082 | 4187 | 0.0033958 | 6.1672 | 6.1706 | -3.5353 | 294.4842 | 2990.1652 | -0.012005
51 |  | 4.1854 | 59.4962 | 4187 | 0.0033951 | 6.1706 | 6.174 | -3.5353 | 294.5436 | 3049.6613 | -0.012002
52 |  | 4.1854 | 59.4842 | 4187 | 0.0033944 | 6.174 | 6.1774 | -3.5353 | 294.603 | 3109.1455 | -0.012
53 |  | 4.1854 | 59.4722 | 4187 | 0.0033937 | 6.1774 | 6.1808 | -3.5353 | 294.6625 | 3168.6177 | -0.011998
54 |  | 4.1854 | 59.4602 | 4187 | 0.003393 | 6.1808 | 6.1842 | -3.5353 | 294.7219 | 3228.0778 | -0.011995
55 |  | 4.1854 | 59.4482 | 4187 | 0.0033923 | 6.1842 | 6.1876 | -3.5353 | 294.7814 | 3287.526 | -0.011993
56 |  | 4.1854 | 59.4362 | 4187 | 0.0033917 | 6.1876 | 6.191 | -3.5353 | 294.8409 | 3346.9622 | -0.01199
57 |  | 4.1854 | 59.4242 | 4187 | 0.003391 | 6.191 | 6.1944 | -3.5353 | 294.9004 | 3406.3864 | -0.011988
58 |  | 4.1854 | 59.4122 | 4187 | 0.0033903 | 6.1944 | 6.1978 | -3.5353 | 294.9599 | 3465.7986 | -0.011986
59 |  | 4.1854 | 59.4002 | 4187 | 0.0033896 | 6.1978 | 6.2012 | -3.5353 | 295.0194 | 3525.1988 | -0.011983
60 |  | 4.1854 | 59.3882 | 4187 | 0.0033889 | 6.2012 | 6.2046 | -3.5353 | 295.0789 | 3584.587 | -0.011981
61 |  | 4.1854 | 59.3763 | 4187 | 0.0033882 | 6.2046 | 6.2079 | -3.5353 | 295.1384 | 3643.9633 | -0.011978
62 |  | 4.1854 | 59.3643 | 4187 | 0.0033876 | 6.2079 | 6.2113 | -3.5353 | 295.198 | 3703.3276 | -0.011976
63 |  | 4.1854 | 59.3523 | 4187 | 0.0033869 | 6.2113 | 6.2147 | -3.5353 | 295.2576 | 3762.6798 | -0.011973
64 |  | 4.1854 | 59.3403 | 4187 | 0.0033862 | 6.2147 | 6.2181 | -3.5353 | 295.3171 | 3822.0202 | -0.011971
65 |  | 4.1854 | 59.3284 | 4187 | 0.0033855 | 6.2181 | 6.2215 | -3.5353 | 295.3767 | 3881.3485 | -0.011969
66 |  | 4.1854 | 59.3164 | 4187 | 0.0033848 | 6.2215 | 6.2249 | -3.5353 | 295.4363 | 3940.6649 | -0.011966
67 |  | 4.1854 | 59.3044 | 4187 | 0.0033841 | 6.2249 | 6.2283 | -3.5353 | 295.4959 | 3999.9693 | -0.011964
68 |  | 4.1854 | 59.2925 | 4187 | 0.0033835 | 6.2283 | 6.2316 | -3.5353 | 295.5556 | 4059.2618 | -0.011961
69 |  | 4.1854 | 59.2805 | 4187 | 0.0033828 | 6.2316 | 6.235 | -3.5353 | 295.6152 | 4118.5423 | -0.011959
70 |  | 4.1854 | 59.2685 | 4187 | 0.0033821 | 6.235 | 6.2384 | -3.5353 | 295.6748 | 4177.8108 | -0.011957
71 |  | 4.1854 | 59.2566 | 4187 | 0.0033814 | 6.2384 | 6.2418 | -3.5353 | 295.7345 | 4237.0674 | -0.011954
72 |  | 4.1854 | 59.2446 | 4187 | 0.0033807 | 6.2418 | 6.2452 | -3.5353 | 295.7942 | 4296.312 | -0.011952
73 |  | 4.1854 | 59.2327 | 4187 | 0.00338 | 6.2452 | 6.2485 | -3.5353 | 295.8539 | 4355.5447 | -0.011949
74 |  | 4.1854 | 59.2207 | 4187 | 0.0033794 | 6.2485 | 6.2519 | -3.5353 | 295.9136 | 4414.7654 | -0.011947
75 |  | 4.1854 | 59.2088 | 4187 | 0.0033787 | 6.2519 | 6.2553 | -3.5353 | 295.9733 | 4473.9742 | -0.011945
76 |  | 4.1854 | 59.1968 | 4187 | 0.003378 | 6.2553 | 6.2587 | -3.5353 | 296.033 | 4533.171 | -0.011942
77 |  | 4.1854 | 59.1849 | 4187 | 0.0033773 | 6.2587 | 6.2621 | -3.5353 | 296.0927 | 4592.3559 | -0.01194
78 |  | 4.1854 | 59.1729 | 4187 | 0.0033766 | 6.2621 | 6.2654 | -3.5353 | 296.1525 | 4651.5288 | -0.011937
79 |  | 4.1854 | 59.161 | 4187 | 0.003376 | 6.2654 | 6.2688 | -3.5353 | 296.2122 | 4710.6898 | -0.011935
80 |  | 4.1854 | 59.1491 | 4187 | 0.0033753 | 6.2688 | 6.2722 | -3.5353 | 296.272 | 4769.8389 | -0.011932
81 |  | 4.1854 | 59.1371 | 4187 | 0.0033746 | 6.2722 | 6.2756 | -3.5353 | 296.3318 | 4828.9761 | -0.01193
82 |  | 4.1854 | 59.1252 | 4187 | 0.0033739 | 6.2756 | 6.2789 | -3.5353 | 296.3916 | 4888.1013 | -0.011928
83 |  | 4.1854 | 59.1133 | 4187 | 0.0033732 | 6.2789 | 6.2823 | -3.5353 | 296.4514 | 4947.2146 | -0.011925
84 |  | 4.1854 | 59.1014 | 4187 | 0.0033726 | 6.2823 | 6.2857 | -3.5353 | 296.5112 | 5006.3159 | -0.011923
85 |  | 4.1854 | 59.0894 | 4187 | 0.0033719 | 6.2857 | 6.2891 | -3.5353 | 296.571 | 5065.4054 | -0.01192
86 |  | 4.1854 | 59.0775 | 4187 | 0.0033712 | 6.2891 | 6.2924 | -3.5353 | 296.6309 | 5124.4829 | -0.011918
87 |  | 4.1854 | 59.0656 | 4187 | 0.0033705 | 6.2924 | 6.2958 | -3.5353 | 296.6907 | 5183.5485 | -0.011916
88 |  | 4.1854 | 59.0537 | 4187 | 0.0033698 | 6.2958 | 6.2992 | -3.5353 | 296.7506 | 5242.6022 | -0.011913
89 |  | 4.1854 | 59.0418 | 4187 | 0.0033692 | 6.2992 | 6.3025 | -3.5353 | 296.8105 | 5301.6439 | -0.011911
90 |  | 4.1854 | 59.0299 | 4187 | 0.0033685 | 6.3025 | 6.3059 | -3.5353 | 296.8703 | 5360.6738 | -0.011908
91 |  | 4.1854 | 59.018 | 4187 | 0.0033678 | 6.3059 | 6.3093 | -3.5353 | 296.9302 | 5419.6917 | -0.011906
92 |  | 4.1854 | 59.006 | 4187 | 0.0033671 | 6.3093 | 6.3126 | -3.5353 | 296.9902 | 5478.6978 | -0.011904
93 |  | 4.1854 | 58.9941 | 4187 | 0.0033664 | 6.3126 | 6.316 | -3.5353 | 297.0501 | 5537.6919 | -0.011901
94 |  | 4.1854 | 58.9822 | 4187 | 0.0033658 | 6.316 | 6.3194 | -3.5353 | 297.11 | 5596.6742 | -0.011899
95 |  | 4.1854 | 58.9703 | 4187 | 0.0033651 | 6.3194 | 6.3227 | -3.5353 | 297.17 | 5655.6445 | -0.011896
96 |  | 4.1854 | 58.9584 | 4187 | 0.0033644 | 6.3227 | 6.3261 | -3.5353 | 297.2299 | 5714.6029 | -0.011894
97 |  | 4.1854 | 58.9466 | 4187 | 0.0033637 | 6.3261 | 6.3295 | -3.5353 | 297.2899 | 5773.5495 | -0.011892
98 |  | 4.1854 | 58.9347 | 4187 | 0.003363 | 6.3295 | 6.3328 | -3.5353 | 297.3499 | 5832.4842 | -0.011889
99 |  | 4.1854 | 58.9228 | 4187 | 0.0033624 | 6.3328 | 6.3362 | -3.5353 | 297.4099 | 5891.4069 | -0.011887
100 |  | 4.1854 | 58.9109 | 4187 | 0.0033617 | 6.3362 | 6.3395 | -3.5353 | 297.4699 | 5950.3178 | -0.011884
101 |  | 4.1854 | 58.899 | 4187 | 0.003361 | 6.3395 | 6.3429 | -3.5353 | 297.5299 | 6009.2168 | -0.011882
102 |  | 4.1854 | 58.8871 | 4187 | 0.0033603 | 6.3429 | 6.3463 | -3.5353 | 297.59 | 6068.1039 | -0.01188
103 |  | 4.1854 | 58.8752 | 4187 | 0.0033597 | 6.3463 | 6.3496 | -3.5353 | 297.65 | 6126.9792 | -0.011877
104 |  | 4.1854 | 58.8634 | 4187 | 0.003359 | 6.3496 | 6.353 | -3.5353 | 297.7101 | 6185.8425 | -0.011875
105 |  | 4.1854 | 58.8515 | 4187 | 0.0033583 | 6.353 | 6.3563 | -3.5353 | 297.7701 | 6244.694 | -0.011872
106 |  | 4.1854 | 58.8396 | 4187 | 0.0033576 | 6.3563 | 6.3597 | -3.5353 | 297.8302 | 6303.5336 | -0.01187
107 |  | 4.1854 | 58.8277 | 4187 | 0.0033569 | 6.3597 | 6.3631 | -3.5353 | 297.8903 | 6362.3614 | -0.011868
108 |  | 4.1854 | 58.8159 | 4187 | 0.0033563 | 6.3631 | 6.3664 | -3.5353 | 297.9504 | 6421.1772 | -0.011865
109 |  | 4.1854 | 58.804 | 4187 | 0.0033556 | 6.3664 | 6.3698 | -3.5353 | 298.0105 | 6479.9812 | -0.011863
110 |  | 4.1854 | 58.7921 | 4187 | 0.0033549 | 6.3698 | 6.3731 | -3.5353 | 298.0707 | 6538.7734 | -0.01186
111 |  | 4.1854 | 58.7803 | 4187 | 0.0033542 | 6.3731 | 6.3765 | -3.5353 | 298.1308 | 6597.5537 | -0.011858
112 |  | 4.1854 | 58.7684 | 4187 | 0.0033536 | 6.3765 | 6.3798 | -3.5353 | 298.191 | 6656.3221 | -0.011856
113 |  | 4.1854 | 58.7566 | 4187 | 0.0033529 | 6.3798 | 6.3832 | -3.5353 | 298.2511 | 6715.0787 | -0.011853
114 |  | 4.1854 | 58.7447 | 4187 | 0.0033522 | 6.3832 | 6.3865 | -3.5353 | 298.3113 | 6773.8234 | -0.011851
115 |  | 4.1854 | 58.7329 | 4187 | 0.0033515 | 6.3865 | 6.3899 | -3.5353 | 298.3715 | 6832.5563 | -0.011849
116 |  | 4.1854 | 58.721 | 4187 | 0.0033509 | 6.3899 | 6.3932 | -3.5353 | 298.4317 | 6891.2773 | -0.011846
117 |  | 4.1854 | 58.7092 | 4187 | 0.0033502 | 6.3932 | 6.3966 | -3.5353 | 298.4919 | 6949.9865 | -0.011844
118 |  | 4.1854 | 58.6973 | 4187 | 0.0033495 | 6.3966 | 6.3999 | -3.5353 | 298.5522 | 7008.6838 | -0.011841
119 |  | 4.1854 | 58.6855 | 4187 | 0.0033488 | 6.3999 | 6.4033 | -3.5353 | 298.6124 | 7067.3693 | -0.011839
120 |  | 4.1854 | 58.6736 | 4187 | 0.0033481 | 6.4033 | 6.4066 | -3.5353 | 298.6727 | 7126.0429 | -0.011837
121 |  | 4.1854 | 58.6618 | 4187 | 0.0033475 | 6.4066 | 6.41 | -3.5353 | 298.7329 | 7184.7047 | -0.011834
122 |  | 4.1854 | 58.65 | 4187 | 0.0033468 | 6.41 | 6.4133 | -3.5353 | 298.7932 | 7243.3547 | -0.011832
123 |  | 4.1854 | 58.6381 | 4187 | 0.0033461 | 6.4133 | 6.4167 | -3.5353 | 298.8535 | 7301.9929 | -0.011829
124 |  | 4.1854 | 58.6263 | 4187 | 0.0033454 | 6.4167 | 6.42 | -3.5353 | 298.9138 | 7360.6192 | -0.011827
125 |  | 4.1854 | 58.6145 | 4187 | 0.0033448 | 6.42 | 6.4234 | -3.5353 | 298.9741 | 7419.2337 | -0.011825
126 |  | 4.1854 | 58.6027 | 4187 | 0.0033441 | 6.4234 | 6.4267 | -3.5353 | 299.0344 | 7477.8363 | -0.011822
127 |  | 4.1854 | 58.5908 | 4187 | 0.0033434 | 6.4267 | 6.4301 | -3.5353 | 299.0948 | 7536.4272 | -0.01182
128 |  | 4.1854 | 58.579 | 4187 | 0.0033427 | 6.4301 | 6.4334 | -3.5353 | 299.1551 | 7595.0062 | -0.011817
129 |  | 4.1854 | 58.5672 | 4187 | 0.0033421 | 6.4334 | 6.4367 | -3.5353 | 299.2155 | 7653.5734 | -0.011815
130 |  | 4.1854 | 58.5554 | 4187 | 0.0033414 | 6.4367 | 6.4401 | -3.5353 | 299.2759 | 7712.1288 | -0.011813
131 |  | 4.1854 | 58.5436 | 4187 | 0.0033407 | 6.4401 | 6.4434 | -3.5353 | 299.3362 | 7770.6724 | -0.01181
132 |  | 4.1854 | 58.5318 | 4187 | 0.0033401 | 6.4434 | 6.4468 | -3.5353 | 299.3966 | 7829.2042 | -0.011808
133 |  | 4.1854 | 58.52 | 4187 | 0.0033394 | 6.4468 | 6.4501 | -3.5353 | 299.457 | 7887.7241 | -0.011806
134 |  | 4.1854 | 58.5082 | 4187 | 0.0033387 | 6.4501 | 6.4534 | -3.5353 | 299.5175 | 7946.2323 | -0.011803
135 |  | 4.1854 | 58.4964 | 4187 | 0.003338 | 6.4534 | 6.4568 | -3.5353 | 299.5779 | 8004.7286 | -0.011801
136 |  | 4.1854 | 58.4846 | 4187 | 0.0033374 | 6.4568 | 6.4601 | -3.5353 | 299.6384 | 8063.2132 | -0.011798
137 |  | 4.1854 | 58.4728 | 4187 | 0.0033367 | 6.4601 | 6.4635 | -3.5353 | 299.6988 | 8121.6859 | -0.011796
138 |  | 4.1854 | 58.461 | 4187 | 0.003336 | 6.4635 | 6.4668 | -3.5353 | 299.7593 | 8180.1469 | -0.011794
139 |  | 4.1854 | 58.4492 | 4187 | 0.0033353 | 6.4668 | 6.4701 | -3.5353 | 299.8198 | 8238.596 | -0.011791
140 |  | 4.1854 | 58.4374 | 4187 | 0.0033347 | 6.4701 | 6.4735 | -3.5353 | 299.8803 | 8297.0334 | -0.011789
141 |  | 4.1854 | 58.4256 | 4187 | 0.003334 | 6.4735 | 6.4768 | -3.5353 | 299.9408 | 8355.459 | -0.011787
142 |  | 4.1854 | 58.4138 | 4187 | 0.0033333 | 6.4768 | 6.4801 | -3.5353 | 300.0013 | 8413.8728 | -0.011784
143 |  | 4.1854 | 58.402 | 4187 | 0.0033326 | 6.4801 | 6.4835 | -3.5353 | 300.0618 | 8472.2748 | -0.011782
144 |  | 4.1854 | 58.3902 | 4187 | 0.003332 | 6.4835 | 6.4868 | -3.5353 | 300.1224 | 8530.665 | -0.011779
145 |  | 4.1854 | 58.3785 | 4187 | 0.0033313 | 6.4868 | 6.4901 | -3.5353 | 300.1829 | 8589.0435 | -0.011777
146 |  | 4.1854 | 58.3667 | 4187 | 0.0033306 | 6.4901 | 6.4935 | -3.5353 | 300.2435 | 8647.4102 | -0.011775
147 |  | 4.1854 | 58.3549 | 4187 | 0.00333 | 6.4935 | 6.4968 | -3.5353 | 300.3041 | 8705.7651 | -0.011772
148 |  | 4.1854 | 58.3431 | 4187 | 0.0033293 | 6.4968 | 6.5001 | -3.5353 | 300.3647 | 8764.1082 | -0.01177
149 |  | 4.1854 | 58.3314 | 4187 | 0.0033286 | 6.5001 | 6.5034 | -3.5353 | 300.4253 | 8822.4395 | -0.011768
150 |  | 4.1854 | 58.3196 | 4187 | 0.0033279 | 6.5034 | 6.5068 | -3.5353 | 300.4859 | 8880.7591 | -0.011765
151 |  | 4.1854 | 58.3078 | 4187 | 0.0033273 | 6.5068 | 6.5101 | -3.5353 | 300.5465 | 8939.067 | -0.011763
152 |  | 4.1854 | 58.2961 | 4187 | 0.0033266 | 6.5101 | 6.5134 | -3.5353 | 300.6072 | 8997.363 | -0.01176
153 |  | 4.1854 | 58.2843 | 4187 | 0.0033259 | 6.5134 | 6.5168 | -3.5353 | 300.6678 | 9055.6473 | -0.011758
154 |  | 4.1854 | 58.2725 | 4187 | 0.0033253 | 6.5168 | 6.5201 | -3.5353 | 300.7285 | 9113.9199 | -0.011756
155 |  | 4.1854 | 58.2608 | 4187 | 0.0033246 | 6.5201 | 6.5234 | -3.5353 | 300.7892 | 9172.1807 | -0.011753
156 |  | 4.1854 | 58.249 | 4187 | 0.0033239 | 6.5234 | 6.5267 | -3.5353 | 300.8499 | 9230.4297 | -0.011751
157 |  | 4.1854 | 58.2373 | 4187 | 0.0033232 | 6.5267 | 6.53 | -3.5353 | 300.9106 | 9288.667 | -0.011749
158 |  | 4.1854 | 58.2255 | 4187 | 0.0033226 | 6.53 | 6.5334 | -3.5353 | 300.9713 | 9346.8925 | -0.011746
159 |  | 4.1854 | 58.2138 | 4187 | 0.0033219 | 6.5334 | 6.5367 | -3.5353 | 301.032 | 9405.1063 | -0.011744
160 |  | 4.1854 | 58.202 | 4187 | 0.0033212 | 6.5367 | 6.54 | -3.5353 | 301.0928 | 9463.3083 | -0.011741
161 |  | 4.1854 | 58.1903 | 4187 | 0.0033206 | 6.54 | 6.5433 | -3.5353 | 301.1535 | 9521.4986 | -0.011739
162 |  | 4.1854 | 58.1786 | 4187 | 0.0033199 | 6.5433 | 6.5467 | -3.5353 | 301.2143 | 9579.6772 | -0.011737
163 |  | 4.1854 | 58.1668 | 4187 | 0.0033192 | 6.5467 | 6.55 | -3.5353 | 301.2751 | 9637.844 | -0.011734
164 |  | 4.1854 | 58.1551 | 4187 | 0.0033186 | 6.55 | 6.5533 | -3.5353 | 301.3359 | 9695.9991 | -0.011732
165 |  | 4.1854 | 58.1434 | 4187 | 0.0033179 | 6.5533 | 6.5566 | -3.5353 | 301.3967 | 9754.1425 | -0.01173
166 |  | 4.1854 | 58.1316 | 4187 | 0.0033172 | 6.5566 | 6.5599 | -3.5353 | 301.4575 | 9812.2741 | -0.011727
167 |  | 4.1854 | 58.1199 | 4187 | 0.0033165 | 6.5599 | 6.5632 | -3.5353 | 301.5183 | 9870.394 | -0.011725
168 |  | 4.1854 | 58.1082 | 4187 | 0.0033159 | 6.5632 | 6.5666 | -3.5353 | 301.5791 | 9928.5022 | -0.011722
169 |  | 4.1854 | 58.0965 | 4187 | 0.0033152 | 6.5666 | 6.5699 | -3.5353 | 301.64 | 9986.5987 | -0.01172
170 |  | 4.1854 | 58.0847 | 4187 | 0.0033145 | 6.5699 | 6.5732 | -3.5353 | 301.7009 | 10044.6834 | -0.011718
171 |  | 4.1854 | 58.073 | 4187 | 0.0033139 | 6.5732 | 6.5765 | -3.5353 | 301.7617 | 10102.7564 | -0.011715
172 |  | 4.1854 | 58.0613 | 4187 | 0.0033132 | 6.5765 | 6.5798 | -3.5353 | 301.8226 | 10160.8177 | -0.011713
173 |  | 4.1854 | 58.0496 | 4187 | 0.0033125 | 6.5798 | 6.5831 | -3.5353 | 301.8835 | 10218.8673 | -0.011711
174 |  | 4.1854 | 58.0379 | 4187 | 0.0033119 | 6.5831 | 6.5864 | -3.5353 | 301.9444 | 10276.9052 | -0.011708
175 |  | 4.1854 | 58.0262 | 4187 | 0.0033112 | 6.5864 | 6.5898 | -3.5353 | 302.0054 | 10334.9314 | -0.011706
176 |  | 4.1854 | 58.0145 | 4187 | 0.0033105 | 6.5898 | 6.5931 | -3.5353 | 302.0663 | 10392.9458 | -0.011704
177 |  | 4.1854 | 58.0028 | 4187 | 0.0033099 | 6.5931 | 6.5964 | -3.5353 | 302.1272 | 10450.9486 | -0.011701
178 |  | 4.1854 | 57.9911 | 4187 | 0.0033092 | 6.5964 | 6.5997 | -3.5353 | 302.1882 | 10508.9397 | -0.011699
179 |  | 4.1854 | 57.9794 | 4187 | 0.0033085 | 6.5997 | 6.603 | -3.5353 | 302.2492 | 10566.919 | -0.011697
180 |  | 4.1854 | 57.9677 | 4187 | 0.0033079 | 6.603 | 6.6063 | -3.5353 | 302.3102 | 10624.8867 | -0.011694
181 |  | 4.1854 | 57.956 | 4187 | 0.0033072 | 6.6063 | 6.6096 | -3.5353 | 302.3712 | 10682.8427 | -0.011692
182 |  | 4.1854 | 57.9443 | 4187 | 0.0033065 | 6.6096 | 6.6129 | -3.5353 | 302.4322 | 10740.7869 | -0.011689
183 |  | 4.1854 | 57.9326 | 4187 | 0.0033059 | 6.6129 | 6.6162 | -3.5353 | 302.4932 | 10798.7195 | -0.011687
184 |  | 4.1854 | 57.9209 | 4187 | 0.0033052 | 6.6162 | 6.6195 | -3.5353 | 302.5542 | 10856.6404 | -0.011685
185 |  | 4.1854 | 57.9092 | 4187 | 0.0033045 | 6.6195 | 6.6228 | -3.5353 | 302.6153 | 10914.5496 | -0.011682
186 |  | 4.1854 | 57.8975 | 4187 | 0.0033039 | 6.6228 | 6.6261 | -3.5353 | 302.6763 | 10972.4472 | -0.01168
187 |  | 4.1854 | 57.8859 | 4187 | 0.0033032 | 6.6261 | 6.6294 | -3.5353 | 302.7374 | 11030.333 | -0.011678
188 |  | 4.1854 | 57.8742 | 4187 | 0.0033025 | 6.6294 | 6.6327 | -3.5353 | 302.7985 | 11088.2072 | -0.011675
189 |  | 4.1854 | 57.8625 | 4187 | 0.0033019 | 6.6327 | 6.636 | -3.5353 | 302.8596 | 11146.0697 | -0.011673
190 |  | 4.1854 | 57.8508 | 4187 | 0.0033012 | 6.636 | 6.6393 | -3.5353 | 302.9207 | 11203.9205 | -0.011671
191 |  | 4.1854 | 57.8392 | 4187 | 0.0033005 | 6.6393 | 6.6426 | -3.5353 | 302.9818 | 11261.7597 | -0.011668
192 |  | 4.1854 | 57.8275 | 4187 | 0.0032999 | 6.6426 | 6.6459 | -3.5353 | 303.043 | 11319.5872 | -0.011666
193 |  | 4.1854 | 57.8158 | 4187 | 0.0032992 | 6.6459 | 6.6492 | -3.5353 | 303.1041 | 11377.403 | -0.011664
194 |  | 4.1854 | 57.8042 | 4187 | 0.0032985 | 6.6492 | 6.6525 | -3.5353 | 303.1653 | 11435.2072 | -0.011661
195 |  | 4.1854 | 57.7925 | 4187 | 0.0032979 | 6.6525 | 6.6558 | -3.5353 | 303.2264 | 11492.9997 | -0.011659
196 |  | 4.1854 | 57.7808 | 4187 | 0.0032972 | 6.6558 | 6.6591 | -3.5353 | 303.2876 | 11550.7805 | -0.011656
197 |  | 4.1854 | 57.7692 | 4187 | 0.0032965 | 6.6591 | 6.6624 | -3.5353 | 303.3488 | 11608.5497 | -0.011654
198 |  | 4.1854 | 57.7575 | 4187 | 0.0032959 | 6.6624 | 6.6657 | -3.5353 | 303.41 | 11666.3072 | -0.011652
199 |  | 4.1854 | 57.7459 | 4187 | 0.0032952 | 6.6657 | 6.669 | -3.5353 | 303.4713 | 11724.0531 | -0.011649
200 |  | 4.1854 | 57.7342 | 4187 | 0.0032945 | 6.669 | 6.6723 | -3.5353 | 303.5325 | 11781.7874 | -0.011647
201 |  | 4.1854 | 57.7226 | 4187 | 0.0032939 | 6.6723 | 6.6756 | -3.5353 | 303.5937 | 11839.5099 | -0.011645
202 |  | 4.1854 | 57.7109 | 4187 | 0.0032932 | 6.6756 | 6.6789 | -3.5353 | 303.655 | 11897.2209 | -0.011642
203 |  | 4.1854 | 57.6993 | 4187 | 0.0032925 | 6.6789 | 6.6822 | -3.5353 | 303.7163 | 11954.9202 | -0.01164
204 |  | 4.1854 | 57.6877 | 4187 | 0.0032919 | 6.6822 | 6.6855 | -3.5353 | 303.7775 | 12012.6078 | -0.011638
205 |  | 4.1854 | 57.676 | 4187 | 0.0032912 | 6.6855 | 6.6888 | -3.5353 | 303.8388 | 12070.2839 | -0.011635
206 |  | 4.1854 | 57.6644 | 4187 | 0.0032906 | 6.6888 | 6.6921 | -3.5353 | 303.9001 | 12127.9482 | -0.011633
207 |  | 4.1854 | 57.6528 | 4187 | 0.0032899 | 6.6921 | 6.6954 | -3.5353 | 303.9615 | 12185.601 | -0.011631
208 |  | 4.1854 | 57.6411 | 4187 | 0.0032892 | 6.6954 | 6.6986 | -3.5353 | 304.0228 | 12243.2421 | -0.011628
209 |  | 4.1854 | 57.6295 | 4187 | 0.0032886 | 6.6986 | 6.7019 | -3.5353 | 304.0841 | 12300.8716 | -0.011626
210 |  | 4.1854 | 57.6179 | 4187 | 0.0032879 | 6.7019 | 6.7052 | -3.5353 | 304.1455 | 12358.4895 | -0.011624
211 |  | 4.1854 | 57.6062 | 4187 | 0.0032872 | 6.7052 | 6.7085 | -3.5353 | 304.2069 | 12416.0957 | -0.011621
212 |  | 4.1854 | 57.5946 | 4187 | 0.0032866 | 6.7085 | 6.7118 | -3.5353 | 304.2683 | 12473.6903 | -0.011619
213 |  | 4.1854 | 57.583 | 4187 | 0.0032859 | 6.7118 | 6.7151 | -3.5353 | 304.3296 | 12531.2733 | -0.011617
214 |  | 4.1854 | 57.5714 | 4187 | 0.0032852 | 6.7151 | 6.7184 | -3.5353 | 304.3911 | 12588.8447 | -0.011614
215 |  | 4.1854 | 57.5598 | 4187 | 0.0032846 | 6.7184 | 6.7217 | -3.5353 | 304.4525 | 12646.4045 | -0.011612
216 |  | 4.1854 | 57.5482 | 4187 | 0.0032839 | 6.7217 | 6.7249 | -3.5353 | 304.5139 | 12703.9526 | -0.01161
217 |  | 4.1854 | 57.5365 | 4187 | 0.0032833 | 6.7249 | 6.7282 | -3.5353 | 304.5753 | 12761.4892 | -0.011607
218 |  | 4.1854 | 57.5249 | 4187 | 0.0032826 | 6.7282 | 6.7315 | -3.5353 | 304.6368 | 12819.0141 | -0.011605
219 |  | 4.1854 | 57.5133 | 4187 | 0.0032819 | 6.7315 | 6.7348 | -3.5353 | 304.6983 | 12876.5275 | -0.011602
220 |  | 4.1854 | 57.5017 | 4187 | 0.0032813 | 6.7348 | 6.7381 | -3.5353 | 304.7598 | 12934.0292 | -0.0116
221 |  | 4.1854 | 57.4901 | 4187 | 0.0032806 | 6.7381 | 6.7413 | -3.5353 | 304.8212 | 12991.5193 | -0.011598
222 |  | 4.1854 | 57.4785 | 4187 | 0.0032799 | 6.7413 | 6.7446 | -3.5353 | 304.8827 | 13048.9979 | -0.011595
223 |  | 4.1854 | 57.4669 | 4187 | 0.0032793 | 6.7446 | 6.7479 | -3.5353 | 304.9443 | 13106.4648 | -0.011593
224 |  | 4.1854 | 57.4553 | 4187 | 0.0032786 | 6.7479 | 6.7512 | -3.5353 | 305.0058 | 13163.9202 | -0.011591
225 |  | 4.1854 | 57.4438 | 4187 | 0.003278 | 6.7512 | 6.7545 | -3.5353 | 305.0673 | 13221.3639 | -0.011588
226 |  | 4.1854 | 57.4322 | 4187 | 0.0032773 | 6.7545 | 6.7577 | -3.5353 | 305.1289 | 13278.7961 | -0.011586
227 |  | 4.1854 | 57.4206 | 4187 | 0.0032766 | 6.7577 | 6.761 | -3.5353 | 305.1905 | 13336.2167 | -0.011584
228 |  | 4.1854 | 57.409 | 4187 | 0.003276 | 6.761 | 6.7643 | -3.5353 | 305.252 | 13393.6257 | -0.011581
229 |  | 4.1854 | 57.3974 | 4187 | 0.0032753 | 6.7643 | 6.7676 | -3.5353 | 305.3136 | 13451.0231 | -0.011579
230 |  | 4.1854 | 57.3858 | 4187 | 0.0032747 | 6.7676 | 6.7708 | -3.5353 | 305.3752 | 13508.4089 | -0.011577
231 |  | 4.1854 | 57.3743 | 4187 | 0.003274 | 6.7708 | 6.7741 | -3.5353 | 305.4369 | 13565.7832 | -0.011574
232 |  | 4.1854 | 57.3627 | 4187 | 0.0032733 | 6.7741 | 6.7774 | -3.5353 | 305.4985 | 13623.1459 | -0.011572
233 |  | 4.1854 | 57.3511 | 4187 | 0.0032727 | 6.7774 | 6.7807 | -3.5353 | 305.5601 | 13680.497 | -0.01157
234 |  | 4.1854 | 57.3395 | 4187 | 0.003272 | 6.7807 | 6.7839 | -3.5353 | 305.6218 | 13737.8366 | -0.011567
235 |  | 4.1854 | 57.328 | 4187 | 0.0032714 | 6.7839 | 6.7872 | -3.5353 | 305.6835 | 13795.1645 | -0.011565
236 |  | 4.1854 | 57.3164 | 4187 | 0.0032707 | 6.7872 | 6.7905 | -3.5353 | 305.7451 | 13852.481 | -0.011563

## Cu88
|  |  | buis | verlies W/M | L /°C/sec
diam | wandikte |  | inhoud l/m |  | W/M
88.9 | 1.6 | 3.1416 | 5.7683 | 70.1227 | 4187
[8 empty] | J/sec/mtr | aantal mtr. | verlies
|  | buis | verlies W/M | L /°C/sec | verlies temp | begintemp | eindtemp | verlies | bij 1°C | totaal J/sec
|  | inhoud L |  | W/M | °C per M | °C | °C | per m°C | daling | aantal mtr
1 | 88.9 | 5.7683 | 70.1227 | 4187 | 0.0029034 | 6 | 6.0029 | -4.1249 | 344.426 | 70.1227 | -0.011976
2 |  | 5.7683 | 70.1107 | 4187 | 0.0029029 | 6.0029 | 6.0058 | -4.1249 | 344.4848 | 140.2334 | -0.011974
3 |  | 5.7683 | 70.0987 | 4187 | 0.0029024 | 6.0058 | 6.0087 | -4.1249 | 344.5436 | 210.3322 | -0.011972
4 |  | 5.7683 | 70.0868 | 4187 | 0.0029019 | 6.0087 | 6.0116 | -4.1249 | 344.6025 | 280.4189 | -0.01197
5 |  | 5.7683 | 70.0748 | 4187 | 0.0029014 | 6.0116 | 6.0145 | -4.1249 | 344.6614 | 350.4937 | -0.011968
6 |  | 5.7683 | 70.0628 | 4187 | 0.0029009 | 6.0145 | 6.0174 | -4.1249 | 344.7202 | 420.5566 | -0.011966
7 |  | 5.7683 | 70.0509 | 4187 | 0.0029004 | 6.0174 | 6.0203 | -4.1249 | 344.7791 | 490.6074 | -0.011964
8 |  | 5.7683 | 70.0389 | 4187 | 0.0028999 | 6.0203 | 6.0232 | -4.1249 | 344.838 | 560.6463 | -0.011962
9 |  | 5.7683 | 70.0269 | 4187 | 0.0028994 | 6.0232 | 6.0261 | -4.1249 | 344.8969 | 630.6733 | -0.01196
10 |  | 5.7683 | 70.015 | 4187 | 0.0028989 | 6.0261 | 6.029 | -4.1249 | 344.9558 | 700.6883 | -0.011958
11 |  | 5.7683 | 70.003 | 4187 | 0.0028984 | 6.029 | 6.0319 | -4.1249 | 345.0148 | 770.6913 | -0.011956
12 |  | 5.7683 | 69.9911 | 4187 | 0.0028979 | 6.0319 | 6.0348 | -4.1249 | 345.0737 | 840.6824 | -0.011954
13 |  | 5.7683 | 69.9791 | 4187 | 0.0028974 | 6.0348 | 6.0377 | -4.1249 | 345.1326 | 910.6615 | -0.011952
14 |  | 5.7683 | 69.9672 | 4187 | 0.0028969 | 6.0377 | 6.0406 | -4.1249 | 345.1916 | 980.6287 | -0.011949
15 |  | 5.7683 | 69.9552 | 4187 | 0.0028964 | 6.0406 | 6.0435 | -4.1249 | 345.2506 | 1050.5839 | -0.011947
16 |  | 5.7683 | 69.9433 | 4187 | 0.002896 | 6.0435 | 6.0464 | -4.1249 | 345.3095 | 1120.5271 | -0.011945
17 |  | 5.7683 | 69.9313 | 4187 | 0.0028955 | 6.0464 | 6.0493 | -4.1249 | 345.3685 | 1190.4585 | -0.011943
18 |  | 5.7683 | 69.9194 | 4187 | 0.002895 | 6.0493 | 6.0522 | -4.1249 | 345.4275 | 1260.3778 | -0.011941
19 |  | 5.7683 | 69.9074 | 4187 | 0.0028945 | 6.0522 | 6.0551 | -4.1249 | 345.4865 | 1330.2853 | -0.011939
20 |  | 5.7683 | 69.8955 | 4187 | 0.002894 | 6.0551 | 6.058 | -4.1249 | 345.5455 | 1400.1808 | -0.011937
21 |  | 5.7683 | 69.8836 | 4187 | 0.0028935 | 6.058 | 6.0609 | -4.1249 | 345.6045 | 1470.0643 | -0.011935
22 |  | 5.7683 | 69.8716 | 4187 | 0.002893 | 6.0609 | 6.0638 | -4.1249 | 345.6636 | 1539.936 | -0.011933
23 |  | 5.7683 | 69.8597 | 4187 | 0.0028925 | 6.0638 | 6.0667 | -4.1249 | 345.7226 | 1609.7957 | -0.011931
24 |  | 5.7683 | 69.8478 | 4187 | 0.002892 | 6.0667 | 6.0695 | -4.1249 | 345.7817 | 1679.6434 | -0.011929
25 |  | 5.7683 | 69.8358 | 4187 | 0.0028915 | 6.0695 | 6.0724 | -4.1249 | 345.8407 | 1749.4793 | -0.011927
26 |  | 5.7683 | 69.8239 | 4187 | 0.002891 | 6.0724 | 6.0753 | -4.1249 | 345.8998 | 1819.3032 | -0.011925
27 |  | 5.7683 | 69.812 | 4187 | 0.0028905 | 6.0753 | 6.0782 | -4.1249 | 345.9589 | 1889.1152 | -0.011923
28 |  | 5.7683 | 69.8001 | 4187 | 0.00289 | 6.0782 | 6.0811 | -4.1249 | 346.018 | 1958.9152 | -0.011921
29 |  | 5.7683 | 69.7881 | 4187 | 0.0028895 | 6.0811 | 6.084 | -4.1249 | 346.0771 | 2028.7034 | -0.011919
30 |  | 5.7683 | 69.7762 | 4187 | 0.002889 | 6.084 | 6.0869 | -4.1249 | 346.1362 | 2098.4796 | -0.011917
31 |  | 5.7683 | 69.7643 | 4187 | 0.0028885 | 6.0869 | 6.0898 | -4.1249 | 346.1954 | 2168.2439 | -0.011915
32 |  | 5.7683 | 69.7524 | 4187 | 0.002888 | 6.0898 | 6.0927 | -4.1249 | 346.2545 | 2237.9963 | -0.011913
33 |  | 5.7683 | 69.7405 | 4187 | 0.0028876 | 6.0927 | 6.0956 | -4.1249 | 346.3136 | 2307.7367 | -0.011911
34 |  | 5.7683 | 69.7286 | 4187 | 0.0028871 | 6.0956 | 6.0984 | -4.1249 | 346.3728 | 2377.4653 | -0.011909
35 |  | 5.7683 | 69.7167 | 4187 | 0.0028866 | 6.0984 | 6.1013 | -4.1249 | 346.432 | 2447.182 | -0.011907
36 |  | 5.7683 | 69.7047 | 4187 | 0.0028861 | 6.1013 | 6.1042 | -4.1249 | 346.4911 | 2516.8867 | -0.011905
37 |  | 5.7683 | 69.6928 | 4187 | 0.0028856 | 6.1042 | 6.1071 | -4.1249 | 346.5503 | 2586.5795 | -0.011903
38 |  | 5.7683 | 69.6809 | 4187 | 0.0028851 | 6.1071 | 6.11 | -4.1249 | 346.6095 | 2656.2605 | -0.011901
39 |  | 5.7683 | 69.669 | 4187 | 0.0028846 | 6.11 | 6.1129 | -4.1249 | 346.6687 | 2725.9295 | -0.011899
40 |  | 5.7683 | 69.6571 | 4187 | 0.0028841 | 6.1129 | 6.1157 | -4.1249 | 346.7279 | 2795.5867 | -0.011897
41 |  | 5.7683 | 69.6452 | 4187 | 0.0028836 | 6.1157 | 6.1186 | -4.1249 | 346.7872 | 2865.2319 | -0.011895
42 |  | 5.7683 | 69.6334 | 4187 | 0.0028831 | 6.1186 | 6.1215 | -4.1249 | 346.8464 | 2934.8653 | -0.011892
43 |  | 5.7683 | 69.6215 | 4187 | 0.0028826 | 6.1215 | 6.1244 | -4.1249 | 346.9056 | 3004.4867 | -0.01189
44 |  | 5.7683 | 69.6096 | 4187 | 0.0028821 | 6.1244 | 6.1273 | -4.1249 | 346.9649 | 3074.0963 | -0.011888
45 |  | 5.7683 | 69.5977 | 4187 | 0.0028816 | 6.1273 | 6.1302 | -4.1249 | 347.0242 | 3143.694 | -0.011886
46 |  | 5.7683 | 69.5858 | 4187 | 0.0028812 | 6.1302 | 6.133 | -4.1249 | 347.0835 | 3213.2798 | -0.011884
47 |  | 5.7683 | 69.5739 | 4187 | 0.0028807 | 6.133 | 6.1359 | -4.1249 | 347.1427 | 3282.8537 | -0.011882
48 |  | 5.7683 | 69.562 | 4187 | 0.0028802 | 6.1359 | 6.1388 | -4.1249 | 347.202 | 3352.4157 | -0.01188
49 |  | 5.7683 | 69.5501 | 4187 | 0.0028797 | 6.1388 | 6.1417 | -4.1249 | 347.2613 | 3421.9658 | -0.011878
50 |  | 5.7683 | 69.5383 | 4187 | 0.0028792 | 6.1417 | 6.1446 | -4.1249 | 347.3207 | 3491.5041 | -0.011876
51 |  | 5.7683 | 69.5264 | 4187 | 0.0028787 | 6.1446 | 6.1474 | -4.1249 | 347.38 | 3561.0305 | -0.011874
52 |  | 5.7683 | 69.5145 | 4187 | 0.0028782 | 6.1474 | 6.1503 | -4.1249 | 347.4393 | 3630.545 | -0.011872
53 |  | 5.7683 | 69.5026 | 4187 | 0.0028777 | 6.1503 | 6.1532 | -4.1249 | 347.4987 | 3700.0477 | -0.01187
54 |  | 5.7683 | 69.4908 | 4187 | 0.0028772 | 6.1532 | 6.1561 | -4.1249 | 347.558 | 3769.5384 | -0.011868
55 |  | 5.7683 | 69.4789 | 4187 | 0.0028767 | 6.1561 | 6.159 | -4.1249 | 347.6174 | 3839.0173 | -0.011866
56 |  | 5.7683 | 69.467 | 4187 | 0.0028762 | 6.159 | 6.1618 | -4.1249 | 347.6768 | 3908.4844 | -0.011864
57 |  | 5.7683 | 69.4552 | 4187 | 0.0028757 | 6.1618 | 6.1647 | -4.1249 | 347.7362 | 3977.9396 | -0.011862
58 |  | 5.7683 | 69.4433 | 4187 | 0.0028753 | 6.1647 | 6.1676 | -4.1249 | 347.7956 | 4047.3829 | -0.01186
59 |  | 5.7683 | 69.4315 | 4187 | 0.0028748 | 6.1676 | 6.1705 | -4.1249 | 347.855 | 4116.8143 | -0.011858
60 |  | 5.7683 | 69.4196 | 4187 | 0.0028743 | 6.1705 | 6.1733 | -4.1249 | 347.9144 | 4186.2339 | -0.011856
61 |  | 5.7683 | 69.4077 | 4187 | 0.0028738 | 6.1733 | 6.1762 | -4.1249 | 347.9738 | 4255.6417 | -0.011854
62 |  | 5.7683 | 69.3959 | 4187 | 0.0028733 | 6.1762 | 6.1791 | -4.1249 | 348.0333 | 4325.0376 | -0.011852
63 |  | 5.7683 | 69.384 | 4187 | 0.0028728 | 6.1791 | 6.1819 | -4.1249 | 348.0927 | 4394.4216 | -0.01185
64 |  | 5.7683 | 69.3722 | 4187 | 0.0028723 | 6.1819 | 6.1848 | -4.1249 | 348.1522 | 4463.7938 | -0.011848
65 |  | 5.7683 | 69.3603 | 4187 | 0.0028718 | 6.1848 | 6.1877 | -4.1249 | 348.2116 | 4533.1541 | -0.011846
66 |  | 5.7683 | 69.3485 | 4187 | 0.0028713 | 6.1877 | 6.1906 | -4.1249 | 348.2711 | 4602.5026 | -0.011844
67 |  | 5.7683 | 69.3366 | 4187 | 0.0028708 | 6.1906 | 6.1934 | -4.1249 | 348.3306 | 4671.8392 | -0.011842
68 |  | 5.7683 | 69.3248 | 4187 | 0.0028703 | 6.1934 | 6.1963 | -4.1249 | 348.3901 | 4741.164 | -0.01184
69 |  | 5.7683 | 69.313 | 4187 | 0.0028699 | 6.1963 | 6.1992 | -4.1249 | 348.4496 | 4810.477 | -0.011838
70 |  | 5.7683 | 69.3011 | 4187 | 0.0028694 | 6.1992 | 6.202 | -4.1249 | 348.5091 | 4879.7781 | -0.011836
71 |  | 5.7683 | 69.2893 | 4187 | 0.0028689 | 6.202 | 6.2049 | -4.1249 | 348.5687 | 4949.0674 | -0.011834
72 |  | 5.7683 | 69.2775 | 4187 | 0.0028684 | 6.2049 | 6.2078 | -4.1249 | 348.6282 | 5018.3449 | -0.011832
73 |  | 5.7683 | 69.2656 | 4187 | 0.0028679 | 6.2078 | 6.2106 | -4.1249 | 348.6878 | 5087.6105 | -0.01183
74 |  | 5.7683 | 69.2538 | 4187 | 0.0028674 | 6.2106 | 6.2135 | -4.1249 | 348.7473 | 5156.8643 | -0.011828
75 |  | 5.7683 | 69.242 | 4187 | 0.0028669 | 6.2135 | 6.2164 | -4.1249 | 348.8069 | 5226.1063 | -0.011826
76 |  | 5.7683 | 69.2301 | 4187 | 0.0028664 | 6.2164 | 6.2192 | -4.1249 | 348.8665 | 5295.3364 | -0.011824
77 |  | 5.7683 | 69.2183 | 4187 | 0.0028659 | 6.2192 | 6.2221 | -4.1249 | 348.9261 | 5364.5547 | -0.011822
78 |  | 5.7683 | 69.2065 | 4187 | 0.0028654 | 6.2221 | 6.225 | -4.1249 | 348.9857 | 5433.7612 | -0.01182
79 |  | 5.7683 | 69.1947 | 4187 | 0.002865 | 6.225 | 6.2278 | -4.1249 | 349.0453 | 5502.9559 | -0.011818
80 |  | 5.7683 | 69.1829 | 4187 | 0.0028645 | 6.2278 | 6.2307 | -4.1249 | 349.1049 | 5572.1388 | -0.011816
81 |  | 5.7683 | 69.171 | 4187 | 0.002864 | 6.2307 | 6.2336 | -4.1249 | 349.1646 | 5641.3098 | -0.011814
82 |  | 5.7683 | 69.1592 | 4187 | 0.0028635 | 6.2336 | 6.2364 | -4.1249 | 349.2242 | 5710.4691 | -0.011812
83 |  | 5.7683 | 69.1474 | 4187 | 0.002863 | 6.2364 | 6.2393 | -4.1249 | 349.2838 | 5779.6165 | -0.011809
84 |  | 5.7683 | 69.1356 | 4187 | 0.0028625 | 6.2393 | 6.2422 | -4.1249 | 349.3435 | 5848.7521 | -0.011807
85 |  | 5.7683 | 69.1238 | 4187 | 0.002862 | 6.2422 | 6.245 | -4.1249 | 349.4032 | 5917.8759 | -0.011805
86 |  | 5.7683 | 69.112 | 4187 | 0.0028615 | 6.245 | 6.2479 | -4.1249 | 349.4629 | 5986.9879 | -0.011803
87 |  | 5.7683 | 69.1002 | 4187 | 0.002861 | 6.2479 | 6.2507 | -4.1249 | 349.5226 | 6056.0881 | -0.011801
88 |  | 5.7683 | 69.0884 | 4187 | 0.0028606 | 6.2507 | 6.2536 | -4.1249 | 349.5823 | 6125.1765 | -0.011799
89 |  | 5.7683 | 69.0766 | 4187 | 0.0028601 | 6.2536 | 6.2565 | -4.1249 | 349.642 | 6194.2531 | -0.011797
90 |  | 5.7683 | 69.0648 | 4187 | 0.0028596 | 6.2565 | 6.2593 | -4.1249 | 349.7017 | 6263.3179 | -0.011795
91 |  | 5.7683 | 69.053 | 4187 | 0.0028591 | 6.2593 | 6.2622 | -4.1249 | 349.7614 | 6332.3709 | -0.011793
92 |  | 5.7683 | 69.0412 | 4187 | 0.0028586 | 6.2622 | 6.265 | -4.1249 | 349.8212 | 6401.4121 | -0.011791
93 |  | 5.7683 | 69.0294 | 4187 | 0.0028581 | 6.265 | 6.2679 | -4.1249 | 349.8809 | 6470.4415 | -0.011789
94 |  | 5.7683 | 69.0176 | 4187 | 0.0028576 | 6.2679 | 6.2708 | -4.1249 | 349.9407 | 6539.4591 | -0.011787
95 |  | 5.7683 | 69.0058 | 4187 | 0.0028571 | 6.2708 | 6.2736 | -4.1249 | 350.0005 | 6608.465 | -0.011785
96 |  | 5.7683 | 68.9941 | 4187 | 0.0028567 | 6.2736 | 6.2765 | -4.1249 | 350.0603 | 6677.459 | -0.011783
97 |  | 5.7683 | 68.9823 | 4187 | 0.0028562 | 6.2765 | 6.2793 | -4.1249 | 350.1201 | 6746.4413 | -0.011781
98 |  | 5.7683 | 68.9705 | 4187 | 0.0028557 | 6.2793 | 6.2822 | -4.1249 | 350.1799 | 6815.4118 | -0.011779
99 |  | 5.7683 | 68.9587 | 4187 | 0.0028552 | 6.2822 | 6.285 | -4.1249 | 350.2397 | 6884.3705 | -0.011777
100 |  | 5.7683 | 68.9469 | 4187 | 0.0028547 | 6.285 | 6.2879 | -4.1249 | 350.2995 | 6953.3174 | -0.011775
101 |  | 5.7683 | 68.9352 | 4187 | 0.0028542 | 6.2879 | 6.2908 | -4.1249 | 350.3593 | 7022.2526 | -0.011773
102 |  | 5.7683 | 68.9234 | 4187 | 0.0028537 | 6.2908 | 6.2936 | -4.1249 | 350.4192 | 7091.176 | -0.011771
103 |  | 5.7683 | 68.9116 | 4187 | 0.0028532 | 6.2936 | 6.2965 | -4.1249 | 350.4791 | 7160.0876 | -0.011769
104 |  | 5.7683 | 68.8998 | 4187 | 0.0028528 | 6.2965 | 6.2993 | -4.1249 | 350.5389 | 7228.9874 | -0.011767
105 |  | 5.7683 | 68.8881 | 4187 | 0.0028523 | 6.2993 | 6.3022 | -4.1249 | 350.5988 | 7297.8755 | -0.011765
106 |  | 5.7683 | 68.8763 | 4187 | 0.0028518 | 6.3022 | 6.305 | -4.1249 | 350.6587 | 7366.7518 | -0.011763
107 |  | 5.7683 | 68.8645 | 4187 | 0.0028513 | 6.305 | 6.3079 | -4.1249 | 350.7186 | 7435.6164 | -0.011761
108 |  | 5.7683 | 68.8528 | 4187 | 0.0028508 | 6.3079 | 6.3107 | -4.1249 | 350.7785 | 7504.4692 | -0.011759
109 |  | 5.7683 | 68.841 | 4187 | 0.0028503 | 6.3107 | 6.3136 | -4.1249 | 350.8384 | 7573.3102 | -0.011757
110 |  | 5.7683 | 68.8293 | 4187 | 0.0028498 | 6.3136 | 6.3164 | -4.1249 | 350.8983 | 7642.1395 | -0.011755
111 |  | 5.7683 | 68.8175 | 4187 | 0.0028493 | 6.3164 | 6.3193 | -4.1249 | 350.9583 | 7710.957 | -0.011753
112 |  | 5.7683 | 68.8058 | 4187 | 0.0028489 | 6.3193 | 6.3221 | -4.1249 | 351.0182 | 7779.7627 | -0.011751
113 |  | 5.7683 | 68.794 | 4187 | 0.0028484 | 6.3221 | 6.325 | -4.1249 | 351.0782 | 7848.5567 | -0.011749
114 |  | 5.7683 | 68.7823 | 4187 | 0.0028479 | 6.325 | 6.3278 | -4.1249 | 351.1382 | 7917.339 | -0.011747
115 |  | 5.7683 | 68.7705 | 4187 | 0.0028474 | 6.3278 | 6.3307 | -4.1249 | 351.1981 | 7986.1095 | -0.011745
116 |  | 5.7683 | 68.7588 | 4187 | 0.0028469 | 6.3307 | 6.3335 | -4.1249 | 351.2581 | 8054.8683 | -0.011743
117 |  | 5.7683 | 68.747 | 4187 | 0.0028464 | 6.3335 | 6.3364 | -4.1249 | 351.3181 | 8123.6153 | -0.011741
118 |  | 5.7683 | 68.7353 | 4187 | 0.0028459 | 6.3364 | 6.3392 | -4.1249 | 351.3781 | 8192.3506 | -0.011739
119 |  | 5.7683 | 68.7235 | 4187 | 0.0028455 | 6.3392 | 6.342 | -4.1249 | 351.4382 | 8261.0742 | -0.011737
120 |  | 5.7683 | 68.7118 | 4187 | 0.002845 | 6.342 | 6.3449 | -4.1249 | 351.4982 | 8329.786 | -0.011735
121 |  | 5.7683 | 68.7001 | 4187 | 0.0028445 | 6.3449 | 6.3477 | -4.1249 | 351.5582 | 8398.486 | -0.011733
122 |  | 5.7683 | 68.6883 | 4187 | 0.002844 | 6.3477 | 6.3506 | -4.1249 | 351.6183 | 8467.1744 | -0.011731
123 |  | 5.7683 | 68.6766 | 4187 | 0.0028435 | 6.3506 | 6.3534 | -4.1249 | 351.6783 | 8535.851 | -0.011729
124 |  | 5.7683 | 68.6649 | 4187 | 0.002843 | 6.3534 | 6.3563 | -4.1249 | 351.7384 | 8604.5159 | -0.011727
125 |  | 5.7683 | 68.6532 | 4187 | 0.0028425 | 6.3563 | 6.3591 | -4.1249 | 351.7985 | 8673.169 | -0.011725
126 |  | 5.7683 | 68.6414 | 4187 | 0.0028421 | 6.3591 | 6.3619 | -4.1249 | 351.8586 | 8741.8105 | -0.011723
127 |  | 5.7683 | 68.6297 | 4187 | 0.0028416 | 6.3619 | 6.3648 | -4.1249 | 351.9187 | 8810.4402 | -0.011721
128 |  | 5.7683 | 68.618 | 4187 | 0.0028411 | 6.3648 | 6.3676 | -4.1249 | 351.9788 | 8879.0581 | -0.011719
129 |  | 5.7683 | 68.6063 | 4187 | 0.0028406 | 6.3676 | 6.3705 | -4.1249 | 352.0389 | 8947.6644 | -0.011717
130 |  | 5.7683 | 68.5945 | 4187 | 0.0028401 | 6.3705 | 6.3733 | -4.1249 | 352.0991 | 9016.259 | -0.011715
131 |  | 5.7683 | 68.5828 | 4187 | 0.0028396 | 6.3733 | 6.3762 | -4.1249 | 352.1592 | 9084.8418 | -0.011713
132 |  | 5.7683 | 68.5711 | 4187 | 0.0028391 | 6.3762 | 6.379 | -4.1249 | 352.2194 | 9153.4129 | -0.011711
133 |  | 5.7683 | 68.5594 | 4187 | 0.0028387 | 6.379 | 6.3818 | -4.1249 | 352.2795 | 9221.9723 | -0.011709
134 |  | 5.7683 | 68.5477 | 4187 | 0.0028382 | 6.3818 | 6.3847 | -4.1249 | 352.3397 | 9290.52 | -0.011707
135 |  | 5.7683 | 68.536 | 4187 | 0.0028377 | 6.3847 | 6.3875 | -4.1249 | 352.3999 | 9359.056 | -0.011705
136 |  | 5.7683 | 68.5243 | 4187 | 0.0028372 | 6.3875 | 6.3903 | -4.1249 | 352.4601 | 9427.5803 | -0.011703
137 |  | 5.7683 | 68.5126 | 4187 | 0.0028367 | 6.3903 | 6.3932 | -4.1249 | 352.5203 | 9496.0929 | -0.011701
138 |  | 5.7683 | 68.5009 | 4187 | 0.0028362 | 6.3932 | 6.396 | -4.1249 | 352.5805 | 9564.5938 | -0.011699
139 |  | 5.7683 | 68.4892 | 4187 | 0.0028357 | 6.396 | 6.3989 | -4.1249 | 352.6407 | 9633.083 | -0.011697
140 |  | 5.7683 | 68.4775 | 4187 | 0.0028353 | 6.3989 | 6.4017 | -4.1249 | 352.701 | 9701.5605 | -0.011695
141 |  | 5.7683 | 68.4658 | 4187 | 0.0028348 | 6.4017 | 6.4045 | -4.1249 | 352.7612 | 9770.0263 | -0.011693
142 |  | 5.7683 | 68.4541 | 4187 | 0.0028343 | 6.4045 | 6.4074 | -4.1249 | 352.8215 | 9838.4804 | -0.011691
143 |  | 5.7683 | 68.4424 | 4187 | 0.0028338 | 6.4074 | 6.4102 | -4.1249 | 352.8817 | 9906.9228 | -0.011689
144 |  | 5.7683 | 68.4307 | 4187 | 0.0028333 | 6.4102 | 6.413 | -4.1249 | 352.942 | 9975.3535 | -0.011687
145 |  | 5.7683 | 68.419 | 4187 | 0.0028328 | 6.413 | 6.4159 | -4.1249 | 353.0023 | 10043.7725 | -0.011685
146 |  | 5.7683 | 68.4073 | 4187 | 0.0028324 | 6.4159 | 6.4187 | -4.1249 | 353.0626 | 10112.1799 | -0.011683
147 |  | 5.7683 | 68.3957 | 4187 | 0.0028319 | 6.4187 | 6.4215 | -4.1249 | 353.1229 | 10180.5755 | -0.011681
148 |  | 5.7683 | 68.384 | 4187 | 0.0028314 | 6.4215 | 6.4244 | -4.1249 | 353.1832 | 10248.9595 | -0.011679
149 |  | 5.7683 | 68.3723 | 4187 | 0.0028309 | 6.4244 | 6.4272 | -4.1249 | 353.2436 | 10317.3318 | -0.011677
150 |  | 5.7683 | 68.3606 | 4187 | 0.0028304 | 6.4272 | 6.43 | -4.1249 | 353.3039 | 10385.6924 | -0.011675
151 |  | 5.7683 | 68.349 | 4187 | 0.0028299 | 6.43 | 6.4328 | -4.1249 | 353.3643 | 10454.0414 | -0.011673
152 |  | 5.7683 | 68.3373 | 4187 | 0.0028295 | 6.4328 | 6.4357 | -4.1249 | 353.4246 | 10522.3787 | -0.011671
153 |  | 5.7683 | 68.3256 | 4187 | 0.002829 | 6.4357 | 6.4385 | -4.1249 | 353.485 | 10590.7043 | -0.011669
154 |  | 5.7683 | 68.3139 | 4187 | 0.0028285 | 6.4385 | 6.4413 | -4.1249 | 353.5454 | 10659.0182 | -0.011667
155 |  | 5.7683 | 68.3023 | 4187 | 0.002828 | 6.4413 | 6.4442 | -4.1249 | 353.6058 | 10727.3205 | -0.011665
156 |  | 5.7683 | 68.2906 | 4187 | 0.0028275 | 6.4442 | 6.447 | -4.1249 | 353.6662 | 10795.6111 | -0.011663
157 |  | 5.7683 | 68.2789 | 4187 | 0.002827 | 6.447 | 6.4498 | -4.1249 | 353.7266 | 10863.89 | -0.011661
158 |  | 5.7683 | 68.2673 | 4187 | 0.0028266 | 6.4498 | 6.4526 | -4.1249 | 353.787 | 10932.1573 | -0.011659
159 |  | 5.7683 | 68.2556 | 4187 | 0.0028261 | 6.4526 | 6.4555 | -4.1249 | 353.8474 | 11000.413 | -0.011657
160 |  | 5.7683 | 68.244 | 4187 | 0.0028256 | 6.4555 | 6.4583 | -4.1249 | 353.9079 | 11068.6569 | -0.011655
161 |  | 5.7683 | 68.2323 | 4187 | 0.0028251 | 6.4583 | 6.4611 | -4.1249 | 353.9683 | 11136.8892 | -0.011653
162 |  | 5.7683 | 68.2207 | 4187 | 0.0028246 | 6.4611 | 6.4639 | -4.1249 | 354.0288 | 11205.1099 | -0.011651
163 |  | 5.7683 | 68.209 | 4187 | 0.0028241 | 6.4639 | 6.4668 | -4.1249 | 354.0893 | 11273.3189 | -0.011649
164 |  | 5.7683 | 68.1974 | 4187 | 0.0028237 | 6.4668 | 6.4696 | -4.1249 | 354.1498 | 11341.5162 | -0.011647
165 |  | 5.7683 | 68.1857 | 4187 | 0.0028232 | 6.4696 | 6.4724 | -4.1249 | 354.2102 | 11409.702 | -0.011645
166 |  | 5.7683 | 68.1741 | 4187 | 0.0028227 | 6.4724 | 6.4752 | -4.1249 | 354.2708 | 11477.876 | -0.011643
167 |  | 5.7683 | 68.1624 | 4187 | 0.0028222 | 6.4752 | 6.4781 | -4.1249 | 354.3313 | 11546.0384 | -0.011641
168 |  | 5.7683 | 68.1508 | 4187 | 0.0028217 | 6.4781 | 6.4809 | -4.1249 | 354.3918 | 11614.1892 | -0.011639
169 |  | 5.7683 | 68.1391 | 4187 | 0.0028213 | 6.4809 | 6.4837 | -4.1249 | 354.4523 | 11682.3284 | -0.011637
170 |  | 5.7683 | 68.1275 | 4187 | 0.0028208 | 6.4837 | 6.4865 | -4.1249 | 354.5129 | 11750.4559 | -0.011635
171 |  | 5.7683 | 68.1159 | 4187 | 0.0028203 | 6.4865 | 6.4893 | -4.1249 | 354.5734 | 11818.5717 | -0.011633
172 |  | 5.7683 | 68.1042 | 4187 | 0.0028198 | 6.4893 | 6.4922 | -4.1249 | 354.634 | 11886.676 | -0.011631
173 |  | 5.7683 | 68.0926 | 4187 | 0.0028193 | 6.4922 | 6.495 | -4.1249 | 354.6946 | 11954.7686 | -0.011629
174 |  | 5.7683 | 68.081 | 4187 | 0.0028188 | 6.495 | 6.4978 | -4.1249 | 354.7552 | 12022.8496 | -0.011627
175 |  | 5.7683 | 68.0693 | 4187 | 0.0028184 | 6.4978 | 6.5006 | -4.1249 | 354.8158 | 12090.9189 | -0.011625
176 |  | 5.7683 | 68.0577 | 4187 | 0.0028179 | 6.5006 | 6.5034 | -4.1249 | 354.8764 | 12158.9766 | -0.011623
177 |  | 5.7683 | 68.0461 | 4187 | 0.0028174 | 6.5034 | 6.5063 | -4.1249 | 354.937 | 12227.0227 | -0.011621
178 |  | 5.7683 | 68.0345 | 4187 | 0.0028169 | 6.5063 | 6.5091 | -4.1249 | 354.9976 | 12295.0572 | -0.011619
179 |  | 5.7683 | 68.0229 | 4187 | 0.0028164 | 6.5091 | 6.5119 | -4.1249 | 355.0583 | 12363.0801 | -0.011617
180 |  | 5.7683 | 68.0112 | 4187 | 0.002816 | 6.5119 | 6.5147 | -4.1249 | 355.1189 | 12431.0913 | -0.011615
181 |  | 5.7683 | 67.9996 | 4187 | 0.0028155 | 6.5147 | 6.5175 | -4.1249 | 355.1796 | 12499.0909 | -0.011613
182 |  | 5.7683 | 67.988 | 4187 | 0.002815 | 6.5175 | 6.5203 | -4.1249 | 355.2402 | 12567.0789 | -0.011611
183 |  | 5.7683 | 67.9764 | 4187 | 0.0028145 | 6.5203 | 6.5231 | -4.1249 | 355.3009 | 12635.0553 | -0.011609
184 |  | 5.7683 | 67.9648 | 4187 | 0.002814 | 6.5231 | 6.526 | -4.1249 | 355.3616 | 12703.0201 | -0.011608
185 |  | 5.7683 | 67.9532 | 4187 | 0.0028136 | 6.526 | 6.5288 | -4.1249 | 355.4223 | 12770.9733 | -0.011606
186 |  | 5.7683 | 67.9416 | 4187 | 0.0028131 | 6.5288 | 6.5316 | -4.1249 | 355.483 | 12838.9149 | -0.011604
187 |  | 5.7683 | 67.93 | 4187 | 0.0028126 | 6.5316 | 6.5344 | -4.1249 | 355.5437 | 12906.8449 | -0.011602
188 |  | 5.7683 | 67.9184 | 4187 | 0.0028121 | 6.5344 | 6.5372 | -4.1249 | 355.6045 | 12974.7632 | -0.0116
189 |  | 5.7683 | 67.9068 | 4187 | 0.0028116 | 6.5372 | 6.54 | -4.1249 | 355.6652 | 13042.67 | -0.011598
190 |  | 5.7683 | 67.8952 | 4187 | 0.0028112 | 6.54 | 6.5428 | -4.1249 | 355.726 | 13110.5652 | -0.011596
191 |  | 5.7683 | 67.8836 | 4187 | 0.0028107 | 6.5428 | 6.5456 | -4.1249 | 355.7867 | 13178.4488 | -0.011594
192 |  | 5.7683 | 67.872 | 4187 | 0.0028102 | 6.5456 | 6.5485 | -4.1249 | 355.8475 | 13246.3207 | -0.011592
193 |  | 5.7683 | 67.8604 | 4187 | 0.0028097 | 6.5485 | 6.5513 | -4.1249 | 355.9083 | 13314.1811 | -0.01159
194 |  | 5.7683 | 67.8488 | 4187 | 0.0028092 | 6.5513 | 6.5541 | -4.1249 | 355.9691 | 13382.0299 | -0.011588
195 |  | 5.7683 | 67.8372 | 4187 | 0.0028088 | 6.5541 | 6.5569 | -4.1249 | 356.0299 | 13449.8672 | -0.011586
196 |  | 5.7683 | 67.8256 | 4187 | 0.0028083 | 6.5569 | 6.5597 | -4.1249 | 356.0907 | 13517.6928 | -0.011584
197 |  | 5.7683 | 67.814 | 4187 | 0.0028078 | 6.5597 | 6.5625 | -4.1249 | 356.1515 | 13585.5068 | -0.011582
198 |  | 5.7683 | 67.8025 | 4187 | 0.0028073 | 6.5625 | 6.5653 | -4.1249 | 356.2124 | 13653.3093 | -0.01158
199 |  | 5.7683 | 67.7909 | 4187 | 0.0028068 | 6.5653 | 6.5681 | -4.1249 | 356.2732 | 13721.1002 | -0.011578
200 |  | 5.7683 | 67.7793 | 4187 | 0.0028064 | 6.5681 | 6.5709 | -4.1249 | 356.3341 | 13788.8795 | -0.011576
201 |  | 5.7683 | 67.7677 | 4187 | 0.0028059 | 6.5709 | 6.5737 | -4.1249 | 356.3949 | 13856.6472 | -0.011574
202 |  | 5.7683 | 67.7562 | 4187 | 0.0028054 | 6.5737 | 6.5765 | -4.1249 | 356.4558 | 13924.4034 | -0.011572
203 |  | 5.7683 | 67.7446 | 4187 | 0.0028049 | 6.5765 | 6.5793 | -4.1249 | 356.5167 | 13992.148 | -0.01157
204 |  | 5.7683 | 67.733 | 4187 | 0.0028044 | 6.5793 | 6.5821 | -4.1249 | 356.5776 | 14059.881 | -0.011568
205 |  | 5.7683 | 67.7214 | 4187 | 0.002804 | 6.5821 | 6.5849 | -4.1249 | 356.6385 | 14127.6024 | -0.011566
206 |  | 5.7683 | 67.7099 | 4187 | 0.0028035 | 6.5849 | 6.5877 | -4.1249 | 356.6994 | 14195.3123 | -0.011564
207 |  | 5.7683 | 67.6983 | 4187 | 0.002803 | 6.5877 | 6.5906 | -4.1249 | 356.7604 | 14263.0106 | -0.011562
208 |  | 5.7683 | 67.6868 | 4187 | 0.0028025 | 6.5906 | 6.5934 | -4.1249 | 356.8213 | 14330.6974 | -0.01156
209 |  | 5.7683 | 67.6752 | 4187 | 0.002802 | 6.5934 | 6.5962 | -4.1249 | 356.8823 | 14398.3726 | -0.011558
210 |  | 5.7683 | 67.6636 | 4187 | 0.0028016 | 6.5962 | 6.599 | -4.1249 | 356.9432 | 14466.0362 | -0.011556
211 |  | 5.7683 | 67.6521 | 4187 | 0.0028011 | 6.599 | 6.6018 | -4.1249 | 357.0042 | 14533.6883 | -0.011554
212 |  | 5.7683 | 67.6405 | 4187 | 0.0028006 | 6.6018 | 6.6046 | -4.1249 | 357.0652 | 14601.3288 | -0.011552
213 |  | 5.7683 | 67.629 | 4187 | 0.0028001 | 6.6046 | 6.6074 | -4.1249 | 357.1262 | 14668.9578 | -0.01155
214 |  | 5.7683 | 67.6174 | 4187 | 0.0027997 | 6.6074 | 6.6102 | -4.1249 | 357.1872 | 14736.5752 | -0.011548
215 |  | 5.7683 | 67.6059 | 4187 | 0.0027992 | 6.6102 | 6.613 | -4.1249 | 357.2482 | 14804.1811 | -0.011546
216 |  | 5.7683 | 67.5943 | 4187 | 0.0027987 | 6.613 | 6.6158 | -4.1249 | 357.3092 | 14871.7754 | -0.011544
217 |  | 5.7683 | 67.5828 | 4187 | 0.0027982 | 6.6158 | 6.6186 | -4.1249 | 357.3702 | 14939.3582 | -0.011542
218 |  | 5.7683 | 67.5712 | 4187 | 0.0027977 | 6.6186 | 6.6214 | -4.1249 | 357.4313 | 15006.9295 | -0.01154
219 |  | 5.7683 | 67.5597 | 4187 | 0.0027973 | 6.6214 | 6.6241 | -4.1249 | 357.4923 | 15074.4892 | -0.011538
220 |  | 5.7683 | 67.5482 | 4187 | 0.0027968 | 6.6241 | 6.6269 | -4.1249 | 357.5534 | 15142.0373 | -0.011536
221 |  | 5.7683 | 67.5366 | 4187 | 0.0027963 | 6.6269 | 6.6297 | -4.1249 | 357.6145 | 15209.574 | -0.011534
222 |  | 5.7683 | 67.5251 | 4187 | 0.0027958 | 6.6297 | 6.6325 | -4.1249 | 357.6756 | 15277.0991 | -0.011532
223 |  | 5.7683 | 67.5136 | 4187 | 0.0027954 | 6.6325 | 6.6353 | -4.1249 | 357.7367 | 15344.6126 | -0.01153
224 |  | 5.7683 | 67.502 | 4187 | 0.0027949 | 6.6353 | 6.6381 | -4.1249 | 357.7978 | 15412.1147 | -0.011528
225 |  | 5.7683 | 67.4905 | 4187 | 0.0027944 | 6.6381 | 6.6409 | -4.1249 | 357.8589 | 15479.6052 | -0.011527
226 |  | 5.7683 | 67.479 | 4187 | 0.0027939 | 6.6409 | 6.6437 | -4.1249 | 357.92 | 15547.0841 | -0.011525
227 |  | 5.7683 | 67.4675 | 4187 | 0.0027934 | 6.6437 | 6.6465 | -4.1249 | 357.9812 | 15614.5516 | -0.011523
228 |  | 5.7683 | 67.4559 | 4187 | 0.002793 | 6.6465 | 6.6493 | -4.1249 | 358.0423 | 15682.0075 | -0.011521
229 |  | 5.7683 | 67.4444 | 4187 | 0.0027925 | 6.6493 | 6.6521 | -4.1249 | 358.1035 | 15749.4519 | -0.011519
230 |  | 5.7683 | 67.4329 | 4187 | 0.002792 | 6.6521 | 6.6549 | -4.1249 | 358.1646 | 15816.8848 | -0.011517
231 |  | 5.7683 | 67.4214 | 4187 | 0.0027915 | 6.6549 | 6.6577 | -4.1249 | 358.2258 | 15884.3062 | -0.011515
232 |  | 5.7683 | 67.4099 | 4187 | 0.0027911 | 6.6577 | 6.6605 | -4.1249 | 358.287 | 15951.7161 | -0.011513
233 |  | 5.7683 | 67.3983 | 4187 | 0.0027906 | 6.6605 | 6.6633 | -4.1249 | 358.3482 | 16019.1144 | -0.011511
234 |  | 5.7683 | 67.3868 | 4187 | 0.0027901 | 6.6633 | 6.6661 | -4.1249 | 358.4094 | 16086.5013 | -0.011509
235 |  | 5.7683 | 67.3753 | 4187 | 0.0027896 | 6.6661 | 6.6688 | -4.1249 | 358.4706 | 16153.8766 | -0.011507
236 |  | 5.7683 | 67.3638 | 4187 | 0.0027892 | 6.6688 | 6.6716 | -4.1249 | 358.5319 | 16221.2404 | -0.011505

## Cu101
|  |  | buis | verlies W/M | L /°C/sec
diam | wandikte |  | inhoud l/m |  | W/M
101.6 | 1.6 | 3.1416 | 7.6047 | 80.1459 | 4187
[8 empty] | J/sec/mtr | aantal mtr. | verlies
|  | buis | verlies W/M | L /°C/sec | verlies temp | begintemp | eindtemp | verlies | bij 1°C | totaal J/sec
|  | inhoud L |  | W/M | °C per M | °C | °C | per m°C | daling | aantal mtr
1 | 101.6 | 7.6047 | 80.1459 | 4187 | 0.0025171 | 6 | 6.0025 | -4.7145 | 397.2844 | 80.1459 | -0.011867
2 |  | 7.6047 | 80.1341 | 4187 | 0.0025167 | 6.0025 | 6.005 | -4.7145 | 397.3432 | 160.28 | -0.011865
3 |  | 7.6047 | 80.1222 | 4187 | 0.0025163 | 6.005 | 6.0076 | -4.7145 | 397.4021 | 240.4022 | -0.011863
4 |  | 7.6047 | 80.1103 | 4187 | 0.002516 | 6.0076 | 6.0101 | -4.7145 | 397.4609 | 320.5126 | -0.011861
5 |  | 7.6047 | 80.0985 | 4187 | 0.0025156 | 6.0101 | 6.0126 | -4.7145 | 397.5198 | 400.611 | -0.01186
6 |  | 7.6047 | 80.0866 | 4187 | 0.0025152 | 6.0126 | 6.0151 | -4.7145 | 397.5787 | 480.6977 | -0.011858
7 |  | 7.6047 | 80.0748 | 4187 | 0.0025149 | 6.0151 | 6.0176 | -4.7145 | 397.6375 | 560.7724 | -0.011856
8 |  | 7.6047 | 80.0629 | 4187 | 0.0025145 | 6.0176 | 6.0201 | -4.7145 | 397.6964 | 640.8353 | -0.011854
9 |  | 7.6047 | 80.0511 | 4187 | 0.0025141 | 6.0201 | 6.0226 | -4.7145 | 397.7553 | 720.8864 | -0.011853
10 |  | 7.6047 | 80.0392 | 4187 | 0.0025137 | 6.0226 | 6.0252 | -4.7145 | 397.8142 | 800.9256 | -0.011851
11 |  | 7.6047 | 80.0274 | 4187 | 0.0025134 | 6.0252 | 6.0277 | -4.7145 | 397.8731 | 880.953 | -0.011849
12 |  | 7.6047 | 80.0155 | 4187 | 0.002513 | 6.0277 | 6.0302 | -4.7145 | 397.932 | 960.9685 | -0.011847
13 |  | 7.6047 | 80.0037 | 4187 | 0.0025126 | 6.0302 | 6.0327 | -4.7145 | 397.991 | 1040.9721 | -0.011846
14 |  | 7.6047 | 79.9918 | 4187 | 0.0025122 | 6.0327 | 6.0352 | -4.7145 | 398.0499 | 1120.9639 | -0.011844
15 |  | 7.6047 | 79.98 | 4187 | 0.0025119 | 6.0352 | 6.0377 | -4.7145 | 398.1088 | 1200.9439 | -0.011842
16 |  | 7.6047 | 79.9681 | 4187 | 0.0025115 | 6.0377 | 6.0402 | -4.7145 | 398.1678 | 1280.912 | -0.01184
17 |  | 7.6047 | 79.9563 | 4187 | 0.0025111 | 6.0402 | 6.0427 | -4.7145 | 398.2268 | 1360.8683 | -0.011839
18 |  | 7.6047 | 79.9444 | 4187 | 0.0025108 | 6.0427 | 6.0453 | -4.7145 | 398.2857 | 1440.8127 | -0.011837
19 |  | 7.6047 | 79.9326 | 4187 | 0.0025104 | 6.0453 | 6.0478 | -4.7145 | 398.3447 | 1520.7453 | -0.011835
20 |  | 7.6047 | 79.9208 | 4187 | 0.00251 | 6.0478 | 6.0503 | -4.7145 | 398.4037 | 1600.6661 | -0.011833
21 |  | 7.6047 | 79.9089 | 4187 | 0.0025096 | 6.0503 | 6.0528 | -4.7145 | 398.4627 | 1680.575 | -0.011832
22 |  | 7.6047 | 79.8971 | 4187 | 0.0025093 | 6.0528 | 6.0553 | -4.7145 | 398.5217 | 1760.4722 | -0.01183
23 |  | 7.6047 | 79.8853 | 4187 | 0.0025089 | 6.0553 | 6.0578 | -4.7145 | 398.5807 | 1840.3574 | -0.011828
24 |  | 7.6047 | 79.8734 | 4187 | 0.0025085 | 6.0578 | 6.0603 | -4.7145 | 398.6398 | 1920.2309 | -0.011826
25 |  | 7.6047 | 79.8616 | 4187 | 0.0025082 | 6.0603 | 6.0628 | -4.7145 | 398.6988 | 2000.0925 | -0.011825
26 |  | 7.6047 | 79.8498 | 4187 | 0.0025078 | 6.0628 | 6.0653 | -4.7145 | 398.7578 | 2079.9423 | -0.011823
27 |  | 7.6047 | 79.838 | 4187 | 0.0025074 | 6.0653 | 6.0678 | -4.7145 | 398.8169 | 2159.7803 | -0.011821
28 |  | 7.6047 | 79.8262 | 4187 | 0.002507 | 6.0678 | 6.0703 | -4.7145 | 398.8759 | 2239.6064 | -0.011819
29 |  | 7.6047 | 79.8143 | 4187 | 0.0025067 | 6.0703 | 6.0728 | -4.7145 | 398.935 | 2319.4208 | -0.011818
30 |  | 7.6047 | 79.8025 | 4187 | 0.0025063 | 6.0728 | 6.0754 | -4.7145 | 398.9941 | 2399.2233 | -0.011816
31 |  | 7.6047 | 79.7907 | 4187 | 0.0025059 | 6.0754 | 6.0779 | -4.7145 | 399.0532 | 2479.014 | -0.011814
32 |  | 7.6047 | 79.7789 | 4187 | 0.0025056 | 6.0779 | 6.0804 | -4.7145 | 399.1123 | 2558.7929 | -0.011812
33 |  | 7.6047 | 79.7671 | 4187 | 0.0025052 | 6.0804 | 6.0829 | -4.7145 | 399.1714 | 2638.5599 | -0.011811
34 |  | 7.6047 | 79.7553 | 4187 | 0.0025048 | 6.0829 | 6.0854 | -4.7145 | 399.2305 | 2718.3152 | -0.011809
35 |  | 7.6047 | 79.7435 | 4187 | 0.0025044 | 6.0854 | 6.0879 | -4.7145 | 399.2896 | 2798.0587 | -0.011807
36 |  | 7.6047 | 79.7316 | 4187 | 0.0025041 | 6.0879 | 6.0904 | -4.7145 | 399.3487 | 2877.7903 | -0.011805
37 |  | 7.6047 | 79.7198 | 4187 | 0.0025037 | 6.0904 | 6.0929 | -4.7145 | 399.4079 | 2957.5101 | -0.011804
38 |  | 7.6047 | 79.708 | 4187 | 0.0025033 | 6.0929 | 6.0954 | -4.7145 | 399.467 | 3037.2182 | -0.011802
39 |  | 7.6047 | 79.6962 | 4187 | 0.002503 | 6.0954 | 6.0979 | -4.7145 | 399.5262 | 3116.9144 | -0.0118
40 |  | 7.6047 | 79.6844 | 4187 | 0.0025026 | 6.0979 | 6.1004 | -4.7145 | 399.5853 | 3196.5989 | -0.011798
41 |  | 7.6047 | 79.6726 | 4187 | 0.0025022 | 6.1004 | 6.1029 | -4.7145 | 399.6445 | 3276.2715 | -0.011797
42 |  | 7.6047 | 79.6608 | 4187 | 0.0025019 | 6.1029 | 6.1054 | -4.7145 | 399.7037 | 3355.9323 | -0.011795
43 |  | 7.6047 | 79.649 | 4187 | 0.0025015 | 6.1054 | 6.1079 | -4.7145 | 399.7629 | 3435.5814 | -0.011793
44 |  | 7.6047 | 79.6373 | 4187 | 0.0025011 | 6.1079 | 6.1104 | -4.7145 | 399.8221 | 3515.2186 | -0.011791
45 |  | 7.6047 | 79.6255 | 4187 | 0.0025007 | 6.1104 | 6.1129 | -4.7145 | 399.8813 | 3594.8441 | -0.01179
46 |  | 7.6047 | 79.6137 | 4187 | 0.0025004 | 6.1129 | 6.1154 | -4.7145 | 399.9405 | 3674.4578 | -0.011788
47 |  | 7.6047 | 79.6019 | 4187 | 0.0025 | 6.1154 | 6.1179 | -4.7145 | 399.9997 | 3754.0597 | -0.011786
48 |  | 7.6047 | 79.5901 | 4187 | 0.0024996 | 6.1179 | 6.1204 | -4.7145 | 400.059 | 3833.6498 | -0.011784
49 |  | 7.6047 | 79.5783 | 4187 | 0.0024993 | 6.1204 | 6.1229 | -4.7145 | 400.1182 | 3913.2281 | -0.011783
50 |  | 7.6047 | 79.5665 | 4187 | 0.0024989 | 6.1229 | 6.1254 | -4.7145 | 400.1775 | 3992.7946 | -0.011781
51 |  | 7.6047 | 79.5548 | 4187 | 0.0024985 | 6.1254 | 6.1279 | -4.7145 | 400.2367 | 4072.3494 | -0.011779
52 |  | 7.6047 | 79.543 | 4187 | 0.0024982 | 6.1279 | 6.1304 | -4.7145 | 400.296 | 4151.8923 | -0.011777
53 |  | 7.6047 | 79.5312 | 4187 | 0.0024978 | 6.1304 | 6.1329 | -4.7145 | 400.3553 | 4231.4235 | -0.011776
54 |  | 7.6047 | 79.5194 | 4187 | 0.0024974 | 6.1329 | 6.1354 | -4.7145 | 400.4145 | 4310.9429 | -0.011774
55 |  | 7.6047 | 79.5076 | 4187 | 0.002497 | 6.1354 | 6.1379 | -4.7145 | 400.4738 | 4390.4506 | -0.011772
56 |  | 7.6047 | 79.4959 | 4187 | 0.0024967 | 6.1379 | 6.1404 | -4.7145 | 400.5331 | 4469.9464 | -0.01177
57 |  | 7.6047 | 79.4841 | 4187 | 0.0024963 | 6.1404 | 6.1429 | -4.7145 | 400.5925 | 4549.4305 | -0.011769
58 |  | 7.6047 | 79.4723 | 4187 | 0.0024959 | 6.1429 | 6.1454 | -4.7145 | 400.6518 | 4628.9029 | -0.011767
59 |  | 7.6047 | 79.4606 | 4187 | 0.0024956 | 6.1454 | 6.1479 | -4.7145 | 400.7111 | 4708.3634 | -0.011765
60 |  | 7.6047 | 79.4488 | 4187 | 0.0024952 | 6.1479 | 6.1504 | -4.7145 | 400.7705 | 4787.8122 | -0.011764
61 |  | 7.6047 | 79.437 | 4187 | 0.0024948 | 6.1504 | 6.1529 | -4.7145 | 400.8298 | 4867.2493 | -0.011762
62 |  | 7.6047 | 79.4253 | 4187 | 0.0024945 | 6.1529 | 6.1554 | -4.7145 | 400.8892 | 4946.6746 | -0.01176
63 |  | 7.6047 | 79.4135 | 4187 | 0.0024941 | 6.1554 | 6.1579 | -4.7145 | 400.9485 | 5026.0881 | -0.011758
64 |  | 7.6047 | 79.4018 | 4187 | 0.0024937 | 6.1579 | 6.1603 | -4.7145 | 401.0079 | 5105.4898 | -0.011757
65 |  | 7.6047 | 79.39 | 4187 | 0.0024933 | 6.1603 | 6.1628 | -4.7145 | 401.0673 | 5184.8798 | -0.011755
66 |  | 7.6047 | 79.3782 | 4187 | 0.002493 | 6.1628 | 6.1653 | -4.7145 | 401.1267 | 5264.2581 | -0.011753
67 |  | 7.6047 | 79.3665 | 4187 | 0.0024926 | 6.1653 | 6.1678 | -4.7145 | 401.1861 | 5343.6246 | -0.011751
68 |  | 7.6047 | 79.3547 | 4187 | 0.0024922 | 6.1678 | 6.1703 | -4.7145 | 401.2455 | 5422.9793 | -0.01175
69 |  | 7.6047 | 79.343 | 4187 | 0.0024919 | 6.1703 | 6.1728 | -4.7145 | 401.3049 | 5502.3223 | -0.011748
70 |  | 7.6047 | 79.3312 | 4187 | 0.0024915 | 6.1728 | 6.1753 | -4.7145 | 401.3643 | 5581.6535 | -0.011746
71 |  | 7.6047 | 79.3195 | 4187 | 0.0024911 | 6.1753 | 6.1778 | -4.7145 | 401.4238 | 5660.973 | -0.011744
72 |  | 7.6047 | 79.3078 | 4187 | 0.0024908 | 6.1778 | 6.1803 | -4.7145 | 401.4832 | 5740.2808 | -0.011743
73 |  | 7.6047 | 79.296 | 4187 | 0.0024904 | 6.1803 | 6.1828 | -4.7145 | 401.5427 | 5819.5768 | -0.011741
74 |  | 7.6047 | 79.2843 | 4187 | 0.00249 | 6.1828 | 6.1853 | -4.7145 | 401.6021 | 5898.8611 | -0.011739
75 |  | 7.6047 | 79.2725 | 4187 | 0.0024897 | 6.1853 | 6.1878 | -4.7145 | 401.6616 | 5978.1336 | -0.011737
76 |  | 7.6047 | 79.2608 | 4187 | 0.0024893 | 6.1878 | 6.1902 | -4.7145 | 401.7211 | 6057.3944 | -0.011736
77 |  | 7.6047 | 79.2491 | 4187 | 0.0024889 | 6.1902 | 6.1927 | -4.7145 | 401.7806 | 6136.6435 | -0.011734
78 |  | 7.6047 | 79.2373 | 4187 | 0.0024886 | 6.1927 | 6.1952 | -4.7145 | 401.8401 | 6215.8808 | -0.011732
79 |  | 7.6047 | 79.2256 | 4187 | 0.0024882 | 6.1952 | 6.1977 | -4.7145 | 401.8996 | 6295.1064 | -0.01173
80 |  | 7.6047 | 79.2139 | 4187 | 0.0024878 | 6.1977 | 6.2002 | -4.7145 | 401.9591 | 6374.3202 | -0.011729
81 |  | 7.6047 | 79.2021 | 4187 | 0.0024874 | 6.2002 | 6.2027 | -4.7145 | 402.0186 | 6453.5224 | -0.011727
82 |  | 7.6047 | 79.1904 | 4187 | 0.0024871 | 6.2027 | 6.2052 | -4.7145 | 402.0782 | 6532.7128 | -0.011725
83 |  | 7.6047 | 79.1787 | 4187 | 0.0024867 | 6.2052 | 6.2077 | -4.7145 | 402.1377 | 6611.8914 | -0.011724
84 |  | 7.6047 | 79.167 | 4187 | 0.0024863 | 6.2077 | 6.2101 | -4.7145 | 402.1972 | 6691.0584 | -0.011722
85 |  | 7.6047 | 79.1552 | 4187 | 0.002486 | 6.2101 | 6.2126 | -4.7145 | 402.2568 | 6770.2136 | -0.01172
86 |  | 7.6047 | 79.1435 | 4187 | 0.0024856 | 6.2126 | 6.2151 | -4.7145 | 402.3164 | 6849.3571 | -0.011718
87 |  | 7.6047 | 79.1318 | 4187 | 0.0024852 | 6.2151 | 6.2176 | -4.7145 | 402.376 | 6928.4889 | -0.011717
88 |  | 7.6047 | 79.1201 | 4187 | 0.0024849 | 6.2176 | 6.2201 | -4.7145 | 402.4355 | 7007.609 | -0.011715
89 |  | 7.6047 | 79.1084 | 4187 | 0.0024845 | 6.2201 | 6.2226 | -4.7145 | 402.4951 | 7086.7174 | -0.011713
90 |  | 7.6047 | 79.0967 | 4187 | 0.0024841 | 6.2226 | 6.2251 | -4.7145 | 402.5547 | 7165.814 | -0.011711
91 |  | 7.6047 | 79.0849 | 4187 | 0.0024838 | 6.2251 | 6.2275 | -4.7145 | 402.6143 | 7244.899 | -0.01171
92 |  | 7.6047 | 79.0732 | 4187 | 0.0024834 | 6.2275 | 6.23 | -4.7145 | 402.674 | 7323.9722 | -0.011708
93 |  | 7.6047 | 79.0615 | 4187 | 0.002483 | 6.23 | 6.2325 | -4.7145 | 402.7336 | 7403.0337 | -0.011706
94 |  | 7.6047 | 79.0498 | 4187 | 0.0024827 | 6.2325 | 6.235 | -4.7145 | 402.7932 | 7482.0835 | -0.011704
95 |  | 7.6047 | 79.0381 | 4187 | 0.0024823 | 6.235 | 6.2375 | -4.7145 | 402.8529 | 7561.1217 | -0.011703
96 |  | 7.6047 | 79.0264 | 4187 | 0.0024819 | 6.2375 | 6.2399 | -4.7145 | 402.9125 | 7640.1481 | -0.011701
97 |  | 7.6047 | 79.0147 | 4187 | 0.0024816 | 6.2399 | 6.2424 | -4.7145 | 402.9722 | 7719.1628 | -0.011699
98 |  | 7.6047 | 79.003 | 4187 | 0.0024812 | 6.2424 | 6.2449 | -4.7145 | 403.0319 | 7798.1658 | -0.011698
99 |  | 7.6047 | 78.9913 | 4187 | 0.0024808 | 6.2449 | 6.2474 | -4.7145 | 403.0916 | 7877.1571 | -0.011696
100 |  | 7.6047 | 78.9796 | 4187 | 0.0024805 | 6.2474 | 6.2499 | -4.7145 | 403.1513 | 7956.1367 | -0.011694
101 |  | 7.6047 | 78.9679 | 4187 | 0.0024801 | 6.2499 | 6.2524 | -4.7145 | 403.211 | 8035.1046 | -0.011692
102 |  | 7.6047 | 78.9562 | 4187 | 0.0024797 | 6.2524 | 6.2548 | -4.7145 | 403.2707 | 8114.0609 | -0.011691
103 |  | 7.6047 | 78.9445 | 4187 | 0.0024794 | 6.2548 | 6.2573 | -4.7145 | 403.3304 | 8193.0054 | -0.011689
104 |  | 7.6047 | 78.9328 | 4187 | 0.002479 | 6.2573 | 6.2598 | -4.7145 | 403.3901 | 8271.9383 | -0.011687
105 |  | 7.6047 | 78.9212 | 4187 | 0.0024786 | 6.2598 | 6.2623 | -4.7145 | 403.4499 | 8350.8594 | -0.011685
106 |  | 7.6047 | 78.9095 | 4187 | 0.0024783 | 6.2623 | 6.2647 | -4.7145 | 403.5096 | 8429.7689 | -0.011684
107 |  | 7.6047 | 78.8978 | 4187 | 0.0024779 | 6.2647 | 6.2672 | -4.7145 | 403.5694 | 8508.6667 | -0.011682
108 |  | 7.6047 | 78.8861 | 4187 | 0.0024775 | 6.2672 | 6.2697 | -4.7145 | 403.6291 | 8587.5528 | -0.01168
109 |  | 7.6047 | 78.8744 | 4187 | 0.0024772 | 6.2697 | 6.2722 | -4.7145 | 403.6889 | 8666.4272 | -0.011678
110 |  | 7.6047 | 78.8628 | 4187 | 0.0024768 | 6.2722 | 6.2747 | -4.7145 | 403.7487 | 8745.29 | -0.011677
111 |  | 7.6047 | 78.8511 | 4187 | 0.0024764 | 6.2747 | 6.2771 | -4.7145 | 403.8085 | 8824.1411 | -0.011675
112 |  | 7.6047 | 78.8394 | 4187 | 0.0024761 | 6.2771 | 6.2796 | -4.7145 | 403.8683 | 8902.9805 | -0.011673
113 |  | 7.6047 | 78.8277 | 4187 | 0.0024757 | 6.2796 | 6.2821 | -4.7145 | 403.9281 | 8981.8082 | -0.011672
114 |  | 7.6047 | 78.8161 | 4187 | 0.0024753 | 6.2821 | 6.2846 | -4.7145 | 403.9879 | 9060.6242 | -0.01167
115 |  | 7.6047 | 78.8044 | 4187 | 0.002475 | 6.2846 | 6.287 | -4.7145 | 404.0477 | 9139.4286 | -0.011668
116 |  | 7.6047 | 78.7927 | 4187 | 0.0024746 | 6.287 | 6.2895 | -4.7145 | 404.1075 | 9218.2214 | -0.011666
117 |  | 7.6047 | 78.7811 | 4187 | 0.0024742 | 6.2895 | 6.292 | -4.7145 | 404.1674 | 9297.0024 | -0.011665
118 |  | 7.6047 | 78.7694 | 4187 | 0.0024739 | 6.292 | 6.2945 | -4.7145 | 404.2272 | 9375.7718 | -0.011663
119 |  | 7.6047 | 78.7577 | 4187 | 0.0024735 | 6.2945 | 6.2969 | -4.7145 | 404.2871 | 9454.5295 | -0.011661
120 |  | 7.6047 | 78.7461 | 4187 | 0.0024731 | 6.2969 | 6.2994 | -4.7145 | 404.347 | 9533.2756 | -0.011659
121 |  | 7.6047 | 78.7344 | 4187 | 0.0024728 | 6.2994 | 6.3019 | -4.7145 | 404.4068 | 9612.01 | -0.011658
122 |  | 7.6047 | 78.7227 | 4187 | 0.0024724 | 6.3019 | 6.3044 | -4.7145 | 404.4667 | 9690.7327 | -0.011656
123 |  | 7.6047 | 78.7111 | 4187 | 0.002472 | 6.3044 | 6.3068 | -4.7145 | 404.5266 | 9769.4438 | -0.011654
124 |  | 7.6047 | 78.6994 | 4187 | 0.0024717 | 6.3068 | 6.3093 | -4.7145 | 404.5865 | 9848.1433 | -0.011653
125 |  | 7.6047 | 78.6878 | 4187 | 0.0024713 | 6.3093 | 6.3118 | -4.7145 | 404.6464 | 9926.831 | -0.011651
126 |  | 7.6047 | 78.6761 | 4187 | 0.0024709 | 6.3118 | 6.3142 | -4.7145 | 404.7064 | 10005.5072 | -0.011649
127 |  | 7.6047 | 78.6645 | 4187 | 0.0024706 | 6.3142 | 6.3167 | -4.7145 | 404.7663 | 10084.1717 | -0.011647
128 |  | 7.6047 | 78.6528 | 4187 | 0.0024702 | 6.3167 | 6.3192 | -4.7145 | 404.8262 | 10162.8245 | -0.011646
129 |  | 7.6047 | 78.6412 | 4187 | 0.0024698 | 6.3192 | 6.3216 | -4.7145 | 404.8862 | 10241.4657 | -0.011644
130 |  | 7.6047 | 78.6295 | 4187 | 0.0024695 | 6.3216 | 6.3241 | -4.7145 | 404.9461 | 10320.0952 | -0.011642
131 |  | 7.6047 | 78.6179 | 4187 | 0.0024691 | 6.3241 | 6.3266 | -4.7145 | 405.0061 | 10398.7131 | -0.01164
132 |  | 7.6047 | 78.6063 | 4187 | 0.0024687 | 6.3266 | 6.3291 | -4.7145 | 405.0661 | 10477.3194 | -0.011639
133 |  | 7.6047 | 78.5946 | 4187 | 0.0024684 | 6.3291 | 6.3315 | -4.7145 | 405.1261 | 10555.914 | -0.011637
134 |  | 7.6047 | 78.583 | 4187 | 0.002468 | 6.3315 | 6.334 | -4.7145 | 405.1861 | 10634.497 | -0.011635
135 |  | 7.6047 | 78.5714 | 4187 | 0.0024676 | 6.334 | 6.3365 | -4.7145 | 405.2461 | 10713.0684 | -0.011634
136 |  | 7.6047 | 78.5597 | 4187 | 0.0024673 | 6.3365 | 6.3389 | -4.7145 | 405.3061 | 10791.6281 | -0.011632
137 |  | 7.6047 | 78.5481 | 4187 | 0.0024669 | 6.3389 | 6.3414 | -4.7145 | 405.3661 | 10870.1762 | -0.01163
138 |  | 7.6047 | 78.5365 | 4187 | 0.0024665 | 6.3414 | 6.3439 | -4.7145 | 405.4261 | 10948.7126 | -0.011628
139 |  | 7.6047 | 78.5248 | 4187 | 0.0024662 | 6.3439 | 6.3463 | -4.7145 | 405.4862 | 11027.2375 | -0.011627
140 |  | 7.6047 | 78.5132 | 4187 | 0.0024658 | 6.3463 | 6.3488 | -4.7145 | 405.5462 | 11105.7507 | -0.011625
141 |  | 7.6047 | 78.5016 | 4187 | 0.0024654 | 6.3488 | 6.3513 | -4.7145 | 405.6063 | 11184.2522 | -0.011623
142 |  | 7.6047 | 78.49 | 4187 | 0.0024651 | 6.3513 | 6.3537 | -4.7145 | 405.6663 | 11262.7422 | -0.011622
143 |  | 7.6047 | 78.4783 | 4187 | 0.0024647 | 6.3537 | 6.3562 | -4.7145 | 405.7264 | 11341.2205 | -0.01162
144 |  | 7.6047 | 78.4667 | 4187 | 0.0024644 | 6.3562 | 6.3587 | -4.7145 | 405.7865 | 11419.6872 | -0.011618
145 |  | 7.6047 | 78.4551 | 4187 | 0.002464 | 6.3587 | 6.3611 | -4.7145 | 405.8466 | 11498.1423 | -0.011616
146 |  | 7.6047 | 78.4435 | 4187 | 0.0024636 | 6.3611 | 6.3636 | -4.7145 | 405.9067 | 11576.5858 | -0.011615
147 |  | 7.6047 | 78.4319 | 4187 | 0.0024633 | 6.3636 | 6.366 | -4.7145 | 405.9668 | 11655.0177 | -0.011613
148 |  | 7.6047 | 78.4203 | 4187 | 0.0024629 | 6.366 | 6.3685 | -4.7145 | 406.0269 | 11733.4379 | -0.011611
149 |  | 7.6047 | 78.4086 | 4187 | 0.0024625 | 6.3685 | 6.371 | -4.7145 | 406.087 | 11811.8466 | -0.011609
150 |  | 7.6047 | 78.397 | 4187 | 0.0024622 | 6.371 | 6.3734 | -4.7145 | 406.1472 | 11890.2436 | -0.011608
151 |  | 7.6047 | 78.3854 | 4187 | 0.0024618 | 6.3734 | 6.3759 | -4.7145 | 406.2073 | 11968.629 | -0.011606
152 |  | 7.6047 | 78.3738 | 4187 | 0.0024614 | 6.3759 | 6.3784 | -4.7145 | 406.2675 | 12047.0028 | -0.011604
153 |  | 7.6047 | 78.3622 | 4187 | 0.0024611 | 6.3784 | 6.3808 | -4.7145 | 406.3276 | 12125.365 | -0.011603
154 |  | 7.6047 | 78.3506 | 4187 | 0.0024607 | 6.3808 | 6.3833 | -4.7145 | 406.3878 | 12203.7157 | -0.011601
155 |  | 7.6047 | 78.339 | 4187 | 0.0024603 | 6.3833 | 6.3857 | -4.7145 | 406.448 | 12282.0547 | -0.011599
156 |  | 7.6047 | 78.3274 | 4187 | 0.00246 | 6.3857 | 6.3882 | -4.7145 | 406.5082 | 12360.3821 | -0.011597
157 |  | 7.6047 | 78.3158 | 4187 | 0.0024596 | 6.3882 | 6.3907 | -4.7145 | 406.5684 | 12438.6979 | -0.011596
158 |  | 7.6047 | 78.3042 | 4187 | 0.0024592 | 6.3907 | 6.3931 | -4.7145 | 406.6286 | 12517.0021 | -0.011594
159 |  | 7.6047 | 78.2926 | 4187 | 0.0024589 | 6.3931 | 6.3956 | -4.7145 | 406.6888 | 12595.2947 | -0.011592
160 |  | 7.6047 | 78.281 | 4187 | 0.0024585 | 6.3956 | 6.398 | -4.7145 | 406.749 | 12673.5757 | -0.011591
161 |  | 7.6047 | 78.2694 | 4187 | 0.0024582 | 6.398 | 6.4005 | -4.7145 | 406.8093 | 12751.8452 | -0.011589
162 |  | 7.6047 | 78.2578 | 4187 | 0.0024578 | 6.4005 | 6.4029 | -4.7145 | 406.8695 | 12830.103 | -0.011587
163 |  | 7.6047 | 78.2463 | 4187 | 0.0024574 | 6.4029 | 6.4054 | -4.7145 | 406.9297 | 12908.3493 | -0.011585
164 |  | 7.6047 | 78.2347 | 4187 | 0.0024571 | 6.4054 | 6.4079 | -4.7145 | 406.99 | 12986.584 | -0.011584
165 |  | 7.6047 | 78.2231 | 4187 | 0.0024567 | 6.4079 | 6.4103 | -4.7145 | 407.0503 | 13064.8071 | -0.011582
166 |  | 7.6047 | 78.2115 | 4187 | 0.0024563 | 6.4103 | 6.4128 | -4.7145 | 407.1106 | 13143.0186 | -0.01158
167 |  | 7.6047 | 78.1999 | 4187 | 0.002456 | 6.4128 | 6.4152 | -4.7145 | 407.1708 | 13221.2185 | -0.011579
168 |  | 7.6047 | 78.1884 | 4187 | 0.0024556 | 6.4152 | 6.4177 | -4.7145 | 407.2311 | 13299.4069 | -0.011577
169 |  | 7.6047 | 78.1768 | 4187 | 0.0024552 | 6.4177 | 6.4201 | -4.7145 | 407.2914 | 13377.5836 | -0.011575
170 |  | 7.6047 | 78.1652 | 4187 | 0.0024549 | 6.4201 | 6.4226 | -4.7145 | 407.3518 | 13455.7488 | -0.011573
171 |  | 7.6047 | 78.1536 | 4187 | 0.0024545 | 6.4226 | 6.425 | -4.7145 | 407.4121 | 13533.9025 | -0.011572
172 |  | 7.6047 | 78.1421 | 4187 | 0.0024542 | 6.425 | 6.4275 | -4.7145 | 407.4724 | 13612.0445 | -0.01157
173 |  | 7.6047 | 78.1305 | 4187 | 0.0024538 | 6.4275 | 6.43 | -4.7145 | 407.5328 | 13690.175 | -0.011568
174 |  | 7.6047 | 78.1189 | 4187 | 0.0024534 | 6.43 | 6.4324 | -4.7145 | 407.5931 | 13768.2939 | -0.011567
175 |  | 7.6047 | 78.1074 | 4187 | 0.0024531 | 6.4324 | 6.4349 | -4.7145 | 407.6535 | 13846.4013 | -0.011565
176 |  | 7.6047 | 78.0958 | 4187 | 0.0024527 | 6.4349 | 6.4373 | -4.7145 | 407.7138 | 13924.4971 | -0.011563
177 |  | 7.6047 | 78.0842 | 4187 | 0.0024523 | 6.4373 | 6.4398 | -4.7145 | 407.7742 | 14002.5813 | -0.011561
178 |  | 7.6047 | 78.0727 | 4187 | 0.002452 | 6.4398 | 6.4422 | -4.7145 | 407.8346 | 14080.6539 | -0.01156
179 |  | 7.6047 | 78.0611 | 4187 | 0.0024516 | 6.4422 | 6.4447 | -4.7145 | 407.895 | 14158.715 | -0.011558
180 |  | 7.6047 | 78.0495 | 4187 | 0.0024512 | 6.4447 | 6.4471 | -4.7145 | 407.9554 | 14236.7646 | -0.011556
181 |  | 7.6047 | 78.038 | 4187 | 0.0024509 | 6.4471 | 6.4496 | -4.7145 | 408.0158 | 14314.8026 | -0.011555
182 |  | 7.6047 | 78.0264 | 4187 | 0.0024505 | 6.4496 | 6.452 | -4.7145 | 408.0762 | 14392.829 | -0.011553
183 |  | 7.6047 | 78.0149 | 4187 | 0.0024502 | 6.452 | 6.4545 | -4.7145 | 408.1367 | 14470.8439 | -0.011551
184 |  | 7.6047 | 78.0033 | 4187 | 0.0024498 | 6.4545 | 6.4569 | -4.7145 | 408.1971 | 14548.8472 | -0.011549
185 |  | 7.6047 | 77.9918 | 4187 | 0.0024494 | 6.4569 | 6.4594 | -4.7145 | 408.2575 | 14626.839 | -0.011548
186 |  | 7.6047 | 77.9802 | 4187 | 0.0024491 | 6.4594 | 6.4618 | -4.7145 | 408.318 | 14704.8192 | -0.011546
187 |  | 7.6047 | 77.9687 | 4187 | 0.0024487 | 6.4618 | 6.4643 | -4.7145 | 408.3785 | 14782.7879 | -0.011544
188 |  | 7.6047 | 77.9571 | 4187 | 0.0024483 | 6.4643 | 6.4667 | -4.7145 | 408.4389 | 14860.745 | -0.011543
189 |  | 7.6047 | 77.9456 | 4187 | 0.002448 | 6.4667 | 6.4692 | -4.7145 | 408.4994 | 14938.6906 | -0.011541
190 |  | 7.6047 | 77.9341 | 4187 | 0.0024476 | 6.4692 | 6.4716 | -4.7145 | 408.5599 | 15016.6247 | -0.011539
191 |  | 7.6047 | 77.9225 | 4187 | 0.0024473 | 6.4716 | 6.4741 | -4.7145 | 408.6204 | 15094.5472 | -0.011538
192 |  | 7.6047 | 77.911 | 4187 | 0.0024469 | 6.4741 | 6.4765 | -4.7145 | 408.6809 | 15172.4582 | -0.011536
193 |  | 7.6047 | 77.8994 | 4187 | 0.0024465 | 6.4765 | 6.479 | -4.7145 | 408.7414 | 15250.3576 | -0.011534
194 |  | 7.6047 | 77.8879 | 4187 | 0.0024462 | 6.479 | 6.4814 | -4.7145 | 408.802 | 15328.2455 | -0.011532
195 |  | 7.6047 | 77.8764 | 4187 | 0.0024458 | 6.4814 | 6.4838 | -4.7145 | 408.8625 | 15406.1219 | -0.011531
196 |  | 7.6047 | 77.8648 | 4187 | 0.0024454 | 6.4838 | 6.4863 | -4.7145 | 408.9231 | 15483.9868 | -0.011529
197 |  | 7.6047 | 77.8533 | 4187 | 0.0024451 | 6.4863 | 6.4887 | -4.7145 | 408.9836 | 15561.8401 | -0.011527
198 |  | 7.6047 | 77.8418 | 4187 | 0.0024447 | 6.4887 | 6.4912 | -4.7145 | 409.0442 | 15639.6819 | -0.011526
199 |  | 7.6047 | 77.8303 | 4187 | 0.0024444 | 6.4912 | 6.4936 | -4.7145 | 409.1048 | 15717.5121 | -0.011524
200 |  | 7.6047 | 77.8187 | 4187 | 0.002444 | 6.4936 | 6.4961 | -4.7145 | 409.1653 | 15795.3309 | -0.011522
201 |  | 7.6047 | 77.8072 | 4187 | 0.0024436 | 6.4961 | 6.4985 | -4.7145 | 409.2259 | 15873.1381 | -0.01152
202 |  | 7.6047 | 77.7957 | 4187 | 0.0024433 | 6.4985 | 6.501 | -4.7145 | 409.2865 | 15950.9338 | -0.011519
203 |  | 7.6047 | 77.7842 | 4187 | 0.0024429 | 6.501 | 6.5034 | -4.7145 | 409.3471 | 16028.718 | -0.011517
204 |  | 7.6047 | 77.7727 | 4187 | 0.0024426 | 6.5034 | 6.5058 | -4.7145 | 409.4078 | 16106.4906 | -0.011515
205 |  | 7.6047 | 77.7611 | 4187 | 0.0024422 | 6.5058 | 6.5083 | -4.7145 | 409.4684 | 16184.2518 | -0.011514
206 |  | 7.6047 | 77.7496 | 4187 | 0.0024418 | 6.5083 | 6.5107 | -4.7145 | 409.529 | 16262.0014 | -0.011512
207 |  | 7.6047 | 77.7381 | 4187 | 0.0024415 | 6.5107 | 6.5132 | -4.7145 | 409.5897 | 16339.7396 | -0.01151
208 |  | 7.6047 | 77.7266 | 4187 | 0.0024411 | 6.5132 | 6.5156 | -4.7145 | 409.6503 | 16417.4662 | -0.011509
209 |  | 7.6047 | 77.7151 | 4187 | 0.0024407 | 6.5156 | 6.5181 | -4.7145 | 409.711 | 16495.1813 | -0.011507
210 |  | 7.6047 | 77.7036 | 4187 | 0.0024404 | 6.5181 | 6.5205 | -4.7145 | 409.7717 | 16572.8849 | -0.011505
211 |  | 7.6047 | 77.6921 | 4187 | 0.00244 | 6.5205 | 6.5229 | -4.7145 | 409.8323 | 16650.577 | -0.011503
212 |  | 7.6047 | 77.6806 | 4187 | 0.0024397 | 6.5229 | 6.5254 | -4.7145 | 409.893 | 16728.2575 | -0.011502
213 |  | 7.6047 | 77.6691 | 4187 | 0.0024393 | 6.5254 | 6.5278 | -4.7145 | 409.9537 | 16805.9266 | -0.0115
214 |  | 7.6047 | 77.6576 | 4187 | 0.0024389 | 6.5278 | 6.5303 | -4.7145 | 410.0144 | 16883.5842 | -0.011498
215 |  | 7.6047 | 77.6461 | 4187 | 0.0024386 | 6.5303 | 6.5327 | -4.7145 | 410.0752 | 16961.2303 | -0.011497
216 |  | 7.6047 | 77.6346 | 4187 | 0.0024382 | 6.5327 | 6.5351 | -4.7145 | 410.1359 | 17038.8649 | -0.011495
217 |  | 7.6047 | 77.6231 | 4187 | 0.0024379 | 6.5351 | 6.5376 | -4.7145 | 410.1966 | 17116.488 | -0.011493
218 |  | 7.6047 | 77.6116 | 4187 | 0.0024375 | 6.5376 | 6.54 | -4.7145 | 410.2574 | 17194.0996 | -0.011491
219 |  | 7.6047 | 77.6001 | 4187 | 0.0024371 | 6.54 | 6.5424 | -4.7145 | 410.3181 | 17271.6997 | -0.01149
220 |  | 7.6047 | 77.5886 | 4187 | 0.0024368 | 6.5424 | 6.5449 | -4.7145 | 410.3789 | 17349.2883 | -0.011488
221 |  | 7.6047 | 77.5771 | 4187 | 0.0024364 | 6.5449 | 6.5473 | -4.7145 | 410.4397 | 17426.8655 | -0.011486
222 |  | 7.6047 | 77.5656 | 4187 | 0.0024361 | 6.5473 | 6.5497 | -4.7145 | 410.5004 | 17504.4311 | -0.011485
223 |  | 7.6047 | 77.5542 | 4187 | 0.0024357 | 6.5497 | 6.5522 | -4.7145 | 410.5612 | 17581.9853 | -0.011483
224 |  | 7.6047 | 77.5427 | 4187 | 0.0024353 | 6.5522 | 6.5546 | -4.7145 | 410.622 | 17659.528 | -0.011481
225 |  | 7.6047 | 77.5312 | 4187 | 0.002435 | 6.5546 | 6.5571 | -4.7145 | 410.6828 | 17737.0591 | -0.01148
226 |  | 7.6047 | 77.5197 | 4187 | 0.0024346 | 6.5571 | 6.5595 | -4.7145 | 410.7436 | 17814.5789 | -0.011478
227 |  | 7.6047 | 77.5082 | 4187 | 0.0024342 | 6.5595 | 6.5619 | -4.7145 | 410.8045 | 17892.0871 | -0.011476
228 |  | 7.6047 | 77.4968 | 4187 | 0.0024339 | 6.5619 | 6.5644 | -4.7145 | 410.8653 | 17969.5839 | -0.011474
229 |  | 7.6047 | 77.4853 | 4187 | 0.0024335 | 6.5644 | 6.5668 | -4.7145 | 410.9261 | 18047.0692 | -0.011473
230 |  | 7.6047 | 77.4738 | 4187 | 0.0024332 | 6.5668 | 6.5692 | -4.7145 | 410.987 | 18124.543 | -0.011471
231 |  | 7.6047 | 77.4623 | 4187 | 0.0024328 | 6.5692 | 6.5717 | -4.7145 | 411.0479 | 18202.0053 | -0.011469
232 |  | 7.6047 | 77.4509 | 4187 | 0.0024324 | 6.5717 | 6.5741 | -4.7145 | 411.1087 | 18279.4562 | -0.011468
233 |  | 7.6047 | 77.4394 | 4187 | 0.0024321 | 6.5741 | 6.5765 | -4.7145 | 411.1696 | 18356.8956 | -0.011466
234 |  | 7.6047 | 77.4279 | 4187 | 0.0024317 | 6.5765 | 6.579 | -4.7145 | 411.2305 | 18434.3236 | -0.011464
235 |  | 7.6047 | 77.4165 | 4187 | 0.0024314 | 6.579 | 6.5814 | -4.7145 | 411.2914 | 18511.74 | -0.011463
236 |  | 7.6047 | 77.405 | 4187 | 0.002431 | 6.5814 | 6.5838 | -4.7145 | 411.3523 | 18589.1451 | -0.011461

## Cu127
|  |  | buis | verlies W/M | L /°C/sec
diam | wandikte |  | inhoud l/m |  | W/M
127 | 1.6 | 3.1416 | 12.0374 | 100.1938 | 4187
[8 empty] | J/sec/mtr | aantal mtr. | verlies
|  | buis | verlies W/M | L /°C/sec | verlies temp | begintemp | eindtemp | verlies | bij 1°C | totaal J/sec
|  | inhoud L |  | W/M | °C per M | °C | °C | per m°C | daling | aantal mtr
1 | 127 | 12.0374 | 100.1938 | 4187 | 0.001988 | 6 | 6.002 | -5.8938 | 503.0291 | 100.1938 | -0.011717
2 |  | 12.0374 | 100.1821 | 4187 | 0.0019877 | 6.002 | 6.004 | -5.8938 | 503.088 | 200.376 | -0.011715
3 |  | 12.0374 | 100.1704 | 4187 | 0.0019875 | 6.004 | 6.006 | -5.8938 | 503.1468 | 300.5464 | -0.011714
4 |  | 12.0374 | 100.1587 | 4187 | 0.0019873 | 6.006 | 6.008 | -5.8938 | 503.2056 | 400.705 | -0.011712
5 |  | 12.0374 | 100.147 | 4187 | 0.001987 | 6.008 | 6.0099 | -5.8938 | 503.2645 | 500.852 | -0.011711
6 |  | 12.0374 | 100.1353 | 4187 | 0.0019868 | 6.0099 | 6.0119 | -5.8938 | 503.3233 | 600.9873 | -0.01171
7 |  | 12.0374 | 100.1236 | 4187 | 0.0019866 | 6.0119 | 6.0139 | -5.8938 | 503.3822 | 701.1108 | -0.011708
8 |  | 12.0374 | 100.1118 | 4187 | 0.0019863 | 6.0139 | 6.0159 | -5.8938 | 503.4411 | 801.2227 | -0.011707
9 |  | 12.0374 | 100.1001 | 4187 | 0.0019861 | 6.0159 | 6.0179 | -5.8938 | 503.5 | 901.3228 | -0.011706
10 |  | 12.0374 | 100.0884 | 4187 | 0.0019859 | 6.0179 | 6.0199 | -5.8938 | 503.5588 | 1001.4113 | -0.011704
11 |  | 12.0374 | 100.0767 | 4187 | 0.0019856 | 6.0199 | 6.0219 | -5.8938 | 503.6177 | 1101.488 | -0.011703
12 |  | 12.0374 | 100.065 | 4187 | 0.0019854 | 6.0219 | 6.0238 | -5.8938 | 503.6766 | 1201.553 | -0.011701
13 |  | 12.0374 | 100.0533 | 4187 | 0.0019852 | 6.0238 | 6.0258 | -5.8938 | 503.7355 | 1301.6064 | -0.0117
14 |  | 12.0374 | 100.0416 | 4187 | 0.0019849 | 6.0258 | 6.0278 | -5.8938 | 503.7945 | 1401.648 | -0.011699
15 |  | 12.0374 | 100.0299 | 4187 | 0.0019847 | 6.0278 | 6.0298 | -5.8938 | 503.8534 | 1501.6779 | -0.011697
16 |  | 12.0374 | 100.0182 | 4187 | 0.0019845 | 6.0298 | 6.0318 | -5.8938 | 503.9123 | 1601.6961 | -0.011696
17 |  | 12.0374 | 100.0065 | 4187 | 0.0019842 | 6.0318 | 6.0338 | -5.8938 | 503.9712 | 1701.7027 | -0.011695
18 |  | 12.0374 | 99.9948 | 4187 | 0.001984 | 6.0338 | 6.0357 | -5.8938 | 504.0302 | 1801.6975 | -0.011693
19 |  | 12.0374 | 99.9831 | 4187 | 0.0019838 | 6.0357 | 6.0377 | -5.8938 | 504.0891 | 1901.6807 | -0.011692
20 |  | 12.0374 | 99.9715 | 4187 | 0.0019835 | 6.0377 | 6.0397 | -5.8938 | 504.1481 | 2001.6521 | -0.011691
21 |  | 12.0374 | 99.9598 | 4187 | 0.0019833 | 6.0397 | 6.0417 | -5.8938 | 504.207 | 2101.6119 | -0.011689
22 |  | 12.0374 | 99.9481 | 4187 | 0.0019831 | 6.0417 | 6.0437 | -5.8938 | 504.266 | 2201.56 | -0.011688
23 |  | 12.0374 | 99.9364 | 4187 | 0.0019828 | 6.0437 | 6.0457 | -5.8938 | 504.325 | 2301.4964 | -0.011686
24 |  | 12.0374 | 99.9247 | 4187 | 0.0019826 | 6.0457 | 6.0476 | -5.8938 | 504.384 | 2401.4211 | -0.011685
25 |  | 12.0374 | 99.913 | 4187 | 0.0019824 | 6.0476 | 6.0496 | -5.8938 | 504.443 | 2501.3341 | -0.011684
26 |  | 12.0374 | 99.9013 | 4187 | 0.0019822 | 6.0496 | 6.0516 | -5.8938 | 504.502 | 2601.2354 | -0.011682
27 |  | 12.0374 | 99.8897 | 4187 | 0.0019819 | 6.0516 | 6.0536 | -5.8938 | 504.561 | 2701.1251 | -0.011681
28 |  | 12.0374 | 99.878 | 4187 | 0.0019817 | 6.0536 | 6.0556 | -5.8938 | 504.62 | 2801.003 | -0.01168
29 |  | 12.0374 | 99.8663 | 4187 | 0.0019815 | 6.0556 | 6.0576 | -5.8938 | 504.679 | 2900.8693 | -0.011678
30 |  | 12.0374 | 99.8546 | 4187 | 0.0019812 | 6.0576 | 6.0595 | -5.8938 | 504.738 | 3000.7239 | -0.011677
31 |  | 12.0374 | 99.8429 | 4187 | 0.001981 | 6.0595 | 6.0615 | -5.8938 | 504.797 | 3100.5669 | -0.011675
32 |  | 12.0374 | 99.8313 | 4187 | 0.0019808 | 6.0615 | 6.0635 | -5.8938 | 504.8561 | 3200.3981 | -0.011674
33 |  | 12.0374 | 99.8196 | 4187 | 0.0019805 | 6.0635 | 6.0655 | -5.8938 | 504.9151 | 3300.2177 | -0.011673
34 |  | 12.0374 | 99.8079 | 4187 | 0.0019803 | 6.0655 | 6.0675 | -5.8938 | 504.9742 | 3400.0256 | -0.011671
35 |  | 12.0374 | 99.7962 | 4187 | 0.0019801 | 6.0675 | 6.0694 | -5.8938 | 505.0332 | 3499.8219 | -0.01167
36 |  | 12.0374 | 99.7846 | 4187 | 0.0019798 | 6.0694 | 6.0714 | -5.8938 | 505.0923 | 3599.6064 | -0.011669
37 |  | 12.0374 | 99.7729 | 4187 | 0.0019796 | 6.0714 | 6.0734 | -5.8938 | 505.1514 | 3699.3793 | -0.011667
38 |  | 12.0374 | 99.7612 | 4187 | 0.0019794 | 6.0734 | 6.0754 | -5.8938 | 505.2104 | 3799.1406 | -0.011666
39 |  | 12.0374 | 99.7496 | 4187 | 0.0019791 | 6.0754 | 6.0774 | -5.8938 | 505.2695 | 3898.8901 | -0.011665
40 |  | 12.0374 | 99.7379 | 4187 | 0.0019789 | 6.0774 | 6.0793 | -5.8938 | 505.3286 | 3998.628 | -0.011663
41 |  | 12.0374 | 99.7262 | 4187 | 0.0019787 | 6.0793 | 6.0813 | -5.8938 | 505.3877 | 4098.3543 | -0.011662
42 |  | 12.0374 | 99.7146 | 4187 | 0.0019784 | 6.0813 | 6.0833 | -5.8938 | 505.4468 | 4198.0689 | -0.01166
43 |  | 12.0374 | 99.7029 | 4187 | 0.0019782 | 6.0833 | 6.0853 | -5.8938 | 505.5059 | 4297.7718 | -0.011659
44 |  | 12.0374 | 99.6913 | 4187 | 0.001978 | 6.0853 | 6.0873 | -5.8938 | 505.5651 | 4397.463 | -0.011658
45 |  | 12.0374 | 99.6796 | 4187 | 0.0019778 | 6.0873 | 6.0892 | -5.8938 | 505.6242 | 4497.1426 | -0.011656
46 |  | 12.0374 | 99.6679 | 4187 | 0.0019775 | 6.0892 | 6.0912 | -5.8938 | 505.6833 | 4596.8106 | -0.011655
47 |  | 12.0374 | 99.6563 | 4187 | 0.0019773 | 6.0912 | 6.0932 | -5.8938 | 505.7425 | 4696.4669 | -0.011654
48 |  | 12.0374 | 99.6446 | 4187 | 0.0019771 | 6.0932 | 6.0952 | -5.8938 | 505.8016 | 4796.1115 | -0.011652
49 |  | 12.0374 | 99.633 | 4187 | 0.0019768 | 6.0952 | 6.0971 | -5.8938 | 505.8608 | 4895.7445 | -0.011651
50 |  | 12.0374 | 99.6213 | 4187 | 0.0019766 | 6.0971 | 6.0991 | -5.8938 | 505.9199 | 4995.3658 | -0.01165
51 |  | 12.0374 | 99.6097 | 4187 | 0.0019764 | 6.0991 | 6.1011 | -5.8938 | 505.9791 | 5094.9755 | -0.011648
52 |  | 12.0374 | 99.598 | 4187 | 0.0019761 | 6.1011 | 6.1031 | -5.8938 | 506.0383 | 5194.5735 | -0.011647
53 |  | 12.0374 | 99.5864 | 4187 | 0.0019759 | 6.1031 | 6.105 | -5.8938 | 506.0974 | 5294.1599 | -0.011645
54 |  | 12.0374 | 99.5747 | 4187 | 0.0019757 | 6.105 | 6.107 | -5.8938 | 506.1566 | 5393.7347 | -0.011644
55 |  | 12.0374 | 99.5631 | 4187 | 0.0019754 | 6.107 | 6.109 | -5.8938 | 506.2158 | 5493.2978 | -0.011643
56 |  | 12.0374 | 99.5515 | 4187 | 0.0019752 | 6.109 | 6.111 | -5.8938 | 506.275 | 5592.8492 | -0.011641
57 |  | 12.0374 | 99.5398 | 4187 | 0.001975 | 6.111 | 6.1129 | -5.8938 | 506.3342 | 5692.389 | -0.01164
58 |  | 12.0374 | 99.5282 | 4187 | 0.0019747 | 6.1129 | 6.1149 | -5.8938 | 506.3935 | 5791.9172 | -0.011639
59 |  | 12.0374 | 99.5165 | 4187 | 0.0019745 | 6.1149 | 6.1169 | -5.8938 | 506.4527 | 5891.4338 | -0.011637
60 |  | 12.0374 | 99.5049 | 4187 | 0.0019743 | 6.1169 | 6.1189 | -5.8938 | 506.5119 | 5990.9387 | -0.011636
61 |  | 12.0374 | 99.4933 | 4187 | 0.0019741 | 6.1189 | 6.1208 | -5.8938 | 506.5712 | 6090.4319 | -0.011635
62 |  | 12.0374 | 99.4816 | 4187 | 0.0019738 | 6.1208 | 6.1228 | -5.8938 | 506.6304 | 6189.9136 | -0.011633
63 |  | 12.0374 | 99.47 | 4187 | 0.0019736 | 6.1228 | 6.1248 | -5.8938 | 506.6897 | 6289.3835 | -0.011632
64 |  | 12.0374 | 99.4584 | 4187 | 0.0019734 | 6.1248 | 6.1268 | -5.8938 | 506.7489 | 6388.8419 | -0.011631
65 |  | 12.0374 | 99.4467 | 4187 | 0.0019731 | 6.1268 | 6.1287 | -5.8938 | 506.8082 | 6488.2886 | -0.011629
66 |  | 12.0374 | 99.4351 | 4187 | 0.0019729 | 6.1287 | 6.1307 | -5.8938 | 506.8674 | 6587.7237 | -0.011628
67 |  | 12.0374 | 99.4235 | 4187 | 0.0019727 | 6.1307 | 6.1327 | -5.8938 | 506.9267 | 6687.1472 | -0.011626
68 |  | 12.0374 | 99.4118 | 4187 | 0.0019724 | 6.1327 | 6.1347 | -5.8938 | 506.986 | 6786.5591 | -0.011625
69 |  | 12.0374 | 99.4002 | 4187 | 0.0019722 | 6.1347 | 6.1366 | -5.8938 | 507.0453 | 6885.9593 | -0.011624
70 |  | 12.0374 | 99.3886 | 4187 | 0.001972 | 6.1366 | 6.1386 | -5.8938 | 507.1046 | 6985.3479 | -0.011622
71 |  | 12.0374 | 99.377 | 4187 | 0.0019717 | 6.1386 | 6.1406 | -5.8938 | 507.1639 | 7084.7249 | -0.011621
72 |  | 12.0374 | 99.3654 | 4187 | 0.0019715 | 6.1406 | 6.1425 | -5.8938 | 507.2232 | 7184.0902 | -0.01162
73 |  | 12.0374 | 99.3537 | 4187 | 0.0019713 | 6.1425 | 6.1445 | -5.8938 | 507.2825 | 7283.444 | -0.011618
74 |  | 12.0374 | 99.3421 | 4187 | 0.0019711 | 6.1445 | 6.1465 | -5.8938 | 507.3419 | 7382.7861 | -0.011617
75 |  | 12.0374 | 99.3305 | 4187 | 0.0019708 | 6.1465 | 6.1485 | -5.8938 | 507.4012 | 7482.1166 | -0.011616
76 |  | 12.0374 | 99.3189 | 4187 | 0.0019706 | 6.1485 | 6.1504 | -5.8938 | 507.4606 | 7581.4355 | -0.011614
77 |  | 12.0374 | 99.3073 | 4187 | 0.0019704 | 6.1504 | 6.1524 | -5.8938 | 507.5199 | 7680.7427 | -0.011613
78 |  | 12.0374 | 99.2957 | 4187 | 0.0019701 | 6.1524 | 6.1544 | -5.8938 | 507.5793 | 7780.0384 | -0.011611
79 |  | 12.0374 | 99.284 | 4187 | 0.0019699 | 6.1544 | 6.1563 | -5.8938 | 507.6386 | 7879.3225 | -0.01161
80 |  | 12.0374 | 99.2724 | 4187 | 0.0019697 | 6.1563 | 6.1583 | -5.8938 | 507.698 | 7978.5949 | -0.011609
81 |  | 12.0374 | 99.2608 | 4187 | 0.0019694 | 6.1583 | 6.1603 | -5.8938 | 507.7574 | 8077.8557 | -0.011607
82 |  | 12.0374 | 99.2492 | 4187 | 0.0019692 | 6.1603 | 6.1622 | -5.8938 | 507.8167 | 8177.1049 | -0.011606
83 |  | 12.0374 | 99.2376 | 4187 | 0.001969 | 6.1622 | 6.1642 | -5.8938 | 507.8761 | 8276.3426 | -0.011605
84 |  | 12.0374 | 99.226 | 4187 | 0.0019688 | 6.1642 | 6.1662 | -5.8938 | 507.9355 | 8375.5686 | -0.011603
85 |  | 12.0374 | 99.2144 | 4187 | 0.0019685 | 6.1662 | 6.1681 | -5.8938 | 507.9949 | 8474.783 | -0.011602
86 |  | 12.0374 | 99.2028 | 4187 | 0.0019683 | 6.1681 | 6.1701 | -5.8938 | 508.0544 | 8573.9858 | -0.011601
87 |  | 12.0374 | 99.1912 | 4187 | 0.0019681 | 6.1701 | 6.1721 | -5.8938 | 508.1138 | 8673.177 | -0.011599
88 |  | 12.0374 | 99.1796 | 4187 | 0.0019678 | 6.1721 | 6.1741 | -5.8938 | 508.1732 | 8772.3566 | -0.011598
89 |  | 12.0374 | 99.168 | 4187 | 0.0019676 | 6.1741 | 6.176 | -5.8938 | 508.2326 | 8871.5246 | -0.011597
90 |  | 12.0374 | 99.1564 | 4187 | 0.0019674 | 6.176 | 6.178 | -5.8938 | 508.2921 | 8970.681 | -0.011595
91 |  | 12.0374 | 99.1448 | 4187 | 0.0019671 | 6.178 | 6.18 | -5.8938 | 508.3515 | 9069.8258 | -0.011594
92 |  | 12.0374 | 99.1332 | 4187 | 0.0019669 | 6.18 | 6.1819 | -5.8938 | 508.411 | 9168.9591 | -0.011593
93 |  | 12.0374 | 99.1216 | 4187 | 0.0019667 | 6.1819 | 6.1839 | -5.8938 | 508.4704 | 9268.0807 | -0.011591
94 |  | 12.0374 | 99.11 | 4187 | 0.0019665 | 6.1839 | 6.1859 | -5.8938 | 508.5299 | 9367.1907 | -0.01159
95 |  | 12.0374 | 99.0984 | 4187 | 0.0019662 | 6.1859 | 6.1878 | -5.8938 | 508.5894 | 9466.2892 | -0.011588
96 |  | 12.0374 | 99.0869 | 4187 | 0.001966 | 6.1878 | 6.1898 | -5.8938 | 508.6488 | 9565.376 | -0.011587
97 |  | 12.0374 | 99.0753 | 4187 | 0.0019658 | 6.1898 | 6.1918 | -5.8938 | 508.7083 | 9664.4513 | -0.011586
98 |  | 12.0374 | 99.0637 | 4187 | 0.0019655 | 6.1918 | 6.1937 | -5.8938 | 508.7678 | 9763.515 | -0.011584
99 |  | 12.0374 | 99.0521 | 4187 | 0.0019653 | 6.1937 | 6.1957 | -5.8938 | 508.8273 | 9862.5671 | -0.011583
100 |  | 12.0374 | 99.0405 | 4187 | 0.0019651 | 6.1957 | 6.1976 | -5.8938 | 508.8868 | 9961.6076 | -0.011582
101 |  | 12.0374 | 99.0289 | 4187 | 0.0019648 | 6.1976 | 6.1996 | -5.8938 | 508.9464 | 10060.6366 | -0.01158
102 |  | 12.0374 | 99.0174 | 4187 | 0.0019646 | 6.1996 | 6.2016 | -5.8938 | 509.0059 | 10159.6539 | -0.011579
103 |  | 12.0374 | 99.0058 | 4187 | 0.0019644 | 6.2016 | 6.2035 | -5.8938 | 509.0654 | 10258.6597 | -0.011578
104 |  | 12.0374 | 98.9942 | 4187 | 0.0019642 | 6.2035 | 6.2055 | -5.8938 | 509.1249 | 10357.6539 | -0.011576
105 |  | 12.0374 | 98.9826 | 4187 | 0.0019639 | 6.2055 | 6.2075 | -5.8938 | 509.1845 | 10456.6365 | -0.011575
106 |  | 12.0374 | 98.9711 | 4187 | 0.0019637 | 6.2075 | 6.2094 | -5.8938 | 509.244 | 10555.6076 | -0.011574
107 |  | 12.0374 | 98.9595 | 4187 | 0.0019635 | 6.2094 | 6.2114 | -5.8938 | 509.3036 | 10654.567 | -0.011572
108 |  | 12.0374 | 98.9479 | 4187 | 0.0019632 | 6.2114 | 6.2134 | -5.8938 | 509.3632 | 10753.515 | -0.011571
109 |  | 12.0374 | 98.9363 | 4187 | 0.001963 | 6.2134 | 6.2153 | -5.8938 | 509.4227 | 10852.4513 | -0.011569
110 |  | 12.0374 | 98.9248 | 4187 | 0.0019628 | 6.2153 | 6.2173 | -5.8938 | 509.4823 | 10951.3761 | -0.011568
111 |  | 12.0374 | 98.9132 | 4187 | 0.0019625 | 6.2173 | 6.2192 | -5.8938 | 509.5419 | 11050.2892 | -0.011567
112 |  | 12.0374 | 98.9016 | 4187 | 0.0019623 | 6.2192 | 6.2212 | -5.8938 | 509.6015 | 11149.1909 | -0.011565
113 |  | 12.0374 | 98.8901 | 4187 | 0.0019621 | 6.2212 | 6.2232 | -5.8938 | 509.6611 | 11248.0809 | -0.011564
114 |  | 12.0374 | 98.8785 | 4187 | 0.0019619 | 6.2232 | 6.2251 | -5.8938 | 509.7207 | 11346.9594 | -0.011563
115 |  | 12.0374 | 98.8669 | 4187 | 0.0019616 | 6.2251 | 6.2271 | -5.8938 | 509.7803 | 11445.8264 | -0.011561
116 |  | 12.0374 | 98.8554 | 4187 | 0.0019614 | 6.2271 | 6.2291 | -5.8938 | 509.8399 | 11544.6818 | -0.01156
117 |  | 12.0374 | 98.8438 | 4187 | 0.0019612 | 6.2291 | 6.231 | -5.8938 | 509.8995 | 11643.5256 | -0.011559
118 |  | 12.0374 | 98.8323 | 4187 | 0.0019609 | 6.231 | 6.233 | -5.8938 | 509.9592 | 11742.3578 | -0.011557
119 |  | 12.0374 | 98.8207 | 4187 | 0.0019607 | 6.233 | 6.2349 | -5.8938 | 510.0188 | 11841.1785 | -0.011556
120 |  | 12.0374 | 98.8091 | 4187 | 0.0019605 | 6.2349 | 6.2369 | -5.8938 | 510.0785 | 11939.9877 | -0.011555
121 |  | 12.0374 | 98.7976 | 4187 | 0.0019603 | 6.2369 | 6.2389 | -5.8938 | 510.1381 | 12038.7853 | -0.011553
122 |  | 12.0374 | 98.786 | 4187 | 0.00196 | 6.2389 | 6.2408 | -5.8938 | 510.1978 | 12137.5713 | -0.011552
123 |  | 12.0374 | 98.7745 | 4187 | 0.0019598 | 6.2408 | 6.2428 | -5.8938 | 510.2575 | 12236.3458 | -0.011551
124 |  | 12.0374 | 98.7629 | 4187 | 0.0019596 | 6.2428 | 6.2447 | -5.8938 | 510.3171 | 12335.1087 | -0.011549
125 |  | 12.0374 | 98.7514 | 4187 | 0.0019593 | 6.2447 | 6.2467 | -5.8938 | 510.3768 | 12433.8601 | -0.011548
126 |  | 12.0374 | 98.7398 | 4187 | 0.0019591 | 6.2467 | 6.2487 | -5.8938 | 510.4365 | 12532.5999 | -0.011546
127 |  | 12.0374 | 98.7283 | 4187 | 0.0019589 | 6.2487 | 6.2506 | -5.8938 | 510.4962 | 12631.3282 | -0.011545
128 |  | 12.0374 | 98.7167 | 4187 | 0.0019586 | 6.2506 | 6.2526 | -5.8938 | 510.5559 | 12730.045 | -0.011544
129 |  | 12.0374 | 98.7052 | 4187 | 0.0019584 | 6.2526 | 6.2545 | -5.8938 | 510.6156 | 12828.7502 | -0.011542
130 |  | 12.0374 | 98.6937 | 4187 | 0.0019582 | 6.2545 | 6.2565 | -5.8938 | 510.6753 | 12927.4438 | -0.011541
131 |  | 12.0374 | 98.6821 | 4187 | 0.001958 | 6.2565 | 6.2585 | -5.8938 | 510.7351 | 13026.1259 | -0.01154
132 |  | 12.0374 | 98.6706 | 4187 | 0.0019577 | 6.2585 | 6.2604 | -5.8938 | 510.7948 | 13124.7965 | -0.011538
133 |  | 12.0374 | 98.659 | 4187 | 0.0019575 | 6.2604 | 6.2624 | -5.8938 | 510.8545 | 13223.4556 | -0.011537
134 |  | 12.0374 | 98.6475 | 4187 | 0.0019573 | 6.2624 | 6.2643 | -5.8938 | 510.9143 | 13322.1031 | -0.011536
135 |  | 12.0374 | 98.636 | 4187 | 0.001957 | 6.2643 | 6.2663 | -5.8938 | 510.974 | 13420.739 | -0.011534
136 |  | 12.0374 | 98.6244 | 4187 | 0.0019568 | 6.2663 | 6.2682 | -5.8938 | 511.0338 | 13519.3635 | -0.011533
137 |  | 12.0374 | 98.6129 | 4187 | 0.0019566 | 6.2682 | 6.2702 | -5.8938 | 511.0936 | 13617.9764 | -0.011532
138 |  | 12.0374 | 98.6014 | 4187 | 0.0019564 | 6.2702 | 6.2722 | -5.8938 | 511.1533 | 13716.5777 | -0.01153
139 |  | 12.0374 | 98.5898 | 4187 | 0.0019561 | 6.2722 | 6.2741 | -5.8938 | 511.2131 | 13815.1676 | -0.011529
140 |  | 12.0374 | 98.5783 | 4187 | 0.0019559 | 6.2741 | 6.2761 | -5.8938 | 511.2729 | 13913.7459 | -0.011528
141 |  | 12.0374 | 98.5668 | 4187 | 0.0019557 | 6.2761 | 6.278 | -5.8938 | 511.3327 | 14012.3127 | -0.011526
142 |  | 12.0374 | 98.5553 | 4187 | 0.0019554 | 6.278 | 6.28 | -5.8938 | 511.3925 | 14110.8679 | -0.011525
143 |  | 12.0374 | 98.5437 | 4187 | 0.0019552 | 6.28 | 6.2819 | -5.8938 | 511.4523 | 14209.4116 | -0.011524
144 |  | 12.0374 | 98.5322 | 4187 | 0.001955 | 6.2819 | 6.2839 | -5.8938 | 511.5121 | 14307.9439 | -0.011522
145 |  | 12.0374 | 98.5207 | 4187 | 0.0019548 | 6.2839 | 6.2858 | -5.8938 | 511.5719 | 14406.4645 | -0.011521
146 |  | 12.0374 | 98.5092 | 4187 | 0.0019545 | 6.2858 | 6.2878 | -5.8938 | 511.6318 | 14504.9737 | -0.01152
147 |  | 12.0374 | 98.4976 | 4187 | 0.0019543 | 6.2878 | 6.2897 | -5.8938 | 511.6916 | 14603.4713 | -0.011518
148 |  | 12.0374 | 98.4861 | 4187 | 0.0019541 | 6.2897 | 6.2917 | -5.8938 | 511.7514 | 14701.9575 | -0.011517
149 |  | 12.0374 | 98.4746 | 4187 | 0.0019538 | 6.2917 | 6.2937 | -5.8938 | 511.8113 | 14800.4321 | -0.011515
150 |  | 12.0374 | 98.4631 | 4187 | 0.0019536 | 6.2937 | 6.2956 | -5.8938 | 511.8712 | 14898.8952 | -0.011514
151 |  | 12.0374 | 98.4516 | 4187 | 0.0019534 | 6.2956 | 6.2976 | -5.8938 | 511.931 | 14997.3468 | -0.011513
152 |  | 12.0374 | 98.4401 | 4187 | 0.0019532 | 6.2976 | 6.2995 | -5.8938 | 511.9909 | 15095.7868 | -0.011511
153 |  | 12.0374 | 98.4286 | 4187 | 0.0019529 | 6.2995 | 6.3015 | -5.8938 | 512.0508 | 15194.2154 | -0.01151
154 |  | 12.0374 | 98.417 | 4187 | 0.0019527 | 6.3015 | 6.3034 | -5.8938 | 512.1107 | 15292.6324 | -0.011509
155 |  | 12.0374 | 98.4055 | 4187 | 0.0019525 | 6.3034 | 6.3054 | -5.8938 | 512.1705 | 15391.038 | -0.011507
156 |  | 12.0374 | 98.394 | 4187 | 0.0019522 | 6.3054 | 6.3073 | -5.8938 | 512.2304 | 15489.432 | -0.011506
157 |  | 12.0374 | 98.3825 | 4187 | 0.001952 | 6.3073 | 6.3093 | -5.8938 | 512.2904 | 15587.8145 | -0.011505
158 |  | 12.0374 | 98.371 | 4187 | 0.0019518 | 6.3093 | 6.3112 | -5.8938 | 512.3503 | 15686.1855 | -0.011503
159 |  | 12.0374 | 98.3595 | 4187 | 0.0019516 | 6.3112 | 6.3132 | -5.8938 | 512.4102 | 15784.545 | -0.011502
160 |  | 12.0374 | 98.348 | 4187 | 0.0019513 | 6.3132 | 6.3151 | -5.8938 | 512.4701 | 15882.893 | -0.011501
161 |  | 12.0374 | 98.3365 | 4187 | 0.0019511 | 6.3151 | 6.3171 | -5.8938 | 512.5301 | 15981.2296 | -0.011499
162 |  | 12.0374 | 98.325 | 4187 | 0.0019509 | 6.3171 | 6.319 | -5.8938 | 512.59 | 16079.5546 | -0.011498
163 |  | 12.0374 | 98.3135 | 4187 | 0.0019506 | 6.319 | 6.321 | -5.8938 | 512.6499 | 16177.8681 | -0.011497
164 |  | 12.0374 | 98.302 | 4187 | 0.0019504 | 6.321 | 6.3229 | -5.8938 | 512.7099 | 16276.1701 | -0.011495
165 |  | 12.0374 | 98.2905 | 4187 | 0.0019502 | 6.3229 | 6.3249 | -5.8938 | 512.7699 | 16374.4606 | -0.011494
166 |  | 12.0374 | 98.279 | 4187 | 0.00195 | 6.3249 | 6.3268 | -5.8938 | 512.8298 | 16472.7397 | -0.011493
167 |  | 12.0374 | 98.2675 | 4187 | 0.0019497 | 6.3268 | 6.3288 | -5.8938 | 512.8898 | 16571.0072 | -0.011491
168 |  | 12.0374 | 98.256 | 4187 | 0.0019495 | 6.3288 | 6.3307 | -5.8938 | 512.9498 | 16669.2632 | -0.01149
169 |  | 12.0374 | 98.2446 | 4187 | 0.0019493 | 6.3307 | 6.3327 | -5.8938 | 513.0098 | 16767.5078 | -0.011489
170 |  | 12.0374 | 98.2331 | 4187 | 0.0019491 | 6.3327 | 6.3346 | -5.8938 | 513.0698 | 16865.7409 | -0.011487
171 |  | 12.0374 | 98.2216 | 4187 | 0.0019488 | 6.3346 | 6.3366 | -5.8938 | 513.1298 | 16963.9624 | -0.011486
172 |  | 12.0374 | 98.2101 | 4187 | 0.0019486 | 6.3366 | 6.3385 | -5.8938 | 513.1898 | 17062.1725 | -0.011485
173 |  | 12.0374 | 98.1986 | 4187 | 0.0019484 | 6.3385 | 6.3405 | -5.8938 | 513.2498 | 17160.3711 | -0.011483
174 |  | 12.0374 | 98.1871 | 4187 | 0.0019481 | 6.3405 | 6.3424 | -5.8938 | 513.3098 | 17258.5583 | -0.011482
175 |  | 12.0374 | 98.1756 | 4187 | 0.0019479 | 6.3424 | 6.3444 | -5.8938 | 513.3699 | 17356.7339 | -0.011481
176 |  | 12.0374 | 98.1642 | 4187 | 0.0019477 | 6.3444 | 6.3463 | -5.8938 | 513.4299 | 17454.8981 | -0.011479
177 |  | 12.0374 | 98.1527 | 4187 | 0.0019475 | 6.3463 | 6.3483 | -5.8938 | 513.49 | 17553.0507 | -0.011478
178 |  | 12.0374 | 98.1412 | 4187 | 0.0019472 | 6.3483 | 6.3502 | -5.8938 | 513.55 | 17651.192 | -0.011476
179 |  | 12.0374 | 98.1297 | 4187 | 0.001947 | 6.3502 | 6.3522 | -5.8938 | 513.6101 | 17749.3217 | -0.011475
180 |  | 12.0374 | 98.1183 | 4187 | 0.0019468 | 6.3522 | 6.3541 | -5.8938 | 513.6701 | 17847.4399 | -0.011474
181 |  | 12.0374 | 98.1068 | 4187 | 0.0019465 | 6.3541 | 6.3561 | -5.8938 | 513.7302 | 17945.5467 | -0.011472
182 |  | 12.0374 | 98.0953 | 4187 | 0.0019463 | 6.3561 | 6.358 | -5.8938 | 513.7903 | 18043.642 | -0.011471
183 |  | 12.0374 | 98.0838 | 4187 | 0.0019461 | 6.358 | 6.36 | -5.8938 | 513.8504 | 18141.7259 | -0.01147
184 |  | 12.0374 | 98.0724 | 4187 | 0.0019459 | 6.36 | 6.3619 | -5.8938 | 513.9105 | 18239.7982 | -0.011468
185 |  | 12.0374 | 98.0609 | 4187 | 0.0019456 | 6.3619 | 6.3638 | -5.8938 | 513.9706 | 18337.8591 | -0.011467
186 |  | 12.0374 | 98.0494 | 4187 | 0.0019454 | 6.3638 | 6.3658 | -5.8938 | 514.0307 | 18435.9086 | -0.011466
187 |  | 12.0374 | 98.038 | 4187 | 0.0019452 | 6.3658 | 6.3677 | -5.8938 | 514.0908 | 18533.9465 | -0.011464
188 |  | 12.0374 | 98.0265 | 4187 | 0.001945 | 6.3677 | 6.3697 | -5.8938 | 514.1509 | 18631.973 | -0.011463
189 |  | 12.0374 | 98.015 | 4187 | 0.0019447 | 6.3697 | 6.3716 | -5.8938 | 514.2111 | 18729.9881 | -0.011462
190 |  | 12.0374 | 98.0036 | 4187 | 0.0019445 | 6.3716 | 6.3736 | -5.8938 | 514.2712 | 18827.9916 | -0.01146
191 |  | 12.0374 | 97.9921 | 4187 | 0.0019443 | 6.3736 | 6.3755 | -5.8938 | 514.3313 | 18925.9838 | -0.011459
192 |  | 12.0374 | 97.9807 | 4187 | 0.001944 | 6.3755 | 6.3775 | -5.8938 | 514.3915 | 19023.9644 | -0.011458
193 |  | 12.0374 | 97.9692 | 4187 | 0.0019438 | 6.3775 | 6.3794 | -5.8938 | 514.4517 | 19121.9336 | -0.011456
194 |  | 12.0374 | 97.9577 | 4187 | 0.0019436 | 6.3794 | 6.3813 | -5.8938 | 514.5118 | 19219.8914 | -0.011455
195 |  | 12.0374 | 97.9463 | 4187 | 0.0019434 | 6.3813 | 6.3833 | -5.8938 | 514.572 | 19317.8376 | -0.011454
196 |  | 12.0374 | 97.9348 | 4187 | 0.0019431 | 6.3833 | 6.3852 | -5.8938 | 514.6322 | 19415.7725 | -0.011452
197 |  | 12.0374 | 97.9234 | 4187 | 0.0019429 | 6.3852 | 6.3872 | -5.8938 | 514.6924 | 19513.6959 | -0.011451
198 |  | 12.0374 | 97.9119 | 4187 | 0.0019427 | 6.3872 | 6.3891 | -5.8938 | 514.7526 | 19611.6078 | -0.01145
199 |  | 12.0374 | 97.9005 | 4187 | 0.0019425 | 6.3891 | 6.3911 | -5.8938 | 514.8128 | 19709.5083 | -0.011448
200 |  | 12.0374 | 97.889 | 4187 | 0.0019422 | 6.3911 | 6.393 | -5.8938 | 514.873 | 19807.3973 | -0.011447
201 |  | 12.0374 | 97.8776 | 4187 | 0.001942 | 6.393 | 6.3949 | -5.8938 | 514.9332 | 19905.2749 | -0.011446
202 |  | 12.0374 | 97.8661 | 4187 | 0.0019418 | 6.3949 | 6.3969 | -5.8938 | 514.9934 | 20003.141 | -0.011444
203 |  | 12.0374 | 97.8547 | 4187 | 0.0019415 | 6.3969 | 6.3988 | -5.8938 | 515.0536 | 20100.9957 | -0.011443
204 |  | 12.0374 | 97.8433 | 4187 | 0.0019413 | 6.3988 | 6.4008 | -5.8938 | 515.1139 | 20198.839 | -0.011442
205 |  | 12.0374 | 97.8318 | 4187 | 0.0019411 | 6.4008 | 6.4027 | -5.8938 | 515.1741 | 20296.6708 | -0.01144
206 |  | 12.0374 | 97.8204 | 4187 | 0.0019409 | 6.4027 | 6.4046 | -5.8938 | 515.2344 | 20394.4912 | -0.011439
207 |  | 12.0374 | 97.8089 | 4187 | 0.0019406 | 6.4046 | 6.4066 | -5.8938 | 515.2946 | 20492.3001 | -0.011438
208 |  | 12.0374 | 97.7975 | 4187 | 0.0019404 | 6.4066 | 6.4085 | -5.8938 | 515.3549 | 20590.0976 | -0.011436
209 |  | 12.0374 | 97.7861 | 4187 | 0.0019402 | 6.4085 | 6.4105 | -5.8938 | 515.4152 | 20687.8836 | -0.011435
210 |  | 12.0374 | 97.7746 | 4187 | 0.00194 | 6.4105 | 6.4124 | -5.8938 | 515.4754 | 20785.6583 | -0.011434
211 |  | 12.0374 | 97.7632 | 4187 | 0.0019397 | 6.4124 | 6.4144 | -5.8938 | 515.5357 | 20883.4214 | -0.011432
212 |  | 12.0374 | 97.7518 | 4187 | 0.0019395 | 6.4144 | 6.4163 | -5.8938 | 515.596 | 20981.1732 | -0.011431
213 |  | 12.0374 | 97.7403 | 4187 | 0.0019393 | 6.4163 | 6.4182 | -5.8938 | 515.6563 | 21078.9135 | -0.01143
214 |  | 12.0374 | 97.7289 | 4187 | 0.001939 | 6.4182 | 6.4202 | -5.8938 | 515.7166 | 21176.6424 | -0.011428
215 |  | 12.0374 | 97.7175 | 4187 | 0.0019388 | 6.4202 | 6.4221 | -5.8938 | 515.7769 | 21274.3599 | -0.011427
216 |  | 12.0374 | 97.706 | 4187 | 0.0019386 | 6.4221 | 6.424 | -5.8938 | 515.8373 | 21372.0659 | -0.011426
217 |  | 12.0374 | 97.6946 | 4187 | 0.0019384 | 6.424 | 6.426 | -5.8938 | 515.8976 | 21469.7606 | -0.011424
218 |  | 12.0374 | 97.6832 | 4187 | 0.0019381 | 6.426 | 6.4279 | -5.8938 | 515.9579 | 21567.4437 | -0.011423
219 |  | 12.0374 | 97.6718 | 4187 | 0.0019379 | 6.4279 | 6.4299 | -5.8938 | 516.0183 | 21665.1155 | -0.011422
220 |  | 12.0374 | 97.6603 | 4187 | 0.0019377 | 6.4299 | 6.4318 | -5.8938 | 516.0786 | 21762.7759 | -0.01142
221 |  | 12.0374 | 97.6489 | 4187 | 0.0019375 | 6.4318 | 6.4337 | -5.8938 | 516.139 | 21860.4248 | -0.011419
222 |  | 12.0374 | 97.6375 | 4187 | 0.0019372 | 6.4337 | 6.4357 | -5.8938 | 516.1993 | 21958.0623 | -0.011418
223 |  | 12.0374 | 97.6261 | 4187 | 0.001937 | 6.4357 | 6.4376 | -5.8938 | 516.2597 | 22055.6884 | -0.011416
224 |  | 12.0374 | 97.6147 | 4187 | 0.0019368 | 6.4376 | 6.4395 | -5.8938 | 516.3201 | 22153.3031 | -0.011415
225 |  | 12.0374 | 97.6033 | 4187 | 0.0019366 | 6.4395 | 6.4415 | -5.8938 | 516.3805 | 22250.9063 | -0.011414
226 |  | 12.0374 | 97.5918 | 4187 | 0.0019363 | 6.4415 | 6.4434 | -5.8938 | 516.4409 | 22348.4982 | -0.011412
227 |  | 12.0374 | 97.5804 | 4187 | 0.0019361 | 6.4434 | 6.4454 | -5.8938 | 516.5013 | 22446.0786 | -0.011411
228 |  | 12.0374 | 97.569 | 4187 | 0.0019359 | 6.4454 | 6.4473 | -5.8938 | 516.5617 | 22543.6476 | -0.01141
229 |  | 12.0374 | 97.5576 | 4187 | 0.0019357 | 6.4473 | 6.4492 | -5.8938 | 516.6221 | 22641.2052 | -0.011408
230 |  | 12.0374 | 97.5462 | 4187 | 0.0019354 | 6.4492 | 6.4512 | -5.8938 | 516.6825 | 22738.7514 | -0.011407
231 |  | 12.0374 | 97.5348 | 4187 | 0.0019352 | 6.4512 | 6.4531 | -5.8938 | 516.7429 | 22836.2862 | -0.011406
232 |  | 12.0374 | 97.5234 | 4187 | 0.001935 | 6.4531 | 6.455 | -5.8938 | 516.8034 | 22933.8096 | -0.011404
233 |  | 12.0374 | 97.512 | 4187 | 0.0019347 | 6.455 | 6.457 | -5.8938 | 516.8638 | 23031.3216 | -0.011403
234 |  | 12.0374 | 97.5006 | 4187 | 0.0019345 | 6.457 | 6.4589 | -5.8938 | 516.9243 | 23128.8222 | -0.011402
235 |  | 12.0374 | 97.4892 | 4187 | 0.0019343 | 6.4589 | 6.4608 | -5.8938 | 516.9847 | 23226.3114 | -0.0114
236 |  | 12.0374 | 97.4778 | 4187 | 0.0019341 | 6.4608 | 6.4628 | -5.8938 | 517.0452 | 23323.7892 | -0.011399

## Cu152
|  |  | buis | verlies W/M | L /°C/sec
diam | wandikte |  | inhoud l/m |  | W/M
152.4 | 2 | 3.1416 | 17.2965 | 120.2306 | 4187
[8 empty] | J/sec/mtr | aantal mtr. | verlies
|  | buis | verlies W/M | L /°C/sec | verlies temp | begintemp | eindtemp | verlies | bij 1°C | totaal J/sec
|  | inhoud L |  | W/M | °C per M | °C | °C | per m°C | daling | aantal mtr
1 | 152.4 | 17.2965 | 120.2306 | 4187 | 0.0016602 | 6 | 6.0017 | -7.0724 | 602.3455 | 120.2306 | -0.011741
2 |  | 17.2965 | 120.2188 | 4187 | 0.00166 | 6.0017 | 6.0033 | -7.0724 | 602.4044 | 240.4494 | -0.01174
3 |  | 17.2965 | 120.2071 | 4187 | 0.0016599 | 6.0033 | 6.005 | -7.0724 | 602.4632 | 360.6565 | -0.011739
4 |  | 17.2965 | 120.1954 | 4187 | 0.0016597 | 6.005 | 6.0066 | -7.0724 | 602.5221 | 480.8519 | -0.011738
5 |  | 17.2965 | 120.1836 | 4187 | 0.0016595 | 6.0066 | 6.0083 | -7.0724 | 602.5809 | 601.0355 | -0.011737
6 |  | 17.2965 | 120.1719 | 4187 | 0.0016594 | 6.0083 | 6.01 | -7.0724 | 602.6398 | 721.2074 | -0.011736
7 |  | 17.2965 | 120.1601 | 4187 | 0.0016592 | 6.01 | 6.0116 | -7.0724 | 602.6986 | 841.3675 | -0.011735
8 |  | 17.2965 | 120.1484 | 4187 | 0.001659 | 6.0116 | 6.0133 | -7.0724 | 602.7575 | 961.5159 | -0.011733
9 |  | 17.2965 | 120.1367 | 4187 | 0.0016589 | 6.0133 | 6.0149 | -7.0724 | 602.8163 | 1081.6526 | -0.011732
10 |  | 17.2965 | 120.1249 | 4187 | 0.0016587 | 6.0149 | 6.0166 | -7.0724 | 602.8752 | 1201.7776 | -0.011731
11 |  | 17.2965 | 120.1132 | 4187 | 0.0016586 | 6.0166 | 6.0183 | -7.0724 | 602.9341 | 1321.8908 | -0.01173
12 |  | 17.2965 | 120.1015 | 4187 | 0.0016584 | 6.0183 | 6.0199 | -7.0724 | 602.993 | 1441.9923 | -0.011729
13 |  | 17.2965 | 120.0898 | 4187 | 0.0016582 | 6.0199 | 6.0216 | -7.0724 | 603.0519 | 1562.082 | -0.011728
14 |  | 17.2965 | 120.078 | 4187 | 0.0016581 | 6.0216 | 6.0232 | -7.0724 | 603.1108 | 1682.1601 | -0.011727
15 |  | 17.2965 | 120.0663 | 4187 | 0.0016579 | 6.0232 | 6.0249 | -7.0724 | 603.1697 | 1802.2264 | -0.011725
16 |  | 17.2965 | 120.0546 | 4187 | 0.0016577 | 6.0249 | 6.0265 | -7.0724 | 603.2286 | 1922.2809 | -0.011724
17 |  | 17.2965 | 120.0429 | 4187 | 0.0016576 | 6.0265 | 6.0282 | -7.0724 | 603.2875 | 2042.3238 | -0.011723
18 |  | 17.2965 | 120.0311 | 4187 | 0.0016574 | 6.0282 | 6.0299 | -7.0724 | 603.3464 | 2162.3549 | -0.011722
19 |  | 17.2965 | 120.0194 | 4187 | 0.0016573 | 6.0299 | 6.0315 | -7.0724 | 603.4054 | 2282.3743 | -0.011721
20 |  | 17.2965 | 120.0077 | 4187 | 0.0016571 | 6.0315 | 6.0332 | -7.0724 | 603.4643 | 2402.382 | -0.01172
21 |  | 17.2965 | 119.996 | 4187 | 0.0016569 | 6.0332 | 6.0348 | -7.0724 | 603.5232 | 2522.378 | -0.011719
22 |  | 17.2965 | 119.9843 | 4187 | 0.0016568 | 6.0348 | 6.0365 | -7.0724 | 603.5822 | 2642.3622 | -0.011717
23 |  | 17.2965 | 119.9725 | 4187 | 0.0016566 | 6.0365 | 6.0381 | -7.0724 | 603.6411 | 2762.3348 | -0.011716
24 |  | 17.2965 | 119.9608 | 4187 | 0.0016565 | 6.0381 | 6.0398 | -7.0724 | 603.7001 | 2882.2956 | -0.011715
25 |  | 17.2965 | 119.9491 | 4187 | 0.0016563 | 6.0398 | 6.0415 | -7.0724 | 603.759 | 3002.2447 | -0.011714
26 |  | 17.2965 | 119.9374 | 4187 | 0.0016561 | 6.0415 | 6.0431 | -7.0724 | 603.818 | 3122.1821 | -0.011713
27 |  | 17.2965 | 119.9257 | 4187 | 0.001656 | 6.0431 | 6.0448 | -7.0724 | 603.877 | 3242.1078 | -0.011712
28 |  | 17.2965 | 119.914 | 4187 | 0.0016558 | 6.0448 | 6.0464 | -7.0724 | 603.936 | 3362.0217 | -0.01171
29 |  | 17.2965 | 119.9023 | 4187 | 0.0016556 | 6.0464 | 6.0481 | -7.0724 | 603.9949 | 3481.924 | -0.011709
30 |  | 17.2965 | 119.8905 | 4187 | 0.0016555 | 6.0481 | 6.0497 | -7.0724 | 604.0539 | 3601.8145 | -0.011708
31 |  | 17.2965 | 119.8788 | 4187 | 0.0016553 | 6.0497 | 6.0514 | -7.0724 | 604.1129 | 3721.6934 | -0.011707
32 |  | 17.2965 | 119.8671 | 4187 | 0.0016552 | 6.0514 | 6.053 | -7.0724 | 604.1719 | 3841.5605 | -0.011706
33 |  | 17.2965 | 119.8554 | 4187 | 0.001655 | 6.053 | 6.0547 | -7.0724 | 604.2309 | 3961.4159 | -0.011705
34 |  | 17.2965 | 119.8437 | 4187 | 0.0016548 | 6.0547 | 6.0564 | -7.0724 | 604.2899 | 4081.2596 | -0.011704
35 |  | 17.2965 | 119.832 | 4187 | 0.0016547 | 6.0564 | 6.058 | -7.0724 | 604.349 | 4201.0916 | -0.011702
36 |  | 17.2965 | 119.8203 | 4187 | 0.0016545 | 6.058 | 6.0597 | -7.0724 | 604.408 | 4320.9119 | -0.011701
37 |  | 17.2965 | 119.8086 | 4187 | 0.0016543 | 6.0597 | 6.0613 | -7.0724 | 604.467 | 4440.7206 | -0.0117
38 |  | 17.2965 | 119.7969 | 4187 | 0.0016542 | 6.0613 | 6.063 | -7.0724 | 604.5261 | 4560.5175 | -0.011699
39 |  | 17.2965 | 119.7852 | 4187 | 0.001654 | 6.063 | 6.0646 | -7.0724 | 604.5851 | 4680.3027 | -0.011698
40 |  | 17.2965 | 119.7735 | 4187 | 0.0016539 | 6.0646 | 6.0663 | -7.0724 | 604.6442 | 4800.0762 | -0.011697
41 |  | 17.2965 | 119.7618 | 4187 | 0.0016537 | 6.0663 | 6.0679 | -7.0724 | 604.7032 | 4919.838 | -0.011696
42 |  | 17.2965 | 119.7501 | 4187 | 0.0016535 | 6.0679 | 6.0696 | -7.0724 | 604.7623 | 5039.5881 | -0.011694
43 |  | 17.2965 | 119.7384 | 4187 | 0.0016534 | 6.0696 | 6.0712 | -7.0724 | 604.8213 | 5159.3266 | -0.011693
44 |  | 17.2965 | 119.7267 | 4187 | 0.0016532 | 6.0712 | 6.0729 | -7.0724 | 604.8804 | 5279.0533 | -0.011692
45 |  | 17.2965 | 119.715 | 4187 | 0.0016531 | 6.0729 | 6.0745 | -7.0724 | 604.9395 | 5398.7683 | -0.011691
46 |  | 17.2965 | 119.7033 | 4187 | 0.0016529 | 6.0745 | 6.0762 | -7.0724 | 604.9986 | 5518.4717 | -0.01169
47 |  | 17.2965 | 119.6917 | 4187 | 0.0016527 | 6.0762 | 6.0779 | -7.0724 | 605.0576 | 5638.1633 | -0.011689
48 |  | 17.2965 | 119.68 | 4187 | 0.0016526 | 6.0779 | 6.0795 | -7.0724 | 605.1167 | 5757.8433 | -0.011688
49 |  | 17.2965 | 119.6683 | 4187 | 0.0016524 | 6.0795 | 6.0812 | -7.0724 | 605.1758 | 5877.5116 | -0.011686
50 |  | 17.2965 | 119.6566 | 4187 | 0.0016523 | 6.0812 | 6.0828 | -7.0724 | 605.2349 | 5997.1682 | -0.011685
51 |  | 17.2965 | 119.6449 | 4187 | 0.0016521 | 6.0828 | 6.0845 | -7.0724 | 605.2941 | 6116.8131 | -0.011684
52 |  | 17.2965 | 119.6332 | 4187 | 0.0016519 | 6.0845 | 6.0861 | -7.0724 | 605.3532 | 6236.4463 | -0.011683
53 |  | 17.2965 | 119.6215 | 4187 | 0.0016518 | 6.0861 | 6.0878 | -7.0724 | 605.4123 | 6356.0679 | -0.011682
54 |  | 17.2965 | 119.6099 | 4187 | 0.0016516 | 6.0878 | 6.0894 | -7.0724 | 605.4714 | 6475.6777 | -0.011681
55 |  | 17.2965 | 119.5982 | 4187 | 0.0016514 | 6.0894 | 6.0911 | -7.0724 | 605.5306 | 6595.2759 | -0.01168
56 |  | 17.2965 | 119.5865 | 4187 | 0.0016513 | 6.0911 | 6.0927 | -7.0724 | 605.5897 | 6714.8624 | -0.011679
57 |  | 17.2965 | 119.5748 | 4187 | 0.0016511 | 6.0927 | 6.0944 | -7.0724 | 605.6489 | 6834.4372 | -0.011677
58 |  | 17.2965 | 119.5631 | 4187 | 0.001651 | 6.0944 | 6.096 | -7.0724 | 605.708 | 6954.0004 | -0.011676
59 |  | 17.2965 | 119.5515 | 4187 | 0.0016508 | 6.096 | 6.0977 | -7.0724 | 605.7672 | 7073.5519 | -0.011675
60 |  | 17.2965 | 119.5398 | 4187 | 0.0016506 | 6.0977 | 6.0993 | -7.0724 | 605.8263 | 7193.0916 | -0.011674
61 |  | 17.2965 | 119.5281 | 4187 | 0.0016505 | 6.0993 | 6.101 | -7.0724 | 605.8855 | 7312.6198 | -0.011673
62 |  | 17.2965 | 119.5164 | 4187 | 0.0016503 | 6.101 | 6.1026 | -7.0724 | 605.9447 | 7432.1362 | -0.011672
63 |  | 17.2965 | 119.5048 | 4187 | 0.0016502 | 6.1026 | 6.1043 | -7.0724 | 606.0038 | 7551.641 | -0.011671
64 |  | 17.2965 | 119.4931 | 4187 | 0.00165 | 6.1043 | 6.1059 | -7.0724 | 606.063 | 7671.1341 | -0.011669
65 |  | 17.2965 | 119.4814 | 4187 | 0.0016498 | 6.1059 | 6.1076 | -7.0724 | 606.1222 | 7790.6155 | -0.011668
66 |  | 17.2965 | 119.4698 | 4187 | 0.0016497 | 6.1076 | 6.1092 | -7.0724 | 606.1814 | 7910.0853 | -0.011667
67 |  | 17.2965 | 119.4581 | 4187 | 0.0016495 | 6.1092 | 6.1109 | -7.0724 | 606.2406 | 8029.5434 | -0.011666
68 |  | 17.2965 | 119.4464 | 4187 | 0.0016493 | 6.1109 | 6.1125 | -7.0724 | 606.2998 | 8148.9898 | -0.011665
69 |  | 17.2965 | 119.4348 | 4187 | 0.0016492 | 6.1125 | 6.1142 | -7.0724 | 606.3591 | 8268.4246 | -0.011664
70 |  | 17.2965 | 119.4231 | 4187 | 0.001649 | 6.1142 | 6.1158 | -7.0724 | 606.4183 | 8387.8477 | -0.011663
71 |  | 17.2965 | 119.4114 | 4187 | 0.0016489 | 6.1158 | 6.1175 | -7.0724 | 606.4775 | 8507.2592 | -0.011661
72 |  | 17.2965 | 119.3998 | 4187 | 0.0016487 | 6.1175 | 6.1191 | -7.0724 | 606.5367 | 8626.6589 | -0.01166
73 |  | 17.2965 | 119.3881 | 4187 | 0.0016485 | 6.1191 | 6.1208 | -7.0724 | 606.596 | 8746.0471 | -0.011659
74 |  | 17.2965 | 119.3765 | 4187 | 0.0016484 | 6.1208 | 6.1224 | -7.0724 | 606.6552 | 8865.4235 | -0.011658
75 |  | 17.2965 | 119.3648 | 4187 | 0.0016482 | 6.1224 | 6.1241 | -7.0724 | 606.7145 | 8984.7883 | -0.011657
76 |  | 17.2965 | 119.3531 | 4187 | 0.0016481 | 6.1241 | 6.1257 | -7.0724 | 606.7737 | 9104.1415 | -0.011656
77 |  | 17.2965 | 119.3415 | 4187 | 0.0016479 | 6.1257 | 6.1274 | -7.0724 | 606.833 | 9223.483 | -0.011655
78 |  | 17.2965 | 119.3298 | 4187 | 0.0016477 | 6.1274 | 6.129 | -7.0724 | 606.8923 | 9342.8128 | -0.011653
79 |  | 17.2965 | 119.3182 | 4187 | 0.0016476 | 6.129 | 6.1307 | -7.0724 | 606.9515 | 9462.131 | -0.011652
80 |  | 17.2965 | 119.3065 | 4187 | 0.0016474 | 6.1307 | 6.1323 | -7.0724 | 607.0108 | 9581.4375 | -0.011651
81 |  | 17.2965 | 119.2949 | 4187 | 0.0016473 | 6.1323 | 6.134 | -7.0724 | 607.0701 | 9700.7324 | -0.01165
82 |  | 17.2965 | 119.2832 | 4187 | 0.0016471 | 6.134 | 6.1356 | -7.0724 | 607.1294 | 9820.0156 | -0.011649
83 |  | 17.2965 | 119.2716 | 4187 | 0.0016469 | 6.1356 | 6.1372 | -7.0724 | 607.1887 | 9939.2872 | -0.011648
84 |  | 17.2965 | 119.2599 | 4187 | 0.0016468 | 6.1372 | 6.1389 | -7.0724 | 607.248 | 10058.5471 | -0.011647
85 |  | 17.2965 | 119.2483 | 4187 | 0.0016466 | 6.1389 | 6.1405 | -7.0724 | 607.3073 | 10177.7954 | -0.011645
86 |  | 17.2965 | 119.2366 | 4187 | 0.0016465 | 6.1405 | 6.1422 | -7.0724 | 607.3666 | 10297.0321 | -0.011644
87 |  | 17.2965 | 119.225 | 4187 | 0.0016463 | 6.1422 | 6.1438 | -7.0724 | 607.4259 | 10416.2571 | -0.011643
88 |  | 17.2965 | 119.2134 | 4187 | 0.0016461 | 6.1438 | 6.1455 | -7.0724 | 607.4852 | 10535.4704 | -0.011642
89 |  | 17.2965 | 119.2017 | 4187 | 0.001646 | 6.1455 | 6.1471 | -7.0724 | 607.5446 | 10654.6721 | -0.011641
90 |  | 17.2965 | 119.1901 | 4187 | 0.0016458 | 6.1471 | 6.1488 | -7.0724 | 607.6039 | 10773.8622 | -0.01164
91 |  | 17.2965 | 119.1784 | 4187 | 0.0016456 | 6.1488 | 6.1504 | -7.0724 | 607.6633 | 10893.0406 | -0.011639
92 |  | 17.2965 | 119.1668 | 4187 | 0.0016455 | 6.1504 | 6.1521 | -7.0724 | 607.7226 | 11012.2074 | -0.011638
93 |  | 17.2965 | 119.1552 | 4187 | 0.0016453 | 6.1521 | 6.1537 | -7.0724 | 607.782 | 11131.3626 | -0.011636
94 |  | 17.2965 | 119.1435 | 4187 | 0.0016452 | 6.1537 | 6.1554 | -7.0724 | 607.8413 | 11250.5061 | -0.011635
95 |  | 17.2965 | 119.1319 | 4187 | 0.001645 | 6.1554 | 6.157 | -7.0724 | 607.9007 | 11369.638 | -0.011634
96 |  | 17.2965 | 119.1202 | 4187 | 0.0016448 | 6.157 | 6.1586 | -7.0724 | 607.9601 | 11488.7582 | -0.011633
97 |  | 17.2965 | 119.1086 | 4187 | 0.0016447 | 6.1586 | 6.1603 | -7.0724 | 608.0194 | 11607.8669 | -0.011632
98 |  | 17.2965 | 119.097 | 4187 | 0.0016445 | 6.1603 | 6.1619 | -7.0724 | 608.0788 | 11726.9638 | -0.011631
99 |  | 17.2965 | 119.0854 | 4187 | 0.0016444 | 6.1619 | 6.1636 | -7.0724 | 608.1382 | 11846.0492 | -0.01163
100 |  | 17.2965 | 119.0737 | 4187 | 0.0016442 | 6.1636 | 6.1652 | -7.0724 | 608.1976 | 11965.1229 | -0.011628
101 |  | 17.2965 | 119.0621 | 4187 | 0.001644 | 6.1652 | 6.1669 | -7.0724 | 608.257 | 12084.185 | -0.011627
102 |  | 17.2965 | 119.0505 | 4187 | 0.0016439 | 6.1669 | 6.1685 | -7.0724 | 608.3164 | 12203.2355 | -0.011626
103 |  | 17.2965 | 119.0388 | 4187 | 0.0016437 | 6.1685 | 6.1701 | -7.0724 | 608.3758 | 12322.2743 | -0.011625
104 |  | 17.2965 | 119.0272 | 4187 | 0.0016436 | 6.1701 | 6.1718 | -7.0724 | 608.4352 | 12441.3016 | -0.011624
105 |  | 17.2965 | 119.0156 | 4187 | 0.0016434 | 6.1718 | 6.1734 | -7.0724 | 608.4947 | 12560.3171 | -0.011623
106 |  | 17.2965 | 119.004 | 4187 | 0.0016432 | 6.1734 | 6.1751 | -7.0724 | 608.5541 | 12679.3211 | -0.011622
107 |  | 17.2965 | 118.9923 | 4187 | 0.0016431 | 6.1751 | 6.1767 | -7.0724 | 608.6135 | 12798.3135 | -0.01162
108 |  | 17.2965 | 118.9807 | 4187 | 0.0016429 | 6.1767 | 6.1784 | -7.0724 | 608.673 | 12917.2942 | -0.011619
109 |  | 17.2965 | 118.9691 | 4187 | 0.0016428 | 6.1784 | 6.18 | -7.0724 | 608.7324 | 13036.2633 | -0.011618
110 |  | 17.2965 | 118.9575 | 4187 | 0.0016426 | 6.18 | 6.1817 | -7.0724 | 608.7919 | 13155.2208 | -0.011617
111 |  | 17.2965 | 118.9459 | 4187 | 0.0016424 | 6.1817 | 6.1833 | -7.0724 | 608.8513 | 13274.1667 | -0.011616
112 |  | 17.2965 | 118.9343 | 4187 | 0.0016423 | 6.1833 | 6.1849 | -7.0724 | 608.9108 | 13393.1009 | -0.011615
113 |  | 17.2965 | 118.9226 | 4187 | 0.0016421 | 6.1849 | 6.1866 | -7.0724 | 608.9703 | 13512.0236 | -0.011614
114 |  | 17.2965 | 118.911 | 4187 | 0.001642 | 6.1866 | 6.1882 | -7.0724 | 609.0297 | 13630.9346 | -0.011613
115 |  | 17.2965 | 118.8994 | 4187 | 0.0016418 | 6.1882 | 6.1899 | -7.0724 | 609.0892 | 13749.834 | -0.011611
116 |  | 17.2965 | 118.8878 | 4187 | 0.0016416 | 6.1899 | 6.1915 | -7.0724 | 609.1487 | 13868.7218 | -0.01161
117 |  | 17.2965 | 118.8762 | 4187 | 0.0016415 | 6.1915 | 6.1931 | -7.0724 | 609.2082 | 13987.598 | -0.011609
118 |  | 17.2965 | 118.8646 | 4187 | 0.0016413 | 6.1931 | 6.1948 | -7.0724 | 609.2677 | 14106.4626 | -0.011608
119 |  | 17.2965 | 118.853 | 4187 | 0.0016412 | 6.1948 | 6.1964 | -7.0724 | 609.3272 | 14225.3156 | -0.011607
120 |  | 17.2965 | 118.8414 | 4187 | 0.001641 | 6.1964 | 6.1981 | -7.0724 | 609.3867 | 14344.157 | -0.011606
121 |  | 17.2965 | 118.8298 | 4187 | 0.0016408 | 6.1981 | 6.1997 | -7.0724 | 609.4462 | 14462.9867 | -0.011605
122 |  | 17.2965 | 118.8182 | 4187 | 0.0016407 | 6.1997 | 6.2013 | -7.0724 | 609.5058 | 14581.8049 | -0.011603
123 |  | 17.2965 | 118.8066 | 4187 | 0.0016405 | 6.2013 | 6.203 | -7.0724 | 609.5653 | 14700.6114 | -0.011602
124 |  | 17.2965 | 118.795 | 4187 | 0.0016404 | 6.203 | 6.2046 | -7.0724 | 609.6248 | 14819.4064 | -0.011601
125 |  | 17.2965 | 118.7834 | 4187 | 0.0016402 | 6.2046 | 6.2063 | -7.0724 | 609.6844 | 14938.1897 | -0.0116
126 |  | 17.2965 | 118.7718 | 4187 | 0.00164 | 6.2063 | 6.2079 | -7.0724 | 609.7439 | 15056.9615 | -0.011599
127 |  | 17.2965 | 118.7602 | 4187 | 0.0016399 | 6.2079 | 6.2096 | -7.0724 | 609.8035 | 15175.7217 | -0.011598
128 |  | 17.2965 | 118.7486 | 4187 | 0.0016397 | 6.2096 | 6.2112 | -7.0724 | 609.863 | 15294.4702 | -0.011597
129 |  | 17.2965 | 118.737 | 4187 | 0.0016396 | 6.2112 | 6.2128 | -7.0724 | 609.9226 | 15413.2072 | -0.011596
130 |  | 17.2965 | 118.7254 | 4187 | 0.0016394 | 6.2128 | 6.2145 | -7.0724 | 609.9822 | 15531.9325 | -0.011594
131 |  | 17.2965 | 118.7138 | 4187 | 0.0016392 | 6.2145 | 6.2161 | -7.0724 | 610.0417 | 15650.6463 | -0.011593
132 |  | 17.2965 | 118.7022 | 4187 | 0.0016391 | 6.2161 | 6.2177 | -7.0724 | 610.1013 | 15769.3485 | -0.011592
133 |  | 17.2965 | 118.6906 | 4187 | 0.0016389 | 6.2177 | 6.2194 | -7.0724 | 610.1609 | 15888.0391 | -0.011591
134 |  | 17.2965 | 118.679 | 4187 | 0.0016388 | 6.2194 | 6.221 | -7.0724 | 610.2205 | 16006.7181 | -0.01159
135 |  | 17.2965 | 118.6674 | 4187 | 0.0016386 | 6.221 | 6.2227 | -7.0724 | 610.2801 | 16125.3855 | -0.011589
136 |  | 17.2965 | 118.6558 | 4187 | 0.0016384 | 6.2227 | 6.2243 | -7.0724 | 610.3397 | 16244.0413 | -0.011588
137 |  | 17.2965 | 118.6442 | 4187 | 0.0016383 | 6.2243 | 6.2259 | -7.0724 | 610.3993 | 16362.6855 | -0.011586
138 |  | 17.2965 | 118.6326 | 4187 | 0.0016381 | 6.2259 | 6.2276 | -7.0724 | 610.4589 | 16481.3182 | -0.011585
139 |  | 17.2965 | 118.6211 | 4187 | 0.001638 | 6.2276 | 6.2292 | -7.0724 | 610.5185 | 16599.9392 | -0.011584
140 |  | 17.2965 | 118.6095 | 4187 | 0.0016378 | 6.2292 | 6.2309 | -7.0724 | 610.5782 | 16718.5487 | -0.011583
141 |  | 17.2965 | 118.5979 | 4187 | 0.0016376 | 6.2309 | 6.2325 | -7.0724 | 610.6378 | 16837.1466 | -0.011582
142 |  | 17.2965 | 118.5863 | 4187 | 0.0016375 | 6.2325 | 6.2341 | -7.0724 | 610.6974 | 16955.7329 | -0.011581
143 |  | 17.2965 | 118.5747 | 4187 | 0.0016373 | 6.2341 | 6.2358 | -7.0724 | 610.7571 | 17074.3076 | -0.01158
144 |  | 17.2965 | 118.5631 | 4187 | 0.0016372 | 6.2358 | 6.2374 | -7.0724 | 610.8167 | 17192.8707 | -0.011579
145 |  | 17.2965 | 118.5516 | 4187 | 0.001637 | 6.2374 | 6.239 | -7.0724 | 610.8764 | 17311.4223 | -0.011577
146 |  | 17.2965 | 118.54 | 4187 | 0.0016368 | 6.239 | 6.2407 | -7.0724 | 610.9361 | 17429.9623 | -0.011576
147 |  | 17.2965 | 118.5284 | 4187 | 0.0016367 | 6.2407 | 6.2423 | -7.0724 | 610.9957 | 17548.4907 | -0.011575
148 |  | 17.2965 | 118.5168 | 4187 | 0.0016365 | 6.2423 | 6.244 | -7.0724 | 611.0554 | 17667.0076 | -0.011574
149 |  | 17.2965 | 118.5053 | 4187 | 0.0016364 | 6.244 | 6.2456 | -7.0724 | 611.1151 | 17785.5128 | -0.011573
150 |  | 17.2965 | 118.4937 | 4187 | 0.0016362 | 6.2456 | 6.2472 | -7.0724 | 611.1748 | 17904.0065 | -0.011572
151 |  | 17.2965 | 118.4821 | 4187 | 0.001636 | 6.2472 | 6.2489 | -7.0724 | 611.2345 | 18022.4886 | -0.011571
152 |  | 17.2965 | 118.4705 | 4187 | 0.0016359 | 6.2489 | 6.2505 | -7.0724 | 611.2942 | 18140.9592 | -0.01157
153 |  | 17.2965 | 118.459 | 4187 | 0.0016357 | 6.2505 | 6.2521 | -7.0724 | 611.3539 | 18259.4182 | -0.011568
154 |  | 17.2965 | 118.4474 | 4187 | 0.0016356 | 6.2521 | 6.2538 | -7.0724 | 611.4136 | 18377.8656 | -0.011567
155 |  | 17.2965 | 118.4358 | 4187 | 0.0016354 | 6.2538 | 6.2554 | -7.0724 | 611.4733 | 18496.3014 | -0.011566
156 |  | 17.2965 | 118.4243 | 4187 | 0.0016352 | 6.2554 | 6.257 | -7.0724 | 611.533 | 18614.7257 | -0.011565
157 |  | 17.2965 | 118.4127 | 4187 | 0.0016351 | 6.257 | 6.2587 | -7.0724 | 611.5927 | 18733.1384 | -0.011564
158 |  | 17.2965 | 118.4011 | 4187 | 0.0016349 | 6.2587 | 6.2603 | -7.0724 | 611.6525 | 18851.5396 | -0.011563
159 |  | 17.2965 | 118.3896 | 4187 | 0.0016348 | 6.2603 | 6.2619 | -7.0724 | 611.7122 | 18969.9291 | -0.011562
160 |  | 17.2965 | 118.378 | 4187 | 0.0016346 | 6.2619 | 6.2636 | -7.0724 | 611.7719 | 19088.3072 | -0.01156
161 |  | 17.2965 | 118.3665 | 4187 | 0.0016344 | 6.2636 | 6.2652 | -7.0724 | 611.8317 | 19206.6736 | -0.011559
162 |  | 17.2965 | 118.3549 | 4187 | 0.0016343 | 6.2652 | 6.2668 | -7.0724 | 611.8914 | 19325.0285 | -0.011558
163 |  | 17.2965 | 118.3433 | 4187 | 0.0016341 | 6.2668 | 6.2685 | -7.0724 | 611.9512 | 19443.3719 | -0.011557
164 |  | 17.2965 | 118.3318 | 4187 | 0.001634 | 6.2685 | 6.2701 | -7.0724 | 612.011 | 19561.7037 | -0.011556
165 |  | 17.2965 | 118.3202 | 4187 | 0.0016338 | 6.2701 | 6.2717 | -7.0724 | 612.0708 | 19680.0239 | -0.011555
166 |  | 17.2965 | 118.3087 | 4187 | 0.0016336 | 6.2717 | 6.2734 | -7.0724 | 612.1305 | 19798.3326 | -0.011554
167 |  | 17.2965 | 118.2971 | 4187 | 0.0016335 | 6.2734 | 6.275 | -7.0724 | 612.1903 | 19916.6297 | -0.011553
168 |  | 17.2965 | 118.2856 | 4187 | 0.0016333 | 6.275 | 6.2766 | -7.0724 | 612.2501 | 20034.9153 | -0.011551
169 |  | 17.2965 | 118.274 | 4187 | 0.0016332 | 6.2766 | 6.2783 | -7.0724 | 612.3099 | 20153.1893 | -0.01155
170 |  | 17.2965 | 118.2625 | 4187 | 0.001633 | 6.2783 | 6.2799 | -7.0724 | 612.3697 | 20271.4518 | -0.011549
171 |  | 17.2965 | 118.2509 | 4187 | 0.0016328 | 6.2799 | 6.2815 | -7.0724 | 612.4295 | 20389.7027 | -0.011548
172 |  | 17.2965 | 118.2394 | 4187 | 0.0016327 | 6.2815 | 6.2832 | -7.0724 | 612.4893 | 20507.9421 | -0.011547
173 |  | 17.2965 | 118.2278 | 4187 | 0.0016325 | 6.2832 | 6.2848 | -7.0724 | 612.5491 | 20626.1699 | -0.011546
174 |  | 17.2965 | 118.2163 | 4187 | 0.0016324 | 6.2848 | 6.2864 | -7.0724 | 612.609 | 20744.3862 | -0.011545
175 |  | 17.2965 | 118.2047 | 4187 | 0.0016322 | 6.2864 | 6.2881 | -7.0724 | 612.6688 | 20862.5909 | -0.011544
176 |  | 17.2965 | 118.1932 | 4187 | 0.001632 | 6.2881 | 6.2897 | -7.0724 | 612.7286 | 20980.7841 | -0.011542
177 |  | 17.2965 | 118.1816 | 4187 | 0.0016319 | 6.2897 | 6.2913 | -7.0724 | 612.7885 | 21098.9657 | -0.011541
178 |  | 17.2965 | 118.1701 | 4187 | 0.0016317 | 6.2913 | 6.293 | -7.0724 | 612.8483 | 21217.1359 | -0.01154
179 |  | 17.2965 | 118.1586 | 4187 | 0.0016316 | 6.293 | 6.2946 | -7.0724 | 612.9082 | 21335.2944 | -0.011539
180 |  | 17.2965 | 118.147 | 4187 | 0.0016314 | 6.2946 | 6.2962 | -7.0724 | 612.9681 | 21453.4415 | -0.011538
181 |  | 17.2965 | 118.1355 | 4187 | 0.0016312 | 6.2962 | 6.2979 | -7.0724 | 613.0279 | 21571.5769 | -0.011537
182 |  | 17.2965 | 118.124 | 4187 | 0.0016311 | 6.2979 | 6.2995 | -7.0724 | 613.0878 | 21689.7009 | -0.011536
183 |  | 17.2965 | 118.1124 | 4187 | 0.0016309 | 6.2995 | 6.3011 | -7.0724 | 613.1477 | 21807.8133 | -0.011535
184 |  | 17.2965 | 118.1009 | 4187 | 0.0016308 | 6.3011 | 6.3028 | -7.0724 | 613.2076 | 21925.9142 | -0.011533
185 |  | 17.2965 | 118.0894 | 4187 | 0.0016306 | 6.3028 | 6.3044 | -7.0724 | 613.2674 | 22044.0036 | -0.011532
186 |  | 17.2965 | 118.0778 | 4187 | 0.0016305 | 6.3044 | 6.306 | -7.0724 | 613.3273 | 22162.0814 | -0.011531
187 |  | 17.2965 | 118.0663 | 4187 | 0.0016303 | 6.306 | 6.3077 | -7.0724 | 613.3872 | 22280.1477 | -0.01153
188 |  | 17.2965 | 118.0548 | 4187 | 0.0016301 | 6.3077 | 6.3093 | -7.0724 | 613.4471 | 22398.2024 | -0.011529
189 |  | 17.2965 | 118.0432 | 4187 | 0.00163 | 6.3093 | 6.3109 | -7.0724 | 613.5071 | 22516.2456 | -0.011528
190 |  | 17.2965 | 118.0317 | 4187 | 0.0016298 | 6.3109 | 6.3125 | -7.0724 | 613.567 | 22634.2773 | -0.011527
191 |  | 17.2965 | 118.0202 | 4187 | 0.0016297 | 6.3125 | 6.3142 | -7.0724 | 613.6269 | 22752.2975 | -0.011526
192 |  | 17.2965 | 118.0086 | 4187 | 0.0016295 | 6.3142 | 6.3158 | -7.0724 | 613.6868 | 22870.3062 | -0.011524
193 |  | 17.2965 | 117.9971 | 4187 | 0.0016293 | 6.3158 | 6.3174 | -7.0724 | 613.7468 | 22988.3033 | -0.011523
194 |  | 17.2965 | 117.9856 | 4187 | 0.0016292 | 6.3174 | 6.3191 | -7.0724 | 613.8067 | 23106.2889 | -0.011522
195 |  | 17.2965 | 117.9741 | 4187 | 0.001629 | 6.3191 | 6.3207 | -7.0724 | 613.8667 | 23224.263 | -0.011521
196 |  | 17.2965 | 117.9626 | 4187 | 0.0016289 | 6.3207 | 6.3223 | -7.0724 | 613.9266 | 23342.2255 | -0.01152
197 |  | 17.2965 | 117.951 | 4187 | 0.0016287 | 6.3223 | 6.3239 | -7.0724 | 613.9866 | 23460.1766 | -0.011519
198 |  | 17.2965 | 117.9395 | 4187 | 0.0016285 | 6.3239 | 6.3256 | -7.0724 | 614.0465 | 23578.1161 | -0.011518
199 |  | 17.2965 | 117.928 | 4187 | 0.0016284 | 6.3256 | 6.3272 | -7.0724 | 614.1065 | 23696.0441 | -0.011517
200 |  | 17.2965 | 117.9165 | 4187 | 0.0016282 | 6.3272 | 6.3288 | -7.0724 | 614.1665 | 23813.9606 | -0.011515
201 |  | 17.2965 | 117.905 | 4187 | 0.0016281 | 6.3288 | 6.3305 | -7.0724 | 614.2265 | 23931.8655 | -0.011514
202 |  | 17.2965 | 117.8935 | 4187 | 0.0016279 | 6.3305 | 6.3321 | -7.0724 | 614.2865 | 24049.759 | -0.011513
203 |  | 17.2965 | 117.8819 | 4187 | 0.0016277 | 6.3321 | 6.3337 | -7.0724 | 614.3465 | 24167.6409 | -0.011512
204 |  | 17.2965 | 117.8704 | 4187 | 0.0016276 | 6.3337 | 6.3353 | -7.0724 | 614.4065 | 24285.5114 | -0.011511
205 |  | 17.2965 | 117.8589 | 4187 | 0.0016274 | 6.3353 | 6.337 | -7.0724 | 614.4665 | 24403.3703 | -0.01151
206 |  | 17.2965 | 117.8474 | 4187 | 0.0016273 | 6.337 | 6.3386 | -7.0724 | 614.5265 | 24521.2177 | -0.011509
207 |  | 17.2965 | 117.8359 | 4187 | 0.0016271 | 6.3386 | 6.3402 | -7.0724 | 614.5865 | 24639.0536 | -0.011508
208 |  | 17.2965 | 117.8244 | 4187 | 0.001627 | 6.3402 | 6.3418 | -7.0724 | 614.6465 | 24756.878 | -0.011506
209 |  | 17.2965 | 117.8129 | 4187 | 0.0016268 | 6.3418 | 6.3435 | -7.0724 | 614.7066 | 24874.6909 | -0.011505
210 |  | 17.2965 | 117.8014 | 4187 | 0.0016266 | 6.3435 | 6.3451 | -7.0724 | 614.7666 | 24992.4922 | -0.011504
211 |  | 17.2965 | 117.7899 | 4187 | 0.0016265 | 6.3451 | 6.3467 | -7.0724 | 614.8266 | 25110.2821 | -0.011503
212 |  | 17.2965 | 117.7784 | 4187 | 0.0016263 | 6.3467 | 6.3484 | -7.0724 | 614.8867 | 25228.0605 | -0.011502
213 |  | 17.2965 | 117.7669 | 4187 | 0.0016262 | 6.3484 | 6.35 | -7.0724 | 614.9467 | 25345.8274 | -0.011501
214 |  | 17.2965 | 117.7554 | 4187 | 0.001626 | 6.35 | 6.3516 | -7.0724 | 615.0068 | 25463.5827 | -0.0115
215 |  | 17.2965 | 117.7439 | 4187 | 0.0016258 | 6.3516 | 6.3532 | -7.0724 | 615.0669 | 25581.3266 | -0.011499
216 |  | 17.2965 | 117.7324 | 4187 | 0.0016257 | 6.3532 | 6.3549 | -7.0724 | 615.1269 | 25699.059 | -0.011497
217 |  | 17.2965 | 117.7209 | 4187 | 0.0016255 | 6.3549 | 6.3565 | -7.0724 | 615.187 | 25816.7799 | -0.011496
218 |  | 17.2965 | 117.7094 | 4187 | 0.0016254 | 6.3565 | 6.3581 | -7.0724 | 615.2471 | 25934.4892 | -0.011495
219 |  | 17.2965 | 117.6979 | 4187 | 0.0016252 | 6.3581 | 6.3597 | -7.0724 | 615.3072 | 26052.1871 | -0.011494
220 |  | 17.2965 | 117.6864 | 4187 | 0.001625 | 6.3597 | 6.3614 | -7.0724 | 615.3673 | 26169.8735 | -0.011493
221 |  | 17.2965 | 117.6749 | 4187 | 0.0016249 | 6.3614 | 6.363 | -7.0724 | 615.4274 | 26287.5484 | -0.011492
222 |  | 17.2965 | 117.6634 | 4187 | 0.0016247 | 6.363 | 6.3646 | -7.0724 | 615.4875 | 26405.2118 | -0.011491
223 |  | 17.2965 | 117.6519 | 4187 | 0.0016246 | 6.3646 | 6.3662 | -7.0724 | 615.5476 | 26522.8637 | -0.01149
224 |  | 17.2965 | 117.6404 | 4187 | 0.0016244 | 6.3662 | 6.3679 | -7.0724 | 615.6077 | 26640.5041 | -0.011488
225 |  | 17.2965 | 117.6289 | 4187 | 0.0016243 | 6.3679 | 6.3695 | -7.0724 | 615.6679 | 26758.1331 | -0.011487
226 |  | 17.2965 | 117.6174 | 4187 | 0.0016241 | 6.3695 | 6.3711 | -7.0724 | 615.728 | 26875.7505 | -0.011486
227 |  | 17.2965 | 117.606 | 4187 | 0.0016239 | 6.3711 | 6.3727 | -7.0724 | 615.7881 | 26993.3565 | -0.011485
228 |  | 17.2965 | 117.5945 | 4187 | 0.0016238 | 6.3727 | 6.3744 | -7.0724 | 615.8483 | 27110.951 | -0.011484
229 |  | 17.2965 | 117.583 | 4187 | 0.0016236 | 6.3744 | 6.376 | -7.0724 | 615.9084 | 27228.534 | -0.011483
230 |  | 17.2965 | 117.5715 | 4187 | 0.0016235 | 6.376 | 6.3776 | -7.0724 | 615.9686 | 27346.1055 | -0.011482
231 |  | 17.2965 | 117.56 | 4187 | 0.0016233 | 6.3776 | 6.3792 | -7.0724 | 616.0287 | 27463.6655 | -0.011481
232 |  | 17.2965 | 117.5485 | 4187 | 0.0016231 | 6.3792 | 6.3808 | -7.0724 | 616.0889 | 27581.214 | -0.011479
233 |  | 17.2965 | 117.5371 | 4187 | 0.001623 | 6.3808 | 6.3825 | -7.0724 | 616.1491 | 27698.7511 | -0.011478
234 |  | 17.2965 | 117.5256 | 4187 | 0.0016228 | 6.3825 | 6.3841 | -7.0724 | 616.2092 | 27816.2767 | -0.011477
235 |  | 17.2965 | 117.5141 | 4187 | 0.0016227 | 6.3841 | 6.3857 | -7.0724 | 616.2694 | 27933.7908 | -0.011476
236 |  | 17.2965 | 117.5026 | 4187 | 0.0016225 | 6.3857 | 6.3873 | -7.0724 | 616.3296 | 28051.2935 | -0.011475

## Cu203
|  |  | buis | verlies W/M | L /°C/sec
diam | wandikte |  | inhoud l/m |  | W/M
203.2 | 2 | 3.1416 | 31.1651 | 160.3261 | 4187
[8 empty] | J/sec/mtr | aantal mtr. | verlies
|  | buis | verlies W/M | L /°C/sec | verlies temp | begintemp | eindtemp | verlies | bij 1°C | totaal J/sec
|  | inhoud L |  | W/M | °C per M | °C | °C | per m°C | daling | aantal mtr
1 | 203.2 | 31.1651 | 160.3261 | 4187 | 0.0012287 | 6 | 6.0012 | -9.4309 | 813.8928 | 160.3261 | -0.011587
2 |  | 31.1651 | 160.3145 | 4187 | 0.0012286 | 6.0012 | 6.0025 | -9.4309 | 813.9516 | 320.6407 | -0.011587
3 |  | 31.1651 | 160.303 | 4187 | 0.0012285 | 6.0025 | 6.0037 | -9.4309 | 814.0104 | 480.9436 | -0.011586
4 |  | 31.1651 | 160.2914 | 4187 | 0.0012284 | 6.0037 | 6.0049 | -9.4309 | 814.0693 | 641.235 | -0.011585
5 |  | 31.1651 | 160.2798 | 4187 | 0.0012283 | 6.0049 | 6.0061 | -9.4309 | 814.1281 | 801.5148 | -0.011584
6 |  | 31.1651 | 160.2682 | 4187 | 0.0012282 | 6.0061 | 6.0074 | -9.4309 | 814.187 | 961.783 | -0.011583
7 |  | 31.1651 | 160.2566 | 4187 | 0.0012281 | 6.0074 | 6.0086 | -9.4309 | 814.2458 | 1122.0396 | -0.011582
8 |  | 31.1651 | 160.245 | 4187 | 0.001228 | 6.0086 | 6.0098 | -9.4309 | 814.3047 | 1282.2847 | -0.011582
9 |  | 31.1651 | 160.2335 | 4187 | 0.001228 | 6.0098 | 6.0111 | -9.4309 | 814.3635 | 1442.5181 | -0.011581
10 |  | 31.1651 | 160.2219 | 4187 | 0.0012279 | 6.0111 | 6.0123 | -9.4309 | 814.4224 | 1602.74 | -0.01158
11 |  | 31.1651 | 160.2103 | 4187 | 0.0012278 | 6.0123 | 6.0135 | -9.4309 | 814.4813 | 1762.9503 | -0.011579
12 |  | 31.1651 | 160.1987 | 4187 | 0.0012277 | 6.0135 | 6.0147 | -9.4309 | 814.5401 | 1923.149 | -0.011578
13 |  | 31.1651 | 160.1871 | 4187 | 0.0012276 | 6.0147 | 6.016 | -9.4309 | 814.599 | 2083.3361 | -0.011577
14 |  | 31.1651 | 160.1756 | 4187 | 0.0012275 | 6.016 | 6.0172 | -9.4309 | 814.6579 | 2243.5117 | -0.011577
15 |  | 31.1651 | 160.164 | 4187 | 0.0012274 | 6.0172 | 6.0184 | -9.4309 | 814.7168 | 2403.6757 | -0.011576
16 |  | 31.1651 | 160.1524 | 4187 | 0.0012273 | 6.0184 | 6.0196 | -9.4309 | 814.7756 | 2563.8281 | -0.011575
17 |  | 31.1651 | 160.1408 | 4187 | 0.0012272 | 6.0196 | 6.0209 | -9.4309 | 814.8345 | 2723.9689 | -0.011574
18 |  | 31.1651 | 160.1293 | 4187 | 0.0012272 | 6.0209 | 6.0221 | -9.4309 | 814.8934 | 2884.0982 | -0.011573
19 |  | 31.1651 | 160.1177 | 4187 | 0.0012271 | 6.0221 | 6.0233 | -9.4309 | 814.9523 | 3044.2159 | -0.011572
20 |  | 31.1651 | 160.1061 | 4187 | 0.001227 | 6.0233 | 6.0246 | -9.4309 | 815.0112 | 3204.322 | -0.011572
21 |  | 31.1651 | 160.0945 | 4187 | 0.0012269 | 6.0246 | 6.0258 | -9.4309 | 815.0701 | 3364.4165 | -0.011571
22 |  | 31.1651 | 160.083 | 4187 | 0.0012268 | 6.0258 | 6.027 | -9.4309 | 815.1291 | 3524.4995 | -0.01157
23 |  | 31.1651 | 160.0714 | 4187 | 0.0012267 | 6.027 | 6.0282 | -9.4309 | 815.188 | 3684.5709 | -0.011569
24 |  | 31.1651 | 160.0598 | 4187 | 0.0012266 | 6.0282 | 6.0295 | -9.4309 | 815.2469 | 3844.6307 | -0.011568
25 |  | 31.1651 | 160.0483 | 4187 | 0.0012265 | 6.0295 | 6.0307 | -9.4309 | 815.3058 | 4004.679 | -0.011567
26 |  | 31.1651 | 160.0367 | 4187 | 0.0012264 | 6.0307 | 6.0319 | -9.4309 | 815.3648 | 4164.7157 | -0.011567
27 |  | 31.1651 | 160.0251 | 4187 | 0.0012264 | 6.0319 | 6.0331 | -9.4309 | 815.4237 | 4324.7408 | -0.011566
28 |  | 31.1651 | 160.0136 | 4187 | 0.0012263 | 6.0331 | 6.0344 | -9.4309 | 815.4826 | 4484.7544 | -0.011565
29 |  | 31.1651 | 160.002 | 4187 | 0.0012262 | 6.0344 | 6.0356 | -9.4309 | 815.5416 | 4644.7564 | -0.011564
30 |  | 31.1651 | 159.9904 | 4187 | 0.0012261 | 6.0356 | 6.0368 | -9.4309 | 815.6005 | 4804.7468 | -0.011563
31 |  | 31.1651 | 159.9789 | 4187 | 0.001226 | 6.0368 | 6.038 | -9.4309 | 815.6595 | 4964.7257 | -0.011562
32 |  | 31.1651 | 159.9673 | 4187 | 0.0012259 | 6.038 | 6.0393 | -9.4309 | 815.7184 | 5124.693 | -0.011562
33 |  | 31.1651 | 159.9557 | 4187 | 0.0012258 | 6.0393 | 6.0405 | -9.4309 | 815.7774 | 5284.6487 | -0.011561
34 |  | 31.1651 | 159.9442 | 4187 | 0.0012257 | 6.0405 | 6.0417 | -9.4309 | 815.8363 | 5444.5929 | -0.01156
35 |  | 31.1651 | 159.9326 | 4187 | 0.0012256 | 6.0417 | 6.043 | -9.4309 | 815.8953 | 5604.5255 | -0.011559
36 |  | 31.1651 | 159.9211 | 4187 | 0.0012256 | 6.043 | 6.0442 | -9.4309 | 815.9543 | 5764.4466 | -0.011558
37 |  | 31.1651 | 159.9095 | 4187 | 0.0012255 | 6.0442 | 6.0454 | -9.4309 | 816.0133 | 5924.3561 | -0.011557
38 |  | 31.1651 | 159.898 | 4187 | 0.0012254 | 6.0454 | 6.0466 | -9.4309 | 816.0722 | 6084.2541 | -0.011557
39 |  | 31.1651 | 159.8864 | 4187 | 0.0012253 | 6.0466 | 6.0479 | -9.4309 | 816.1312 | 6244.1405 | -0.011556
40 |  | 31.1651 | 159.8748 | 4187 | 0.0012252 | 6.0479 | 6.0491 | -9.4309 | 816.1902 | 6404.0153 | -0.011555
41 |  | 31.1651 | 159.8633 | 4187 | 0.0012251 | 6.0491 | 6.0503 | -9.4309 | 816.2492 | 6563.8786 | -0.011554
42 |  | 31.1651 | 159.8517 | 4187 | 0.001225 | 6.0503 | 6.0515 | -9.4309 | 816.3082 | 6723.7303 | -0.011553
43 |  | 31.1651 | 159.8402 | 4187 | 0.0012249 | 6.0515 | 6.0528 | -9.4309 | 816.3672 | 6883.5705 | -0.011552
44 |  | 31.1651 | 159.8286 | 4187 | 0.0012249 | 6.0528 | 6.054 | -9.4309 | 816.4262 | 7043.3991 | -0.011552
45 |  | 31.1651 | 159.8171 | 4187 | 0.0012248 | 6.054 | 6.0552 | -9.4309 | 816.4852 | 7203.2162 | -0.011551
46 |  | 31.1651 | 159.8055 | 4187 | 0.0012247 | 6.0552 | 6.0564 | -9.4309 | 816.5442 | 7363.0217 | -0.01155
47 |  | 31.1651 | 159.794 | 4187 | 0.0012246 | 6.0564 | 6.0577 | -9.4309 | 816.6033 | 7522.8157 | -0.011549
48 |  | 31.1651 | 159.7824 | 4187 | 0.0012245 | 6.0577 | 6.0589 | -9.4309 | 816.6623 | 7682.5981 | -0.011548
49 |  | 31.1651 | 159.7709 | 4187 | 0.0012244 | 6.0589 | 6.0601 | -9.4309 | 816.7213 | 7842.369 | -0.011547
50 |  | 31.1651 | 159.7593 | 4187 | 0.0012243 | 6.0601 | 6.0613 | -9.4309 | 816.7803 | 8002.1283 | -0.011546
51 |  | 31.1651 | 159.7478 | 4187 | 0.0012242 | 6.0613 | 6.0625 | -9.4309 | 816.8394 | 8161.8761 | -0.011546
52 |  | 31.1651 | 159.7362 | 4187 | 0.0012241 | 6.0625 | 6.0638 | -9.4309 | 816.8984 | 8321.6124 | -0.011545
53 |  | 31.1651 | 159.7247 | 4187 | 0.0012241 | 6.0638 | 6.065 | -9.4309 | 816.9575 | 8481.3371 | -0.011544
54 |  | 31.1651 | 159.7131 | 4187 | 0.001224 | 6.065 | 6.0662 | -9.4309 | 817.0165 | 8641.0502 | -0.011543
55 |  | 31.1651 | 159.7016 | 4187 | 0.0012239 | 6.0662 | 6.0674 | -9.4309 | 817.0756 | 8800.7518 | -0.011542
56 |  | 31.1651 | 159.6901 | 4187 | 0.0012238 | 6.0674 | 6.0687 | -9.4309 | 817.1346 | 8960.4419 | -0.011541
57 |  | 31.1651 | 159.6785 | 4187 | 0.0012237 | 6.0687 | 6.0699 | -9.4309 | 817.1937 | 9120.1204 | -0.011541
58 |  | 31.1651 | 159.667 | 4187 | 0.0012236 | 6.0699 | 6.0711 | -9.4309 | 817.2528 | 9279.7874 | -0.01154
59 |  | 31.1651 | 159.6554 | 4187 | 0.0012235 | 6.0711 | 6.0723 | -9.4309 | 817.3118 | 9439.4428 | -0.011539
60 |  | 31.1651 | 159.6439 | 4187 | 0.0012234 | 6.0723 | 6.0736 | -9.4309 | 817.3709 | 9599.0867 | -0.011538
61 |  | 31.1651 | 159.6324 | 4187 | 0.0012233 | 6.0736 | 6.0748 | -9.4309 | 817.43 | 9758.7191 | -0.011537
62 |  | 31.1651 | 159.6208 | 4187 | 0.0012233 | 6.0748 | 6.076 | -9.4309 | 817.4891 | 9918.3399 | -0.011536
63 |  | 31.1651 | 159.6093 | 4187 | 0.0012232 | 6.076 | 6.0772 | -9.4309 | 817.5482 | 10077.9492 | -0.011536
64 |  | 31.1651 | 159.5978 | 4187 | 0.0012231 | 6.0772 | 6.0785 | -9.4309 | 817.6072 | 10237.547 | -0.011535
65 |  | 31.1651 | 159.5862 | 4187 | 0.001223 | 6.0785 | 6.0797 | -9.4309 | 817.6663 | 10397.1332 | -0.011534
66 |  | 31.1651 | 159.5747 | 4187 | 0.0012229 | 6.0797 | 6.0809 | -9.4309 | 817.7254 | 10556.7079 | -0.011533
67 |  | 31.1651 | 159.5632 | 4187 | 0.0012228 | 6.0809 | 6.0821 | -9.4309 | 817.7845 | 10716.271 | -0.011532
68 |  | 31.1651 | 159.5516 | 4187 | 0.0012227 | 6.0821 | 6.0833 | -9.4309 | 817.8437 | 10875.8226 | -0.011531
69 |  | 31.1651 | 159.5401 | 4187 | 0.0012226 | 6.0833 | 6.0846 | -9.4309 | 817.9028 | 11035.3627 | -0.011531
70 |  | 31.1651 | 159.5286 | 4187 | 0.0012226 | 6.0846 | 6.0858 | -9.4309 | 817.9619 | 11194.8913 | -0.01153
71 |  | 31.1651 | 159.517 | 4187 | 0.0012225 | 6.0858 | 6.087 | -9.4309 | 818.021 | 11354.4083 | -0.011529
72 |  | 31.1651 | 159.5055 | 4187 | 0.0012224 | 6.087 | 6.0882 | -9.4309 | 818.0801 | 11513.9138 | -0.011528
73 |  | 31.1651 | 159.494 | 4187 | 0.0012223 | 6.0882 | 6.0895 | -9.4309 | 818.1393 | 11673.4078 | -0.011527
74 |  | 31.1651 | 159.4824 | 4187 | 0.0012222 | 6.0895 | 6.0907 | -9.4309 | 818.1984 | 11832.8902 | -0.011526
75 |  | 31.1651 | 159.4709 | 4187 | 0.0012221 | 6.0907 | 6.0919 | -9.4309 | 818.2575 | 11992.3611 | -0.011526
76 |  | 31.1651 | 159.4594 | 4187 | 0.001222 | 6.0919 | 6.0931 | -9.4309 | 818.3167 | 12151.8205 | -0.011525
77 |  | 31.1651 | 159.4479 | 4187 | 0.0012219 | 6.0931 | 6.0943 | -9.4309 | 818.3758 | 12311.2684 | -0.011524
78 |  | 31.1651 | 159.4363 | 4187 | 0.0012218 | 6.0943 | 6.0956 | -9.4309 | 818.435 | 12470.7048 | -0.011523
79 |  | 31.1651 | 159.4248 | 4187 | 0.0012218 | 6.0956 | 6.0968 | -9.4309 | 818.4941 | 12630.1296 | -0.011522
80 |  | 31.1651 | 159.4133 | 4187 | 0.0012217 | 6.0968 | 6.098 | -9.4309 | 818.5533 | 12789.5429 | -0.011521
81 |  | 31.1651 | 159.4018 | 4187 | 0.0012216 | 6.098 | 6.0992 | -9.4309 | 818.6125 | 12948.9446 | -0.011521
82 |  | 31.1651 | 159.3903 | 4187 | 0.0012215 | 6.0992 | 6.1005 | -9.4309 | 818.6716 | 13108.3349 | -0.01152
83 |  | 31.1651 | 159.3787 | 4187 | 0.0012214 | 6.1005 | 6.1017 | -9.4309 | 818.7308 | 13267.7136 | -0.011519
84 |  | 31.1651 | 159.3672 | 4187 | 0.0012213 | 6.1017 | 6.1029 | -9.4309 | 818.79 | 13427.0809 | -0.011518
85 |  | 31.1651 | 159.3557 | 4187 | 0.0012212 | 6.1029 | 6.1041 | -9.4309 | 818.8492 | 13586.4366 | -0.011517
86 |  | 31.1651 | 159.3442 | 4187 | 0.0012211 | 6.1041 | 6.1053 | -9.4309 | 818.9084 | 13745.7807 | -0.011516
87 |  | 31.1651 | 159.3327 | 4187 | 0.001221 | 6.1053 | 6.1066 | -9.4309 | 818.9675 | 13905.1134 | -0.011516
88 |  | 31.1651 | 159.3211 | 4187 | 0.001221 | 6.1066 | 6.1078 | -9.4309 | 819.0267 | 14064.4345 | -0.011515
89 |  | 31.1651 | 159.3096 | 4187 | 0.0012209 | 6.1078 | 6.109 | -9.4309 | 819.0859 | 14223.7442 | -0.011514
90 |  | 31.1651 | 159.2981 | 4187 | 0.0012208 | 6.109 | 6.1102 | -9.4309 | 819.1451 | 14383.0423 | -0.011513
91 |  | 31.1651 | 159.2866 | 4187 | 0.0012207 | 6.1102 | 6.1114 | -9.4309 | 819.2043 | 14542.3289 | -0.011512
92 |  | 31.1651 | 159.2751 | 4187 | 0.0012206 | 6.1114 | 6.1127 | -9.4309 | 819.2636 | 14701.604 | -0.011511
93 |  | 31.1651 | 159.2636 | 4187 | 0.0012205 | 6.1127 | 6.1139 | -9.4309 | 819.3228 | 14860.8676 | -0.011511
94 |  | 31.1651 | 159.2521 | 4187 | 0.0012204 | 6.1139 | 6.1151 | -9.4309 | 819.382 | 15020.1197 | -0.01151
95 |  | 31.1651 | 159.2406 | 4187 | 0.0012203 | 6.1151 | 6.1163 | -9.4309 | 819.4412 | 15179.3602 | -0.011509
96 |  | 31.1651 | 159.2291 | 4187 | 0.0012203 | 6.1163 | 6.1175 | -9.4309 | 819.5004 | 15338.5893 | -0.011508
97 |  | 31.1651 | 159.2175 | 4187 | 0.0012202 | 6.1175 | 6.1188 | -9.4309 | 819.5597 | 15497.8068 | -0.011507
98 |  | 31.1651 | 159.206 | 4187 | 0.0012201 | 6.1188 | 6.12 | -9.4309 | 819.6189 | 15657.0129 | -0.011507
99 |  | 31.1651 | 159.1945 | 4187 | 0.00122 | 6.12 | 6.1212 | -9.4309 | 819.6782 | 15816.2074 | -0.011506
100 |  | 31.1651 | 159.183 | 4187 | 0.0012199 | 6.1212 | 6.1224 | -9.4309 | 819.7374 | 15975.3904 | -0.011505
101 |  | 31.1651 | 159.1715 | 4187 | 0.0012198 | 6.1224 | 6.1236 | -9.4309 | 819.7967 | 16134.5619 | -0.011504
102 |  | 31.1651 | 159.16 | 4187 | 0.0012197 | 6.1236 | 6.1249 | -9.4309 | 819.8559 | 16293.722 | -0.011503
103 |  | 31.1651 | 159.1485 | 4187 | 0.0012196 | 6.1249 | 6.1261 | -9.4309 | 819.9152 | 16452.8705 | -0.011502
104 |  | 31.1651 | 159.137 | 4187 | 0.0012196 | 6.1261 | 6.1273 | -9.4309 | 819.9744 | 16612.0075 | -0.011502
105 |  | 31.1651 | 159.1255 | 4187 | 0.0012195 | 6.1273 | 6.1285 | -9.4309 | 820.0337 | 16771.133 | -0.011501
106 |  | 31.1651 | 159.114 | 4187 | 0.0012194 | 6.1285 | 6.1297 | -9.4309 | 820.093 | 16930.247 | -0.0115
107 |  | 31.1651 | 159.1025 | 4187 | 0.0012193 | 6.1297 | 6.131 | -9.4309 | 820.1522 | 17089.3495 | -0.011499
108 |  | 31.1651 | 159.091 | 4187 | 0.0012192 | 6.131 | 6.1322 | -9.4309 | 820.2115 | 17248.4405 | -0.011498
109 |  | 31.1651 | 159.0795 | 4187 | 0.0012191 | 6.1322 | 6.1334 | -9.4309 | 820.2708 | 17407.52 | -0.011497
110 |  | 31.1651 | 159.068 | 4187 | 0.001219 | 6.1334 | 6.1346 | -9.4309 | 820.3301 | 17566.5881 | -0.011497
111 |  | 31.1651 | 159.0565 | 4187 | 0.0012189 | 6.1346 | 6.1358 | -9.4309 | 820.3894 | 17725.6446 | -0.011496
112 |  | 31.1651 | 159.045 | 4187 | 0.0012188 | 6.1358 | 6.1371 | -9.4309 | 820.4487 | 17884.6896 | -0.011495
113 |  | 31.1651 | 159.0335 | 4187 | 0.0012188 | 6.1371 | 6.1383 | -9.4309 | 820.508 | 18043.7231 | -0.011494
114 |  | 31.1651 | 159.022 | 4187 | 0.0012187 | 6.1383 | 6.1395 | -9.4309 | 820.5673 | 18202.7452 | -0.011493
115 |  | 31.1651 | 159.0105 | 4187 | 0.0012186 | 6.1395 | 6.1407 | -9.4309 | 820.6266 | 18361.7557 | -0.011492
116 |  | 31.1651 | 158.999 | 4187 | 0.0012185 | 6.1407 | 6.1419 | -9.4309 | 820.6859 | 18520.7547 | -0.011492
117 |  | 31.1651 | 158.9876 | 4187 | 0.0012184 | 6.1419 | 6.1432 | -9.4309 | 820.7452 | 18679.7423 | -0.011491
118 |  | 31.1651 | 158.9761 | 4187 | 0.0012183 | 6.1432 | 6.1444 | -9.4309 | 820.8046 | 18838.7184 | -0.01149
119 |  | 31.1651 | 158.9646 | 4187 | 0.0012182 | 6.1444 | 6.1456 | -9.4309 | 820.8639 | 18997.6829 | -0.011489
120 |  | 31.1651 | 158.9531 | 4187 | 0.0012181 | 6.1456 | 6.1468 | -9.4309 | 820.9232 | 19156.636 | -0.011488
121 |  | 31.1651 | 158.9416 | 4187 | 0.0012181 | 6.1468 | 6.148 | -9.4309 | 820.9826 | 19315.5776 | -0.011487
122 |  | 31.1651 | 158.9301 | 4187 | 0.001218 | 6.148 | 6.1492 | -9.4309 | 821.0419 | 19474.5077 | -0.011487
123 |  | 31.1651 | 158.9186 | 4187 | 0.0012179 | 6.1492 | 6.1505 | -9.4309 | 821.1012 | 19633.4264 | -0.011486
124 |  | 31.1651 | 158.9071 | 4187 | 0.0012178 | 6.1505 | 6.1517 | -9.4309 | 821.1606 | 19792.3335 | -0.011485
125 |  | 31.1651 | 158.8957 | 4187 | 0.0012177 | 6.1517 | 6.1529 | -9.4309 | 821.2199 | 19951.2292 | -0.011484
126 |  | 31.1651 | 158.8842 | 4187 | 0.0012176 | 6.1529 | 6.1541 | -9.4309 | 821.2793 | 20110.1133 | -0.011483
127 |  | 31.1651 | 158.8727 | 4187 | 0.0012175 | 6.1541 | 6.1553 | -9.4309 | 821.3387 | 20268.986 | -0.011482
128 |  | 31.1651 | 158.8612 | 4187 | 0.0012174 | 6.1553 | 6.1565 | -9.4309 | 821.398 | 20427.8472 | -0.011482
129 |  | 31.1651 | 158.8497 | 4187 | 0.0012173 | 6.1565 | 6.1578 | -9.4309 | 821.4574 | 20586.697 | -0.011481
130 |  | 31.1651 | 158.8382 | 4187 | 0.0012173 | 6.1578 | 6.159 | -9.4309 | 821.5168 | 20745.5352 | -0.01148
131 |  | 31.1651 | 158.8268 | 4187 | 0.0012172 | 6.159 | 6.1602 | -9.4309 | 821.5762 | 20904.362 | -0.011479
132 |  | 31.1651 | 158.8153 | 4187 | 0.0012171 | 6.1602 | 6.1614 | -9.4309 | 821.6355 | 21063.1772 | -0.011478
133 |  | 31.1651 | 158.8038 | 4187 | 0.001217 | 6.1614 | 6.1626 | -9.4309 | 821.6949 | 21221.981 | -0.011477
134 |  | 31.1651 | 158.7923 | 4187 | 0.0012169 | 6.1626 | 6.1639 | -9.4309 | 821.7543 | 21380.7734 | -0.011477
135 |  | 31.1651 | 158.7809 | 4187 | 0.0012168 | 6.1639 | 6.1651 | -9.4309 | 821.8137 | 21539.5542 | -0.011476
136 |  | 31.1651 | 158.7694 | 4187 | 0.0012167 | 6.1651 | 6.1663 | -9.4309 | 821.8731 | 21698.3236 | -0.011475
137 |  | 31.1651 | 158.7579 | 4187 | 0.0012166 | 6.1663 | 6.1675 | -9.4309 | 821.9325 | 21857.0815 | -0.011474
138 |  | 31.1651 | 158.7464 | 4187 | 0.0012166 | 6.1675 | 6.1687 | -9.4309 | 821.9919 | 22015.8279 | -0.011473
139 |  | 31.1651 | 158.735 | 4187 | 0.0012165 | 6.1687 | 6.1699 | -9.4309 | 822.0513 | 22174.5629 | -0.011472
140 |  | 31.1651 | 158.7235 | 4187 | 0.0012164 | 6.1699 | 6.1712 | -9.4309 | 822.1108 | 22333.2864 | -0.011472
141 |  | 31.1651 | 158.712 | 4187 | 0.0012163 | 6.1712 | 6.1724 | -9.4309 | 822.1702 | 22491.9984 | -0.011471
142 |  | 31.1651 | 158.7005 | 4187 | 0.0012162 | 6.1724 | 6.1736 | -9.4309 | 822.2296 | 22650.6989 | -0.01147
143 |  | 31.1651 | 158.6891 | 4187 | 0.0012161 | 6.1736 | 6.1748 | -9.4309 | 822.289 | 22809.388 | -0.011469
144 |  | 31.1651 | 158.6776 | 4187 | 0.001216 | 6.1748 | 6.176 | -9.4309 | 822.3485 | 22968.0656 | -0.011468
145 |  | 31.1651 | 158.6661 | 4187 | 0.0012159 | 6.176 | 6.1772 | -9.4309 | 822.4079 | 23126.7317 | -0.011467
146 |  | 31.1651 | 158.6547 | 4187 | 0.0012159 | 6.1772 | 6.1784 | -9.4309 | 822.4674 | 23285.3864 | -0.011467
147 |  | 31.1651 | 158.6432 | 4187 | 0.0012158 | 6.1784 | 6.1797 | -9.4309 | 822.5268 | 23444.0296 | -0.011466
148 |  | 31.1651 | 158.6317 | 4187 | 0.0012157 | 6.1797 | 6.1809 | -9.4309 | 822.5863 | 23602.6613 | -0.011465
149 |  | 31.1651 | 158.6203 | 4187 | 0.0012156 | 6.1809 | 6.1821 | -9.4309 | 822.6457 | 23761.2816 | -0.011464
150 |  | 31.1651 | 158.6088 | 4187 | 0.0012155 | 6.1821 | 6.1833 | -9.4309 | 822.7052 | 23919.8904 | -0.011463
151 |  | 31.1651 | 158.5973 | 4187 | 0.0012154 | 6.1833 | 6.1845 | -9.4309 | 822.7646 | 24078.4877 | -0.011463
152 |  | 31.1651 | 158.5859 | 4187 | 0.0012153 | 6.1845 | 6.1857 | -9.4309 | 822.8241 | 24237.0736 | -0.011462
153 |  | 31.1651 | 158.5744 | 4187 | 0.0012152 | 6.1857 | 6.187 | -9.4309 | 822.8836 | 24395.648 | -0.011461
154 |  | 31.1651 | 158.563 | 4187 | 0.0012152 | 6.187 | 6.1882 | -9.4309 | 822.9431 | 24554.2109 | -0.01146
155 |  | 31.1651 | 158.5515 | 4187 | 0.0012151 | 6.1882 | 6.1894 | -9.4309 | 823.0025 | 24712.7624 | -0.011459
156 |  | 31.1651 | 158.54 | 4187 | 0.001215 | 6.1894 | 6.1906 | -9.4309 | 823.062 | 24871.3025 | -0.011458
157 |  | 31.1651 | 158.5286 | 4187 | 0.0012149 | 6.1906 | 6.1918 | -9.4309 | 823.1215 | 25029.8311 | -0.011458
158 |  | 31.1651 | 158.5171 | 4187 | 0.0012148 | 6.1918 | 6.193 | -9.4309 | 823.181 | 25188.3482 | -0.011457
159 |  | 31.1651 | 158.5057 | 4187 | 0.0012147 | 6.193 | 6.1942 | -9.4309 | 823.2405 | 25346.8538 | -0.011456
160 |  | 31.1651 | 158.4942 | 4187 | 0.0012146 | 6.1942 | 6.1955 | -9.4309 | 823.3 | 25505.348 | -0.011455
161 |  | 31.1651 | 158.4828 | 4187 | 0.0012145 | 6.1955 | 6.1967 | -9.4309 | 823.3595 | 25663.8308 | -0.011454
162 |  | 31.1651 | 158.4713 | 4187 | 0.0012144 | 6.1967 | 6.1979 | -9.4309 | 823.419 | 25822.3021 | -0.011453
163 |  | 31.1651 | 158.4598 | 4187 | 0.0012144 | 6.1979 | 6.1991 | -9.4309 | 823.4785 | 25980.7619 | -0.011453
164 |  | 31.1651 | 158.4484 | 4187 | 0.0012143 | 6.1991 | 6.2003 | -9.4309 | 823.5381 | 26139.2103 | -0.011452
165 |  | 31.1651 | 158.4369 | 4187 | 0.0012142 | 6.2003 | 6.2015 | -9.4309 | 823.5976 | 26297.6473 | -0.011451
166 |  | 31.1651 | 158.4255 | 4187 | 0.0012141 | 6.2015 | 6.2027 | -9.4309 | 823.6571 | 26456.0727 | -0.01145
167 |  | 31.1651 | 158.414 | 4187 | 0.001214 | 6.2027 | 6.204 | -9.4309 | 823.7167 | 26614.4868 | -0.011449
168 |  | 31.1651 | 158.4026 | 4187 | 0.0012139 | 6.204 | 6.2052 | -9.4309 | 823.7762 | 26772.8894 | -0.011448
169 |  | 31.1651 | 158.3911 | 4187 | 0.0012138 | 6.2052 | 6.2064 | -9.4309 | 823.8357 | 26931.2805 | -0.011448
170 |  | 31.1651 | 158.3797 | 4187 | 0.0012137 | 6.2064 | 6.2076 | -9.4309 | 823.8953 | 27089.6602 | -0.011447
171 |  | 31.1651 | 158.3682 | 4187 | 0.0012137 | 6.2076 | 6.2088 | -9.4309 | 823.9548 | 27248.0284 | -0.011446
172 |  | 31.1651 | 158.3568 | 4187 | 0.0012136 | 6.2088 | 6.21 | -9.4309 | 824.0144 | 27406.3852 | -0.011445
173 |  | 31.1651 | 158.3454 | 4187 | 0.0012135 | 6.21 | 6.2112 | -9.4309 | 824.0739 | 27564.7306 | -0.011444
174 |  | 31.1651 | 158.3339 | 4187 | 0.0012134 | 6.2112 | 6.2125 | -9.4309 | 824.1335 | 27723.0645 | -0.011443
175 |  | 31.1651 | 158.3225 | 4187 | 0.0012133 | 6.2125 | 6.2137 | -9.4309 | 824.1931 | 27881.387 | -0.011443
176 |  | 31.1651 | 158.311 | 4187 | 0.0012132 | 6.2137 | 6.2149 | -9.4309 | 824.2527 | 28039.698 | -0.011442
177 |  | 31.1651 | 158.2996 | 4187 | 0.0012131 | 6.2149 | 6.2161 | -9.4309 | 824.3122 | 28197.9976 | -0.011441
178 |  | 31.1651 | 158.2881 | 4187 | 0.001213 | 6.2161 | 6.2173 | -9.4309 | 824.3718 | 28356.2857 | -0.01144
179 |  | 31.1651 | 158.2767 | 4187 | 0.001213 | 6.2173 | 6.2185 | -9.4309 | 824.4314 | 28514.5624 | -0.011439
180 |  | 31.1651 | 158.2653 | 4187 | 0.0012129 | 6.2185 | 6.2197 | -9.4309 | 824.491 | 28672.8277 | -0.011439
181 |  | 31.1651 | 158.2538 | 4187 | 0.0012128 | 6.2197 | 6.2209 | -9.4309 | 824.5506 | 28831.0815 | -0.011438
182 |  | 31.1651 | 158.2424 | 4187 | 0.0012127 | 6.2209 | 6.2222 | -9.4309 | 824.6102 | 28989.3239 | -0.011437
183 |  | 31.1651 | 158.2309 | 4187 | 0.0012126 | 6.2222 | 6.2234 | -9.4309 | 824.6698 | 29147.5548 | -0.011436
184 |  | 31.1651 | 158.2195 | 4187 | 0.0012125 | 6.2234 | 6.2246 | -9.4309 | 824.7294 | 29305.7744 | -0.011435
185 |  | 31.1651 | 158.2081 | 4187 | 0.0012124 | 6.2246 | 6.2258 | -9.4309 | 824.789 | 29463.9824 | -0.011434
186 |  | 31.1651 | 158.1966 | 4187 | 0.0012123 | 6.2258 | 6.227 | -9.4309 | 824.8486 | 29622.1791 | -0.011434
187 |  | 31.1651 | 158.1852 | 4187 | 0.0012123 | 6.227 | 6.2282 | -9.4309 | 824.9082 | 29780.3643 | -0.011433
188 |  | 31.1651 | 158.1738 | 4187 | 0.0012122 | 6.2282 | 6.2294 | -9.4309 | 824.9679 | 29938.5381 | -0.011432
189 |  | 31.1651 | 158.1623 | 4187 | 0.0012121 | 6.2294 | 6.2306 | -9.4309 | 825.0275 | 30096.7004 | -0.011431
190 |  | 31.1651 | 158.1509 | 4187 | 0.001212 | 6.2306 | 6.2319 | -9.4309 | 825.0871 | 30254.8513 | -0.01143
191 |  | 31.1651 | 158.1395 | 4187 | 0.0012119 | 6.2319 | 6.2331 | -9.4309 | 825.1468 | 30412.9908 | -0.011429
192 |  | 31.1651 | 158.1281 | 4187 | 0.0012118 | 6.2331 | 6.2343 | -9.4309 | 825.2064 | 30571.1189 | -0.011429
193 |  | 31.1651 | 158.1166 | 4187 | 0.0012117 | 6.2343 | 6.2355 | -9.4309 | 825.266 | 30729.2355 | -0.011428
194 |  | 31.1651 | 158.1052 | 4187 | 0.0012116 | 6.2355 | 6.2367 | -9.4309 | 825.3257 | 30887.3407 | -0.011427
195 |  | 31.1651 | 158.0938 | 4187 | 0.0012116 | 6.2367 | 6.2379 | -9.4309 | 825.3853 | 31045.4345 | -0.011426
196 |  | 31.1651 | 158.0823 | 4187 | 0.0012115 | 6.2379 | 6.2391 | -9.4309 | 825.445 | 31203.5168 | -0.011425
197 |  | 31.1651 | 158.0709 | 4187 | 0.0012114 | 6.2391 | 6.2403 | -9.4309 | 825.5047 | 31361.5877 | -0.011424
198 |  | 31.1651 | 158.0595 | 4187 | 0.0012113 | 6.2403 | 6.2416 | -9.4309 | 825.5643 | 31519.6472 | -0.011424
199 |  | 31.1651 | 158.0481 | 4187 | 0.0012112 | 6.2416 | 6.2428 | -9.4309 | 825.624 | 31677.6953 | -0.011423
200 |  | 31.1651 | 158.0366 | 4187 | 0.0012111 | 6.2428 | 6.244 | -9.4309 | 825.6837 | 31835.7319 | -0.011422
201 |  | 31.1651 | 158.0252 | 4187 | 0.001211 | 6.244 | 6.2452 | -9.4309 | 825.7434 | 31993.7572 | -0.011421
202 |  | 31.1651 | 158.0138 | 4187 | 0.0012109 | 6.2452 | 6.2464 | -9.4309 | 825.803 | 32151.771 | -0.01142
203 |  | 31.1651 | 158.0024 | 4187 | 0.0012109 | 6.2464 | 6.2476 | -9.4309 | 825.8627 | 32309.7733 | -0.01142
204 |  | 31.1651 | 157.991 | 4187 | 0.0012108 | 6.2476 | 6.2488 | -9.4309 | 825.9224 | 32467.7643 | -0.011419
205 |  | 31.1651 | 157.9795 | 4187 | 0.0012107 | 6.2488 | 6.25 | -9.4309 | 825.9821 | 32625.7439 | -0.011418
206 |  | 31.1651 | 157.9681 | 4187 | 0.0012106 | 6.25 | 6.2512 | -9.4309 | 826.0418 | 32783.712 | -0.011417
207 |  | 31.1651 | 157.9567 | 4187 | 0.0012105 | 6.2512 | 6.2524 | -9.4309 | 826.1015 | 32941.6687 | -0.011416
208 |  | 31.1651 | 157.9453 | 4187 | 0.0012104 | 6.2524 | 6.2537 | -9.4309 | 826.1612 | 33099.614 | -0.011415
209 |  | 31.1651 | 157.9339 | 4187 | 0.0012103 | 6.2537 | 6.2549 | -9.4309 | 826.221 | 33257.5479 | -0.011415
210 |  | 31.1651 | 157.9225 | 4187 | 0.0012102 | 6.2549 | 6.2561 | -9.4309 | 826.2807 | 33415.4703 | -0.011414
211 |  | 31.1651 | 157.9111 | 4187 | 0.0012102 | 6.2561 | 6.2573 | -9.4309 | 826.3404 | 33573.3814 | -0.011413
212 |  | 31.1651 | 157.8996 | 4187 | 0.0012101 | 6.2573 | 6.2585 | -9.4309 | 826.4001 | 33731.281 | -0.011412
213 |  | 31.1651 | 157.8882 | 4187 | 0.00121 | 6.2585 | 6.2597 | -9.4309 | 826.4599 | 33889.1693 | -0.011411
214 |  | 31.1651 | 157.8768 | 4187 | 0.0012099 | 6.2597 | 6.2609 | -9.4309 | 826.5196 | 34047.0461 | -0.01141
215 |  | 31.1651 | 157.8654 | 4187 | 0.0012098 | 6.2609 | 6.2621 | -9.4309 | 826.5793 | 34204.9115 | -0.01141
216 |  | 31.1651 | 157.854 | 4187 | 0.0012097 | 6.2621 | 6.2633 | -9.4309 | 826.6391 | 34362.7655 | -0.011409
217 |  | 31.1651 | 157.8426 | 4187 | 0.0012096 | 6.2633 | 6.2645 | -9.4309 | 826.6988 | 34520.6081 | -0.011408
218 |  | 31.1651 | 157.8312 | 4187 | 0.0012095 | 6.2645 | 6.2658 | -9.4309 | 826.7586 | 34678.4392 | -0.011407
219 |  | 31.1651 | 157.8198 | 4187 | 0.0012095 | 6.2658 | 6.267 | -9.4309 | 826.8183 | 34836.259 | -0.011406
220 |  | 31.1651 | 157.8084 | 4187 | 0.0012094 | 6.267 | 6.2682 | -9.4309 | 826.8781 | 34994.0674 | -0.011405
221 |  | 31.1651 | 157.797 | 4187 | 0.0012093 | 6.2682 | 6.2694 | -9.4309 | 826.9379 | 35151.8643 | -0.011405
222 |  | 31.1651 | 157.7856 | 4187 | 0.0012092 | 6.2694 | 6.2706 | -9.4309 | 826.9976 | 35309.6499 | -0.011404
223 |  | 31.1651 | 157.7742 | 4187 | 0.0012091 | 6.2706 | 6.2718 | -9.4309 | 827.0574 | 35467.424 | -0.011403
224 |  | 31.1651 | 157.7627 | 4187 | 0.001209 | 6.2718 | 6.273 | -9.4309 | 827.1172 | 35625.1868 | -0.011402
225 |  | 31.1651 | 157.7513 | 4187 | 0.0012089 | 6.273 | 6.2742 | -9.4309 | 827.177 | 35782.9381 | -0.011401
226 |  | 31.1651 | 157.7399 | 4187 | 0.0012088 | 6.2742 | 6.2754 | -9.4309 | 827.2368 | 35940.6781 | -0.011401
227 |  | 31.1651 | 157.7285 | 4187 | 0.0012088 | 6.2754 | 6.2766 | -9.4309 | 827.2966 | 36098.4066 | -0.0114
228 |  | 31.1651 | 157.7171 | 4187 | 0.0012087 | 6.2766 | 6.2778 | -9.4309 | 827.3564 | 36256.1238 | -0.011399
229 |  | 31.1651 | 157.7057 | 4187 | 0.0012086 | 6.2778 | 6.2791 | -9.4309 | 827.4162 | 36413.8295 | -0.011398
230 |  | 31.1651 | 157.6943 | 4187 | 0.0012085 | 6.2791 | 6.2803 | -9.4309 | 827.476 | 36571.5239 | -0.011397
231 |  | 31.1651 | 157.683 | 4187 | 0.0012084 | 6.2803 | 6.2815 | -9.4309 | 827.5358 | 36729.2068 | -0.011396
232 |  | 31.1651 | 157.6716 | 4187 | 0.0012083 | 6.2815 | 6.2827 | -9.4309 | 827.5956 | 36886.8784 | -0.011396
233 |  | 31.1651 | 157.6602 | 4187 | 0.0012082 | 6.2827 | 6.2839 | -9.4309 | 827.6554 | 37044.5385 | -0.011395
234 |  | 31.1651 | 157.6488 | 4187 | 0.0012081 | 6.2839 | 6.2851 | -9.4309 | 827.7152 | 37202.1873 | -0.011394
235 |  | 31.1651 | 157.6374 | 4187 | 0.0012081 | 6.2851 | 6.2863 | -9.4309 | 827.775 | 37359.8247 | -0.011393
236 |  | 31.1651 | 157.626 | 4187 | 0.001208 | 6.2863 | 6.2875 | -9.4309 | 827.8349 | 37517.4506 | -0.011392