## Calculation
Sagging of the pipe (f) between 2 pipe clamps = (1/"?") x L (at 20⁰C) |  |  |  |  | Material | E modulus [N/mm²]* | Specific Gravity [kg/dm³]*
L = Support Interval for horizontal pipes |  |  |  |  | aquatherm PP-R (80) pipe | 800 | 0.9
[5 empty] | aquatherm PP-R (80) MF pipe | 1200 | 0.995
f=(1/"?") x L = (5/384) x (q x L4)/(E x I) |  | ("Forget-Me-Nots") |  |  | PE-100 | 900 | 0.958
L = ³√((384/(5x"?") x (E x I)/q) |  |  |  |  | PE-80 | 850 | 0.954
[5 empty] | PP-H (100) | 1200 | 0.915
I=π/64 x (D4 - d4) [mm4] |  | (Moment of Inertia) |  |  | PVDF | 2400 | 1.78
E = Modulus of Elasticity of pipe material [N/mm²] |  |  |  |  | PB | 450 | 0.94
[5 empty] | PVC-U | 2500 | 1.38
q (weight of filled pipe) = (π/4x((D/100)²-(d/100)²)x9.81xρ1)/100 + ((π/4x(d/100)²)x9.81xρ2)/100 [N/mm] |  |  |  |  | PVC-C | 2500 | 1.55
D = Outer pipe diameter [mm] |  |  |  |  | ABS | 2200 | 1.03
d = Internal pipe diameter [mm]
ρ1 = specific gravity pipe [kg/dm³] |  |  |  |  | Carbon Steel | 210000 | 7.8
ρ2 = specific gravity medium [kg/dm³] |  |  |  |  | Copper | 17000 | 8.94
* at 20⁰C (varies with temperature)
Pipe type | aquatherm PP-R (80) MF pipe |  | Only the green cells can be edited
E modulus [N/mm²] | 1200 |  | Sagging of the pipe (f) between 2 pipe clamps =< (1/"?") x L
ρ pipe [kg/dm³] | 0.995 |  |  | "?" = | 580
ρ medium [kg/dm³] | 0 |  | L = Support Interval
D [mm] | Wall thickness [mm] | d [mm] | q [N/mm] | Weight [kg/m] | I [mm4] | Support Interval L [cm] | Sagging [mm]
SDR7.4
160 | 21.9 | 116.2 | 0.092743 | 9.4539 | 23220498.6486 | 341.3779 | 5.8858
SDR9
32 | 3.6 | 24.8 | 0.0031352 | 0.31959 | 32903.3626 | 118.5852 | 2.0446
SDR11
32 | 2.9 | 26.2 | 0.0025878 | 0.26379 | 28341.8843 | 120.2828 | 2.0738
SDR17.6
630 | 35.7 | 558.6 | 0.6506 | 66.3204 | 2953313952.9546 | 896.8147 | 15.4623
Vertical: +20%
aquatherm green pipe SDR11 S, aquatherm lilac pipe SDR11 S:
aquatherm green pipe SDR 9 MF RP / aquatherm green pipe SDR 9 MF RP U.V:
aquatherm green pipe SDR 7.4 MF / aquatherm green pipe SDR7.4 MF U.V:
aquatherm blue pipe SDR11 MF / aquatherm blue pipe SDR11 MF OT or UV:
aquatherm blue pipe SDR17.6 MF:
Note on C17: Select pipe type
Note on G19: Select "?"
Note on C20: Water ~ 1 kg/dm³ Air ~ 0 kg/dm³
Note on B22: Select pipe diameter from pull down list.
Note on H22: Support Interval [cm] for horizontal pipes at 20⁰C.
Note on I22: Sagging [mm] of pipe between 2 horizontal pipe clamps at 20⁰C.

## Dimensions
| SDR7.4 | SDR9 | SDR11 | SDR17.6
OD | Wall Thickness | Wall Thickness | Wall Thickness | Wall Thickness
20 | 2.8 |  | 1.9
25 | 3.5 |  | 2.3
32 | 4.4 | 3.6 | 2.9
40 | 5.5 | 4.5 | 3.7
50 | 6.9 | 5.6 | 4.6
63 | 8.6 | 7.1 | 5.8
75 | 10.3 | 8.4 | 6.8
90 | 12.3 | 10.1 | 8.2
110 | 15.1 | 12.3 | 10
125 | 17.1 | 14 | 11.4
160 | 21.9 | 17.9 | 14.6 | 9.1
200 | 27.4 | 22.4 | 18.2 | 11.4
250 | 34.2 | 27.9 | 22.7 | 14.2
315 | 42.6 | 35.2 | 28.6 | 17.9
355 | 48 | 39.7 | 32.2 | 20.1
400 |  |  | 36.3 | 22.7
450 |  |  | 40.9 | 25.5
500 |  |  |  | 28.4
560 |  |  |  | 31.7
630 |  |  |  | 35.7